## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-06 | Friday
|  | Date (day): | 2019-12-06 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11539.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14072 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-05 | 2019-12-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 133 | 189 | 150 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 80 | 107 | 105 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 377 | 344 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 334 | 327 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 360 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 37 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 270 | 236 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 10 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 55 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 51 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 174 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 88 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1945 | 2211 | 3670 | 4214 | 598 | 1014
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.86 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 82 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 203 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 144 | 144 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 10 | 5 | 10
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 98 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 589.26 | 911 | 1472 | 1632 | 216 | 278
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 30 | 100 | 100
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 199 | 200 | 200
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 140 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 315 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 30 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 64 | 64 | 45 | 45 | 131 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Maintenance at S/S.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 90 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 110 | 103 | 131
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 2 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1222 | 1326 | 1704 | 2132 | 275 | 179
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 160 | 160 | 161 | 41 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 40 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 200 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 176.2 | 422 | 493.6 | 593 | 41 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 62 | 62
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 49 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 66 | 55 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 79 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 27 | 36 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 265 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 360 | 366 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1067 | 1181 | 1368 | 1368 | 0 | 492
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 446 | 733 | 175 | 446
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 185 | 300 | 300 |  | 132 | ST under S/D
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 20 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 54 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 696 | 1029 | 615 | 1556 | 0 | 132
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 25 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 60 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 126 | 195 | 371 | 441 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 50 | 71 | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 187 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 202 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 395 | 381 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 3 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 97 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 887 | 1014 | 1525 | 1789 | 320 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 290 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 204.5 | 403 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6912.96 | 8692 | 11539.6 | 14072 | 1450 | 2280
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6539.1575 | 8222 | 10915.6225 | 13311.0888
A. |  | 2019-12-05 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8692 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5196 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8692 | MW
3 | Day peak Generation : |  |  | 6912.96 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8222 | MW
4 | Evening peak Generation : |  |  | 8692 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 163.7423 | MKWHr | By Solar | 0.19879 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 135.1423 | MKWHr |  | By Oil: | 8.9178 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 5.798 | MKWHr |  | By Hydro: | 2.2307 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1450 | MW | Dhaka | 3195 | 3195 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2280 | MW | Chittagong | 851 | 851 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3730 | MW | Khulna | 990 | 990 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1099.3 | MMCFD |  |  | Rajshahi | 824 | 824 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 125795449.9 | ii) Oil : | Taka | 88207410.68 | Comilla | 692 | 692 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 23713820 | Total | Taka | 237716680.58 | Mymensingh | 632 | 632 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.8975 | MKWHr. | Sylhet | 327 | 327 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -70 | MW (E to W) at | 19:00 | hrs | Barisal | 221 | 221 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -335 | MW at | 23:00 | hrs | Rangpur | 490 | 490 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 8222 | 8222 |  | 0
B. |  | 2019-12-06 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14072 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6000 | MW
4 | Reserve(Generation end) |  |  |  | 6072 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 150.7062 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5338 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.3869 | MKWHr. | ii) HVDC Flow at Peak Time |  | 733 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0678 | MKWHr. | iii) Maximum HVDC Flow : |  | 733 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.17 |  | (b) Today: | 99.01 |  | (c) Rule Curve: |  | 105.55
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 127 | 0 | 0 | 0 | 12 | 0 | 342 | 368 |  | 0 | 450 | 0 | 0 | 0 | 0 | 209 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 69 | 40 | 100 | 0 | 0 | 230 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 130 | 85 | 320 | 204 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 21 | 78 | 161 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 140 | 0 | 56 | 5 | 0 | 0 | 0 | 6 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4479 | 1439 | 5918 | 3610 | 140 | 1717 | 64 | 200 | 109 | 0 | 78 | 0 | 0 | 99.22
2:00 | 35 | 110 | 0 | 0 | 0 | 12 | 0 | 345 | 273 |  | 0 | 360 | 0 | 0 | 0 | 0 | 353 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 71 | 40 | 100 | 0 | 0 | 229 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 100 | 0 | 0 | 115 | 275 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 76 | 161 | 0 | 0 | 0 | 30 | 36 | 5 | 5 | 100 | 0 | 56 | 5 | 0 | 0 | 0 | 6 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4105 | 1447 | 5552 | 3444 | 140 | 1517 | 64 | 200 | 111 | 0 | 76 | 0 | 0 | 99.21
3:00 | 35 | 110 | 0 | 0 | 0 | 12 | 0 | 344 | 274 |  | 0 | 360 | 0 | 0 | 0 | 0 | 250 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 30 | 0 | 0 | 72 | 40 | 100 | 0 | 0 | 228 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 100 | 0 | 0 | 140 | 260 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 74 | 162 | 0 | 0 | 0 | 30 | 36 | 5 | 5 | 100 | 0 | 56 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4011 | 1324 | 5335 | 3219 | 140 | 1526 | 64 | 200 | 112 | 0 | 74 | 0 | 0 | 99.2
4:00 | 35 | 110 | 0 | 0 | 0 | 12 | 0 | 320 | 252 |  | 0 | 330 | 0 | 0 | 0 | 0 | 220 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 30 | 0 | 0 | 72 | 40 | 100 | 0 | 0 | 230 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 100 | 0 | 0 | 166 | 285 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 72 | 164 | 0 | 0 | 0 | 30 | 36 | 5 | 5 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3916 | 1335 | 5251 | 3163 | 140 | 1500 | 64 | 200 | 112 | 0 | 72 | 0 | 0 | 99.19
5:00 | 35 | 109 | 0 | 0 | 0 | 12 | 0 | 300 | 252 |  | 0 | 330 | 0 | 0 | 0 | 0 | 220 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 30 | 0 | 0 | 72 | 40 | 100 | 0 | 0 | 229 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 100 | 0 | 0 | 225 | 260 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 70 | 164 | 0 | 0 | 0 | 30 | 40 | 5 | 5 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3905 | 1291 | 5196 | 3148 | 140 | 1462 | 64 | 200 | 112 | 0 | 70 | 0 | 0 | 99.18
6:00 | 35 | 109 | 0 | 0 | 0 | 12 | 0 | 317 | 252 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 30 | 0 | 0 | 72 | 40 | 100 | 0 | 0 | 223 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 100 | 0 | 0 | 260 | 270 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 68 | 163 | 0 | 0 | 0 | 30 | 40 | 5 | 5 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3929 | 1371 | 5300 | 3247 | 140 | 1473 | 60 | 200 | 112 | 0 | 68 | 0 | 0 | 99.17
7:00 | 35 | 108 | 0 | 0 | 0 | 12 | 0 | 369 | 286 |  | 0 | 330 | 0 | 0 | 0 | 0 | 220 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 72 | 40 | 100 | 0 | 0 | 216 | 0 | 152 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 100 | 0 | 0 | 350 | 345 | 171 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 68 | 161 | 0 | 0 | 0.1 | 30 | 40 | 5 | 5 | 100 | 0 | 53 | 5 | 0 | 0 | 0 | 6 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0.37 | 0 | 0 | 0 | 0 |  | 140 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4341.97 | 1518.1 | 5860.07 | 3726 | 140 | 1547 | 64 | 200 | 112 | 0 | 68 | 3.07 | 0 | 99.16
8:00 | 35 | 109 | 0 | 0 | 0 | 30 | 0 | 382 | 366 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 30 | 0 | 0 | 77 | 40 | 100 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 120 | 0 | 0 | 392 | 335 | 206 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 163 | 0 | 0 | 0.7 | 30 | 40 | 5 | 7 | 100 | 0 | 52 | 5 | 0 | 0 | 0 | 6 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 |  | 140 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 |  | 4608.5 | 1585.6 | 6194.1 | 3909 | 140 | 1686 | 64 | 200 | 117 | 0 | 74 | 4.1 | 0 | 99.15
9:00 | 35 | 109 | 0 | 0 | 0 | 44 | 0 | 351 | 333 |  | 0 | 370 | 0 | 0 | 0 | 0 | 287 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 77 | 40 | 100 | 0 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 0 | 400 | 320 | 205 | 64 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 80 | 161 | 0 | 22 | 1.5 | 29 | 40 | 5 | 46 | 130 | 0 | 67 | 5 | 0 | 0 | 0 | 7 | 10 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.61 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 320 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 0 | 0 | 200 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4764.11 | 1784.8 | 6548.91 | 3984 | 320 | 1717 | 110 | 200 | 117 | 0 | 80 | 20.91 | 0 | 99.14
10:00 | 35 | 109 | 0 | 0 | 0 | 42 | 0 | 347 | 333 |  | 0 | 340 | 0 | 0 | 0 | 0 | 280 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 17 | 0 | 42 | 40 | 100 | 0 | 0 | 202 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 0 | 365 | 325 | 205 | 64 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 12 | 72 | 157 | 0 | 22 | 1.9 | 30 | 40 | 5 | 46 | 100 | 0 | 65 | 5 | 0 | 0 | 0 | 7 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 466 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 199 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 |  | 4607.6 | 1909.6 | 6517.2 | 3871 | 466 | 1673 | 127 | 199 | 82 | 0 | 72 | 27.2 | 0 | 99.14
11:00 | 35 | 109 | 0 | 0 | 0 | 42 | 0 | 354 | 334 |  | 0 | 340 | 0 | 0 | 0 | 0 | 260 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 25 | 31 | 33 | 32 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 214 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 130 | 0 | 0 | 355 | 360 | 203 | 64 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 12 | 82 | 152 | 0 | 22 | 2.2 | 30 | 40 | 5 | 50 | 100 | 0 | 65 | 5 | 0 | 0 | 0 | 7 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.49 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 446 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 199 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 |  | 4710.99 | 1914.3 | 6625.29 | 3947 | 446 | 1692 | 147 | 199 | 82 | 0 | 82 | 30.29 | 0 | 99.13
12:00 | 35 | 133 | 0 | 0 | 0 | 80 | 0 | 377 | 334 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 31 | 33 | 32 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 216 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 0 | 315 | 350 | 200 | 64 | 0 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 22 | 0 | 2 | 12 | 90 | 152 | 0 | 22 | 2.2 | 60 | 60 | 5 | 49 | 100 | 0 | 66 | 5 | 0 | 0 | 0 | 27 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.86 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 446 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 9 | 0 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 |  | 4999.46 | 1913.5 | 6912.96 | 4047 | 446 | 1840 | 178 | 199 | 82 | 0 | 90 | 30.96 | 0 | 99.13
13:00 | 35 | 128 | 0 | 0 | 0 | 107 | 0 | 381 | 358 |  | 0 | 430 | 0 | 0 | 0 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 25 | 31 | 33 | 32 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 206 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 120 | 0 | 0 | 165 | 320 | 200 | 64 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 33 | 12 | 88 | 152 | 0 | 22 | 2 | 60 | 60 | 44 | 49 | 130 | 0 | 65 | 50 | 0 | 0 | 17 | 31 | 10 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.72 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 |  | 446 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 9 | 0 | 0 | 236 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 5086.82 | 1987.2 | 7074.02 | 3921 | 446 | 2094 | 178 | 236 | 82 | 0 | 88 | 29.02 | 0 | 99.12
14:00 | 35 | 128 | 0 | 0 | 0 | 107 | 0 | 347 | 277 |  | 0 | 350 | 0 | 0 | 0 | 0 | 260 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 29 | 33 | 31 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 205 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 120 | 0 | 0 | 130 | 305 | 181 | 64 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 12 | 90 | 153 | 0 | 22 | 1.7 | 60 | 60 | 53 | 49 | 130 | 0 | 65 | 76 | 0 | 0 | 17 | 32 | 10 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 15.2 | 0 | 0 | 0 | 355 | 0 | 0 | 14 | 3.3 | 0 | 0 | 0 | 0 |  | 445 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 110 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 295 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4747.2 | 1990.2 | 6737.4 | 3679 | 445 | 1923 | 199 | 295 | 82 | 0 | 90 | 24.4 | 0 | 99.12
15:00 | 35 | 128 | 0 | 0 | 0 | 107 | 0 | 371 | 355 |  | 0 | 350 | 0 | 0 | 0 | 0 | 260 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 25 | 29 | 33 | 31 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 206 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 120 | 0 | 0 | 20 | 290 | 197 | 64 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 10 | 92 | 152 | 0 | 22 | 1.1 | 58 | 60 | 50 | 49 | 130 | 0 | 63 | 76 | 0 | 0 | 17 | 32 | 10 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 11 | 0 | 0 | 0 | 378 | 0 | 0 | 34 | 2.2 | 0 | 0 | 0 | 0 |  | 447 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 34 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 290 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 0 |  | 4812.3 | 1946.5 | 6758.8 | 3648 | 447 | 2039 | 143 | 290 | 82 | 0 | 92 | 17.8 | 0 | 0
16:00 | 35 | 129 | 0 | 0 | 0 | 107 | 0 | 354 | 358 |  | 0 | 350 | 0 | 0 | 0 | 0 | 245 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | 19 | 25 | 28 | 33 | 31 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 4 | 120 | 0 | 0 | 30 | 265 | 196 | 64 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 10 | 90 | 152 | 0 | 22 | 0.4 | 58 | 60 | 53 | 49 | 130 | 0 | 65 | 76 | 0 | 0 | 17 | 29 | 10 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 5.4 | 0 | 0 | 0 | 353 | 0 | 0 | 63 | 1 | 0 | 0 | 0 | 0 |  | 447 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 290 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4805.8 | 1878.2 | 6684 | 3564 | 447 | 1989 | 214 | 290 | 82 | 0 | 90 | 8 | 0 | 0
17:00 | 35 | 129 | 0 | 0 | 0 | 107 | 0 | 346 | 275 |  | 0 | 320 | 0 | 0 | 0 | 11 | 228 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 27 | 0 | 35 | 35 | 19 | 25 | 28 | 33 | 31 | 51 | 0 | 42 | 40 | 100 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 11 | 90 | 20 | 8 | 19 | 3 | 120 | 0 | 0 | 50 | 265 | 150 | 64 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 16 | 92 | 157 | 0 | 22 | 0 | 59 | 60 | 53 | 49 | 100 | 0 | 40 | 79 | 0 | 0 | 17 | 31 | 10 | 290 | 24 | 8 | 0 | 31 | 0 | 0 | 57 | 0 | 0 | 0.2 | 10 | 12 | 0 | 296 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 595 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 45 | 18 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 353 | 35 | 0 | 1 | 0 | 35 | 0 | 0.1 | 0 |  | 4887.2 | 2069.1 | 6956.3 | 3331 | 595 | 1831 | 724 | 290 | 82 | 11 | 92 | 0.3 | 0 | 0
18:00 | 35 | 148 | 0 | 0 | 0 | 107 | 0 | 327 | 358 |  | 0 | 360 | 0 | 0 | 0 | 30 | 300 | 0 | 62 | 0 | 0 | 0 | 10 | 0 | 72 | 0 | 48 | 0 | 35 | 35 | 19 | 25 | 17 | 33 | 31 | 51 | 0 | 42 | 40 | 100 | 0 | 0 | 204 | 0 | 144 | 0 |  | 0 | 0 | 34 | 100 | 71 | 50 | 19 | 3 | 120 | 0 | 0 | 65 | 315 | 197 | 64 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 114 | 157 | 10 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 66 | 79 | 0 | 0 | 17 | 34 | 10 | 285 | 24 | 8 | 0 | 96 | 0 | 0 | 151 | 0 | 0 | 0 | 10 | 79 | 100 | 365 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 24 | 110 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 405 | 17 | 0 | 62 | 36 | 108 | 0 | 0 | 0 |  | 5933 | 2605 | 8538 | 3752 | 733 | 2040 | 1483 | 290 | 82 | 44 | 114 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 344 | 327 |  | 0 | 360 | 0 | 0 | 0 | 15 | 270 | 0 | 37 | 0 | 0 | 0 | 10 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 19 | 25 | 30 | 33 | 31 | 51 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 98 | 50 | 19 | 10 | 120 | 0 | 30 | 140 | 315 | 199 | 64 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 110 | 160 | 40 | 22 | 0 | 59 | 60 | 53 | 49 | 100 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 265 | 24 | 8 | 0 | 174 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 90 | 100 | 366 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 25 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 381 | 17 | 0 | 97 | 54 | 113 | 0 | 0 | 0 |  | 6051 | 2641 | 8692 | 3864 | 733 | 1945 | 1658 | 290 | 82 | 10 | 110 | 0 | 0 | 0
19:30 | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 358 | 327 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 19 | 25 | 30 | 33 | 31 | 51 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 19 | 13 | 120 | 0 | 30 | 195 | 320 | 200 | 64 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 110 | 160 | 10 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 320 | 24 | 11 | 0 | 134 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 34 | 0 | 370 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 26 | 110 | 0 | 0 | 45 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 433 | 17 | 0 | 35 | 54 | 55 | 0 | 0 | 0 |  | 5925 | 2530 | 8455 | 3907 | 733 | 2086 | 1247 | 290 | 82 | 0 | 110 | 0 | 0 | 0
20:00 | 35 | 189 | 0 | 0 | 0 | 109 | 0 | 346 | 327 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 19 | 25 | 30 | 33 | 31 | 26 | 0 | 42 | 40 | 100 | 0 | 0 | 211 | 0 | 145 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 19 | 20 | 120 | 0 | 0 | 275 | 320 | 200 | 64 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 110 | 160 | 0 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 52 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 34 | 0 | 370 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 26 | 110 | 0 | 0 | 40 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 433 | 17 | 0 | 35 | 54 | 35 | 0 | 0 | 0 |  | 5840 | 2502 | 8342 | 3942 | 733 | 2075 | 1110 | 290 | 82 | 0 | 110 | 0 | 0 | 0
21:00 | 35 | 189 | 0 | 0 | 0 | 109 | 0 | 353 | 326 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 31 | 26 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 144 | 0 |  | 0 | 0 | 0 | 100 | 52 | 0 | 19 | 25 | 120 | 0 | 0 | 395 | 320 | 201 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 106 | 162 | 0 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 56 | 79 | 0 | 0 | 17 | 36 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 17 | 0 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 26 | 110 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 437 | 17 | 0 | 35 | 54 | 20 | 0 | 0 | 0 |  | 5704 | 2443 | 8147 | 4046 | 733 | 2027 | 863 | 290 | 82 | 0 | 106 | 0 | 0 | 0
22:00 | 35 | 189 | 0 | 0 | 0 | 109 | 0 | 345 | 328 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 208 | 0 | 145 | 0 |  | 0 | 0 | 0 | 40 | 0 | 0 | 19 | 30 | 120 | 0 | 0 | 388 | 330 | 203 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 98 | 160 | 0 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 644 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 397 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 |  | 5351 | 2126 | 7477 | 4014 | 644 | 1972 | 377 | 290 | 82 | 0 | 98 | 0 | 0 | 99.08
23:00 | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 345 | 327 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 120 | 0 | 0 | 388 | 270 | 203 | 8 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 92 | 161 | 0 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 |  | 343 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 270 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 396 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 |  | 5140 | 1731 | 6871 | 3956 | 343 | 1972 | 156 | 270 | 82 | 0 | 92 | 0 | 0 | 99.07
24:00 | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 347 | 328 |  | 0 | 360 | 0 | 0 | 0 | 0 | 274 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 120 | 0 | 55 | 285 | 265 | 203 | 8 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 84 | 161 | 0 | 22 | 0 | 60 | 60 | 53 | 49 | 130 | 0 | 56 | 79 | 0 | 0 | 17 | 35 | 10 | 310 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 198 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5020 | 1468 | 6488 | 3916 | 198 | 1985 | 23 | 200 | 82 | 0 | 84 | 0 | 0 | 99.07
KWH | 856000 | 3430000 | 0 | 0 | 0 | 1618363 | 0 | 8472580 | 7548000 |  | 0 | 8664250 | 0 | 0 | 0 | 69527 | 6335020 | 0 | 1368000 | 0 | 0 | 0 | 11040 | 0 | 215040 | 0 | 249456 | 0 | 93056 | 340598 | 206028 | 600000 | 686160 | 782300 | 797300 | 456540 | 0 | 1262673 | 968000 | 2400000 | 0 | 0 | 5061265 | 0 | 3339886 | 0 |  | 0 | 0 | 55665 | 566280 | 345600 | 110400 | 425088 | 341760 | 2807624 | 0 | 240432 | 5602200 | 7509500 | 4624000 | 920000 | 21375 | 639504 | 0 | 0 | 655108 | 0 | 0 | 0 | 338868 | 91260 | 408400 | 462190 | 2067840 | 3730720 | 70080 | 363132 | 13900 | 1121000 | 1227360 | 664800 | 859824 | 3067363 | 0 | 1333536 | 983040 | 0 | 0 | 227000 | 492160 | 168120 | 7528500 | 194528 | 106032 | 0 | 524400 | 0 | 0 | 1051200 | 0 | 0 | 122445 | 23040 | 243840 | 257600 | 8725000 | 0 | 45204 | 899090 | 28200 | 0 | 0 | 0 | 0 |  | 9386909 | 0 | 5344416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179625 | 614000 | 427000 | 1946880 | 0 | 0 | 720000 | 0 | 0 | 0 | 208770 | 0 | 0 | 0 | 0 | 286080 | 210852 | 223920 | 0 | 0 | 5798000 | 0 | 0 | 4656609 | 0 | 0 | 0 | 0 | 0 | 4808491 | 0 | 9806363 | 103680 | 0 | 270720 | 266544 | 313920 | 0 | 34246 | 0 |  | 118135290 | 45607025 | 163742315 | 90900724 | 9386909 | 44241583 | 8851090 | 5798000 | 2230673 | 66705 | 2067840 | 198791 | 0
Fuel Cost | 958720 | 3704400 | 0 | 0 | 0 | 1569812.11 | 0 | 6100257.6 | 5736480 |  | 0 | 6931400 | 0 | 0 | 0 | 713347.02 | 7855424.8 | 0 | 1710000 | 0 | 0 | 0 | 109406.4 | 0 | 1956864 | 0 | 2334908.16 | 0 | 887754.24 | 3392356.08 | 154521 | 450000 | 0 | 0 | 0 | 4373653.2 | 0 | 328294.98 | 251680 | 3672000 | 0 | 0 | 5314328.25 | 0 | 4241655.22 | 0 |  | 0 | 0 | 583925.85 | 5827021.2 | 3286656 | 1033344 | 391080.96 | 950092.8 | 2948005.2 | 0 | 252453.6 | 4145628 | 6307980 | 4254080 | 901600 | 28428.75 | 524393.28 | 0 | 0 | 936804.44 | 0 | 0 | 0 | 345645.36 | 68445 | 771876 | 346642.5 | 14268096 | 3059190.4 | 666460.8 | 370394.64 | 227960 | 1524560 | 1669209.6 | 904128 | 1074780 | 3803530.12 | 0 | 1986968.64 | 1730150.4 | 0 | 0 | 360930 | 575827.2 | 395082 | 5345235 | 145896 | 80584.32 | 0 | 5490468 | 0 | 0 | 10112544 | 0 | 0 | 1413015.3 | 214732.8 | 2287219.2 | 2413712 | 8201500 | 0 | 402767.64 | 8496400.5 | 0 | 0 | 0 | 0 | 0 |  | 25344654.3 | 0 | 4168644.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1776491.25 | 491200 | 661850 | 20909491.2 | 0 | 0 | 1353600 | 0 | 0 | 0 | 2164944.9 | 0 | 0 | 0 | 0 | 314688 | 347905.8 | 169507.44 | 0 | 0 | 23713820 | 0 | 0 | 4097815.92 | 0 | 0 | 0 | 0 | 0 | 4231472.08 | 0 | 7158644.99 | 980812.8 | 0 | 2485209.6 | 2374907.04 | 2932012.8 | 0 | 0 | 0 |  | 173872708.56 | 105677672.6 | 279550381.16 | 86457439.04 | 25344654.3 | 39338010.86 | 87514078.43 | 23713820 | 579974.98 | 693332.25 | 14268096 | 1640975.3 | 0
Yesterday Day Peak | 35 | 133 | 0 | 0 | 0 | 80 | 0 | 377 | 334 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 31 | 33 | 32 | 33 | 0 | 42 | 40 | 100 | 0 | 0 | 216 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 120 | 0 | 0 | 315 | 350 | 200 | 64 | 0 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 22 | 0 | 2 | 12 | 90 | 152 | 0 | 22 | 2.2 | 60 | 60 | 5 | 49 | 100 | 0 | 66 | 5 | 0 | 0 | 0 | 27 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.86 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 446 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 110 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 9 | 0 | 0 | 199 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 |  | 6912.96 | DayPeak
Yesterday Evening Peak | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 344 | 327 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 270 | 0 | 37 | 0 | 0 | 0 | 10 | 0 | 72 | 0 | 47 | 0 | 0 | 35 | 19 | 25 | 30 | 33 | 31 | 51 | 0 | 42 | 40 | 100 | 0 | 0 | 203 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 100 | 98 | 50 | 19 | 10 | 120 | 0 | 30 | 140 | 315 | 199 | 64 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 33 | 21 | 110 | 160 | 40 | 22 | 0 | 59 | 60 | 53 | 49 | 100 | 0 | 55 | 79 | 0 | 0 | 17 | 36 | 10 | 265 | 24 | 8 | 0 | 174 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 90 | 100 | 366 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 25 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 290 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 381 | 17 | 0 | 97 | 54 | 113 | 0 | 0 | 0 |  | 8692 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 10 | 120 | 0 | 100 | 360 | 360 | 200 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 131 | 161 | 95 | 22 | 0 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 446 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 26 | 110 | 30 | 0 | 71 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 200 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 150 | 0 | 0 | 0 | 105 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 236 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 100 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 5 | 120 | 0 | 100 | 360 | 360 | 200 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 103 | 160 | 95 | 22 | 1.6 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 100 | 400 | 115 | 88 | 105 | 5 | 230 | 54 | 50 | 0 |  | 175 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 70 | 0 | 0 | 71 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 20 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 360 | 288 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 40 | 40 | 100 | 0 | 0 | 203 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 80 | 0 | 55 | 265 | 265 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 64 | 164 | 0 | 0 | 0.7 | 39 | 60 | 5 | 2 | 100 | 0 | 53 | 5 | 0 | 0 | 0 | 8 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 351 | 0 | 0 | 26 | 1.6 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0
199
| Minimum Generation |  | 5196 | 5:00
| Highest Generation |  | 8692 | 19:00
| Day Peak Generation |  | 6912.96 | 12:00
| Evening Peak Generation |  | 8692 | 19:00
| HVDC Max Flow |  | 733 | 18:00
| HVDC EvPeak Flow |  | 733 | 19:00
| Load factor L.F |  | 78.49%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6912.96 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5338 | MW
Evening Peak Generation : |  | 8692 | MW Hour : | 19:00 | Available Max Generation : |  | 14072 | MW
E.P. Demand (at gen end) : |  | 8692 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8000 | MW
Maximum Generation : |  | 8692 | MW Hour : | 19:00 | Reserve(Generation end) |  | 6072 | MW
Total Gen. (MKWH) : |  | 163.7423 | System Load Factor : | 78.49% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -335 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-06
Actual : | 99.01 | Ft.(MSL) , | Rule curve : | 105.55 | Ft.( MSL )
Gas Consumed : | Total = | 1099.3 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125795449.9
: |  | Coal : | 23713820 | Oil : | 88207410.68 | Total : | 237716680.58
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2833.3861 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 955.4275 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 854.5915 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 771.6843 |  |  | 0 | 0%
) | 0 | 0:00 | 697.6418 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 562.9519 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 325.1734 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 145.2202 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 434.1267 |  |  | 0 | 0%
Total | 0 |  | 7580.2034 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2.
2) Sylhet-150 MW.
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Ashuganj Precision
9) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sherpur (Mymensingh) 132/33 kV T3 transformer was under shut down from 08:15 to 16:36 for A/M.
b) Jamalpur-Mymensingh 132 kV Ckt-1 was under shut down from 09:07 to 17:06 for A/M.
c) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 08:24 to 16:48 for A/M.
d) Siddhirganj-Haripur 132 kV Ckt-1 was under shut down from 08:58 to 14:19 for A/M.
e) GPH 230/132 kV T02 was under shut down from 11:24 to 11:54 for D/W.
f) GPH 230/132 kV T01 was under shut down from 10:11 to 11:04 for D/W.
g) Barapukuria-Saidpur 132 kV Ckt-1 was under shut down from 08:14 to 17:02 for A/M.
h) Barapukuria 132 kV Bus-2 was under shut down from 10:28 to 16:50 for A/M.
i) Natore-Bogura 132 kV Ckt-1 was under shut down from 09:34 to 16:10 for A/M.
j) Baghabari-Ishurdi 230 kV Ckt-2 was under shut down from 08:27 to 16:54 for A/M.
k) Bogura (New) -Confidence bogura-1 P/S 132 kV Ckt was under shut down from 09:00 to 16:40 for
D/W.
l) Manikganj 132/33 kV GT-4 was under shut down from 10:20 to 10:52 for red hot maintenance.
m) Tongi (Old)-Tongi (New) 132 kV Ckt-2 was under shut down from 13:15 to 20:35 for A/M.
n) Bashundhara 132/33 kV T3 transformer tripped at 15:06 due to LA burst and was switched on at |  |  |  |  | About 78 MW power interruption occurred under Bashundhara S/S area
15:15. |  |  |  |  | from 15:06 to 11:15.
o) Chandpur-Comilla 132 kV Ckt-2 was under shut down from 15:49 to 16:38 for removing bird nest.
p) Khulshi-Madunaghat 132 kV Ckt-1 tripped at 16:52 showing dist.relay and is still under maintenance.
q) Ashuganj (N) ST was synchronized at 17:16.
r) Bhola CCPP GT-1 was synchronized at 22:54.
s) Ashuganj Unit-5 was synchronized at 23:34.
t) Jhenaidah-Chuadanga 132 kV Ckt was shut down at 07:03 (06/12/19) for A/M. |  |  |  |  | About 30 MW power interruption occurred under Chuadanga S/S area
from 07:03 (06/12/19) to till now.
u) Kabirpur 33 kV Bus of 132/33 kV T2 & T3 transformers shut down at 07:09 (06/12/19) for C/M |  |  |  |  | About 40 MW power interruption occurred under Kabirpur S/S area
and were synchronized at 10:30 & 10:31 (06/12/19) for C/M. |  |  |  |  | from 07:09 to 10:30.
v) Hasnabad 230/132 kV T2 transformer was shut down at 07:22 (06/12/19) for A/M.
w) Hathazari 132 kV main bus was shut down at 07:39 (06/12/19) for C/M.
x) Maniknagar-Matuail 132 kV Ckt was shut down at 07:30 (06/12/19) for A/M.
y) Jamalpur 132/33 kV T4 transformer was shut down at 07:50 (06/12/19) for 33 kV bus maintenance. |  |  |  |  | About 10 MW power interruption occurred under Jamalpur S/S area
from 07:50 to 11:26 (06/12/19) .

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 856000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 189 | 3430000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1618363
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8472580 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 327 | 7548000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8664250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 69527 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 206028
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 37 | 1368000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6335020 | Low demand
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 249456 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 10 | 11040 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 93056 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 340598 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 215040 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1286160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 782300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 797300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 456540
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 174 | 524400 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 45204 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2211 | 43368862
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122445
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 110400
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 2230673 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 5061265 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 3339886 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 899090
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 55665 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 566280
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 23040 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 425088
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 341760
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 98 | 345600 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28200
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 911 | 15949392
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2807624 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 30 | 240432 | Synchronizing process.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 199 | 4624000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 140 | 5602200 | ST Synchronized
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7509500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 639504 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 64 | 920000 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 655108 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 257600 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 21375 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 90 | 243840 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 338868
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 91260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2067840
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 408400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 462190 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1326 | 26889741
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 160 | 3730720 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 363132
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 40 | 70080 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13900
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 1051200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 422 | 5229032
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1121000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1227360
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3067363 | Low demand
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 664800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 859824
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 106032
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1333536 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 983040 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 227000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 36 | 492160 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 194528
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 7528500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 366 | 8725000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 168120
| Sylhet Area Total |  |  |  | 1949 | 1181 | 26698263
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 733 | 9386909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 185 | 5344416 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 179625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 103680 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 54 | 266544 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1029 | 15281174
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1946880
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 427000 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 614000 | Machine tripped
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Reserve
| Barisal Area Total |  |  |  | 462 | 195 | 2987880
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 720000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 208770
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 187 | 4656609 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 202 | 4808491 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 381 | 9806363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 286080
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 210852
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223920
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 97 | 270720
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1014 | 21191805
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 290 | 5798000
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 313920
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34246
| Rangpur Area Total |  |  |  | 605 | 403 | 6146166
| Total |  |  |  | 19047 | 8692 | 163742315
| Eastern Grid Total |  |  |  | 13483 | 6051 | 118135290
| Western Grid Total |  |  |  | 5564 | 2641 | 45607025
| National Grid Total |  |  |  | 19047 | 8692 | 163742315
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-05
(a) ENTIRE EASTERN GRID : |  | 5697 | MW | (b) ENTIRE WESTERN GRID : |  | 2525 | MW
i) Dhaka area |  | 3195 | MW | i) Khulna area |  | 990 | MW
ii) Chittagong area |  | 851 | MW | ii) Rajshahi area |  | 824 | MW
iii) Comilla area |  | 692 | MW | iii) Barisal area |  | 221 | MW
iv) Mymensingh area |  | 632 | MW | iv) Rangpur area |  | 490 | MW
v) Sylhet area |  | 327 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8222 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 12:00 | Shahjibazar | 81 | 19:00 | Bottail | 104 | 18:00
Munsiganj | 74 | 19:30 | Fenchuganj | 25 | 18:00 | G.K Project | 25 | 18:30
Sonargaon | 68 | 11:00 | Kulawara | 29 | 18:00 | Faridpur | 124 | 19:30
Shyampur | 170 | 16:00 | Sylhet | 96 | 18:00 | Madaripur | 54 | 19:00
Bhulta | 169 | 19:00 | Chatak | 16 | 18:00 | Sariatpur | 36 | 19:00
Madanganj | 46 | 18:00 | Sunamganj | 28 | 18:00 | Gopalganj | 62 | 18:00
Shitalakhya | 96 | 12:00 | Biani Bazar | 31 | 19:00 | Bagerhat | 62 | 19:00
Rahim steel | 13 | 10:00 | Comilla (S) | 114 | 18:00 | Mongla | 32 | 18:00
Matuail | 80 | 10:00 | Comilla(N) | 61 | 18:00 | Satkhira | 66 | 18:30
Ghorasal | 66 | 19:00 | Chandpur | 66 | 20:00 | Gallamari | 34 | 13:00
Narsingdi | 104 | 18:30 | Feni | 87 | 18:00 | Magura | 35 | 19:00
Haripur (SBU) | 77 | 9:00 | Chowmuhani | 118 | 19:30 | Norail | 22 | 19:00
Ullon | 51 | 18:00 | Ashuganj | 40 | 18:30 | Chuadanga | 59 | 18:00
Hasnabad | 149 | 18:00 | Daudkandi | 88 | 19:00 | Barisal(N) | 30 | 21:00
Magbazar | 87 | 14:00 | B.Baria | 88 | 19:30 | Barisal (S) | 68 | 19:00
Maniknagar | 84 | 13:00 | Ramganj | 44 | 18:30 | Patuakhali | 76 | 21:00
Bangabhaban | 24 | 13:00 | Chaddagram | 6 | 18:00 | Bhandaria | 38 | 20:00
Narinda | 76 | 13:00 | PHP | 0 |  | Borhan Uddin | 24 | 21:00
Dhanmondi | 113 | 12:00 | Madunaghat | 41 | 18:00 | Ishurdi | 44 | 18:00
Lalbag | 61 | 13:00 | Hathazari | 68 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 42 | 13:00 | Khulshi | 158 | 15:00 | Natore | 85 | 18:30
Mirpur | 77 | 18:00 | Halishahar | 96 | 18:00 | Bogra | 143 | 18:00
Kalyanpur | 72 | 18:00 | Baraulia | 133 | 9:00 | Noagaon | 76 | 19:00
Gulshan | 118 | 13:00 | Sikalbaha | 30 | 20:00 | Rajshahi | 90 | 20:00
Uttara | S/D |  | Dohazari | 64 | 18:00 | Rajshahi New | 8 | 12:00
Uttara New | 32 | 18:00 | Cox'sbazar | 72 | 18:00 | C.Nawabganj | 49 | 18:30
Kamrangirchar | 62 | 18:00 | Chandraghona | 22 | 18:00 | Amnura | 21 | 18:00
Savar | 102 | 18:30 | Kaptai | 3.5 | 18:00 | Pabna | 71 | 18:30
Bhasantec | 121 | 18:00 | A. Khaer Stl. | 7 | 11:00 | Shahjadpur | 77 | 18:30
Agargaon | 38 | 13:00 | Bakulia | 78 | 18:00 | Serajganj | 55 | 18:30
Satmosjid | 75 | 13:00 | Julda | 18 | 1:00 | Niyamatpur | 42 | 18:30
Tongi | 130 | 11:00 | TK chemical | 2.4 | 13:00 | Joypurhat | 49 | 18:30
Kabirpur | 155 | 11:00 | Modern Steel | 16 | 15:00 | Sherpur(Bogura) | 34 | 18:30
Basundhara | 93 | 18:00 | Shahmirpur | 21 | 2:00 | Mohastangor | 11 | 18:30
Manikganj | 58 | 18:00 | Khagrachhari | 14 | 18:00 | Rangpur | 102 | 18:30
Joydevpur | 174 | 18:30 | Matarbari | 21 | 18:00 | Lalmonirhat | 40 | 18:00
New Tongi | 84 | 12:00 | Baroiar Hat | 18 | 18:00 | Saidpur | 84 | 18:00
Korda | 191 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 56 | 7:00
Dhamrai | 52 | 18:30 | Abul Khair 230 | 98 | 17:00 | Thakurgaon | 34 | 1:00
Valuka | 76 | 18:00 | BSRM | 108 | 12:00 | Palashbari | 88 | 18:00
Tangail | 137 | 18:00 | GPH Ispat | 5 | 15:00 | Barapukuria | 38 | 19:30
Mymensing | 153 | 18:00 | Goalpara | 19 | 8:00 | Panchagar | 25 | 8:00
Kishorganj | 76 | 19:30 | Central s/s | 63 | 18:00 | Joldhaka | 20 | 18:30
Netrokona | 67 | 19:00 | Noapara | 45 | 18:00 | Kurigram | 44 | 18:00
Jamalpur | 84 | 18:30 | Jessore | 82 | 18:00
Sherpur | 64 | 18:00 | Benapol | 28 | 18:00
Srimongal | 26 | 18:00 | Jhenida | 76 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-05 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 389 | 0.041667 | 379 | 0.45833 | Kaliakoir | 373 | 0.16667 | 357 | 0.5
Bheramara | 410 | 0.125 | 393 | 0.75 | Bhulta | 387 | 0.25 | 370 | 0.625
Ashuganj(N) | 391 | 0.20833 | 372 | 0.625
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 0.041667 | 222 | 0.45833 | Hathazari | 221 | 0.25 | 215 | 0.625
Ishurdi | 237 | 0.041667 | 226 | 0.33333 | Megnaghat | 225 | 0.20833 | 216 | 0.5
Ashuganj | 235 | 0.20833 | 230 | 0.41667 | Fenchuganj | 236 | 0.041667 | 229 | 0.45833
Serajganj | 234 | 0.20833 | 229 | 0.33333 | Siddhirganj | 226 | 0.20833 | 217 | 0.45833
Baghabari | 238 | 0.041667 | 231 | 0.33333 | Maniknagar | 224 | 0.20833 | 215 | 0.45833
Barapukuria | 231 | 0.70833 | 227 | 0.5 | Old Airport | 224 | 0.20833 | 212 | 0.45833
Bogra | 232 | 0.041667 | 224 | 0.33333 | Barisal | 237 | 0.20833 | 224 | 0.29167
Khulna South | 234 | 0.16667 | 216 | 0.33333 | AKSML | 217 | 0.125 | 210 | 0.41667
Rampura | 222 | 0.083333 | 218 | 0.5 | BSRM | 220 | 0.125 | 211 | 0.625
Haripur | 221 | 0.16667 | 216 | 0.5 | Bibiyana | 233 | 0.77083 | 227 | 0.41667
Hasnabad | 224 | 0.16667 | 215 | 0.41667 | Bhulta | 225 | 0.125 | 216 | 0.5
Aminbazar | 224 | 0.16667 | 214 | 0.41667 | Ashuganj (S) | 233 | 0.20833 | 226 | 0.54167
Tongi | 217 | 0.20833 | 207 | 0.45833 | Kaliakoir | 224 | 0.29167 | 216 | 0.5
Comilla (N) | 230 | 0.25 | 221 | 0.45833 | GPH | 217 | 0.083333 | 210 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 5:00 | 129 | 11:00 | Halishahar | 132 | 18:00 | 126 | 12:00
Munsiganj | 135 | 4:00 | 128 | 12:00 | Baraulia | 130 | 18:00 | 125 | 11:00
Sonargaon | 131 | 8:00 | 127 | 11:00 | Sikalbaha | 131 | 18:00 | 126 | 15:00
Shyampur | 136 | 2:00 | 129 | 11:00 | Dohazari | 130 | 18:00 | 126 | 12:00
Bhulta | 130 | 3:00 | 124 | 12:00 | Cox'sbazar | 126 | 4:00 | 122 | 10:00
Madanganj | 133 | 4:00 | 127 | 11:00 | Chandraghona | 132 | 3:00 | 128 | 10:00
Shitalakhya | 138 | 5:00 | 127 | 10:00 | Kaptai | 132 | 1:00 | 129 | 9:00
Rahim steal | 134 | 1:00 | 130 | 11:00 | A. Khaer Stl. | 130 | 3:00 | 125 | 13:00
Matuail | 135 | 5:00 | 128 | 12:00 | Bakulia | 130 | 18:30 | 124 | 15:00
Ghorasal | 136 | 7:00 | 135 | 1:00 | Julda | 130 | 18:00 | 125 | 11:00
Narsinghdi | 133 | 1:00 | 129 | 15:00 | TK Chemical | 130 | 1:00 | 126 | 11:00
Haripur (SBU) | 136 | 6:00 | 131 | 10:00 | Modern Steel | 130 | 18:00 | 124 | 15:00
Ullon | 133 | 6:00 | 127 | 11:00 | Shahmirpur | 131 | 1:00 | 125 | 10:00
Hasnabad | 136 | 6:00 | 128 | 12:00 | Khagrachhari | 131 | 1:00 | 127 | 13:00
Magbazar | 134 | 4:00 | 127 | 15:00 | Matarbari | 128 | 2:00 | 124 | 12:00
Maniknagar | 137 | 5:00 | 132 | 13:00 | Baroiar Hat | 130 | 1:00 | 125 | 12:00
Bangabhaban | 137 | 5:00 | 132 | 13:00 | Rangamati | 131 | 1:00 | 127 | 11:00
Narinda | 137 | 5:00 | 132 | 13:00 | Goalpara | 137 | 4:00 | 126 | 13:00
Dhanmondi | 133 | 6:00 | 127 | 11:00 | Central s/s | 136 | 3:00 | 126 | 8:00
Lalbag | 138 | 6:00 | 127 | 10:00 | Noapara | 135 | 1:00 | 118 | 7:00
Madartek | 134 | 5:00 | 127 | 11:00 | Jessore | 132 | 1:00 | 122 | 8:00
Mirpur | 136 | 2:00 | 125 | 12:00 | Benapol | 136 | 4:00 | 123 | 8:00
Kalyanpur | 139 | 2:00 | 129 | 12:00 | Jhenida | 133 | 2:00 | 119 | 18:00
Gulshan | 133 | 5:00 | 133 | 5:00 | Bottail | 136 | 4:00 | 125 | 18:00
Uttara | 134 | 5:00 | 124 | 13:00 | G.K Project | 139 | 3:00 | 133 | 11:00
Uttara New | 136 | 5:00 | 125 | 12:00 | Faridpur | 132 | 1:00 | 126 | 13:00
Kamrangirchar | 137 | 6:00 | 127 | 12:00 | Madaripur | 133 | 19:00 | 126 | 7:00
Savar | 136 | 5:00 | 124 | 12:00 | Sariatpur | 133 | 9:00 | 127 | 12:00
Bhasantec | 136 | 5:00 | 127 | 12:00 | Gopalganj | 141 | 21:00 | 128 | 12:00
Agargaon | 136 | 5:00 | 128 | 12:00 | Bagerhat | 135 | 4:00 | 123 | 18:00
Satmosjid | 136 | 5:00 | 127 | 12:00 | Mongla | 131 | 4:00 | 121 | 18:00
Tongi | 134 | 5:00 | 126 | 11:00 | Satkhira | 136 | 3:00 | 125 | 13:00
Kabirpur | 132 | 3:00 | 125 | 15:00 | Gallamari | 137 | 4:00 | 126 | 8:00
Basundhara | 132 | 1:00 | 123 | 12:00 | Magura | 135 | 4:00 | 119 | 18:00
Manikganj | 137 | 3:00 | 130 | 14:00 | Norail | 132 | 5:00 | 118 | 18:00
Joydevpur | 135 | 2:00 | 128 | 12:00 | Chuadanga | 133 | 3:00 | 115 | 18:00
New Tongi | 133 | 1:00 | 124 | 11:00 | Barisal(N) | 138 | 5:00 | 130 | 16:00
Kodda | 133 | 18:00 | 125 | 16:00 | Barisal (S) | 138 | 9:00 | 127 | 14:00
Dhamrai | 132 | 4:00 | 124 | 12:00 | Patuakhali | 137 | 5:00 | 130 | 11:00
Valuka | 131 | 6:00 | 120 | 13:00 | Bhandaria | 135 | 5:00 | 126 | 12:00
Tangail | 134 | 2:00 | 125 | 15:00 | Ishurdi | 136 | 2:00 | 130 | 18:00
Mymensing | 132 | 1:00 | 123 | 13:00 | Ruppur Paromanobik | 136 | 1:00 | 129 | 9:00
Kishorganj | 133 | 4:00 | 126 | 13:00 | Natore | 134 | 5:00 | 127 | 8:00
Netrokona | 132 | 1:00 | 121 | 13:00 | Bogra | 137 | 2:00 | 129 | 8:00
Jamalpur | 137 | 18:30 | 120 | 15:00 | Noagaon | 133 | 4:00 | 126 | 8:00
Sherpur | 136 | 18:30 | 119 | 23:00 | Rajshahi | 132 | 3:00 | 124 | 11:00
Srimongal | 137 | 4:00 | 134 | 11:00 | Rajshahi New | 133 | 4:00 | 122 | 8:00
Shahjibazar | 138 | 21:00 | 132 | 11:00 | C.Nawabganj | 133 | 17:00 | 121 | 13:00
Fenchuganj | 136 | 5:00 | 131 | 11:00 | Amnura | 132 | 17:00 | 120 | 8:00
Khulawara | 135 | 1:00 | 132 | 11:00 | Pabna | 135 | 3:00 | 129 | 7:00
Sylhet | 135 | 24:00 | 130 | 11:00 | Shahjadpur | 142 | 1:00 | 135 | 7:00
Chatak | 134 | 1:00 | 130 | 11:00 | Serajganj | 138 | 3:00 | 130 | 8:00
Sunamganj | 135 | 24:00 | 129 | 11:00 | Niyamatpur | 134 | 4:00 | 124 | 8:00
Biani Bazar | 134 | 1:00 | 129 | 11:00 | Joypurhat | 135 | 1:00 | 125 | 8:00
Comilla(s) | 131 | 4:00 | 126 | 12:00 | Sherpur(Bogura) | 139 | 8:00 | 131 | 12:00
Comilla(n) | 136 | 7:00 | 131 | 15:00 | Mohastangor | 135 | 1:00 | 128 | 8:00
Chandpur | 134 | 2:00 | 132 | 1:00 | Rangpur | 130 | 18:30 | 122 | 8:00
Feni | 129 | 7:00 | 125 | 13:00 | Lalmonirhat | 125 | 1:00 | 120 | 7:00
Chowmuhani | 129 | 7:00 | 122 | 13:00 | Saidpur | 130 | 5:00 | 122 | 13:00
Ashuganj | 136 | 5:00 | 132 | 15:00 | Purbasadipur | 128 | 19:00 | 115 | 8:00
Daudkandi | 133 | 7:00 | 127 | 12:00 | Thakurgaon | 124 | 3:00 | 116 | 8:00
B.Baria | 135 | 4:00 | 131 | 11:00 | Palashbari | 131 | 18:30 | 124 | 8:00
Ramganj | 128 | 18:00 | 121 | 16:00 | Barapukuria | 131 | 17:00 | 127 | 12:00
Chaddagram | 134 | 4:00 | 126 | 12:00 | Panchagar | 121 | 19:00 | 112 | 7:00
PHP | 129 | 5:00 | 124 | 16:00 | Joldhaka | 129 | 4:00 | 120 | 12:00
Madanhat | 133 | 7:00 | 129 | 15:00 | Kurigram | 129 | 1:00 | 122 | 8:00
Hathazari | 132 | 18:00 | 128 | 11:00
Khulshi | 128 | 4:00 | 123 | 11:00

## L-Curve
Date | 2019-12-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 327 | 5020 | 1468 | 6488 |  |  |  | QF-LDC-12
0:30 | 283.5 | 4749.5 | 1453.5 | 6203 | Date: | 2019-12-05
1:00 | 240 | 4479 | 1439 | 5918
1:30 | 200 | 4292 | 1443 | 5735
2:00 | 160 | 4105 | 1447 | 5552
2:30 | 165 | 4058 | 1385.5 | 5443.5 | [5 empty] | Gen. at Eve. Peak | 8692 | 8692 MW (19:00 )
3:00 | 170 | 4011 | 1324 | 5335 | [6 empty] | 19:00
3:30 | 165 | 3963.5 | 1329.5 | 5293 | [5 empty] | Gen. at Day Peak | 6912.96 | 6912.96 MW (12:00 )
4:00 | 160 | 3916 | 1335 | 5251 | [6 empty] | 12:00
4:30 | 162.5 | 3910.5 | 1313 | 5223.5 | [5 empty] | Highest Generation | 8692
5:00 | 165 | 3905 | 1291 | 5196 | [6 empty] | 19:00
5:30 | 170 | 3917 | 1331 | 5248
6:00 | 175 | 3929 | 1371 | 5300
6:30 | 235 | 4135.485 | 1444.55 | 5580.035
7:00 | 295 | 4341.97 | 1518.1 | 5860.07
7:30 | 288.5 | 4475.235 | 1551.85 | 6027.085
8:00 | 282 | 4608.5 | 1585.6 | 6194.1
8:30 | 151 | 4686.305 | 1685.2 | 6371.505
9:00 | 20 | 4764.11 | 1784.8 | 6548.91
9:30 | 118.5 | 4685.855 | 1847.2 | 6533.055
10:00 | 217 | 4607.6 | 1909.6 | 6517.2
10:30 | 211 | 4659.295 | 1911.95 | 6571.245
11:00 | 205 | 4710.99 | 1914.3 | 6625.29
11:30 | 146.5 | 4855.225 | 1913.9 | 6769.125
12:00 | 88 | 4999.46 | 1913.5 | 6912.96
12:30 | 79.5 | 5043.14 | 1950.35 | 6993.49
13:00 | 71 | 5086.82 | 1987.2 | 7074.02
13:30 | 139.5 | 4917.01 | 1988.7 | 6905.71
14:00 | 208 | 4747.2 | 1990.2 | 6737.4
14:30 | 251.5 | 4779.75 | 1968.35 | 6748.1
15:00 | 295 | 4812.3 | 1946.5 | 6758.8
15:30 | 277.5 | 4809.05 | 1912.35 | 6721.4
16:00 | 260 | 4805.8 | 1878.2 | 6684
16:30 | 290 | 4846.5 | 1973.65 | 6820.15
17:00 | 320 | 4887.2 | 2069.1 | 6956.3
17:30 | 202.5 | 5410.1 | 2337.05 | 7747.15
18:00 | 85 | 5933 | 2605 | 8538
18:30 | 77.5 | 5992 | 2623 | 8615
19:00 | 70 | 6051 | 2641 | 8692
19:30 | 123 | 5925 | 2530 | 8455
20:00 | 113 | 5840 | 2502 | 8342 |  |  |  | Executive Engineer
20:30 | 91.5 | 5772 | 2472.5 | 8244.5 |  |  |  | Network Operation Division
21:00 | 70 | 5704 | 2443 | 8147
21:30 | 98.5 | 5527.5 | 2284.5 | 7812
22:00 | 127 | 5351 | 2126 | 7477 |  |  |  |  | Page 6 of 7
22:30 | 231 | 5245.5 | 1928.5 | 7174
23:00 | 335 | 5140 | 1731 | 6871
23:30 | 331 | 5080 | 1599.5 | 6679.5
24:00 | 327 | 5020 | 1468 | 6488
8692 MW (19:00 )
6912.96 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-05 |  | Energy | 163742315
[10 empty] | 2019-12-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3916 | 198 | 1985 | 156 | 200 | 82 | 0 | 0 | 84
0:30 | 3763 | 169 | 1851 | 110 | 200 | 95.5 | 0 | 0 | 81 | Date: | 2019-12-05
1:00 | 3610 | 140 | 1717 | 64 | 200 | 109 | 0 | 0 | 78
1:30 | 3527 | 140 | 1617 | 64 | 200 | 110 | 0 | 0 | 77 | [7 empty] | Total Energy | 163.7423 | Total Energy Gen 163.742 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.742 MKWHr
2:00 | 3444 | 140 | 1517 | 64 | 200 | 111 | 0 | 0 | 76 | [7 empty] | Energy not Served | 0
2:30 | 3331.5 | 140 | 1521.5 | 64 | 200 | 111.5 | 0 | 0 | 75 | [7 empty] | Energy Requirement | 163.7423
3:00 | 3219 | 140 | 1526 | 64 | 200 | 112 | 0 | 0 | 74
3:30 | 3191 | 140 | 1513 | 64 | 200 | 112 | 0 | 0 | 73 | [6 empty] | Shortage
4:00 | 3163 | 140 | 1500 | 64 | 200 | 112 | 0 | 0 | 72
4:30 | 3155.5 | 140 | 1481 | 64 | 200 | 112 | 0 | 0 | 71
5:00 | 3148 | 140 | 1462 | 64 | 200 | 112 | 0 | 0 | 70
5:30 | 3197.5 | 140 | 1467.5 | 62 | 200 | 112 | 0 | 0 | 69
6:00 | 3247 | 140 | 1473 | 60 | 200 | 112 | 0 | 0 | 68
6:30 | 3486.5 | 140 | 1510 | 62 | 200 | 112 | 0 | 0 | 68 |  |  |  |  | Coal
7:00 | 3726 | 140 | 1547 | 64 | 200 | 112 | 0 | 0 | 68
7:30 | 3817.5 | 140 | 1616.5 | 64 | 200 | 114.5 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 3909 | 140 | 1686 | 64 | 200 | 117 | 0 | 0 | 74
8:30 | 3946.5 | 230 | 1701.5 | 87 | 200 | 117 | 0 | 0 | 77
9:00 | 3984 | 320 | 1717 | 110 | 200 | 117 | 0 | 0 | 80
9:30 | 3927.5 | 393 | 1695 | 118.5 | 199.5 | 99.5 | 0 | 0 | 76
10:00 | 3871 | 466 | 1673 | 127 | 199 | 82 | 0 | 0 | 72
10:30 | 3909 | 456 | 1682.5 | 137 | 199 | 82 | 0 | 0 | 77
11:00 | 3947 | 446 | 1692 | 147 | 199 | 82 | 0 | 0 | 82
11:30 | 3997 | 446 | 1766 | 162.5 | 199 | 82 | 0 | 0 | 86
12:00 | 4047 | 446 | 1840 | 178 | 199 | 82 | 0 | 0 | 90
12:30 | 3984 | 446 | 1967 | 178 | 217.5 | 82 | 0 | 0 | 89
13:00 | 3921 | 446 | 2094 | 178 | 236 | 82 | 0 | 0 | 88
13:30 | 3921 | 446 | 2094 | 178 | 236 | 82 | 0 | 0 | 88
14:00 | 3921 | 446 | 2094 | 178 | 236 | 82 | 0 | 0 | 88
14:30 | 3784.5 | 446.5 | 2066.5 | 160.5 | 263 | 82 | 0 | 0 | 90
15:00 | 3648 | 447 | 2039 | 143 | 290 | 82 | 0 | 0 | 92
15:30 | 3606 | 447 | 2014 | 178.5 | 290 | 82 | 0 | 0 | 91
16:00 | 3564 | 447 | 1989 | 214 | 290 | 82 | 0 | 0 | 90
16:30 | 3447.5 | 521 | 1910 | 469 | 290 | 82 | 5.5 | 0 | 91
17:00 | 3331 | 595 | 1831 | 724 | 290 | 82 | 11 | 0 | 92
17:30 | 3541.5 | 664 | 1935.5 | 1103.5 | 290 | 82 | 27.5 | 0 | 103
18:00 | 3752 | 733 | 2040 | 1483 | 290 | 82 | 44 | 0 | 114
18:30 | 3808 | 733 | 1992.5 | 1570.5 | 290 | 82 | 27 | 0 | 112
19:00 | 3864 | 733 | 1945 | 1658 | 290 | 82 | 10 | 0 | 110
19:30 | 3907 | 733 | 2086 | 1247 | 290 | 82 | 0 | 0 | 110
20:00 | 3942 | 733 | 2075 | 1110 | 290 | 82 | 0 | 0 | 110
20:30 | 3994 | 733 | 2051 | 986.5 | 290 | 82 | 0 | 0 | 108
21:00 | 4046 | 733 | 2027 | 863 | 290 | 82 | 0 | 0 | 106
21:30 | 4030 | 688.5 | 1999.5 | 620 | 290 | 82 | 0 | 0 | 102
22:00 | 4014 | 644 | 1972 | 377 | 290 | 82 | 0 | 0 | 98
22:30 | 3985 | 493.5 | 1972 | 266.5 | 280 | 82 | 0 | 0 | 95
23:00 | 3956 | 343 | 1972 | 156 | 270 | 82 | 0 | 0 | 92
23:30 | 3936 | 270.5 | 1978.5 | 156 | 235 | 82 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 3916 | 198 | 1985 | 156 | 200 | 82 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 163.742 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 163.742 MKWHr
Note on W13: Author:

## Generation
2019-12-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 69 | 71 | 72 | 72 | 72 | 72 | 72 | 77 | 77 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1262673
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 0 | [16 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.5 |  | 13.61 | 16.7 | 18.49 | 18.86 | 17.72 | 15.2 | 11 | 5.4 | 0.2 | [9 empty] | 122445
6 | Sikalbaha 225MW CCPP (Gas) | 230 | 229 | 228 | 230 | 229 | 223 | 216 | 204 | 203 | 202 | 214 | 216 | 206 | 205 | 206 | 204 | 204 | 204 |  | 203 | 203 | 211 | 203 | 208 | 203 | 203 | 5061265
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 145 | 144 | 106 | 104 | 107 | 152 | 140 | 144 | 145 | 145 | 144 | 144 | 145 | 145 | 145 | 105 | 144 |  | 144 | 145 | 145 | 144 | 145 | 145 | 145 | 3339886
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 11 | 34 |  | 0 | [6 empty] | 55665
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [13 empty] | 14 | 34 | 63 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 84 | 17 | 899090
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 70 | 70 | 70 | 40 | 40 | 60 | 60 | 60 | 60 | 40 | 40 | 97 | 97 | 37 | 37 | 37 | 37 | 62 |  | 37 | 40 | 37 | 37 | 37 | 42 | 37 | 1368000
17 | Siddhirganj 335 MW CCPP | 209 | 353 | 250 | 220 | 220 | 200 | 220 | 280 | 287 | 280 | 260 | 300 | 300 | 260 | 260 | 245 | 228 | 300 |  | 270 | 270 | 270 | 270 | 270 | 270 | 274 | 6335020
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 31 | 96 |  | 174 | 134 | 52 | 45 | 0 |  |  | 524400
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 64 | 64 | 64 | 8 | 8 | 8 | 8 | 920000
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 856000
21 | Ghorasal Repowered CCPP Unit-3 | 127 | 110 | 110 | 110 | 109 | 109 | 108 | 109 | 109 | 109 | 109 | 133 | 128 | 128 | 128 | 129 | 129 | 148 |  | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 3430000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2807624
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 130 | 0 | [17 empty] | 30 | 30 | 0 |  |  | 0 | 55 | 240432
32 | Ashuganj 50 MW PP | 37 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 37 | 37 | 37 | 33 | 33 | 30 | 33 | 33 | 33 |  | 30 | 30 | 30 | 33 | 33 | 30 | 30 | 639504
33 | Ashuganj 225 MW CCPP | 204 | 171 | 171 | 171 | 171 | 171 | 171 | 206 | 205 | 205 | 203 | 200 | 200 | 181 | 197 | 196 | 150 | 197 |  | 199 | 200 | 200 | 201 | 203 | 203 | 203 | 4624000
34 | Ashuganj 450 MW CCPP(South) | 320 | 275 | 260 | 285 | 260 | 270 | 345 | 335 | 320 | 325 | 360 | 350 | 320 | 305 | 290 | 265 | 265 | 315 |  | 315 | 320 | 320 | 320 | 330 | 270 | 265 | 7509500
| Ashuganj 450 MW CCPP(North) | 85 | 115 | 140 | 166 | 225 | 260 | 350 | 392 | 400 | 365 | 355 | 315 | 165 | 130 | 20 | 30 | 50 | 65 |  | 140 | 195 | 275 | 395 | 388 | 388 | 285 | 5602200
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 0 | [25 empty] | 21375
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 345 | 344 | 320 | 300 | 317 | 369 | 382 | 351 | 347 | 354 | 377 | 381 | 347 | 371 | 354 | 346 | 327 |  | 344 | 358 | 346 | 353 | 345 | 345 | 347 | 8472580
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 360 | 360 | 330 | 330 | 300 | 330 | 370 | 370 | 340 | 340 | 400 | 430 | 350 | 350 | 350 | 320 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8664250
41 | Haripur 360MW CCPP(HPL) | 368 | 273 | 274 | 252 | 252 | 252 | 286 | 366 | 333 | 333 | 334 | 334 | 358 | 277 | 355 | 358 | 275 | 358 |  | 327 | 327 | 327 | 326 | 328 | 327 | 328 | 7548000
42 | RPCL 210MW CCPP | 161 | 161 | 162 | 164 | 164 | 163 | 161 | 163 | 161 | 157 | 152 | 152 | 152 | 153 | 152 | 152 | 157 | 157 |  | 160 | 160 | 160 | 162 | 160 | 161 | 161 | 3730720
43
44 | Fenchugonj CCPP Phase-1 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 30 | 30 | 60 | 60 | 60 | 58 | 58 | 59 | 60 |  | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 1121000
45 | Fenchugonj CCPP Phase-2 | 52 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1227360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 40 | 40 | 40 | 53 | 52 | 67 | 65 | 65 | 66 | 65 | 65 | 63 | 65 | 40 | 66 |  | 55 | 55 | 55 | 56 | 55 | 55 | 56 | 1333536
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 76 | 76 | 76 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 983040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 227000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 27 | 31 | 32 | 32 | 29 | 31 | 34 |  | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 492160
53 | Sylhet 10MW PP (Desh) | 0 | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 168120
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 106032
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 44 | 53 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 664800
56 | Shahjahanulla 25 MW PP | [16 empty] | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 194528
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 290 | 305 | 310 | 310 | 320 | 325 | 305 | 300 | 310 | 325 | 320 | 280 | 320 | 300 | 290 | 285 |  | 265 | 320 | 300 | 300 | 280 | 290 | 310 | 7528500
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 4 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 340598
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 425088
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 206028
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 363132
63 | Impoprt (Tripura) | 78 | 76 | 74 | 72 | 70 | 68 | 68 | 74 | 80 | 72 | 82 | 90 | 88 | 90 | 92 | 90 | 92 | 114 |  | 110 | 110 | 110 | 106 | 98 | 92 | 84 | 2067840
64 | Malancha, Ctg. EPZ (United) | 5 | 4 | 4 | 4 | 5 | 16 | 15 | 10 | 5 | 5 | 2 | 5 | 11 | 6 | 3 | 4 | 3 | 3 |  | 10 | 13 | 20 | 25 | 30 | 25 | 35 | 341760
65 | Feni 22MW PP (Doreen) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 |  | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 338868
66 | Feni 11 MW PP (Doreen) | [14 empty] | 8 | 8 |  | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 91260
67 | Jangalia 33MW PP (Summit) | 8 | [10 empty] | 2 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 408400
68 | Cumilla 25 MW PP (Summit) | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 16 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 462190
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 28 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 29 | 29 | 28 | 28 | 17 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 686160
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 782300
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 30 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 797300
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 44 | 42 | 42 | 80 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 109 | 109 | 109 | 107 | 107 | 1618363
Feni Lanka Power
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [9 empty] | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 51 | 51 |  | 51 | 51 | 26 | 26 | 0 |  |  | 456540
79 | Kodda 150MW PP | [17 empty] | 10 |  | 10 | [6 empty] | 11040
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 10 |  | 40 | 10 | 0 |  |  |  |  | 70080
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [16 empty] | 17 | 17 | [8 empty] | 45204
| Kaptai 7 MW Solar PP | [6 empty] | 0.37 | 1.8 | 3 | 4 | 4.3 | 4.4 | 4.1 | 3.3 | 2.2 | 1 | 0 | [9 empty] | 28200
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 50 | 90 | 100 |  | 100 | 100 | 100 | 100 | 40 | 0 |  | 566280
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 46 | 46 | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 859824
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 35 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 655108
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [16 empty] | 8 | 50 |  | 50 | [6 empty] | 110400
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 20 | 71 |  | 98 | 98 | 98 | 52 | 0 |  |  | 345600
97 | Katpotti 52 MW PP (Sinha) | [15 empty] | 5 | 27 | 48 |  | 47 | 47 | 47 | 24 | 12 | 6 | 6 | 249456
98 | Bosila 108MW PP(CLC) | [16 empty] | 58 | 72 |  | 72 | 72 | 72 |  |  |  |  | 215040
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 11 | 30 |  | 15 | 0 | [5 empty] | 69527
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 35 | 35 | [8 empty] | 93056
101 | Kushiara 163 MW CCPP (KP) | 140 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 100 | 130 |  | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 3067363
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.7 | 1.5 | 1.9 | 2.2 | 2.2 | 2 | 1.7 | 1.1 | 0.4 | 0 | [9 empty] | 13900
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [13 empty] | 7 | 7 | 12 | 57 | 151 |  | 200 | 200 | 200 | 200 | 70 | 0 |  | 1051200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 10 |  | 0 | [6 empty] | 23040
116 | Chandpur 200MW (Desh energy) | [16 empty] | 12 | 79 |  | 90 | 34 | 34 | 17 | 0 |  |  | 243840
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 100 |  | 100 | [6 empty] | 257600
118 | Bibiyana-III 400 MW CCPP | 353 | 358 | 352 | 379 | 350 | 356 | 384 | 368 | 354 | 354 | 386 | 360 | 353 | 355 | 378 | 353 | 296 | 365 |  | 366 | 370 | 370 | 365 | 375 | 366 | 362 | 8725000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4479 | 4105 | 4011 | 3916 | 3905 | 3929 | 4341.97 | 4608.5 | 4764.11 | 4607.6 | 4710.99 | 4999.46 | 5086.82 | 4747.2 | 4812.3 | 4805.8 | 4887.2 | 5933 |  | 6051 | 5925 | 5840 | 5704 | 5351 | 5140 | 5020 | 118135290
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 0 | 35 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 103680
130
131
132
133
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 64 | 60 | 64 | 64 | 110 | 110 | 110 | 110 | 110 | 110 | 34 | 16 | 48 | 110 |  | 110 | 110 | 110 | 110 | 96 | 48 | 0 | 1946880
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [13 empty] | 15 | 65 | 55 | 45 | 60 |  | 60 | 60 | 60 | 60 | 60 | 75 | 110 | 614000
140 | Bhola 33 MW PP (Venture) | 21 | 21 | 19 | 18 | 13 | 14 | 13 | 12 | 6 | 11 | 15 | 16 | 18 | 18 | 17 | 16 | 18 | 24 |  | 25 | 26 | 26 | 26 | 24 | 23 | 22 | 427000
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 0 | 8 | 40 |  | 40 | 40 | 40 | 40 | 0 |  |  | 179625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 0 | 36 |  | 54 | 54 | 54 | 54 | 54 | 18 | 0 | 266544
146 | Bheramara HVDC | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 320 | 466 | 446 | 446 | 446 | 445 | 447 | 447 | 595 | 733 |  | 733 | 733 | 733 | 733 | 644 | 343 | 198 | 9386909
147 | Bheramara 360 MW CCPP | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 310 | 290 | 275 | 280 | 250 | 240 | 225 | 215 | 215 | 150 | 195 |  | 185 | 175 | 175 | 160 | 160 | 155 | 155 | 5344416
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 236 | 295 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 270 | 200 | 5798000
153 | Baghabari 71 MW GTPP | [8 empty] | 50 | 60 | 60 | 60 | 60 | 70 | 60 | 60 | 60 | 55 |  | 50 | 45 | 40 | 35 | 0 |  |  | 720000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 199 | 189 | 130 | 130 | 130 | 146 | 202 | 205 | 203 | 180 | 183 | 214 | 214 | 180 | 189 | 183 | 174 | 193 |  | 187 | 174 | 177 | 183 | 176 | 171 | 170 | 4656609
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 200 | 192 | 130 | 130 | 130 | 168 | 204 | 208 | 210 | 196 | 205 | 194 | 212 | 192 | 185 | 187 | 183 | 180 |  | 202 | 186 | 180 | 178 | 178 | 185 | 186 | 4808491
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 401 | 427 | 427 | 439 | 400 | 429 | 431 | 431 | 376 | 394 | 397 | 395 | 402 | 393 | 398 | 365 | 353 | 405 |  | 381 | 433 | 433 | 437 | 397 | 396 | 380 | 9806363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 286080
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 210852
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 9 | 9 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223920
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 30 | 50 |  | 50 | 50 | 50 | 18 | 0 |  |  | 208770
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 1 | 62 |  | 97 | 35 | 35 | 35 | 0 |  |  | 270720
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 108 |  | 113 | 55 | 35 | 20 | 0 |  |  | 313920
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 1.6 | 2.8 | 4.6 | 5.3 | 5.5 | 5.2 | 4.2 | 3.5 | 1.2 | 0.1 | [9 empty] | 34246
178
178