## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-07 | Saturday
|  | Date (day): | 2019-12-07 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11340.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13883 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-06 | 2019-12-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 134 | 134 | 150 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under S/D
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 110 | 100 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 302 | 380 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 280 | 330 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 42 | 67 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 300 | 240 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 24 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 8 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 48 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 90 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1438 | 1909 | 3671 | 4214 | 598 | 1014
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.2 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 78 | 82 | 94 | 94 | 136 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 215 | 216 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 111 | 140 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under Maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 21 | 39 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 564.4 | 731 | 1497 | 1657 | 196 | 278
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 90 | 0 | 0 |  |  | Under Maint.
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 160 | 200 | 0 | 0 |  |  | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 370 | 360 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 345 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 33 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 45 | 45 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 7 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Maintenance at S/S.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 100 | 102 | 127
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1105 | 1365 | 1453 | 1828 | 331 | 179
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 160 | 170 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 156.1 | 232 | 503.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 30 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 62 | 62
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 2 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 68 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 33 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 330 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 387 | 397 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 967 | 1289 | 1368 | 1368 | 0 | 492
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 175 | 434 | 191 | 537
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 245 | 300 | 300 |  | 132 | ST under S/D
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 20 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 17 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 390 | 720 | 631 | 1647 | 0 | 132
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 24 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 110 | 117 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 126 | 189 | 371 | 441 | 0 | 7
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 71 | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 214 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 194 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 427 | 396 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 822 | 936 | 1525 | 1789 | 320 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 37 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 165.8 | 197 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 5734.3 | 7568 | 11340.6 | 13883 | 1487 | 2280
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5468.3461 | 7217 | 10814.6287 | 13239.1135
A. |  | 2019-12-06 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 7568 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5302.4 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7568 | MW
3 | Day peak Generation : |  |  | 5734.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7217 | MW
4 | Evening peak Generation : |  |  | 7568 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 145.7943 | MKWHr | By Solar | 0.19756 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.0156 | MKWHr |  | By Oil: | 2.0126 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.8963 | MKWHr |  | By Hydro: | 1.9393 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1487 | MW | Dhaka | 2519 | 2519 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2280 | MW | Chittagong | 825 | 825 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3767 | MW | Khulna | 881 | 881 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1035.42 | MMCFD |  |  | Rajshahi | 751 | 751 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 120477077.336 | ii) Oil : | Taka | 19590390.01 | Comilla | 673 | 673 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15935867 | Total | Taka | 156003334.346 | Mymensingh | 594 | 594 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.5985 | MKWHr. | Sylhet | 310 | 310 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -361 | MW (E to W) at | 19:30 | hrs | Barisal | 213 | 213 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -403 | MW at | 18:00 | hrs | Rangpur | 451 | 451 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.8° C |  |  | Total | 7217 | 7217 |  | 0
B. |  | 2019-12-07 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 27.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13883 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve(Generation end) |  |  |  | 5383 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 163.7488 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4858 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 4.8705 | MKWHr. | ii) HVDC Flow at Peak Time |  | 434 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8624 | MKWHr. | iii) Maximum HVDC Flow : |  | 435 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.01 |  | (b) Today: | 98.89 |  | (c) Rule Curve: |  | 105.46
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 189 | 0 | 0 | 0 | 107 | 0 | 346 | 328 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 206 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 120 | 0 | 55 | 285 | 270 | 203 | 8 | 0 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 78 | 163 | 0 | 22 | 0 | 60 | 60 | 5 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4640 | 1334 | 5974 | 3816 | 105 | 1727 | 6 | 160 | 82 | 0 | 78 | 0 | 0 | 99.06
2:00 | 35 | 147 | 0 | 0 | 0 | 0 | 0 | 358 | 328 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 206 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 55 | 295 | 280 | 203 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 74 | 161 | 0 | 0 | 0 | 60 | 60 | 5 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4390 | 1339 | 5729 | 3709 | 104 | 1600 | 0 | 160 | 82 | 0 | 74 | 0 | 0 | 99.05
3:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 347 | 328 |  | 0 | 320 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 42 | 40 | 100 | 0 | 0 | 207 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 55 | 272 | 280 | 203 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 72 | 163 | 0 | 0 | 0 | 60 | 60 | 5 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4252 | 1337 | 5589 | 3620 | 105 | 1550 | 0 | 160 | 82 | 0 | 72 | 0 | 0 | 99.04
4:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 347 | 328 |  | 0 | 320 | 0 | 0 | 0 | 0 | 240 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 43 | 40 | 100 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 55 | 265 | 265 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 70 | 109 | 0 | 0 | 0 | 40 | 60 | 5 | 2 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4077 | 1328 | 5405 | 3459 | 104 | 1529 | 0 | 160 | 83 | 0 | 70 | 0 | 0 | 99.03
5:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 348 | 288 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 43 | 40 | 100 | 0 | 0 | 202 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 55 | 272 | 280 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 70 | 111 | 0 | 0 | 0 | 40 | 60 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3973 | 1365 | 5338 | 3462 | 105 | 1458 | 0 | 160 | 83 | 0 | 70 | 0 | 0 | 99.02
6:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 362 | 288 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 43 | 40 | 100 | 0 | 0 | 214 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 0 | 55 | 290 | 290 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 68 | 110 | 0 | 0 | 0 | 40 | 60 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 10 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4061 | 1371 | 5432 | 3546 | 104 | 1471 | 0 | 160 | 83 | 0 | 68 | 0 | 0 | 99.01
7:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 353 | 288 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 41 | 40 | 100 | 0 | 0 | 208 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 55 | 280 | 285 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 66 | 112 | 0 | 0 | 0.1 | 40 | 60 | 5 | 2 | 100 | 0 | 53 | 5 | 0 | 0 | 0 | 10 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  | 104 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4011.6 | 1370.1 | 5381.7 | 3502 | 104 | 1467 | 0 | 159 | 81 | 0 | 66 | 2.7 | 0 | 99.01
8:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 360 | 288 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 40 | 40 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 80 | 0 | 55 | 265 | 265 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 64 | 164 | 0 | 0 | 0.7 | 39 | 60 | 5 | 2 | 100 | 0 | 53 | 5 | 0 | 0 | 0 | 8 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 351 | 0 | 0 | 26 | 1.6 | 0 | 0 | 0 | 0 |  | 104 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4102.4 | 1344.2 | 5446.6 | 3548 | 104 | 1452 | 26 | 160 | 80 | 0 | 64 | 12.6 | 0 | 99
9:00 | 35 | 135 | 0 | 0 | 0 | 0 | 0 | 343 | 270 |  | 0 | 300 | 0 | 0 | 0 | 0 | 210 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 31 | 0 | 0 | 39 | 40 | 100 | 0 | 0 | 203 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 80 | 0 | 55 | 265 | 265 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 64 | 163 | 0 | 0 | 1.4 | 40 | 60 | 5 | 2 | 100 | 0 | 53 | 5 | 0 | 0 | 0 | 8 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 3 | 0 | 0 | 0 | 0 |  | 104 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 159 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 |  | 4038.3 | 1264.1 | 5302.4 | 3512 | 104 | 1346 | 17 | 159 | 79 | 0 | 64 | 21.4 | 0 | 99
10:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 300 | 250 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 28 | 31 | 0 | 0 | 39 | 40 | 100 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 80 | 0 | 55 | 265 | 280 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 160 | 0 | 0 | 1.9 | 40 | 60 | 5 | 2 | 100 | 0 | 52 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 3.8 | 0 | 0 | 0 | 0 |  | 104 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 3951.9 | 1289.2 | 5241.1 | 3434 | 104 | 1360 | 17 | 160 | 79 | 0 | 60 | 27.1 | 0 | 98.99
11:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 300 | 250 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 28 | 31 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 215 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | 80 | 0 | 55 | 280 | 290 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 158 | 0 | 0 | 2 | 40 | 60 | 5 | 2 | 100 | 0 | 51 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9 | 0 | 0 | 0 | 382 | 0 | 0 | 17 | 4.3 | 0 | 0 | 0 | 0 |  | 105 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 |  | 4030.2 | 1349.4 | 5379.6 | 3543 | 105 | 1382 | 17 | 160 | 78 | 0 | 64 | 30.6 | 0 | 98.98
12:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 302 | 280 |  | 0 | 320 | 0 | 0 | 0 | 0 | 230 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 28 | 31 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 215 | 0 | 111 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 80 | 0 | 80 | 370 | 310 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 154 | 0 | 0 | 2.1 | 40 | 60 | 5 | 2 | 100 | 0 | 51 | 5 | 0 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 |  | 175 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0 |  | 4230.5 | 1503.8 | 5734.3 | 3714 | 175 | 1508 | 0 | 160 | 78 | 0 | 70 | 29.3 | 0 | 98.98
13:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 376 | 330 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 28 | 29 | 0 | 0 | 39 | 40 | 100 | 0 | 0 | 206 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | 80 | 0 | 80 | 355 | 280 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 83 | 153 | 0 | 0 | 1.9 | 40 | 60 | 5 | 2 | 130 | 0 | 51 | 5 | 0 | 0 | 0 | 6 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 175 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0 |  | 4381.3 | 1506.5 | 5887.8 | 3716 | 175 | 1644 | 0 | 160 | 79 | 0 | 83 | 30.8 | 0 | 98.98
14:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 378 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 29 | 0 | 0 | 39 | 40 | 100 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 80 | 0 | 80 | 265 | 275 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 153 | 0 | 0 | 1.6 | 40 | 60 | 5 | 2 | 100 | 0 | 51 | 5 | 0 | 0 | 0 | 7 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 |  | 176 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 |  | 4012.8 | 1431.4 | 5444.2 | 3549 | 176 | 1387 | 0 | 160 | 79 | 0 | 72 | 21.2 | 0 | 98.97
15:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 300 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 211 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 29 | 0 | 0 | 41 | 40 | 100 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 80 | 0 | 80 | 265 | 270 | 161 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 72 | 154 | 0 | 0 | 1.1 | 40 | 60 | 5 | 2 | 100 | 0 | 51 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 0 |  | 176 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 |  | 3928.2 | 1376.2 | 5304.4 | 3437 | 176 | 1362 | 0 | 160 | 81 | 0 | 72 | 16.4 | 0 | 98.96
16:00 | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 270 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 211 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 29 | 0 | 0 | 41 | 40 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 80 | 0 | 90 | 280 | 265 | 162 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 70 | 125 | 0 | 0 | 0.4 | 45 | 60 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 6 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 |  | 176 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 3872.2 | 1412.4 | 5284.6 | 3406 | 176 | 1385 | 0 | 160 | 81 | 0 | 70 | 6.6 | 0 | 98.96
17:00 | 35 | 133 | 0 | 0 | 0 | 12 | 0 | 270 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 210 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 206 | 0 | 105 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 38 | 80 | 0 | 90 | 295 | 285 | 162 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 78 | 125 | 0 | 0 | 0 | 45 | 60 | 5 | 2 | 100 | 0 | 52 | 5 | 0 | 0 | 0 | 7 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 176 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 9 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 368 | 0 | 0 | 5 | 0 | 35 | 0 | 0.1 | 0 |  | 4000 | 1555.1 | 5555.1 | 3512 | 176 | 1458 | 89 | 160 | 82 | 0 | 78 | 0.1 | 0 | 98.95
18:00 | 35 | 134 | 0 | 0 | 0 | 104 | 0 | 341 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 11 | 0 | 0 | 0 | 19 | 25 | 10 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 90 | 0 | 90 | 360 | 320 | 201 | 8 | 0 | 33 | 0 | 0 | 33 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 98 | 156 | 0 | 22 | 0 | 60 | 60 | 53 | 30 | 100 | 0 | 67 | 76 | 0 | 0 | 17 | 34 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 |  | 435 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 117 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 395 | 0 | 0 | 35 | 17 | 40 | 0 | 0 | 0 |  | 5336 | 2025 | 7361 | 4248 | 435 | 1993 | 345 | 160 | 82 | 0 | 98 | 0 | 0 | 98.95
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 372 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 20 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 210 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 100 | 0 | 90 | 350 | 330 | 201 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 160 | 0 | 22 | 0 | 60 | 60 | 53 | 50 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 34 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 117 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 397 | 0 | 0 | 35 | 17 | 38 | 0 | 0 | 0 |  | 5489 | 2055 | 7544 | 4321 | 434 | 2065 | 386 | 160 | 82 | 0 | 96 | 0 | 0 | 98.94
19:30 | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 380 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 23 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 100 | 0 | 90 | 360 | 345 | 200 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 160 | 0 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 33 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 117 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 396 | 0 | 0 | 35 | 17 | 37 | 0 | 0 | 0 |  | 5526 | 2042 | 7568 | 4316 | 434 | 2068 | 408 | 160 | 82 | 0 | 100 | 0 | 0 | 0
20:00 | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 372 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 24 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 100 | 0 | 90 | 355 | 340 | 200 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 160 | 0 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 34 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 117 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 396 | 0 | 0 | 35 | 17 | 38 | 0 | 0 | 0 |  | 5505 | 2046 | 7551 | 4306 | 434 | 2060 | 409 | 160 | 82 | 0 | 100 | 0 | 0 | 99.94
21:00 | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 361 | 338 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 24 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 100 | 0 | 90 | 330 | 310 | 200 | 8 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 98 | 161 | 0 | 22 | 0 | 30 | 60 | 53 | 47 | 130 | 0 | 69 | 76 | 0 | 0 | 17 | 36 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 111 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 390 | 0 | 0 | 35 | 17 | 38 | 0 | 0 | 0 |  | 5390 | 2029 | 7419 | 4195 | 434 | 2051 | 399 | 160 | 82 | 0 | 98 | 0 | 0 | 99.93
22:00 | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 342 | 340 |  | 0 | 400 | 0 | 0 | 0 | 0 | 311 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 100 | 0 | 90 | 330 | 310 | 204 | 8 | 0 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 92 | 162 | 0 | 22 | 0 | 30 | 60 | 53 | 47 | 130 | 0 | 70 | 10 | 0 | 0 | 17 | 36 | 10 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5029 | 1788 | 6817 | 4087 | 434 | 1885 | 77 | 160 | 82 | 0 | 92 | 0 | 0 | 99.93
23:00 | 35 | 134 | 0 | 0 | 0 | 52 | 0 | 344 | 339 |  | 0 | 400 | 0 | 0 | 0 | 0 | 312 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 29 | 0 | 0 | 39 | 40 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 100 | 0 | 90 | 330 | 315 | 205 | 8 | 0 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 86 | 161 | 0 | 0 | 0 | 30 | 60 | 5 | 47 | 130 | 0 | 69 | 10 | 0 | 0 | 0 | 36 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 213 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4752 | 1601 | 6353 | 3990 | 213 | 1765 | 60 | 160 | 79 | 0 | 86 | 0 | 0 | 99.92
24:00 | 35 | 133 | 0 | 0 | 0 | 12 | 0 | 350 | 339 |  | 0 | 400 | 0 | 0 | 0 | 0 | 312 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 38 | 40 | 120 | 0 | 0 | 191 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 0 | 0 | 260 | 285 | 205 | 8 | 0 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 161 | 0 | 0 | 0 | 30 | 60 | 5 | 47 | 130 | 0 | 69 | 76 | 0 | 0 | 0 | 37 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 190 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 161 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4506 | 1538 | 6044 | 3732 | 190 | 1787 | 16 | 161 | 78 | 0 | 80 | 0 | 0 | 99.92
KWH | 870000 | 3478500 | 0 | 0 | 0 | 763181 | 0 | 8238080 | 7312000 |  | 0 | 8250000 | 0 | 0 | 0 | 0 | 6049003 | 0 | 1246000 | 0 | 0 | 0 | 0 | 0 | 20160 | 0 | 137376 | 0 | 0 | 0 | 72288 | 600000 | 508320 | 730500 | 774100 | 0 | 0 | 975273 | 964000 | 2600000 | 0 | 0 | 4895324 | 0 | 2855337 | 0 |  | 0 | 0 | 0 | 53280 | 0 | 0 | 303072 | 766080 | 2125490 | 0 | 1662988 | 7463000 | 7087000 | 4308000 | 200727 | 0 | 339408 | 0 | 0 | 364928 | 0 | 0 | 0 | 130248 | 48600 | 174700 | 477410 | 1862400 | 3452000 | 0 | 149004 | 13300 | 1005000 | 1429200 | 369600 | 430560 | 2973649 | 0 | 1292544 | 498240 | 0 | 0 | 98000 | 382540 | 79920 | 7584750 | 121275 | 48240 | 0 | 0 | 0 | 0 | 232800 | 0 | 0 | 125550 | 0 | 0 | 0 | 8772000 | 0 | 0 | 551999 | 27720 | 0 | 0 | 0 | 0 |  | 4870545 | 0 | 5392224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98250 | 2669000 | 449400 | 304030 | 0 | 0 | 0 | 0 | 0 | 0 | 186620 | 0 | 0 | 0 | 0 | 110160 | 87588 | 225648 | 0 | 0 | 3896300 | 0 | 0 | 4725282 | 0 | 0 | 0 | 0 | 0 | 4813118 | 0 | 9162363 | 0 | 0 | 158208 | 65376 | 204480 | 0 | 30994 | 0 |  | 108344664 | 37449586 | 145794250 | 91229903 | 4870545 | 39785686 | 2012579 | 3896300 | 1939273 | 0 | 1862400 | 197564 | 0
Fuel Cost | 974400 | 3756780 | 0 | 0 | 0 | 740285.57 | 0 | 5931417.6 | 5557120 |  | 0 | 6600000 | 0 | 0 | 0 | 0 | 7500763.72 | 0 | 1557500 | 0 | 0 | 0 | 0 | 0 | 183456 | 0 | 1285839.36 | 0 | 0 | 0 | 54216 | 450000 | 0 | 0 | 0 | 0 | 0 | 253570.98 | 250640 | 3978000 | 0 | 0 | 5140090.2 | 0 | 3626277.99 | 0 |  | 0 | 0 | 0 | 548251.2 | 0 | 0 | 278826.24 | 2129702.4 | 2231764.5 | 0 | 1746137.4 | 5522620 | 5953080 | 3963360 | 196712.46 | 0 | 278314.56 | 0 | 0 | 521847.04 | 0 | 0 | 0 | 132852.96 | 36450 | 330183 | 358057.5 | 12850560 | 2830640 | 0 | 151984.08 | 218120 | 1366800 | 1943712 | 502656 | 538200 | 3687324.76 | 0 | 1925890.56 | 876902.4 | 0 | 0 | 155820 | 447571.8 | 187812 | 5385172.5 | 90956.25 | 36662.4 | 0 | 0 | 0 | 0 | 2239536 | 0 | 0 | 1448847 | 0 | 0 | 0 | 8245680 | 0 | 0 | 5216390.55 | 0 | 0 | 0 | 0 | 0 |  | 13150471.5 | 0 | 4205934.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 971692.5 | 2135200 | 696570 | 3265282.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1935249.4 | 0 | 0 | 0 | 0 | 121176 | 144520.2 | 170815.536 | 0 | 0 | 15935867 | 0 | 0 | 4158248.16 | 0 | 0 | 0 | 0 | 0 | 4235543.84 | 0 | 6688524.99 | 0 | 0 | 1452349.44 | 582500.16 | 1909843.2 | 0 | 0 | 0 |  | 122415754.98 | 61759788.846 | 184175543.826 | 85454979.216 | 13150471.5 | 35022098.12 | 19590390.01 | 15935867 | 504210.98 | 0 | 12850560 | 1666967 | 0
Yesterday Day Peak | 35 | 134 | 0 | 0 | 0 | 0 | 0 | 302 | 280 |  | 0 | 320 | 0 | 0 | 0 | 0 | 230 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 28 | 31 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 215 | 0 | 111 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 80 | 0 | 80 | 370 | 310 | 160 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 154 | 0 | 0 | 2.1 | 40 | 60 | 5 | 2 | 100 | 0 | 51 | 5 | 0 | 0 | 0 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 |  | 175 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0 |  | 5734.3 | DayPeak
Yesterday Evening Peak | 35 | 134 | 0 | 0 | 0 | 110 | 0 | 380 | 330 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 23 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 39 | 100 | 0 | 90 | 360 | 345 | 200 | 8 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 160 | 0 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 0 | 68 | 76 | 0 | 0 | 17 | 33 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 117 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 396 | 0 | 0 | 35 | 17 | 37 | 0 | 0 | 0 |  | 7568 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 120 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 15 | 120 | 0 | 0 | 360 | 360 | 0 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 127 | 160 | 95 | 22 | 0 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 0 |  | 537 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 26 | 110 | 30 | 0 | 71 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 200 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 150 | 0 | 0 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 240 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 50 | 120 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 10 | 120 | 0 | 0 | 360 | 360 | 0 | 45 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 102 | 170 | 95 | 22 | 1.6 | 60 | 62 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 90 | 105 | 5 | 230 | 54 | 50 | 0 |  | 191 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 70 | 0 | 0 | 71 | 0 | 0 | 80 | 50 | 42 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 20 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 134 | 0 | 0 | 0 | 12 | 0 | 370 | 370 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 240 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 23 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 215 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 0 | 310 | 260 | 0 | 8 | 0 | 20 | 0 | 0 | 5 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 74 | 172 | 0 | 20 | 0.4 | 25 | 36 | 53 | 35 | 163 | 0 | 69 | 10 | 0 | 0 | 17 | 35 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.9 | 0 | 0 | 142 | 395 | 0 | 0 | 0 | 1.611 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0
199
| Minimum Generation |  | 5302.4 | 9:00
| Highest Generation |  | 7568 | 19:30
| Day Peak Generation |  | 5734.3 | 12:00
| Evening Peak Generation |  | 7568 | 19:30
| HVDC Max Flow |  | 435 | 18:00
| HVDC EvPeak Flow |  | 434 | 19:30
| Load factor L.F |  | 80.27%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-07
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5734.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4858 | MW
Evening Peak Generation : |  | 7568 | MW Hour : | 19:30 | Available Max Generation : |  | 13883 | MW
E.P. Demand (at gen end) : |  | 7568 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 7568 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5383 | MW
Total Gen. (MKWH) : |  | 145.7943 | System Load Factor : | 80.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -403 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-07
Actual : | 98.89 | Ft.(MSL) , | Rule curve : | 105.46 | Ft.( MSL )
Gas Consumed : | Total = | 1035.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120477077.336
: |  | Coal : | 15935867 | Oil : | 19590390.01 | Total : | 156003334.346
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3030.4714 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1023.8763 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 916.174 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 827.4197 |  |  | 0 | 0%
) | 0 | 0:00 | 747.9592 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 603.5598 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 346.0407 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 155.627 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 465.4544 |  |  | 0 | 0%
Total | 0 |  | 8116.5824 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj unit-5
|  |  |  | 2) Sylhet-150 MW. | 11) Ashuganj 225 MW CCPP
3) Ghorasal Unit-2,4
4) Ashuganj unit-4
5) Chandpur CCPP ST
6) Sylhet 150 MW
7) Sirajganj unit-2
8) Ashuganj Precision
9) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sherpur (Mymensingh) 132/33 kV T4 transformer was under shut down from 08:10 to 09:15 for D/W.
b) Sherpur (Mymensingh) 132 kV Bus-A was under shut down from 08:05 to 09:10 for D/W.
c) Sherpur (Mymensingh) 132 kV Bus-B was under shut down from 09:35 to 10:45 for D/W.
d) Jhenaidah-Chuadanga 132 kV Ckt was under shut down from 07:03 to 13:03 for A/M.
e) Patuakhali 132/33 kV T-3 transformer was shut down at 09:11 for A/M.
f) Gopalganj 400/132 kV T1 & T2 transformers were under shut down from 11:33 to 15:07 for
project work.
g) Kabirpur 132/33 kV T1 transformer tripped at 08:40 due to 33 kV feeder fault and was switched |  |  |  |  | About 10 MW power interruption occurred under Kabirpur S/S area
on at 10:30. |  |  |  |  | from 08:40 to 10:30.
h) Kabirpur 132/33 kV T2 & T3 transformers were shut down at 07:16 due to PBS work and were
switched on at 10:30,10:31 respectively.
i) Madunaghat-Khulshi 132 kV Ckt-1 was switched on at 17:05.
j) Ashuganj 225 MW CCPP ST was shut down at 00:38(07/12/2019) due to HGPI.
k) Ashuganj 225 MW CCPP GT was shut down at 00:47(07/12/2019) due to HGPI.
l) Ashuganj Unit-5 tripped at 23:13 due to tripping of boiler.
m) Hasnabad-Kamrangirchar 132 kV Ckt tripped at 03:19(07/12/2019) from Hasnabad end showing |  |  |  |  | About 35 MW power interruption occurred under Hasnabad S/S area
Dist. Z1 C-phase relay and was switched on at 03:38(07/12/2019). |  |  |  |  | from 03:19 to 03:28(07/12/2019).
n) Siddhirganj-Maniknagar 230 kV Ckt-2 was shut down at 07:09 (07/12/19) for A/M.
o) Ghorasal-Ashuganj(S) 230 kV Ckt-1 was shut down at 07:30 (07/12/19) for A/M.
p) Goalpara-Khulna© 132 kV Ckt-1 was shut down at 07:06 (07/12/19) for A/M.
q) Rampura-Bashundhara 132 kV Ckt-2 was shut down at 07:38 (07/12/19) for A/M.
r) Jhenaidah 132/33 kV T1 transformer was shut down at 07:31 (07/12/19) for A/M.
s) Saidpur 132 kV Bus-A of 132/33 kV T4 transformer were shut down at 07:20 (07/12/19) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 870000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 134 | 3478500
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 763181
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 380 | 8238080 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 330 | 7312000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8250000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 72288
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 67 | 1246000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6049003 | Gas shortage.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 24 | 137376 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 20160 | Low demand
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 48 | 1108320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 730500 | Machine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 774100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1909 | 39049508
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 125550
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1939273 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 216 | 4895324 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 2855337 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 551999
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 53280 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 303072
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 39 | 766080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27720
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 731 | 14117635
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2125490 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 1662988 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4308000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7463000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 7087000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 339408 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 364928 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 130248
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 48600
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 1862400
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 174700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 477410 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1365 | 26244899
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 160 | 3452000 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 149004
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13300
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 232800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 232 | 3847104
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 1005000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1429200
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2973649 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 369600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 430560
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 48240
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 68 | 1292544 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 498240 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 98000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 33 | 382540 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 121275
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 7584750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 397 | 8772000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 79920
| Sylhet Area Total |  |  |  | 1949 | 1289 | 25085518
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 434 | 4870545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 5392224 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 98250 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 17 | 65376 | Low demand
| Khulna Area Total |  |  |  | 2314 | 720 | 10426395
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 304030 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 24 | 449400 | Machine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 117 | 2669000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0
| Barisal Area Total |  |  |  | 462 | 189 | 3422430
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 186620
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4725282 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 4813118 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 396 | 9162363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 110160
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 87588
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225648
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 158208 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 936 | 19468987
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3896300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 37 | 204480 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30994
| Rangpur Area Total |  |  |  | 605 | 197 | 4131774
| Total |  |  |  | 19047 | 7568 | 145794250
| Eastern Grid Total |  |  |  | 13483 | 5526 | 108344664
| Western Grid Total |  |  |  | 5564 | 2042 | 37449586
| National Grid Total |  |  |  | 19047 | 7568 | 145794250
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-06
(a) ENTIRE EASTERN GRID : |  | 4921 | MW | (b) ENTIRE WESTERN GRID : |  | 2296 | MW
i) Dhaka area |  | 2519 | MW | i) Khulna area |  | 881 | MW
ii) Chittagong area |  | 825 | MW | ii) Rajshahi area |  | 751 | MW
iii) Comilla area |  | 673 | MW | iii) Barisal area |  | 213 | MW
iv) Mymensingh area |  | 594 | MW | iv) Rangpur area |  | 451 | MW
v) Sylhet area |  | 310 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7217 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 82 | 0.75 | Shahjibazar | 79 | 19:30 | Bottail | 82 | 18:00
Munsiganj | 72 | 0.875 | Fenchuganj | 23 | 18:00 | G.K Project | 23 | 18:30
Sonargaon | 66 | 0.41667 | Kulawara | 29 | 18:00 | Faridpur | 110 | 19:00
Shyampur | 180 | 0.041667 | Sylhet | 84 | 20:00 | Madaripur | 55 | 21:00
Bhulta | 147 | 0.041667 | Chatak | 17 | 18:00 | Sariatpur | 36 | 19:30
Madanganj | 45 | 0.45833 | Sunamganj | 27 | 18:30 | Gopalganj | 61 | 18:00
Shitalakhya | 65 | 0.041667 | Biani Bazar | 31 | 19:00 | Bagerhat | 57 | 19:30
Rahim steel | 17 | 0.91667 | Comilla (S) | 100 | 19:30 | Mongla | 26 | 1:00
Matuail | 70 | 0.041667 | Comilla(N) | 63 | 19:30 | Satkhira | 59 | 18:30
Ghorasal | 55 | 0.83333 | Chandpur | 64 | 20:00 | Gallamari | 34 | 1:00
Narsingdi | 104 | 0.875 | Feni | 84 | 18:00 | Magura | 34 | 18:00
Haripur (SBU) | 71 | 0.041667 | Chowmuhani | 114 | 18:30 | Norail | 24 | 18:00
Ullon | 50 | 0.75 | Ashuganj | 35 | 19:00 | Chuadanga | 59 | 18:30
Hasnabad | 126 | 0.8125 | Daudkandi | 86 | 20:00 | Barisal(N) | 28 | 19:00
Magbazar | 65 | 0.79167 | B.Baria | 86 | 19:30 | Barisal (S) | 60 | 21:00
Maniknagar | 64 | 0.54167 | Ramganj | 42 | 19:30 | Patuakhali | 73 | 21:00
Bangabhaban | 10 | 0.45833 | Chaddagram | 6 | 17:00 | Bhandaria | 36 | 19:00
Narinda | 60 | 0.5 | PHP | 0 | 7:00 | Borhan Uddin | 23 | 21:00
Dhanmondi | 87 | 0.75 | Madunaghat | 35 | 18:00 | Ishurdi | 39 | 18:30
Lalbag | 43 | 0.041667 | Hathazari | 61 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 46 | 0.91667 | Khulshi | 139 | 12:00 | Natore | 74 | 18:00
Mirpur | 67 | 0.75 | Halishahar | 89 | 19:30 | Bogra | 133 | 18:30
Kalyanpur | 66 | 0.75 | Baraulia | 111 | 19:00 | Noagaon | 73 | 18:30
Gulshan | 88 | 0.75 | Sikalbaha | 25 | 18:00 | Rajshahi | 81 | 19:00
Uttara | 0 | 0.75 | Dohazari | 62 | 18:00 | Rajshahi New | 6 | 18:00
Uttara New | 27 | 0.75 | Cox'sbazar | 65 | 18:00 | C.Nawabganj | 46 | 20:00
Kamrangirchar | 46 | 0.75 | Chandraghona | 22 | 18:00 | Amnura | 22 | 18:00
Savar | 72 | 0.75 | Kaptai | 3.5 | 18:00 | Pabna | 60 | 19:30
Bhasantec | 107 | 0.75 | A. Khaer Stl. | 7 | 19:30 | Shahjadpur | 68 | 18:30
Agargaon | 34 | 0.75 | Bakulia | 61 | 18:30 | Serajganj | 49 | 18:00
Satmosjid | 71 | 0.54167 | Julda | 17 | 12:00 | Niyamatpur | 41 | 19:30
Tongi | 100 | 0.54167 | TK chemical | 2 | 1:00 | Joypurhat | 45 | 18:30
Kabirpur | 95 | 0.5 | Modern Steel | 11 | 1:00 | Sherpur(Bogura) | 33 | 18:00
Basundhara | 83 | 0.77083 | Shahmirpur | 19 | 1:00 | Mohastangor | 10 | 18:00
Manikganj | 52 | 0.77083 | Khagrachhari | 12 | 18:30 | Rangpur | 89 | 19:00
Joydevpur | 136 | 0.83333 | Matarbari | 21 | 18:00 | Lalmonirhat | 40 | 18:00
New Tongi | 57 | 0.5 | Baroiar Hat | 16 | 18:00 | Saidpur | 70 | 19:00
Korda | 131 | 0.83333 | Rangamati | 8 | 18:00 | Purbasadipur | 58 | 7:00
Dhamrai | 40 | 0.75 | Abul Khair 230 | 84 | 1:00 | Thakurgaon | 35 | 7:00
Valuka | 66 | 0.75 | BSRM | 106 | 13:00 | Palashbari | 82 | 18:00
Tangail | 124 | 0.8125 | GPH Ispat | 4 | 2:00 | Barapukuria | 35 | 19:30
Mymensing | 141 | 0.75 | Goalpara | 14 | 13:00 | Panchagar | 24 | 17:00
Kishorganj | 72 | 0.83333 | Central s/s | 54 | 19:00 | Joldhaka | 18 | 18:00
Netrokona | 66 | 0.79167 | Noapara | 36 | 18:00 | Kurigram | 40 | 18:00
Jamalpur | 85 | 0.75 | Jessore | 76 | 18:00
Sherpur | 60 | 0.83333 | Benapol | 26 | 18:00
Srimongal | 24 | 0.77083 | Jhenida | 73 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-06 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 391 | 0.375 | 384 | 0.5 | Kaliakoir | 372 | 0.16667 | 365 | 0.875
Bheramara | 409 | 0.041667 | 397 | 0.77083 | Bhulta | 388 | 0.54167 | 384 | 0.5
Ashuganj(N) | 393 | 0.91667 | 388 | 0.58333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 0.29167 | 228 | 0.041667 | Hathazari | 221 | 0.33333 | 217 | 0.041667
Ishurdi | 241 | 0.20833 | 227 | 0.75 | Megnaghat | 223 | 0.33333 | 219 | 0.8125
Ashuganj | 236 | 0.125 | 232 | 0.54167 | Fenchuganj | 236 | 0.91667 | 231 | 0.45833
Serajganj | 234 | 0.20833 | 228 | 0.75 | Siddhirganj | 225 | 0.375 | 223 | 0.041667
Baghabari | 240 | 0.125 | 233 | 0.77083 | Maniknagar | 224 | 24:00 | 221 | 0.5
Barapukuria | 231 | 0.16667 | 226 | 0.75 | Old Airport | 222 | 0.16667 | 219 | 0.5
Bogra | 233 | 0.125 | 225 | 0.75 | Barisal | 232 | 0.95833 | 223 | 0.54167
Khulna South | 237 | 0.125 | 215 | 0.75 | AKSML | 218 | 0.375 | 211 | 0.125
Rampura | 225 | 0.16667 | 222 | 0.45833 | BSRM | 219 | 0.16667 | 214 | 0.5
Haripur | 223 | 0.29167 | 220 | 0.041667 | Bibiyana | 232 | 0.375 | 228 | 0.70833
Hasnabad | 224 | 0.16667 | 220 | 0.041667 | Bhulta | 225 | 0.16667 | 223 | 0.45833
Aminbazar | 224 | 24:00 | 221 | 0.041667 | Ashuganj (S) | 232 | 0.16667 | 230 | 0.375
Tongi | 219 | 24:00 | 216 | 0.041667 | Kaliakoir | 227 | 0.20833 | 221 | 0.875
Comilla (N) | 230 | 0.25 | 226 | 0.5 | GPH | 218 | 0.16667 | 213 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 8:00 | 134 | 1:00 | Halishahar | 130 | 2:00 | 128 | 12:00
Munsiganj | 134 | 5:00 | 132 | 1:00 | Baraulia | 130 | 9:00 | 127 | 19:00
Sonargaon | 134 | 15:00 | 130 | 5:00 | Sikalbaha | 130 | 4:00 | 128 | 12:00
Shyampur | 137 | 8:00 | 134 | 1:00 | Dohazari | 130 | 7:00 | 126 | 13:00
Bhulta | 130 | 5:00 | 128 | 1:00 | Cox'sbazar | 127 | 9:00 | 120 | 18:00
Madanganj | 137 | 14:00 | 132 | 1:00 | Chandraghona | 132 | 8:00 | 129 | 18:00
Shitalakhya | 138 | 14:00 | 134 | 12:00 | Kaptai | 132 | 1:00 | 130 | 7:00
Rahim steal | 136 | 4:00 | 134 | 1:00 | A. Khaer Stl. | 131 | 3:00 | 127 | 16:00
Matuail | 135 | 7:00 | 132 | 1:00 | Bakulia | 129 | 3:00 | 126 | 12:00
Ghorasal | 137 | 9:00 | 135 | 1:00 | Julda | 129 | 1:00 | 127 | 18:00
Narsinghdi | 134 | 9:00 | 131 | 18:00 | TK Chemical | 130 | 1:00 | 129 | 3:00
Haripur (SBU) | 136 | 9:00 | 132 | 1:00 | Modern Steel | 129 | 4:00 | 127 | 13:00
Ullon | 135 | 5:00 | 131 | 11:00 | Shahmirpur | 129 | 7:00 | 127 | 12:00
Hasnabad | 137 | 13:00 | 135 | 9:00 | Khagrachhari | 131 | 5:00 | 129 | 12:00
Magbazar | 135 | 6:00 | 132 | 11:00 | Matarbari | 130 | 9:00 | 121 | 18:00
Maniknagar | 138 | 9:00 | 136 | 11:00 | Baroiar Hat | 130 | 7:00 | 128 | 18:00
Bangabhaban | 138 | 9:00 | 136 | 11:00 | Rangamati | 131 | 9:00 | 129 | 12:00
Narinda | 138 | 9:00 | 136 | 11:00 | Goalpara | 135 | 3:00 | 125 | 18:00
Dhanmondi | 135 | 5:00 | 131 | 11:00 | Central s/s | 136 | 1:00 | 125 | 18:0
Lalbag | 138 | 14:00 | 134 | 12:00 | Noapara | 134 | 1:00 | 123 | 18:00
Madartek | 135 | 4:00 | 131 | 12:00 | Jessore | 132 | 6:00 | 120 | 18:00
Mirpur | 136 | 2:00 | 134 | 12:00 | Benapol | 133 | 2:00 | 121 | 18:00
Kalyanpur | 138 | 3:00 | 136 | 12:00 | Jhenida | 134 | 3:00 | 120 | 19:00
Gulshan | 133 | 2:00 | 131 | 12:00 | Bottail | 135 | 5:00 | 125 | 18:00
Uttara | 133 | 4:00 | 130 | 12:00 | G.K Project | 140 | 2:00 | 133 | 18:00
Uttara New | 135 | 2:00 | 133 | 12:00 | Faridpur | 134 | 6:00 | 125 | 18:00
Kamrangirchar | 137 | 7:00 | 134 | 12:00 | Madaripur | 132 | 9:00 | 125 | 19:30
Savar | 135 | 3:00 | 132 | 12:00 | Sariatpur | 133 | 23:00 | 126 | 13:00
Bhasantec | 135 | 4:00 | 132 | 12:00 | Gopalganj | 137 | 23:00 | 129 | 18:00
Agargaon | 135 | 3:00 | 133 | 12:00 | Bagerhat | 135 | 4:00 | 122 | 18:30
Satmosjid | 135 | 4:00 | 132 | 12:00 | Mongla | 133 | 3:00 | 122 | 19:30
Tongi | 135 | 24:00 | 131 | 13:00 | Satkhira | 136 | 5:00 | 123 | 18:30
Kabirpur | 133 | 24:00 | 128 | 10:00 | Gallamari | 139 | 3:00 | 125 | 18:00
Basundhara | 133 | 23:00 | 129 | 12:00 | Magura | 135 | 4:00 | 118 | 18:00
Manikganj | 138 | 3:00 | 133 | 18:00 | Norail | 134 | 4:00 | 118 | 18:30
Joydevpur | 135 | 24:00 | 132 | 21:00 | Chuadanga | 131 | 2:00 | 115 | 18:30
New Tongi | 134 | 24:00 | 129 | 13:00 | Barisal(N) | 135 | 3:00 | 129 | 13:00
Kodda | 133 | 24:00 | 127 | 5:00 | Barisal (S) | 134 | 3:00 | 127 | 13:00
Dhamrai | 132 | 24:00 | 128 | 12:00 | Patuakhali | 134 | 6:00 | 125 | 13:00
Valuka | 130 | 5:00 | 121 | 18:00 | Bhandaria | 134 | 2:00 | 125 | 18:00
Tangail | 132 | 4:00 | 125 | 18:30 | Ishurdi | 137 | 3:00 | 130 | 18:00
Mymensing | 131 | 6:00 | 122 | 18:00 | Ruppur Paromanobik | 136 | 6:00 | 131 | 20:00
Kishorganj | 132 | 4:00 | 127 | 19:30 | Natore | 135 | 4:00 | 129 | 18:00
Netrokona | 131 | 5:00 | 121 | 18:00 | Bogra | 137 | 2:00 | 131 | 18:00
Jamalpur | 129 | 5:00 | 122 | 18:00 | Noagaon | 134 | 3:00 | 127 | 18:00
Sherpur | 127 | 4:00 | 119 | 22:00 | Rajshahi | 132 | 1:00 | 127 | 12:00
Srimongal | 136 | 1:00 | 135 | 8:00 | Rajshahi New | 133 | 5:00 | 125 | 12:00
Shahjibazar | 135 | 5:00 | 133 | 1:00 | C.Nawabganj | 131 | 17:00 | 125 | 7:00
Fenchuganj | 136 | 21:00 | 132 | 12:00 | Amnura | 131 | 13:00 | 125 | 11:00
Khulawara | 135 | 22:00 | 132 | 10:00 | Pabna | 138 | 3:00 | 131 | 18:00
Sylhet | 134 | 21:00 | 130 | 12:00 | Shahjadpur | 142 | 14:00 | 136 | 18:00
Chatak | 134 | 24:00 | 129 | 12:00 | Serajganj | 136 | 1:00 | 132 | 18:30
Sunamganj | 133 | 1:00 | 129 | 12:00 | Niyamatpur | 134 | 3:00 | 124 | 18:00
Biani Bazar | 134 | 1:00 | 130 | 12:00 | Joypurhat | 135 | 3:00 | 126 | 18:00
Comilla(s) | 130 | 24:00 | 126 | 13:00 | Sherpur(Bogura) | 138 | 5:00 | 131 | 18:00
Comilla(n) | 136 | 7:00 | 133 | 15:00 | Mohastangor | 136 | 3:00 | 130 | 18:00
Chandpur | 135 | 10:00 | 130 | 19:00 | Rangpur | 130 | 3:00 | 124 | 18:00
Feni | 130 | 8:00 | 126 | 13:00 | Lalmonirhat | 126 | 14:00 | 120 | 18:00
Chowmuhani | 129 | 8:00 | 125 | 12:00 | Saidpur | 129 | 4:00 | 124 | 8:00
Ashuganj | 136 | 7:00 | 134 | 19:00 | Purbasadipur | 126 | 7:00 | 120 | 19:30
Daudkandi | 134 | 7:00 | 131 | 18:00 | Thakurgaon | 123 | 2:00 | 118 | 8:00
B.Baria | 134 | 8:00 | 132 | 22:00 | Palashbari | 131 | 5:00 | 126 | 18:00
Ramganj | 127 | 10:00 | 123 | 21:00 | Barapukuria | 131 | 4:00 | 126 | 18:00
Chaddagram | 131 | 4:00 | 129 | 20:00 | Panchagar | 122 | 5:00 | 114 | 18:00
PHP | 129 | 9:00 | 126 | 18:00 | Joldhaka | 128 | 5:00 | 121 | 18:00
Madanhat | 133 | 7:00 | 130 | 13:00 | Kurigram | 130 | 3:00 | 121 | 18:00
Hathazari | 132 | 4:00 | 130 | 12:00
Khulshi | 128 | 1:00 | 126 | 11:00

## L-Curve
Date | 2019-12-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 196 | 4506 | 1538 | 6044 |  |  |  | QF-LDC-12
0:30 | 285.5 | 4573 | 1436 | 6009 | Date: | 2019-12-06
1:00 | 375 | 4640 | 1334 | 5974
1:30 | 332.5 | 4515 | 1336.5 | 5851.5
2:00 | 290 | 4390 | 1339 | 5729
2:30 | 247.5 | 4321 | 1338 | 5659 | [5 empty] | Gen. at Eve. Peak | 7568 | 7568 MW (19:30 )
3:00 | 205 | 4252 | 1337 | 5589 | [6 empty] | 19:30
3:30 | 158.5 | 4164.5 | 1332.5 | 5497 | [5 empty] | Gen. at Day Peak | 5734.3 | 5734.3 MW (12:00 )
4:00 | 112 | 4077 | 1328 | 5405 | [6 empty] | 12:00
4:30 | 116 | 4025 | 1346.5 | 5371.5 | [5 empty] | Highest Generation | 7568
5:00 | 120 | 3973 | 1365 | 5338 | [6 empty] | 19:30
5:30 | 147.5 | 4017 | 1368 | 5385
6:00 | 175 | 4061 | 1371 | 5432
6:30 | 200.5 | 4036.3 | 1370.55 | 5406.85
7:00 | 226 | 4011.6 | 1370.1 | 5381.7
7:30 | 303 | 4057 | 1357.15 | 5414.15
8:00 | 380 | 4102.4 | 1344.2 | 5446.6
8:30 | 343.5 | 4070.35 | 1304.15 | 5374.5
9:00 | 307 | 4038.3 | 1264.1 | 5302.4
9:30 | 223.5 | 3995.1 | 1276.65 | 5271.75
10:00 | 140 | 3951.9 | 1289.2 | 5241.1
10:30 | 122.5 | 3991.05 | 1319.3 | 5310.35
11:00 | 105 | 4030.2 | 1349.4 | 5379.6
11:30 | 92.5 | 4130.35 | 1426.6 | 5556.95
12:00 | 80 | 4230.5 | 1503.8 | 5734.3
12:30 | 112.5 | 4305.9 | 1505.15 | 5811.05
13:00 | 145 | 4381.3 | 1506.5 | 5887.8
13:30 | 82.5 | 4197.05 | 1468.95 | 5666
14:00 | 20 | 4012.8 | 1431.4 | 5444.2
14:30 | 21.5 | 3970.5 | 1403.8 | 5374.3
15:00 | 23 | 3928.2 | 1376.2 | 5304.4
15:30 | 14 | 3900.2 | 1394.3 | 5294.5
16:00 | 5 | 3872.2 | 1412.4 | 5284.6
16:30 | 9 | 3936.1 | 1483.75 | 5419.85
17:00 | 13 | 4000 | 1555.1 | 5555.1
17:30 | 208 | 4668 | 1790.05 | 6458.05
18:00 | 403 | 5336 | 2025 | 7361
18:30 | 383 | 5412.5 | 2040 | 7452.5
19:00 | 363 | 5489 | 2055 | 7544
19:30 | 361 | 5526 | 2042 | 7568
20:00 | 361 | 5505 | 2046 | 7551 |  |  |  | Executive Engineer
20:30 | 334 | 5447.5 | 2037.5 | 7485 |  |  |  | Network Operation Division
21:00 | 307 | 5390 | 2029 | 7419
21:30 | 301 | 5209.5 | 1908.5 | 7118
22:00 | 295 | 5029 | 1788 | 6817 |  |  |  |  | Page 6 of 7
22:30 | 289 | 4890.5 | 1694.5 | 6585
23:00 | 283 | 4752 | 1601 | 6353
23:30 | 239.5 | 4629 | 1569.5 | 6198.5
24:00 | 196 | 4506 | 1538 | 6044
7568 MW (19:30 )
5734.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-06 |  | Energy | 145794250
[10 empty] | 2019-12-06 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3732 | 190 | 1787 | 60 | 161 | 78 | 0 | 0 | 80
0:30 | 3774 | 147.5 | 1757 | 33 | 160.5 | 80 | 0 | 0 | 79 | Date: | 2019-12-06
1:00 | 3816 | 105 | 1727 | 6 | 160 | 82 | 0 | 0 | 78
1:30 | 3762.5 | 104.5 | 1663.5 | 3 | 160 | 82 | 0 | 0 | 76 | [7 empty] | Total Energy | 145.7943 | Total Energy Gen 145.794 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 145.794 MKWHr
2:00 | 3709 | 104 | 1600 | 0 | 160 | 82 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3664.5 | 104.5 | 1575 | 0 | 160 | 82 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 145.7943
3:00 | 3620 | 105 | 1550 | 0 | 160 | 82 | 0 | 0 | 72
3:30 | 3539.5 | 104.5 | 1539.5 | 0 | 160 | 82.5 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3459 | 104 | 1529 | 0 | 160 | 83 | 0 | 0 | 70
4:30 | 3460.5 | 104.5 | 1493.5 | 0 | 160 | 83 | 0 | 0 | 70
5:00 | 3462 | 105 | 1458 | 0 | 160 | 83 | 0 | 0 | 70
5:30 | 3504 | 104.5 | 1464.5 | 0 | 160 | 83 | 0 | 0 | 69
6:00 | 3546 | 104 | 1471 | 0 | 160 | 83 | 0 | 0 | 68
6:30 | 3524 | 104 | 1469 | 0 | 159.5 | 82 | 0 | 0 | 67 |  |  |  |  | Coal
7:00 | 3502 | 104 | 1467 | 0 | 159 | 81 | 0 | 0 | 66
7:30 | 3525 | 104 | 1459.5 | 13 | 159.5 | 80.5 | 0 | 0 | 65 |  |  |  | Oil |  |  |  | ,
8:00 | 3548 | 104 | 1452 | 26 | 160 | 80 | 0 | 0 | 64
8:30 | 3530 | 104 | 1399 | 21.5 | 159.5 | 79.5 | 0 | 0 | 64
9:00 | 3512 | 104 | 1346 | 17 | 159 | 79 | 0 | 0 | 64
9:30 | 3473 | 104 | 1353 | 17 | 159.5 | 79 | 0 | 0 | 62
10:00 | 3434 | 104 | 1360 | 17 | 160 | 79 | 0 | 0 | 60
10:30 | 3488.5 | 104.5 | 1371 | 17 | 160 | 78.5 | 0 | 0 | 62
11:00 | 3543 | 105 | 1382 | 17 | 160 | 78 | 0 | 0 | 64
11:30 | 3628.5 | 140 | 1445 | 8.5 | 160 | 78 | 0 | 0 | 67
12:00 | 3714 | 175 | 1508 | 0 | 160 | 78 | 0 | 0 | 70
12:30 | 3715 | 175 | 1576 | 0 | 160 | 78.5 | 0 | 0 | 76.5
13:00 | 3716 | 175 | 1644 | 0 | 160 | 79 | 0 | 0 | 83
13:30 | 3716 | 175 | 1644 | 0 | 160 | 79 | 0 | 0 | 83
14:00 | 3716 | 175 | 1644 | 0 | 160 | 79 | 0 | 0 | 83
14:30 | 3576.5 | 175.5 | 1503 | 0 | 160 | 80 | 0 | 0 | 77.5
15:00 | 3437 | 176 | 1362 | 0 | 160 | 81 | 0 | 0 | 72
15:30 | 3421.5 | 176 | 1373.5 | 0 | 160 | 81 | 0 | 0 | 71
16:00 | 3406 | 176 | 1385 | 0 | 160 | 81 | 0 | 0 | 70
16:30 | 3459 | 176 | 1421.5 | 44.5 | 160 | 81.5 | 0 | 0 | 74
17:00 | 3512 | 176 | 1458 | 89 | 160 | 82 | 0 | 0 | 78
17:30 | 3880 | 305.5 | 1725.5 | 217 | 160 | 82 | 0 | 0 | 88
18:00 | 4248 | 435 | 1993 | 345 | 160 | 82 | 0 | 0 | 98
18:30 | 4284.5 | 434.5 | 2029 | 365.5 | 160 | 82 | 0 | 0 | 97
19:00 | 4321 | 434 | 2065 | 386 | 160 | 82 | 0 | 0 | 96
19:30 | 4316 | 434 | 2068 | 408 | 160 | 82 | 0 | 0 | 100
20:00 | 4306 | 434 | 2060 | 409 | 160 | 82 | 0 | 0 | 100
20:30 | 4250.5 | 434 | 2055.5 | 404 | 160 | 82 | 0 | 0 | 99
21:00 | 4195 | 434 | 2051 | 399 | 160 | 82 | 0 | 0 | 98
21:30 | 4141 | 434 | 1968 | 238 | 160 | 82 | 0 | 0 | 95
22:00 | 4087 | 434 | 1885 | 77 | 160 | 82 | 0 | 0 | 92
22:30 | 4038.5 | 323.5 | 1825 | 68.5 | 160 | 80.5 | 0 | 0 | 89
23:00 | 3990 | 213 | 1765 | 60 | 160 | 79 | 0 | 0 | 86
23:30 | 3861 | 201.5 | 1776 | 60 | 160.5 | 78.5 | 0 | 0 | 83 | Max Temp. in Dhaka |  | 30.8° C
24:00 | 3732 | 190 | 1787 | 60 | 161 | 78 | 0 | 0 | 80
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 145.794 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 145.794 MKWHr
Note on W13: Author:

## Generation
2019-12-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 43 | 43 | 43 | 41 | 40 | 39 | 39 | 38 | 38 | 39 | 39 | 41 | 41 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 39 | 38 | 975273
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.2 | 9.1 | 13.9 | 17.2 | 18.9 | 17.2 | 18 | 12 | 10 | 4 | 0 | [9 empty] | 125550
6 | Sikalbaha 225MW CCPP (Gas) | 206 | 206 | 207 | 203 | 202 | 214 | 208 | 203 | 203 | 204 | 215 | 215 | 206 | 203 | 203 | 205 | 206 | 216 |  | 210 | 216 | 215 | 203 | 203 | 203 | 191 | 4895324
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 146 | 146 | 105 | 104 | 105 | 105 | 105 | 140 | 135 | 105 | 105 | 111 | 105 | 105 | 104 | 104 | 105 | 139 |  | 139 | 140 | 139 | 139 | 139 | 140 | 105 | 2855337
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 0 | [5 empty] | 0 | 26 | 17 | 17 | 17 | [5 empty] | 2 | 62 |  | 82 | 105 | 105 | 105 | 17 |  |  | 551999
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 40 | 40 | 40 | 42 | 42 | 40 | 42 | 40 | 44 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 67 |  | 67 | 67 | 67 | 67 | 67 | 42 | 42 | 1246000
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 240 | 200 | 200 | 200 | 200 | 210 | 200 | 200 | 230 | 250 | 200 | 211 | 211 | 210 | 310 |  | 310 | 300 | 310 | 310 | 311 | 312 | 312 | 6049003
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 870000
21 | Ghorasal Repowered CCPP Unit-3 | 189 | 147 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 3478500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2125490
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 80 | 80 | 80 | 80 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 1662988
32 | Ashuganj 50 MW PP | 30 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 33 |  | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 339408
33 | Ashuganj 225 MW CCPP | 203 | 203 | 203 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 161 | 162 | 162 | 201 |  | 201 | 200 | 200 | 200 | 204 | 205 | 205 | 4308000
34 | Ashuganj 450 MW CCPP(South) | 270 | 280 | 280 | 265 | 280 | 290 | 285 | 265 | 265 | 280 | 290 | 310 | 280 | 275 | 270 | 265 | 285 | 320 |  | 330 | 345 | 340 | 310 | 310 | 315 | 285 | 7087000
| Ashuganj 450 MW CCPP(North) | 285 | 295 | 272 | 265 | 272 | 290 | 280 | 265 | 265 | 265 | 280 | 370 | 355 | 265 | 265 | 280 | 295 | 360 |  | 350 | 360 | 355 | 330 | 330 | 330 | 260 | 7463000
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 346 | 358 | 347 | 347 | 348 | 362 | 353 | 360 | 343 | 300 | 300 | 302 | 376 | 378 | 300 | 270 | 270 | 341 |  | 372 | 380 | 372 | 361 | 342 | 344 | 350 | 8238080
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 350 | 300 | 300 | 300 | 300 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8250000
41 | Haripur 360MW CCPP(HPL) | 328 | 328 | 328 | 328 | 288 | 288 | 288 | 288 | 270 | 250 | 250 | 280 | 330 | 260 | 260 | 260 | 260 | 330 |  | 330 | 330 | 330 | 338 | 340 | 339 | 339 | 7312000
42 | RPCL 210MW CCPP | 163 | 161 | 163 | 109 | 111 | 110 | 112 | 164 | 163 | 160 | 158 | 154 | 153 | 153 | 154 | 125 | 125 | 156 |  | 160 | 160 | 160 | 161 | 162 | 161 | 161 | 3452000
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 45 | 45 | 60 |  | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 1005000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1429200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 53 | 53 | 52 | 51 | 51 | 51 | 51 | 51 | 40 | 52 | 67 |  | 68 | 68 | 68 | 69 | 70 | 69 | 69 | 1292544
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 76 |  | 76 | 76 | 76 | 76 | 10 | 10 | 76 | 498240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [15 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 98000
52 | Sylhet 50MW PP (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 6 | 6 | 7 | 6 | 7 | 6 | 6 | 7 | 34 |  | 34 | 33 | 34 | 36 | 36 | 36 | 37 | 382540
53 | Sylhet 10MW PP (Desh) | 0 | [15 empty] | 0 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 79920
54 | Hobiganj 11MW PP Cofidence-E | 0 | [16 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 | 0 |  | 48240
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 53 |  | 53 | 53 | 53 | 53 | 53 | 5 | 5 | 369600
56 | Shahjahanulla 25 MW PP | 0 | [16 empty] | 24 |  | 24 | 24 | 24 | 24 |  |  |  | 121275
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 320 | 310 | 315 | 310 | 320 | 315 | 320 | 290 | 300 | 310 | 310 | 320 | 280 | 300 | 295 | 305 | 325 |  | 325 | 330 | 320 | 310 | 285 | 300 | 300 | 7584750
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 0 | [5 empty] | 14 | 14 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 303072
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 19 |  | 19 | 19 | 19 | 19 |  |  |  | 72288
62 | Tangail 22 MW PP (Doreen) | 22 | 0 | [15 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 149004
63 | Impoprt (Tripura) | 78 | 74 | 72 | 70 | 70 | 68 | 66 | 64 | 64 | 60 | 64 | 70 | 83 | 72 | 72 | 70 | 78 | 98 |  | 96 | 100 | 100 | 98 | 92 | 86 | 80 | 1862400
64 | Malancha, Ctg. EPZ (United) | 34 | 10 | 10 | 10 | 10 | 12 | 14 | 15 | 20 | 20 | 28 | 21 | 39 | 32 | 32 | 32 | 38 | 39 |  | 39 | 39 | 39 | 39 | 40 | 5 | 5 | 766080
65 | Feni 22MW PP (Doreen) | 21 | 0 | [15 empty] | 21 |  | 21 | 21 | 21 | 21 | 21 |  |  | 130248
66 | Feni 11 MW PP (Doreen) | 0 | [16 empty] | 11 |  | 11 | 11 | 11 | 11 |  |  |  | 48600
67 | Jangalia 33MW PP (Summit) | 0 | [16 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 174700
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 19 | 19 | 12 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477410
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 22 | 16 | 16 | 11 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 23 | 24 | 24 | 24 | 24 | 24 | 508320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 730500
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 25 | 774100
73 | Ghorashal 108MW PP (Regent) | 107 | 0 | [14 empty] | 12 | 104 |  | 110 | 110 | 110 | 110 | 110 | 52 | 12 | 763181
| Feni Lanka Power | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.6 | 3 | 3.8 | 4.3 | 4.2 | 4.4 | 3.2 | 2.1 | 0.8 | [10 empty] | 27720
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [15 empty] | 0 | 10 | 10 |  | 10 | 10 | 10 | 10 | 0 |  |  | 53280
92 | Fenchuganj 44MW (Energyprima) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 30 |  | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 430560
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 33 |  | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 364928
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | Katpotti 52 MW PP (Sinha) | 6 | 0 | [15 empty] | 11 |  | 24 | 24 | 24 | 24 | 12 | 12 |  | 137376
98 | Bosila 108MW PP(CLC) | [16 empty] | 2 | 8 |  | 8 | 8 | 8 | 8 |  |  |  | 20160
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2973649
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.7 | 1.4 | 1.9 | 2 | 2.1 | 1.9 | 1.6 | 1.1 | 0.4 | [10 empty] | 13300
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 7 | 40 |  | 50 | 50 | 50 | 50 |  |  |  | 232800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn)
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 363 | 370 | 368 | 363 | 367 | 392 | 365 | 351 | 353 | 355 | 382 | 387 | 358 | 353 | 318 | 319 | 333 | 397 |  | 393 | 397 | 394 | 363 | 365 | 362 | 363 | 8772000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [20 empty] | 0 | [5 empty] | 0
120 | Eastern Zone Total | 4640 | 4390 | 4252 | 4077 | 3973 | 4061 | 4011.6 | 4102.4 | 4038.3 | 3951.9 | 4030.2 | 4230.5 | 4381.3 | 4012.8 | 3928.2 | 3872.2 | 4000 | 5336 |  | 5489 | 5526 | 5505 | 5390 | 5029 | 4752 | 4506 | 108344664
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [15 empty] | 0 | 16 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 304030
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 117 |  | 117 | 117 | 117 | 111 | 95 | 110 | 113 | 2669000
140 | Bhola 33 MW PP (Venture) | 21 | 19 | 18 | 18 | 19 | 19 | 19 | 18 | 17 | 15 | 16 | 16 | 17 | 15 | 15 | 15 | 17 | 24 |  | 24 | 24 | 25 | 25 | 25 | 23 | 22 | 449400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 24 |  | 24 | 24 | 24 | 24 | 0 |  |  | 98250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 65376
146 | Bheramara HVDC | 105 | 104 | 105 | 104 | 105 | 104 | 104 | 104 | 104 | 104 | 105 | 175 | 175 | 176 | 176 | 176 | 176 | 435 |  | 434 | 434 | 434 | 434 | 434 | 213 | 190 | 4870545
147 | Bheramara 360 MW CCPP | 165 | 180 | 185 | 195 | 210 | 210 | 210 | 200 | 200 | 200 | 210 | 215 | 210 | 210 | 225 | 235 | 260 | 255 |  | 255 | 245 | 245 | 245 | 245 | 265 | 275 | 5392224
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 161 | 3896300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 171 | 180 | 174 | 176 | 175 | 180 | 180 | 179 | 167 | 170 | 202 | 189 | 194 | 181 | 170 | 171 | 175 | 187 |  | 214 | 214 | 214 | 214 | 198 | 200 | 184 | 4725282
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 182 | 180 | 186 | 184 | 185 | 186 | 188 | 180 | 175 | 187 | 197 | 200 | 201 | 187 | 186 | 189 | 195 |  | 195 | 194 | 196 | 201 | 186 | 176 | 175 | 4813118
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 396 | 396 | 397 | 371 | 394 | 395 | 394 | 376 | 314 | 342 | 345 | 427 | 425 | 366 | 322 | 350 | 368 | 395 |  | 397 | 396 | 396 | 390 | 350 | 395 | 391 | 9162363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [16 empty] | 15 | 18 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 110160
163 | Bogura 20 MW PP (Energyprima) | 14 | 0 | [14 empty] | 9 | 14 |  | 14 | 14 | 14 | 14 | 14 | 0 |  | 87588
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225648
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 12 | 50 |  | 50 | 50 | 50 | 40 | 0 | 0 |  | 186620
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 5 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 158208
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 40 |  | 38 | 37 | 38 | 38 | 0 | 0 |  | 204480
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.1 | 1.2 | 3.1 | 4.2 | 5.4 | 5.8 | 6.5 | 4.4 | 3.2 | 1.4 | 0.1 | [9 empty] | 30994
178
178