## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-10 | Tuesday
|  | Date (day): | 2019-12-10 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11484.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14046 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-09 | 2019-12-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 159 | 159 | 134 | 190
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 110 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 344 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 358 | 318 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 3 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 2 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 60 | 57 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 338 | 352 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 10 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 18 | 47 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 75 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 16 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 145 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 70 | 90 | 90 |  | 15 | Engine problem
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2147 | 2530 | 3758 | 4214 | 598 | 1014
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 81 | 80 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 229 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 10 | 13
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.148 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 516.148 | 694 | 1333 | 1491 | 210 | 428
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 340 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 180 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 45 | 45 | 150 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 80 | 90 | 90 |  | 73 | ST under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 17 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 110 | 99 | 125
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1036 | 1329 | 1620 | 2110 | 214 | 444
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 146 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 110 | 127 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 294.9 | 303 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 29 | 30 | 30
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 52 | 60 | 52 | 52
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 69 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 35 | 39 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 399 | 366 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1203 | 1264 | 1328 | 1328 | 0 | 492
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 286 | 627 | 288 | 635
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 210 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 20 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 54 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 536 | 948 | 728 | 1705 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 25 | 26 | 26 |  | 7 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 115 | 101 | 120 | 120 |  | 74 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 134 | 190 | 311 | 381 | 0 | 81
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 191 | 190 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 140 | 140 | 80 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 200 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 344 | 397 | 400 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 913 | 1170 | 1592 | 1858 | 251 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 200 | 220
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 185.2 | 293 | 321 | 367 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6965.248 | 8721 | 11484.6 | 14046 | 1315 | 2747
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6593.0653 | 8255 | 10870.9291 | 13295.4627
A. |  | 2019-12-09 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8721 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5388 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8721 | MW
3 | Day peak Generation : |  |  | 6965.248 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8255 | MW
4 | Evening peak Generation : |  |  | 8721 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 165.1691 | MKWHr | By Solar | 0.10018 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 140.0403 | MKWHr |  | By Oil: | 9.4255 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.1747 | MKWHr |  | By Hydro: | 1.9072 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1315 | MW | Dhaka | 3202 | 3202 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2747 | MW | Chittagong | 889 | 889 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4062 | MW | Khulna | 962 | 962 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1107.39 | MMCFD |  |  | Rajshahi | 834 | 834 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 130385227.526 | ii) Oil : | Taka | 90259065.2 | Comilla | 681 | 681 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 17074523 | Total | Taka | 237718815.726 | Mymensingh | 634 | 634 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.56 | MKWHr. | Sylhet | 325 | 325 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -110 | MW (E to W) at | 19:00 | hrs | Barisal | 234 | 234 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -355 | MW at | 8:00 | hrs | Rangpur | 494 | 494 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.4° C |  |  | Total | 8255 | 8255 |  | 0
B. |  | 2019-12-10 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 25.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14046 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6900 | MW
4 | Reserve(Generation end) |  |  |  | 5346 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 164.7714 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5279 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.4044 | MKWHr. | ii) HVDC Flow at Peak Time |  | 627 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1168 | MKWHr. | iii) Maximum HVDC Flow : |  | 628 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.67 |  | (b) Today: | 98.52 |  | (c) Rule Curve: |  | 105.19
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 199 | 0 | 0 | 0 | 110 | 0 | 343 | 358 |  | 0 | 380 | 0 | 0 | 0 | 0 | 340 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 31 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 183 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 100 | 100 | 0 | 345 | 330 | 0 | 8 | 88 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 146 | 0 | 0 | 0 | 28 | 52 | 0 | 0 | 130 | 0 | 69 | 40 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 151 | 0 | 136 | 0 | 0 | 0 | 182 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4584 | 1405 | 5989 | 3728 | 137 | 1733 | 72 | 159 | 80 | 0 | 80 | 0 | 0 | 98.72
2:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 343 | 366 |  | 0 | 380 | 0 | 0 | 0 | 0 | 340 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 183 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 70 | 100 | 0 | 345 | 330 | 0 | 8 | 86 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 78 | 114 | 0 | 0 | 0 | 30 | 52 | 0 | 0 | 100 | 0 | 69 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 151 | 0 | 136 | 0 | 0 | 0 | 183 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4273 | 1440 | 5713 | 3649 | 136 | 1545 | 66 | 159 | 80 | 0 | 78 | 0 | 0 | 98.71
3:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 346 | 310 |  | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 183 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 70 | 100 | 0 | 335 | 320 | 0 | 8 | 86 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 78 | 114 | 0 | 0 | 0 | 30 | 52 | 0 | 0 | 100 | 0 | 69 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 155 | 0 | 140 | 0 | 0 | 0 | 181 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4094 | 1468 | 5562 | 3583 | 137 | 1459 | 66 | 159 | 80 | 0 | 78 | 0 | 0 | 98.7
4:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 347 | 260 |  | 0 | 350 | 0 | 0 | 0 | 0 | 240 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 40 | 40 | 110 | 0 | 0 | 182 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 70 | 100 | 0 | 290 | 275 | 0 | 8 | 87 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 76 | 142 | 0 | 0 | 0 | 29 | 52 | 0 | 0 | 100 | 0 | 69 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 129 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 156 | 0 | 140 | 0 | 0 | 0 | 182 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3903 | 1485 | 5388 | 3519 | 129 | 1408 | 16 | 160 | 80 | 0 | 76 | 0 | 0 | 98.69
5:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 347 | 259 |  | 0 | 350 | 0 | 0 | 0 | 0 | 240 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 42 | 40 | 110 | 0 | 0 | 182 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 70 | 100 | 0 | 265 | 265 | 0 | 8 | 90 | 33 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 76 | 162 | 0 | 0 | 0 | 30 | 52 | 0 | 0 | 100 | 0 | 69 | 5 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 129 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 140 | 0 | 0 | 0 | 183 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3907 | 1508 | 5415 | 3556 | 129 | 1412 | 0 | 160 | 82 | 0 | 76 | 0 | 0 | 98.68
6:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 360 | 259 |  | 0 | 350 | 0 | 0 | 0 | 0 | 240 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 31 | 0 | 0 | 42 | 40 | 110 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 70 | 100 | 0 | 280 | 280 | 0 | 8 | 91 | 33 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 74 | 162 | 0 | 0 | 0 | 30 | 52 | 47 | 8 | 100 | 0 | 70 | 5 | 0 | 0 | 17 | 31 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 161 | 0 | 140 | 0 | 0 | 0 | 183 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4081 | 1522 | 5603 | 3642 | 128 | 1517 | 0 | 160 | 82 | 0 | 74 | 0 | 0 | 98.67
7:00 | 35 | 169 | 0 | 0 | 0 | 0 | 0 | 363 | 311 |  | 0 | 350 | 0 | 0 | 0 | 0 | 240 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 31 | 0 | 0 | 42 | 40 | 110 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 29 | 70 | 100 | 0 | 285 | 280 | 0 | 8 | 91 | 33 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 16 | 72 | 162 | 0 | 0 | 0.1 | 28 | 52 | 47 | 47 | 100 | 0 | 70 | 73 | 0 | 0 | 17 | 30 | 10 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  | 128 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 164 | 0 | 140 | 0 | 0 | 0 | 184 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4406.9 | 1535.1 | 5942 | 3808 | 128 | 1690 | 0 | 160 | 82 | 0 | 72 | 2 | 0 | 0
8:00 | 35 | 168 | 0 | 0 | 0 | 80 | 0 | 370 | 370 |  | 0 | 400 | 0 | 0 | 0 | 0 | 350 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 31 | 0 | 0 | 41 | 40 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 70 | 100 | 0 | 340 | 180 | 0 | 8 | 90 | 33 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 8 | 33 | 16 | 78 | 161 | 0 | 0 | 0.5 | 27 | 52 | 47 | 47 | 130 | 0 | 69 | 73 | 0 | 0 | 17 | 30 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 6.63 | 0 | 0 | 0 | 371 | 0 | 0 | 4 | 1.461 | 0 | 0 | 0 | 0 |  | 128 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 140 | 0 | 0 | 0 | 190 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4809.591 | 1578 | 6387.591 | 3936 | 128 | 1935 | 61 | 160 | 81 | 0 | 78 | 8.591 | 0 | 98.66
9:00 | 35 | 159 | 0 | 0 | 0 | 107 | 0 | 344 | 369 |  | 0 | 380 | 0 | 0 | 0 | 0 | 354 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 31 | 31 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 70 | 100 | 0 | 330 | 180 | 0 | 8 | 80 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 16 | 82 | 160 | 0 | 22 | 1.1 | 30 | 52 | 47 | 50 | 130 | 0 | 40 | 73 | 0 | 0 | 17 | 30 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 12.91 | 0 | 0 | 0 | 365 | 0 | 0 | 41 | 2.708 | 0 | 0 | 0 | 0 |  | 285 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 140 | 0 | 0 | 0 | 190 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 4949.718 | 1680 | 6629.718 | 3870 | 285 | 1902 | 229 | 160 | 82 | 0 | 82 | 19.718 | 0 | 98.65
10:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 343 | 366 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 31 | 25 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 100 | 0 | 330 | 180 | 0 | 8 | 85 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 16 | 82 | 157 | 0 | 22 | 1.6 | 30 | 52 | 47 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 31 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 51 | 3.68 | 0 | 0 | 0 | 0 |  | 286 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 166 | 0 | 140 | 0 | 0 | 0 | 190 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 |  | 4833.28 | 1681.2 | 6514.48 | 3823 | 286 | 1864 | 208 | 160 | 82 | 0 | 82 | 9.48 | 0 | 98.65
11:00 | 35 | 159 | 0 | 0 | 0 | 107 | 0 | 346 | 364 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 38 | 0 | 0 | 3 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 10 | 19 | 25 | 31 | 33 | 31 | 25 | 0 | 42 | 40 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 100 | 0 | 340 | 180 | 0 | 8 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 16 | 74 | 155 | 8 | 22 | 1.8 | 28 | 52 | 47 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 33 | 10 | 305 | 24 | 8 | 0 | 5 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 5 | 51 | 4.167 | 0 | 0 | 0 | 0 |  | 286 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 141 | 0 | 0 | 0 | 192 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 4931.967 | 1741.2 | 6673.167 | 3879 | 286 | 1913 | 248 | 180 | 82 | 0 | 74 | 11.167 | 0 | 0
12:00 | 35 | 159 | 0 | 0 | 0 | 104 | 0 | 374 | 358 |  | 0 | 450 | 0 | 0 | 0 | 3 | 338 | 0 | 60 | 0 | 0 | 10 | 0 | 2 | 16 | 0 | 18 | 0 | 0 | 25 | 19 | 25 | 30 | 33 | 31 | 25 | 0 | 41 | 40 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 100 | 0 | 360 | 180 | 0 | 8 | 91 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 88 | 153 | 8 | 22 | 1.9 | 28 | 52 | 50 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 35 | 10 | 320 | 24 | 8 | 0 | 15 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 17 | 51 | 4.148 | 0 | 0 | 0 | 0 |  | 286 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 191 | 0 | 140 | 0 | 0 | 0 | 197 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 5197.048 | 1768.2 | 6965.248 | 4013 | 286 | 1996 | 310 | 180 | 81 | 0 | 88 | 11.248 | 0 | 98.64
13:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 368 | 328 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 90 | 0 | 0 | 32 | 0 | 20 | 32 | 0 | 18 | 0 | 0 | 35 | 19 | 25 | 30 | 33 | 31 | 25 | 0 | 38 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 7 | 80 | 100 | 0 | 330 | 260 | 0 | 26 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 8 | 33 | 16 | 90 | 154 | 8 | 22 | 1.7 | 28 | 52 | 50 | 47 | 163 | 0 | 40 | 73 | 0 | 0 | 17 | 37 | 10 | 305 | 24 | 8 | 0 | 15 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 17 | 51 | 3.77 | 0 | 0 | 0 | 0 |  | 286 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 162 | 0 | 0 | 0 | 181 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 5333.47 | 1759.8 | 7093.27 | 4024 | 286 | 2037 | 388 | 180 | 78 | 0 | 90 | 10.27 | 0 | 98.63
14:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 344 | 302 |  | 0 | 390 | 0 | 0 | 0 | 15 | 337 | 0 | 35 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 18 | 0 | 0 | 35 | 19 | 25 | 26 | 33 | 31 | 0 | 0 | 38 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 5 | 80 | 100 | 0 | 265 | 360 | 0 | 26 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 94 | 140 | 8 | 22 | 1.4 | 28 | 52 | 50 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 36 | 10 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 13.31 | 0 | 0 | 0 | 369 | 0 | 0 | 51 | 3 | 0 | 0 | 0 | 0 |  | 286 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 183 | 0 | 179 | 0 | 0 | 0 | 175 | 0 | 331 | 0 | 0 | 0 | 17 | 0 | 0 | 4.2 | 0 |  | 5009.71 | 1742.2 | 6751.91 | 3962 | 286 | 1858 | 272 | 180 | 78 | 0 | 94 | 21.91 | 0 | 0
15:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 347 | 306 |  | 0 | 390 | 0 | 0 | 0 | 15 | 337 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 35 | 0 | 25 | 30 | 33 | 31 | 0 | 0 | 38 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 100 | 0 | 265 | 365 | 0 | 26 | 86 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 92 | 140 | 8 | 22 | 0.9 | 27 | 60 | 53 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 38 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 51 | 1.9 | 0 | 0 | 0 | 0 |  | 287 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 183 | 0 | 141 | 0 | 0 | 0 | 183 | 0 | 344 | 0 | 0 | 0 | 17 | 0 | 0 | 2.6 | 0 |  | 5011.8 | 1729.6 | 6741.4 | 3940 | 287 | 1907 | 252 | 180 | 78 | 0 | 92 | 5.4 | 0 | 0
16:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 343 | 306 |  | 0 | 390 | 0 | 0 | 0 | 15 | 338 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 35 | 0 | 25 | 30 | 33 | 31 | 0 | 0 | 39 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 100 | 0 | 265 | 370 | 0 | 26 | 82 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 90 | 142 | 8 | 22 | 0.3 | 28 | 60 | 53 | 47 | 100 | 0 | 40 | 76 | 0 | 0 | 17 | 37 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 51 | 0.8 | 0 | 0 | 0 | 0 |  | 286 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 179 | 0 | 0 | 175 | 0 | 141 | 0 | 0 | 0 | 182 | 0 | 325 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 0 |  | 5010.1 | 1694 | 6704.1 | 3931 | 286 | 1885 | 252 | 179 | 79 | 0 | 90 | 2.1 | 0 | 0
17:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 337 | 274 |  | 0 | 350 | 0 | 0 | 0 | 15 | 270 | 0 | 35 | 0 | 0 | 0 | 32 | 0 | 43 | 0 | 18 | 0 | 17 | 35 | 19 | 25 | 30 | 33 | 31 | 8 | 0 | 39 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 11 | 30 | 10 | 0 | 19 | 3 | 80 | 100 | 0 | 265 | 365 | 0 | 26 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 100 | 145 | 8 | 22 | 0 | 28 | 60 | 53 | 47 | 100 | 0 | 40 | 76 | 0 | 0 | 17 | 40 | 10 | 290 | 24 | 8 | 0 | 11 | 0 | 0 | 90 | 0 | 0 | 0 | 10 | 7 | 10 | 366 | 0 | 2 | 54 | 0 | 0 | 0 | 0 | 0 |  | 431 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 168 | 0 | 141 | 0 | 0 | 0 | 180 | 0 | 296 | 0 | 0 | 10 | 17 | 109 | 0 | 0.1 | 4 |  | 5047 | 1932.1 | 6979.1 | 3862 | 431 | 1771 | 513 | 180 | 79 | 43 | 100 | 0.1 | 0 | 0
18:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 329 | 334 |  | 0 | 450 | 0 | 0 | 0 | 15 | 347 | 0 | 36 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 38 | 0 | 55 | 35 | 19 | 25 | 22 | 33 | 31 | 47 | 0 | 40 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 34 | 100 | 25 | 0 | 19 | 3 | 95 | 100 | 0 | 340 | 365 | 0 | 40 | 86 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 114 | 145 | 8 | 22 | 0 | 28 | 60 | 53 | 47 | 163 | 0 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 295 | 24 | 8 | 0 | 97 | 0 | 0 | 98 | 0 | 0 | 0 | 10 | 17 | 50 | 363 | 0 | 70 | 95 | 0 | 0 | 0 | 0 | 0 |  | 628 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 114 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 140 | 0 | 0 | 0 | 191 | 0 | 433 | 17 | 0 | 100 | 17 | 109 | 0 | 0 | 35 |  | 6044 | 2561 | 8605 | 4075 | 628 | 2156 | 1238 | 180 | 80 | 134 | 114 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 344 | 318 |  | 0 | 450 | 0 | 0 | 0 | 15 | 352 | 0 | 57 | 0 | 0 | 0 | 75 | 0 | 72 | 0 | 47 | 0 | 55 | 35 | 19 | 25 | 31 | 33 | 31 | 52 | 0 | 40 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 100 | 25 | 0 | 19 | 14 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 146 | 8 | 22 | 0 | 29 | 60 | 53 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 127 | 0 | 0 | 0 | 10 | 17 | 50 | 366 | 0 | 70 | 105 | 0 | 0 | 0 | 0 | 0 |  | 627 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 101 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 190 | 0 | 140 | 0 | 0 | 0 | 200 | 0 | 397 | 17 | 0 | 113 | 54 | 113 | 0 | 0 | 35 |  | 6120 | 2601 | 8721 | 4089 | 627 | 2124 | 1419 | 180 | 80 | 92 | 110 | 0 | 0 | 0
19:30 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 342 | 317 |  | 0 | 450 | 0 | 0 | 0 | 0 | 352 | 0 | 62 | 0 | 0 | 0 | 40 | 0 | 72 | 0 | 47 | 0 | 55 | 35 | 19 | 25 | 31 | 33 | 31 | 52 | 0 | 40 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 25 | 0 | 19 | 12 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 145 | 8 | 22 | 0 | 28 | 60 | 53 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 310 | 24 | 11 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 0 | 50 | 366 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 628 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 106 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 187 | 0 | 140 | 0 | 0 | 0 | 201 | 0 | 409 | 17 | 0 | 113 | 54 | 75 | 0 | 0 | 0 |  | 6019 | 2519 | 8538 | 4093 | 628 | 2144 | 1263 | 180 | 80 | 40 | 110 | 0 | 0 | 0
20:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 342 | 313 |  | 0 | 450 | 0 | 0 | 0 | 0 | 351 | 0 | 61 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 47 | 0 | 17 | 35 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 25 | 0 | 19 | 17 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 145 | 8 | 22 | 0 | 28 | 60 | 53 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 305 | 24 | 11 | 0 | 145 | 0 | 0 | 150 | 0 | 0 | 0 | 10 | 0 | 50 | 365 | 0 | 17 | 105 | 0 | 0 | 0 | 0 | 0 |  | 627 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 108 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 190 | 0 | 140 | 0 | 0 | 0 | 201 | 0 | 430 | 17 | 0 | 113 | 54 | 55 | 0 | 0 | 0 |  | 5963 | 2514 | 8477 | 4087 | 627 | 2161 | 1200 | 180 | 80 | 32 | 110 | 0 | 0 | 0
21:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 342 | 313 |  | 0 | 450 | 0 | 0 | 0 | 0 | 354 | 0 | 57 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 36 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 52 | 0 | 41 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 0 | 0 | 19 | 25 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 80 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 147 | 8 | 22 | 0 | 29 | 60 | 50 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 628 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 88 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 188 | 0 | 140 | 0 | 0 | 0 | 199 | 0 | 374 | 17 | 0 | 113 | 54 | 35 | 0 | 0 | 0 |  | 5718 | 2398 | 8116 | 4055 | 628 | 2095 | 953 | 180 | 81 | 16 | 108 | 0 | 0 | 0
22:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 342 | 316 |  | 0 | 450 | 0 | 0 | 0 | 0 | 338 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 25 | 0 | 41 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 33 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 140 | 0 | 22 | 0 | 28 | 60 | 50 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 530 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 189 | 0 | 140 | 0 | 0 | 0 | 200 | 0 | 386 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 |  | 5384 | 2092 | 7476 | 4062 | 530 | 2117 | 406 | 180 | 81 | 0 | 100 | 0 | 0 | 0
23:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 347 | 291 |  | 0 | 400 | 0 | 0 | 0 | 0 | 339 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 178 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 100 | 100 | 0 | 285 | 320 | 0 | 45 | 90 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 140 | 0 | 0 | 0 | 29 | 60 | 50 | 47 | 100 | 0 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 316 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 179 | 0 | 140 | 0 | 0 | 0 | 187 | 0 | 432 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 |  | 4935 | 1865 | 6800 | 3949 | 316 | 1984 | 200 | 180 | 81 | 0 | 90 | 0 | 0 | 0
24:00 | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 351 | 291 |  | 0 | 400 | 0 | 0 | 0 | 0 | 341 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 41 | 40 | 120 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 100 | 100 | 0 | 262 | 265 | 0 | 45 | 80 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 84 | 144 | 0 | 22 | 0 | 28 | 60 | 50 | 47 | 100 | 0 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 189 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 146 | 0 | 0 | 0 | 180 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4817 | 1621 | 6438 | 3874 | 189 | 1938 | 92 | 180 | 81 | 0 | 84 | 0 | 0 | 0
KWH | 856000 | 4228400 | 0 | 0 | 0 | 1910045 | 0 | 8486770 | 7615000 |  | 0 | 9338250 | 0 | 0 | 0 | 119880 | 7717340 | 0 | 1119000 | 0 | 0 | 51696 | 258720 | 68016 | 397440 | 0 | 435552 | 0 | 161960 | 334783 | 243828 | 600000 | 681660 | 827900 | 809700 | 434112 | 0 | 931216 | 976000 | 2800000 | 0 | 0 | 4756151 | 0 | 0 | 0 |  | 0 | 0 | 62629 | 506760 | 95040 | 0 | 438576 | 350400 | 2056288 | 2364905 | 0 | 7790900 | 7032500 | 0 | 552000 | 2041480 | 712008 | 0 | 0 | 735096 | 0 | 0 | 0 | 325512 | 151920 | 569500 | 449920 | 2116800 | 3439680 | 93120 | 314100 | 11100 | 685000 | 1324920 | 931800 | 886104 | 3057954 | 0 | 1390368 | 1474560 | 0 | 0 | 352000 | 692500 | 195480 | 7485700 | 407544 | 146160 | 0 | 579600 | 0 | 0 | 2296800 | 0 | 0 | 32000 | 39360 | 51360 | 182327 | 8443000 | 0 | 217932 | 1037922 | 25800 | 0 | 0 | 0 | 0 |  | 7404363 | 0 | 5567328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152250 | 2697000 | 487900 | 304224 | 0 | 0 | 0 | 0 | 0 | 0 | 135680 | 0 | 0 | 0 | 0 | 341760 | 205272 | 500808 | 0 | 0 | 4174700 | 0 | 0 | 4431382 | 0 | 3629564 | 0 | 0 | 0 | 4732945 | 0 | 8658454 | 72000 | 0 | 528672 | 344736 | 383040 | 0 | 31284 | 79872 |  | 120305844 | 44863234 | 165169078 | 95122057 | 7404363 | 44918275 | 9104134 | 4174700 | 1907216 | 321349 | 2116800 | 100184 | 0
Fuel Cost | 958720 | 4566672 | 0 | 0 | 0 | 1852743.65 | 0 | 6110474.4 | 5787400 |  | 0 | 7470600 | 0 | 0 | 0 | 1229968.8 | 9569501.6 | 0 | 1398750 | 0 | 0 | 525231.36 | 2563915.2 | 712807.68 | 3616704 | 0 | 4076766.72 | 0 | 1545098.4 | 3334438.68 | 182871 | 450000 | 0 | 0 | 0 | 4158792.96 | 0 | 242116.16 | 253760 | 4284000 | 0 | 0 | 4993958.55 | 0 | 0 | 0 |  | 0 | 0 | 656978.21 | 5214560.4 | 903830.4 | 0 | 403489.92 | 974112 | 2159102.4 | 2483150.25 | 0 | 5765266 | 5907300 | 0 | 540960 | 2715168.4 | 583846.56 | 0 | 0 | 1051187.28 | 0 | 0 | 0 | 332022.24 | 113940 | 1076355 | 337440 | 14605920 | 2820537.6 | 885571.2 | 320382 | 182040 | 931600 | 1801891.2 | 1267248 | 1107630 | 3791862.96 | 0 | 2071648.32 | 2595225.6 | 0 | 0 | 559680 | 810225 | 459378 | 5314847 | 305658 | 111081.6 | 0 | 6068412 | 0 | 0 | 22095216 | 0 | 0 | 369280 | 366835.2 | 481756.8 | 1708403.99 | 7936420 | 0 | 1941774.12 | 9808362.9 | 0 | 0 | 0 | 0 | 0 |  | 19991780.1 | 0 | 4342515.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505752.5 | 2157600 | 756245 | 3267365.76 | 0 | 0 | 0 | 0 | 0 | 0 | 1407001.6 | 0 | 0 | 0 | 0 | 375936 | 338698.8 | 379111.656 | 0 | 0 | 17074523 | 0 | 0 | 3899616.16 | 0 | 3375494.52 | 0 | 0 | 0 | 4164991.6 | 0 | 6320671.42 | 681120 | 0 | 4853208.96 | 3071597.76 | 3577593.6 | 0 | 0 | 0 |  | 191822887.71 | 81540824.276 | 273363711.986 | 89570256.816 | 19991780.1 | 40814970.71 | 87038171.79 | 17074523 | 495876.16 | 3220893.41 | 14605920 | 551320 | 0
Yesterday Day Peak | 35 | 159 | 0 | 0 | 0 | 104 | 0 | 374 | 358 |  | 0 | 450 | 0 | 0 | 0 | 3 | 338 | 0 | 60 | 0 | 0 | 10 | 0 | 2 | 16 | 0 | 18 | 0 | 0 | 25 | 19 | 25 | 30 | 33 | 31 | 25 | 0 | 41 | 40 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 100 | 0 | 360 | 180 | 0 | 8 | 91 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 88 | 153 | 8 | 22 | 1.9 | 28 | 52 | 50 | 47 | 100 | 0 | 40 | 73 | 0 | 0 | 17 | 35 | 10 | 320 | 24 | 8 | 0 | 15 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 17 | 51 | 4.148 | 0 | 0 | 0 | 0 |  | 286 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 8 | 0 | 0 | 180 | 0 | 0 | 191 | 0 | 140 | 0 | 0 | 0 | 197 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 |  | 6965.248 | DayPeak
Yesterday Evening Peak | 35 | 159 | 0 | 0 | 0 | 110 | 0 | 344 | 318 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 352 | 0 | 57 | 0 | 0 | 0 | 75 | 0 | 72 | 0 | 47 | 0 | 55 | 35 | 19 | 25 | 31 | 33 | 31 | 52 | 0 | 40 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 25 | 0 | 19 | 14 | 100 | 100 | 0 | 340 | 320 | 0 | 45 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 146 | 8 | 22 | 0 | 29 | 60 | 53 | 47 | 163 | 0 | 69 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 145 | 0 | 0 | 127 | 0 | 0 | 0 | 10 | 17 | 50 | 366 | 0 | 70 | 105 | 0 | 0 | 0 | 0 | 0 |  | 627 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 101 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 180 | 0 | 0 | 190 | 0 | 140 | 0 | 0 | 0 | 200 | 0 | 397 | 17 | 0 | 113 | 54 | 113 | 0 | 0 | 35 |  | 8721 | EvPeak
Forecast for Evening | 35 | 190 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 19 | 13 | 100 | 100 | 0 | 360 | 360 | 0 | 45 | 90 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 125 | 160 | 95 | 22 | 0 | 30 | 52 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 114 |  | 635 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 0 | 70 | 40 | 120 | 26 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 220 | 17 | 17 | 210 | 0 | 140 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 134 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 19 | 10 | 100 | 100 | 0 | 360 | 360 | 0 | 45 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 99 | 160 | 95 | 22 | 1.6 | 30 | 52 | 51 | 44 | 163 | 0 | 66 | 76 | 0 | 0 | 20 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 200 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 90 | 105 | 5 | 230 | 54 | 50 | 0 |  | 288 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 26 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 140 |  | 95 | 80 | 220 | 0 | 400 | 20 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 159 | 0 | 0 | 0 | 13 | 0 | 370 | 257 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 17 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 100 | 0 | 355 | 350 | 0 | 8 | 50 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 80 | 162 | 0 | 0 | 0.5 | 30 | 60 | 44 | 43 | 100 | 0 | 67 | 40 | 0 | 0 | 0 | 38 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 6.72 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0.817 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 179 | 0 | 0 | 205 | 0 | 223 | 0 | 0 | 0 | 195 | 0 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0
199
| Minimum Generation |  | 5388 | 4:00
| Highest Generation |  | 8721 | 19:00
| Day Peak Generation |  | 6965.248 | 12:00
| Evening Peak Generation |  | 8721 | 19:00
| HVDC Max Flow |  | 628 | 18:00
| HVDC EvPeak Flow |  | 627 | 19:00
| Load factor L.F |  | 78.91%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6965.248 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5279 | MW
Evening Peak Generation : |  | 8721 | MW Hour : | 19:00 | Available Max Generation : |  | 14046 | MW
E.P. Demand (at gen end) : |  | 8721 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8700 | MW
Maximum Generation : |  | 8721 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5346 | MW
Total Gen. (MKWH) : |  | 165.1691 | System Load Factor : | 78.91% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -355 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-10
Actual : | 98.52 | Ft.(MSL) , | Rule curve : | 105.19 | Ft.( MSL )
Gas Consumed : | Total = | 1107.39 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 130385227.526
: |  | Coal : | 17074523 | Oil : | 90259065.2 | Total : | 237718815.726
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3078.6418 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1040.6061 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 931.2256 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 841.0421 |  |  | 0 | 0%
) | 0 | 0:00 | 760.2575 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 613.485 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 351.1409 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 158.1705 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 473.1113 |  |  | 0 | 0%
Total | 0 |  | 8247.6808 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Sylhet-150 MW. | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-2,4,5,7 | 12) Bhola-225 MW ST
4) Chandpur CCPP ST
5) Sylhet 150 MW
6) Sikalbaha-150 MW
7) Ashuganj Precision
8) Raozan #2
9) Ashuganj unit-5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Joydebpur 132/33 kV GT-2 transformer and auxiliary transformer were under shut down from 09:09 |  |  |  |  | About 15 MW power interruption occurred under Joydebpur S/S area
to 16:50 for A/M. |  |  |  |  | from 09:09 to 16:50.
b) Hathazari-Raozan 230 kV Ckt-1 was under shut down from 09:21 to 16:09 for A/M.
c) Aminbazar-Agargaon 230 kV Ckt-1 was under shut down from 09:17 to 16:02 for A/M.
d) Kallyanpur 132 kV bus-coupler breaker was under shut down from 08:30 to 16:29 for A/M.
e) Daudkandi-Sonargaon 132 kV Ckt-1 was under shut down from 08:01 to 16:22 for A/M.
f) Mymensingh-Netrokona 132 kV Ckt-2 was under shut down from 08:34 to 16:30 for A/M.
g) Haripur-Narshingdi 132 kV Ckt was under shut down from 10:09 to 15:34 for A/M.
h) Narshingdi 132/33 kV T1 transformer was under shut down from 08:16 to 16:51 for A/M. |  |  |  |  | About 20 MW power interruption occurred under Narshingdi S/S area
from 08:16 to 16:51.
i) Bakulia-Khulshi 132 kV bay was under shut down from 08:22 to 14:12 for A/M.
j) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 08:54 to 16:05 for A/M.
k) Jamalpur-Mymensingh 132 kV Ckt-2 was under shut down from 09:19 to 15:46 for A/M.
l) Rajshahi(New)-Chapai 132 kV Ckt-1 was under shut down from 08:32 to 14:47 for A/M.
m) Khulna(S)-Satkhira 132 kV Ckt-2 was under shut down from 08:17 to 15:13 for A/M.
n) Madaripur-Gopalganj 132 kV Ckt-2 was under shut down from 08:54 to 15:47 for A/M.
o) Madaripur 132/33 kV T3 transformer was under shut down from 08:32 to 09:32 to attend R/H at |  |  |  |  | About 10 MW power interruption occurred under Madaripur S/S area
33 kV Tekerhat feeder. |  |  |  |  | from 08:32 to 09:32.
p) Bogura-Natore 132 kV Ckt-2 and Bogura-Naogaon 132 kV Ckt-2 was under shut down from 12:37 to
16:00 to work at 132 kV auxiliary bus at Bogura(Old) S/S.
q) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 12:05 to 13:19 for A/M.
r) AKSML 230/33 kV T1 & T2 transformers were under shut down from 12:40 to 14:00 to install new
meter by BPDB.
s) Tongi 132/33 kV T3 transformer was shut down at 18:25 to attend R/H at 33 kV side B-phase CT terminal.
t) Rampura-Bhulta 230 kV Ckt-1 was shut down at 07:04(10/12/19) for A/M.
u) Shyampur-APR 230 kV Ckt was shut down at 07:08(10/12/2019) for A/M of APR PP.
v) Hasnabad-APR 230 kV Ckt was shut down at 07:13(10/12/2019) for A/M of APR PP.
w) Jashore 132/33 kV T1 transformer was shut down at 07:06(10/12/2019) for A/M.
x) Barishal-Bhandaria 132 kV Ckt was shut down at 07:07(10/12/19) for D/W.
y) Tangail-Kaliakoir 132 kV Ckt-2 was shut down at 07:37(10/12/2019) for A/M.
z) Kallyanpur 132/33 kV T1 transformer was shut down at 07:44(10/12/2019) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 856000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 159 | 4228400
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 1910045
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8486770 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 318 | 7615000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9338250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 119880 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 68016 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 243828
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 57 | 1119000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 352 | 7717340
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 51696 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 435552 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 75 | 258720 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 161960
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 334783 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 397440 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1281660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 827900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 809700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 434112
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 579600 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 217932 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2530 | 47493584
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 32000
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1907216 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4756151 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1037922
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 62629 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 506760
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 39360 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 438576
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 350400
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 95040 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 694 | 12051854
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2056288 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2364905 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 340 | 7790900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7032500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 712008 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 552000 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 735096 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 182327 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2041480 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 17 | 51360 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 325512
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 151920
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2116800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 569500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 449920
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1329 | 27132516
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 146 | 3439680 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 314100
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 93120 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 127 | 2296800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 303 | 6154800
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 29 | 685000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1324920
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3057954
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 931800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 886104
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 146160
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1390368 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1474560 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 352000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 692500 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 407544
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7485700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 366 | 8443000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 195480
| Sylhet Area Total |  |  |  | 1949 | 1264 | 27473090
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 627 | 7404363
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 210 | 5567328 | ST under maint.& gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 152250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 72000 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 54 | 344736 | Low demand
| Khulna Area Total |  |  |  | 2314 | 948 | 13540677
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 304224 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 487900 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 101 | 2697000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Machine problem
| Barisal Area Total |  |  |  | 462 | 190 | 3489124
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 135680
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4431382 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3629564 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 200 | 4732945 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 397 | 8658454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 341760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 205272
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 500808
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 528672
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 79872 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1170 | 23244409
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4174700
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 383040
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31284
| Rangpur Area Total |  |  |  | 605 | 293 | 4589024
| Total |  |  |  | 19047 | 8721 | 165169078
| Eastern Grid Total |  |  |  | 13483 | 6120 | 120305844
| Western Grid Total |  |  |  | 5564 | 2601 | 44863234
| National Grid Total |  |  |  | 19047 | 8721 | 165169078
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-09
(a) ENTIRE EASTERN GRID : |  | 5731 | MW | (b) ENTIRE WESTERN GRID : |  | 2524 | MW
i) Dhaka area |  | 3202 | MW | i) Khulna area |  | 962 | MW
ii) Chittagong area |  | 889 | MW | ii) Rajshahi area |  | 834 | MW
iii) Comilla area |  | 681 | MW | iii) Barisal area |  | 234 | MW
iv) Mymensingh area |  | 634 | MW | iv) Rangpur area |  | 494 | MW
v) Sylhet area |  | 325 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8255 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 17:00 | Shahjibazar | 79 | 19:00 | Bottail | 100 | 18:00
Munsiganj | 74 | 19:00 | Fenchuganj | 25 | 18:00 | G.K Project | 25 | 18:00
Sonargaon | 68 | 18:30 | Kulawara | 30 | 18:00 | Faridpur | 124 | 19:30
Shyampur | 180 | 12:00 | Sylhet | 95 | 18:00 | Madaripur | 55 | 19:00
Bhulta | 163 | 11:00 | Chatak | 16 | 18:00 | Sariatpur | 36 | 18:30
Madanganj | 54 | 18:00 | Sunamganj | 27 | 19:00 | Gopalganj | 63 | 18:30
Shitalakhya | 95 | 12:00 | Biani Bazar | 32 | 18:00 | Bagerhat | 63 | 19:30
Rahim steel | 17 | 12:00 | Comilla (S) | 114 | 18:00 | Mongla | 34 | 0.375
Matuail | 78 | 12:00 | Comilla(N) | 73 | 19:30 | Satkhira | 60 | 18:00
Ghorasal | 63 | 19:00 | Chandpur | 60 | 18:00 | Gallamari | 32 | 18:00
Narsingdi | 101 | 18:30 | Feni | 89 | 18:00 | Magura | 35 | 18:30
Haripur (SBU) | 82 | 11:00 | Chowmuhani | 118 | 19:30 | Norail | 24 | 19:00
Ullon | 53 | 18:00 | Ashuganj | 35 | 18:00 | Chuadanga | 56 | 18:00
Hasnabad | 128 | 19:30 | Daudkandi | 78 | 18:00 | Barisal(N) | 30 | 19:00
Magbazar | 83 | 18:00 | B.Baria | 86 | 19:30 | Barisal (S) | 68 | 21:00
Maniknagar | 86 | 14:00 | Ramganj | 48 | 20:00 | Patuakhali | 86 | 20:00
Bangabhaban | 20 | 13:00 | Chaddagram | 6 | 18:00 | Bhandaria | 36 | 19:30
Narinda | 78 | 12:00 | PHP | 0 | 7:00 | Borhan Uddin | 24 | 19:30
Dhanmondi | 97 | 12:00 | Madunaghat | 41 | 18:00 | Ishurdi | 45 | 19:30
Lalbag | 85 | 18:00 | Hathazari | 67 | 19:00 | Ruppur Paromanobik | 1 | 20:00
Madartek | 48 | 21:00 | Khulshi | 160 | 13:00 | Natore | 82 | 18:00
Mirpur | 77 | 18:30 | Halishahar | 101 | 15:00 | Bogra | 136 | 18:00
Kalyanpur | 78 | 18:00 | Baraulia | 125 | 13:00 | Noagaon | 80 | 18:00
Gulshan | 104 | 19:00 | Sikalbaha | 28 | 18:30 | Rajshahi | 90 | 20:00
Uttara | 41 | 13:00 | Dohazari | 64 | 18:30 | Rajshahi New | 8 | 20:00
Uttara New | 25 | 10:00 | Cox'sbazar | 70 | 19:30 | C.Nawabganj | 48 | 18:00
Kamrangirchar | 59 | 13:00 | Chandraghona | 22 | 18:00 | Amnura | 23 | 19:00
Savar | 102 | 18:30 | Kaptai | 4 | 18:00 | Pabna | 70 | 18:30
Bhasantec | 118 | 18:30 | A. Khaer Stl. | 14 | 16:00 | Shahjadpur | 77 | 19:00
Agargaon | 39 | 13:00 | Bakulia | 77 | 18:00 | Serajganj | 66 | 18:30
Satmosjid | 79 | 13:00 | Julda | 16 | 1:00 | Niyamatpur | 42 | 19:00
Tongi | 113 | 15:00 | TK chemical | 2.4 | 7:00 | Joypurhat | 44 | 20:00
Kabirpur | 165 | 15:00 | Modern Steel | 15 | 12:00 | Sherpur(Bogura) | 35 | 18:00
Basundhara | 97 | 13:00 | Shahmirpur | 22 | 17:00 | Mohastangor | 10 | 8:00
Manikganj | 60 | 19:30 | Khagrachhari | 12 | 7:00 | Rangpur | 96 | 18:30
Joydevpur | 164 | 18:00 | Matarbari | 21 | 18:30 | Lalmonirhat | 39 | 18:00
New Tongi | 95 | 19:00 | Baroiar Hat | 16 | 19:00 | Saidpur | 82 | 18:00
Korda | 208 | 10:00 | Rangamati | 8 | 18:00 | Purbasadipur | 58 | 6:00
Dhamrai | 48 | 18:30 | Abul Khair 230 | 32 | 21:00 | Thakurgaon | 36 | 17:00
Valuka | 76 | 18:30 | BSRM | 109 | 11:00 | Palashbari | 81 | 18:00
Tangail | 130 | 18:00 | GPH Ispat | 5 | 5:00 | Barapukuria | 42 | 19:00
Mymensing | 149 | 18:00 | Goalpara | 18 | 18:30 | Panchagar | 25 | 17:00
Kishorganj | 80 | 20:00 | Central s/s | 60 | 18:00 | Joldhaka | 18 | 18:00
Netrokona | 68 | 18:00 | Noapara | 45 | 18:30 | Kurigram | 42 | 18:00
Jamalpur | 84 | 21:00 | Jessore | 80 | 18:30
Sherpur | 66 | 21:00 | Benapol | 28 | 19:30
Srimongal | 26 | 18:00 | Jhenida | 69 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-09 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 389 | 0.875 | 383 | 0.45833 | Kaliakoir | 374 | 0.125 | 363 | 0.5
Bheramara | 409 | 0.16667 | 393 | 0.75 | Bhulta | 391 | 0.91667 | 381 | 0.5
Ashuganj(N) | 394 | 0.875 | 386 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 0.625 | 225 | 0.041667 | Hathazari | 221 | 0.875 | 212 | 0.45833
Ishurdi | 241 | 0.20833 | 226 | 0.75 | Megnaghat | 223 | 0.16667 | 220 | 0.41667
Ashuganj | 235 | 0.041667 | 231 | 0.45833 | Fenchuganj | 235 | 0.25 | 231 | 0.45833
Serajganj | 234 | 0.083333 | 230 | 0.29167 | Siddhirganj | 225 | 0.041667 | 220 | 0.5
Baghabari | 240 | 0.95833 | 233 | 0.75 | Maniknagar | 224 | 0.041667 | 218 | 0.5
Barapukuria | 232 | 0.70833 | 225 | 0.33333 | Old Airport | 223 | 0.125 | 214 | 0.5
Bogra | 232 | 0.16667 | 224 | 0.5 | Barisal | 232 | 0.20833 | 220 | 0.75
Khulna South | 237 | 0.20833 | 213 | 0.75 | AKSML | 220 | 0.875 | 0 | 0.54167
Rampura | 224 | 0.041667 | 221 | 0.375 | BSRM | 221 | 0.875 | 214 | 0.45833
Haripur | 222 | 0.125 | 220 | 0.375 | Bibiyana | 232 | 0.125 | 227 | 0.45833
Hasnabad | 222 | 0.16667 | 217 | 0.58333 | Bhulta | 226 | 0.125 | 220 | 0.5
Aminbazar | 224 | 0.041667 | 217 | 0.45833 | Ashuganj (S) | 233 | 0.79167 | 229 | 0.45833
Tongi | 219 | 0.75 | 212 | 0.45833 | Kaliakoir | 227 | 0.041667 | 220 | 0.5
Comilla (N) | 230 | 0.20833 | 224 | 0.45833 | GPH | 217 | 0.875 | 210 | 0.041667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.041667 | 132 | 0.45833 | Halishahar | 132 | 0.875 | 125 | 0.5
Munsiganj | 134 | 0.041667 | 130 | 0.5 | Baraulia | 129 | 0.83333 | 124 | 0.45833
Sonargaon | 133 | 0.041667 | 131 | 0.5 | Sikalbaha | 130 | 0.79167 | 125 | 0.45833
Shyampur | 136 | 0.083333 | 131 | 0.5 | Dohazari | 129 | 0.70833 | 124 | 0.45833
Bhulta | 128 | 0.041667 | 126 | 0.41667 | Cox'sbazar | 126 | 0.16667 | 117 | 0.45833
Madanganj | 134 | 0.16667 | 129 | 0.5 | Chandraghona | 131 | 0.8125 | 127 | 0.45833
Shitalakhya | 137 | 0.041667 | 130 | 0.41667 | Kaptai | 132 | 0.875 | 127 | 0.41667
Rahim steal | 136 | 3:00 | 132 | 0.5 | A. Khaer Stl. | 130 | 0.875 | 125 | 0.45833
Matuail | 135 | 0.125 | 130 | 0.54167 | Bakulia | 128 | 0.29167 | 123 | 0.66667
Ghorasal | 137 | 0.70833 | 134 | 0.625 | Julda | 129 | 0.79167 | 124 | 0.58333
Narsinghdi | 132 | 0.41667 | 123 | 0.77083 | TK Chemical | 130 | 0.83333 | 125 | 0.45833
Haripur (SBU) | 136 | 0.16667 | 133 | 0.41667 | Modern Steel | 129 | 0.8125 | 124 | 0.5
Ullon | 134 | 0.20833 | 131 | 0.66667 | Shahmirpur | 130 | 0.875 | 124 | 0.5
Hasnabad | 137 | 0.25 | 129 | 0.5 | Khagrachhari | 131 | 0.875 | 126 | 0.5
Magbazar | 135 | 0.125 | 130 | 0.45833 | Matarbari | 129 | 0.70833 | 123 | 0.83333
Maniknagar | 138 | 0.16667 | 135 | 0.5 | Baroiar Hat | 131 | 0.29167 | 126 | 0.45833
Bangabhaban | 138 | 0.16667 | 135 | 0.5 | Rangamati | 131 | 0.875 | 126 | 0.5
Narinda | 138 | 0.16667 | 135 | 0.5 | Goalpara | 138 | 0.125 | 126 | 18:30
Dhanmondi | 134 | 0.20833 | 131 | 0.66667 | Central s/s | 138 | 0.20833 | 126 | 18:30
Lalbag | 137 | 0.25 | 129 | 0.45833 | Noapara | 133 | 0.625 | 122 | 0.33333
Madartek | 134 | 0.25 | 130 | 0.5 | Jessore | 131 | 0.625 | 120 | 0.375
Mirpur | 136 | 0.25 | 131 | 0.58333 | Benapol | 134 | 0.16667 | 122 | 0.33333
Kalyanpur | 137 | 0.041667 | 134 | 0.5 | Jhenida | 133 | 0.125 | 117 | 0.75
Gulshan | 134 | 0.041667 | 129 | 0.5 | Bottail | 136 | 0.25 | 120 | 0.77083
Uttara | 136 | 0.083333 | 131 | 0.54167 | G.K Project | 140 | 0.125 | 131 | 0.8125
Uttara New | 135 | 0.041667 | 130 | 0.5 | Faridpur | 133 | 0.625 | 120 | 0.75
Kamrangirchar | 135 | 0.041667 | 128 | 0.5 | Madaripur | 133 | 0.70833 | 121 | 0.75
Savar | 135 | 0.79167 | 129 | 0.5 | Sariatpur | 134 | 0.91667 | 122 | 0.75
Bhasantec | 135 | 0.25 | 128 | 0.5 | Gopalganj | 141 | 0.91667 | 125 | 0.75
Agargaon | 136 | 0.16667 | 129 | 0.5 | Bagerhat | 135 | 0.16667 | 121 | 0.75
Satmosjid | 135 | 0.125 | 129 | 0.5 | Mongla | 132 | 0.25 | 120 | 0.75
Tongi | 134 | 0.95833 | 129 | 0.45833 | Satkhira | 136 | 0.20833 | 122 | 0.75
Kabirpur | 133 | 1904-01-02 | 128 | 0.75 | Gallamari | 139 | 0.16667 | 125 | 0.75
Basundhara | 133 | 22:00 | 127 | 0.5 | Magura | 133 | 0.20833 | 120 | 0.75
Manikganj | 136 | 17:00 | 130 | 0.625 | Norail | 134 | 0.16667 | 121 | 0.8125
Joydevpur | 138 | 0.79167 | 132 | 0.5 | Chuadanga | 132 | 0.16667 | 114 | 0.75
New Tongi | 133 | 1904-01-02 | 127 | 0.625 | Barisal(N) | 135 | 0.16667 | 126 | 0.75
Kodda | 137 | 0.54167 | 126 | 0.33333 | Barisal (S) | 135 | 0.91667 | 125 | 0.041667
Dhamrai | 132 | 1904-01-02 | 128 | 0.75 | Patuakhali | 130 | 0.91667 | 120 | 0.75
Valuka | 130 | 0.91667 | 122 | 0.75 | Bhandaria | 134 | 0.041667 | 123 | 0.75
Tangail | 134 | 0 | 126 | 0.5 | Ishurdi | 137 | 0.20833 | 129 | 0.75
Mymensing | 133 | 0.041667 | 124 | 0.75 | Ruppur Paromanobik | 135 | 0.25 | 131 | 0.5
Kishorganj | 131 | 0.16667 | 125 | 0.75 | Natore | 135 | 0.25 | 126 | 0.54167
Netrokona | 131 | 0.91667 | 122 | 0.75 | Bogra | 138 | 0.70833 | 130 | 0.54167
Jamalpur | 136 | 0.54167 | 127 | 0.16667 | Noagaon | 135 | 0.16667 | 122 | 0.54167
Sherpur | 136 | 0.91667 | 122 | 0.25 | Rajshahi | 131 | 0.083333 | 123 | 0.54167
Srimongal | 136 | 1:00 | 135 | 0.45833 | Rajshahi New | 132 | 0.25 | 121 | 0.5
Shahjibazar | 136 | 0.20833 | 131 | 0.375 | C.Nawabganj | 131 | 0.70833 | 116 | 0.5
Fenchuganj | 136 | 0.25 | 133 | 0.041667 | Amnura | 130 | 0.041667 | 116 | 0.54167
Khulawara | 136 | 0.16667 | 133 | 15:00 | Pabna | 137 | 0.25 | 130 | 0.70833
Sylhet | 135 | 0.25 | 132 | 0.041667 | Shahjadpur | 142 | 0.25 | 135 | 0.54167
Chatak | 134 | 0.25 | 131 | 0.125 | Serajganj | 137 | 0.25 | 130 | 0.54167
Sunamganj | 135 | 0.29167 | 130 | 0.083333 | Niyamatpur | 133 | 0.70833 | 122 | 0.54167
Biani Bazar | 135 | 0.041667 | 132 | 0.625 | Joypurhat | 135 | 0.25 | 122 | 0.54167
Comilla(s) | 131 | 0.125 | 125 | 0.75 | Sherpur(Bogura) | 138 | 0.16667 | 130 | 0.5
Comilla(n) | 137 | 0.29167 | 133 | 0.45833 | Mohastangor | 137 | 0.70833 | 128 | 0.33333
Chandpur | 134 | 7:00 | 132 | 0.041667 | Rangpur | 132 | 0.70833 | 122 | 0.5
Feni | 132 | 0.29167 | 127 | 0.5 | Lalmonirhat | 128 | 0.70833 | 119 | 0.5
Chowmuhani | 130 | 0.33333 | 125 | 0.75 | Saidpur | 129 | 0.20833 | 122 | 0.5
Ashuganj | 132 | 0.54167 | 130 | 0.66667 | Purbasadipur | 129 | 0.29167 | 114 | 0.33333
Daudkandi | 134 | 0.91667 | 131 | 0.41667 | Thakurgaon | 122 | 0.70833 | 115 | 0.5
B.Baria | 131 | 0.041667 | 127 | 0.625 | Palashbari | 134 | 0.25 | 125 | 0.5
Ramganj | 128 | 0.625 | 126 | 0.70833 | Barapukuria | 132 | 0.70833 | 125 | 0.5
Chaddagram | 133 | 0.33333 | 129 | 0.5 | Panchagar | 121 | 0.20833 | 110 | 0.33333
PHP | 130 | 0.29167 | 127 | 0.45833 | Joldhaka | 128 | 0.70833 | 120 | 0.5
Madanhat | 132 | 0.83333 | 127 | 0.5 | Kurigram | 130 | 0.70833 | 122 | 0.5
Hathazari | 132 | 0.8125 | 126 | 0.45833
Khulshi | 128 | 0.83333 | 123 | 0.45833

## L-Curve
Date | 2019-12-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 202 | 4817 | 1621 | 6438 |  |  |  | QF-LDC-12
0:30 | 238.5 | 4700.5 | 1513 | 6213.5 | Date: | 2019-12-09
1:00 | 275 | 4584 | 1405 | 5989
1:30 | 241 | 4428.5 | 1422.5 | 5851
2:00 | 207 | 4273 | 1440 | 5713
2:30 | 161 | 4183.5 | 1454 | 5637.5 | [5 empty] | Gen. at Eve. Peak | 8721 | 8721 MW (19:00 )
3:00 | 115 | 4094 | 1468 | 5562 | [6 empty] | 19:00
3:30 | 80 | 3998.5 | 1476.5 | 5475 | [5 empty] | Gen. at Day Peak | 6965.248 | 6965.248 MW (12:00 )
4:00 | 45 | 3903 | 1485 | 5388 | [6 empty] | 12:00
4:30 | 60 | 3905 | 1496.5 | 5401.5 | [5 empty] | Highest Generation | 8721
5:00 | 75 | 3907 | 1508 | 5415 | [6 empty] | 19:00
5:30 | 37.5 | 3994 | 1515 | 5509
6:00 | 0 | 4081 | 1522 | 5603
6:30 | 141 | 4243.95 | 1528.55 | 5772.5
7:00 | 282 | 4406.9 | 1535.1 | 5942
7:30 | 318.5 | 4608.2455 | 1556.55 | 6164.7955
8:00 | 355 | 4809.591 | 1578 | 6387.591
8:30 | 279 | 4879.6545 | 1629 | 6508.6545
9:00 | 203 | 4949.718 | 1680 | 6629.718
9:30 | 149 | 4891.499 | 1680.6 | 6572.099
10:00 | 95 | 4833.28 | 1681.2 | 6514.48
10:30 | 67 | 4882.6235 | 1711.2 | 6593.8235
11:00 | 39 | 4931.967 | 1741.2 | 6673.167
11:30 | 80 | 5064.5075 | 1754.7 | 6819.2075
12:00 | 121 | 5197.048 | 1768.2 | 6965.248
12:30 | 164 | 5265.259 | 1764 | 7029.259
13:00 | 207 | 5333.47 | 1759.8 | 7093.27
13:30 | 158.5 | 5171.59 | 1751 | 6922.59
14:00 | 110 | 5009.71 | 1742.2 | 6751.91
14:30 | 60 | 5010.755 | 1735.9 | 6746.655
15:00 | 10 | 5011.8 | 1729.6 | 6741.4
15:30 | 16 | 5010.95 | 1711.8 | 6722.75
16:00 | 22 | 5010.1 | 1694 | 6704.1
16:30 | 86.5 | 5028.55 | 1813.05 | 6841.6
17:00 | 151 | 5047 | 1932.1 | 6979.1
17:30 | 117.5 | 5545.5 | 2246.55 | 7792.05
18:00 | 84 | 6044 | 2561 | 8605
18:30 | 97 | 6082 | 2581 | 8663
19:00 | 110 | 6120 | 2601 | 8721
19:30 | 126 | 6019 | 2519 | 8538
20:00 | 134 | 5963 | 2514 | 8477 |  |  |  | Executive Engineer
20:30 | 112 | 5840.5 | 2456 | 8296.5 |  |  |  | Network Operation Division
21:00 | 90 | 5718 | 2398 | 8116
21:30 | 118 | 5551 | 2245 | 7796
22:00 | 146 | 5384 | 2092 | 7476 |  |  |  |  | Page 6 of 7
22:30 | 136.5 | 5159.5 | 1978.5 | 7138
23:00 | 127 | 4935 | 1865 | 6800
23:30 | 164.5 | 4876 | 1743 | 6619
24:00 | 202 | 4817 | 1621 | 6438
8721 MW (19:00 )
6965.248 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-09 |  | Energy | 165169078
[10 empty] | 2019-12-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3874 | 189 | 1938 | 200 | 180 | 81 | 0 | 0 | 84
0:30 | 3801 | 163 | 1835.5 | 136 | 169.5 | 80.5 | 0 | 0 | 82 | Date: | 2019-12-09
1:00 | 3728 | 137 | 1733 | 72 | 159 | 80 | 0 | 0 | 80
1:30 | 3688.5 | 136.5 | 1639 | 69 | 159 | 80 | 0 | 0 | 79 | [7 empty] | Total Energy | 165.1691 | Total Energy Gen 165.169 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.169 MKWHr
2:00 | 3649 | 136 | 1545 | 66 | 159 | 80 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3616 | 136.5 | 1502 | 66 | 159 | 80 | 0 | 0 | 78 | [7 empty] | Energy Requirement | 165.1691
3:00 | 3583 | 137 | 1459 | 66 | 159 | 80 | 0 | 0 | 78
3:30 | 3551 | 133 | 1433.5 | 41 | 159.5 | 80 | 0 | 0 | 77 | [6 empty] | Shortage
4:00 | 3519 | 129 | 1408 | 16 | 160 | 80 | 0 | 0 | 76
4:30 | 3537.5 | 129 | 1410 | 8 | 160 | 81 | 0 | 0 | 76
5:00 | 3556 | 129 | 1412 | 0 | 160 | 82 | 0 | 0 | 76
5:30 | 3599 | 128.5 | 1464.5 | 0 | 160 | 82 | 0 | 0 | 75
6:00 | 3642 | 128 | 1517 | 0 | 160 | 82 | 0 | 0 | 74
6:30 | 3725 | 128 | 1603.5 | 0 | 160 | 82 | 0 | 0 | 73 |  |  |  |  | Coal
7:00 | 3808 | 128 | 1690 | 0 | 160 | 82 | 0 | 0 | 72
7:30 | 3872 | 128 | 1812.5 | 30.5 | 160 | 81.5 | 0 | 0 | 75 |  |  |  | Oil |  |  |  | ,
8:00 | 3936 | 128 | 1935 | 61 | 160 | 81 | 0 | 0 | 78
8:30 | 3903 | 206.5 | 1918.5 | 145 | 160 | 81.5 | 0 | 0 | 80
9:00 | 3870 | 285 | 1902 | 229 | 160 | 82 | 0 | 0 | 82
9:30 | 3846.5 | 285.5 | 1883 | 218.5 | 160 | 82 | 0 | 0 | 82
10:00 | 3823 | 286 | 1864 | 208 | 160 | 82 | 0 | 0 | 82
10:30 | 3851 | 286 | 1888.5 | 228 | 170 | 82 | 0 | 0 | 78
11:00 | 3879 | 286 | 1913 | 248 | 180 | 82 | 0 | 0 | 74
11:30 | 3946 | 286 | 1954.5 | 279 | 180 | 81.5 | 0 | 0 | 81
12:00 | 4013 | 286 | 1996 | 310 | 180 | 81 | 0 | 0 | 88
12:30 | 4018.5 | 286 | 2016.5 | 349 | 180 | 79.5 | 0 | 0 | 89
13:00 | 4024 | 286 | 2037 | 388 | 180 | 78 | 0 | 0 | 90
13:30 | 4024 | 286 | 2037 | 388 | 180 | 78 | 0 | 0 | 90
14:00 | 4024 | 286 | 2037 | 388 | 180 | 78 | 0 | 0 | 90
14:30 | 3982 | 286.5 | 1972 | 320 | 180 | 78 | 0 | 0 | 91
15:00 | 3940 | 287 | 1907 | 252 | 180 | 78 | 0 | 0 | 92
15:30 | 3935.5 | 286.5 | 1896 | 252 | 179.5 | 78.5 | 0 | 0 | 91
16:00 | 3931 | 286 | 1885 | 252 | 179 | 79 | 0 | 0 | 90
16:30 | 3896.5 | 358.5 | 1828 | 382.5 | 179.5 | 79 | 21.5 | 0 | 95
17:00 | 3862 | 431 | 1771 | 513 | 180 | 79 | 43 | 0 | 100
17:30 | 3968.5 | 529.5 | 1963.5 | 875.5 | 180 | 79.5 | 88.5 | 0 | 107
18:00 | 4075 | 628 | 2156 | 1238 | 180 | 80 | 134 | 0 | 114
18:30 | 4082 | 627.5 | 2140 | 1328.5 | 180 | 80 | 113 | 0 | 112
19:00 | 4089 | 627 | 2124 | 1419 | 180 | 80 | 92 | 0 | 110
19:30 | 4093 | 628 | 2144 | 1263 | 180 | 80 | 40 | 0 | 110
20:00 | 4087 | 627 | 2161 | 1200 | 180 | 80 | 32 | 0 | 110
20:30 | 4071 | 627.5 | 2128 | 1076.5 | 180 | 80.5 | 24 | 0 | 109
21:00 | 4055 | 628 | 2095 | 953 | 180 | 81 | 16 | 0 | 108
21:30 | 4058.5 | 579 | 2106 | 679.5 | 180 | 81 | 8 | 0 | 104
22:00 | 4062 | 530 | 2117 | 406 | 180 | 81 | 0 | 0 | 100
22:30 | 4005.5 | 423 | 2050.5 | 303 | 180 | 81 | 0 | 0 | 95
23:00 | 3949 | 316 | 1984 | 200 | 180 | 81 | 0 | 0 | 90
23:30 | 3911.5 | 252.5 | 1961 | 200 | 180 | 81 | 0 | 0 | 87 | Max Temp. in Dhaka |  | 27.4° C
24:00 | 3874 | 189 | 1938 | 200 | 180 | 81 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.169 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.169 MKWHr
Note on W13: Author:

## Generation
2019-12-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 41 | 42 | 42 | 42 | 41 | 38 | 38 | 38 | 39 | 39 | 40 |  | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 931216
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.5 | 6.63 | 12.91 | 0 |  |  | 0 | 13.31 | [12 empty] | 32000
6 | Sikalbaha 225MW CCPP (Gas) | 183 | 183 | 183 | 182 | 182 | 186 | 215 | 206 | 204 | 204 | 229 | 229 | 204 | 204 | 204 | 204 | 204 | 205 |  | 204 | 204 | 204 | 203 | 203 | 178 | 177 | 4756151
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 11 | 34 |  | 17 | 0 | 0 |  |  |  |  | 62629
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 0 | 4 | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 54 | 95 |  | 105 | 105 | 105 | 105 | 105 |  | 0 | 1037922
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 60 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 35 | 35 | 38 | 60 | 90 | 35 | 37 | 37 | 35 | 36 |  | 57 | 62 | 61 | 57 | 60 | 38 | 38 | 1119000
17 | Siddhirganj 335 MW CCPP | 340 | 340 | 270 | 240 | 240 | 240 | 240 | 350 | 354 | 300 | 300 | 338 | 335 | 337 | 337 | 338 | 270 | 347 |  | 352 | 352 | 351 | 354 | 338 | 339 | 341 | 7717340
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 0 | 5 | 15 | 15 | 0 |  |  | 11 | 97 |  | 145 | 150 | 145 | 95 | 0 |  |  | 579600
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 40 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 552000
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 856000
21 | Ghorasal Repowered CCPP Unit-3 | 199 | 169 | 169 | 169 | 169 | 169 | 169 | 168 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 |  | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 4228400
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2056288
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2364905
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 33 | 33 | 33 | 33 | 33 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 33 | 37 | 37 | 37 | 712008
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 330 | 330 | 320 | 275 | 265 | 280 | 280 | 180 | 180 | 180 | 180 | 180 | 260 | 360 | 365 | 370 | 365 | 365 |  | 320 | 320 | 320 | 320 | 320 | 320 | 265 | 7032500
| Ashuganj 450 MW CCPP(North) | 345 | 345 | 335 | 290 | 265 | 280 | 285 | 340 | 330 | 330 | 340 | 360 | 330 | 265 | 265 | 265 | 265 | 340 |  | 340 | 340 | 340 | 340 | 340 | 285 | 262 | 7790900
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 88 | 86 | 86 | 87 | 90 | 91 | 91 | 90 | 80 | 85 | 90 | 91 | 80 | 90 | 86 | 82 | 81 | 86 |  | 80 | 80 | 80 | 80 | 90 | 90 | 80 | 2041480
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 343 | 346 | 347 | 347 | 360 | 363 | 370 | 344 | 343 | 346 | 374 | 368 | 344 | 347 | 343 | 337 | 329 |  | 344 | 342 | 342 | 342 | 342 | 347 | 351 | 8486770
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 350 | 350 | 350 | 350 | 350 | 400 | 380 | 380 | 380 | 450 | 450 | 390 | 390 | 390 | 350 | 450 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 9338250
41 | Haripur 360MW CCPP(HPL) | 358 | 366 | 310 | 260 | 259 | 259 | 311 | 370 | 369 | 366 | 364 | 358 | 328 | 302 | 306 | 306 | 274 | 334 |  | 318 | 317 | 313 | 313 | 316 | 291 | 291 | 7615000
42 | RPCL 210MW CCPP | 146 | 114 | 114 | 142 | 162 | 162 | 162 | 161 | 160 | 157 | 155 | 153 | 154 | 140 | 140 | 142 | 145 | 145 |  | 146 | 145 | 145 | 147 | 140 | 140 | 144 | 3439680
43
44 | Fenchugonj CCPP Phase-1 | 28 | 30 | 30 | 29 | 30 | 30 | 28 | 27 | 30 | 30 | 28 | 28 | 28 | 28 | 27 | 28 | 28 | 28 |  | 29 | 28 | 28 | 29 | 28 | 29 | 28 | 685000
45 | Fenchugonj CCPP Phase-2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1324920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 69 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 68 |  | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 1390368
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 5 | 5 | 5 | 5 | 5 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1474560
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP |  |  |  |  | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 352000
52 | Sylhet 50MW PP (EPL) |  |  |  |  | 0 | 31 | 30 | 30 | 30 | 31 | 33 | 35 | 37 | 36 | 38 | 37 | 40 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 692500
53 | Sylhet 10MW PP (Desh) |  |  |  |  | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 195480
54 | Hobiganj 11MW PP Cofidence-E | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 146160
55 | Fenchugonj 51 MW PP (Barakatullah) | [5 empty] | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 931800
56 | Shahjahanulla 25 MW PP | [7 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 407544
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 310 | 310 | 315 | 320 | 315 | 320 | 290 | 290 | 305 | 320 | 305 | 285 | 315 | 310 | 290 | 295 |  | 300 | 310 | 305 | 290 | 290 | 285 | 300 | 7485700
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 0 | 10 | 25 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 334783
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 438576
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 243828
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 22 | 314100
63 | Impoprt (Tripura) | 80 | 78 | 78 | 76 | 76 | 74 | 72 | 78 | 82 | 82 | 74 | 88 | 90 | 94 | 92 | 90 | 100 | 114 |  | 110 | 110 | 110 | 108 | 100 | 90 | 84 | 2116800
64 | Malancha, Ctg. EPZ (United) | 35 | 5 | 5 | 5 | 5 | 8 | 29 | 10 | 4 | 2 | 2 | 2 | 7 | 5 | 2 | 2 | 3 | 3 |  | 14 | 12 | 17 | 25 | 33 | 36 | 35 | 350400
65 | Feni 22MW PP (Doreen) | [6 empty] | 22 | 22 | 22 | 19 | 19 | 0 | 0 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 325512
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 151920
67 | Jangalia 33MW PP (Summit) | [7 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 569500
68 | Cumilla 25 MW PP (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 449920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 28 | 28 | 28 | 28 | 24 | 24 | 28 | 31 | 31 | 31 | 30 | 30 | 26 | 30 | 30 | 30 | 22 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 681660
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 827900
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 809700
73 | Ghorashal 108MW PP (Regent) | 110 | 0 |  |  |  |  | 0 | 80 | 107 | 110 | 107 | 104 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1910045
| Feni Lanka Power | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [7 empty] | 0 | 31 | 25 | 25 | 25 | 25 |  |  |  | 8 | 47 |  | 52 | 52 | 52 | 52 | 25 | 8 | 0 | 434112
79 | Kodda 150MW PP | [16 empty] | 32 | 100 |  | 75 | 40 | 32 | 16 |  |  | 0 | 258720
80 | Jamalpur 95 MW PP(Powerpac) | [9 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 0 |  |  | 93120
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [9 empty] | 0 | 5 | 17 | 17 |  |  |  | 2 | 70 |  | 70 | 17 | 17 |  |  |  | 0 | 217932
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.461 | 2.708 | 3.68 | 4.167 | 4.148 | 3.77 | 3 | 1.9 | 0.8 | 0 | 0 | [8 empty] | 25800
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 0 | 2 | 20 | 20 | [11 empty] | 0 | 68016
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 100 |  | 100 | 100 | 100 | 100 | 0 |  |  | 506760
92 | Fenchuganj 44MW (Energyprima) | [5 empty] | 8 | 47 | 47 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 886104
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 7 | 7 | 735096
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 0 | 3 | 10 | 32 | 0 | [12 empty] | 51696
95 | Patenga 50MW PP (Baraka) | [21 empty] | 0 |  |  |  | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 10 | 25 |  | 25 | 25 | 25 |  |  |  | 0 | 95040
97 | Katpotti 52 MW PP (Sinha) | 12 | 6 | 6 | 0 |  |  |  | 0 | 7 | 12 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 38 |  | 47 | 47 | 47 | 36 | 24 | 18 | 12 | 435552
98 | Bosila 108MW PP(CLC) | [9 empty] | 0 | 4 | 16 | 32 | 8 | 8 | 8 | 43 | 72 |  | 72 | 72 | 72 | 72 |  |  | 0 | 397440
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 0 | 3 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 0 | 0 |  |  |  |  | 119880
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 | 55 | 17 |  |  |  | 0 | 161960
101 | Kushiara 163 MW CCPP (KP) | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 163 | 100 | 100 | 100 | 100 | 163 |  | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 3057954
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 1.1 | 1.6 | 1.8 | 1.9 | 1.7 | 1.4 | 0.9 | 0.3 | 0 | 0 | [8 empty] | 11100
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 60 | 60 | 60 | 16 | 0 |  | 0 | 57 | 150 | 110 | 110 | 110 | 110 | 90 | 90 | 90 | 90 | 98 |  | 127 | 150 | 150 | 150 | 150 | 120 | 80 | 2296800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 10 |  | 10 | 10 | 10 | 0 |  |  |  | 39360
116 | Chandpur 200MW (Desh energy) | [16 empty] | 7 | 17 |  | 17 | 0 | 0 |  |  |  |  | 51360
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 10 | 50 |  | 50 | 50 | 50 |  |  |  | 0 | 182327
118 | Bibiyana-III 400 MW CCPP | 296 | 298 | 292 | 295 | 291 | 301 | 388 | 371 | 365 | 367 | 369 | 399 | 366 | 369 | 366 | 366 | 366 | 363 |  | 366 | 366 | 365 | 365 | 365 | 378 | 364 | 8443000
Jamalpur 115 MW PP (United)
| Anwara 300 MW PP (United) | [20 empty] | 0
120 | Eastern Zone Total | 4584 | 4273 | 4094 | 3903 | 3907 | 4081 | 4406.9 | 4809.591 | 4949.718 | 4833.28 | 4931.967 | 5197.048 | 5333.47 | 5009.71 | 5011.8 | 5010.1 | 5047 | 6044 |  | 6120 | 6019 | 5963 | 5718 | 5384 | 4935 | 4817 | 120305844
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 72000
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 5 | 38 |  | 64 | 64 | 64 | 64 | 48 | 0 |  | 304224
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 117 | 118 | 119 | 117 | 118 | 118 | 118 | 119 | 106 | 110 | 115 | 115 | 115 | 109 | 114 | 110 | 110 | 114 |  | 101 | 106 | 108 | 88 | 100 | 115 | 111 | 2697000
140 | Bhola 33 MW PP (Venture) | 22 | 21 | 22 | 20 | 20 | 20 | 20 | 18 | 17 | 17 | 17 | 19 | 19 | 17 | 17 | 17 | 20 | 26 |  | 25 | 26 | 26 | 26 | 25 | 23 | 23 | 487900
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 0 |  |  | 152250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 344736
146 | Bheramara HVDC | 137 | 136 | 137 | 129 | 129 | 128 | 128 | 128 | 285 | 286 | 286 | 286 | 286 | 286 | 287 | 286 | 431 | 628 |  | 627 | 628 | 627 | 628 | 530 | 316 | 189 | 7404363
147 | Bheramara 360 MW CCPP | 150 | 185 | 205 | 230 | 250 | 260 | 270 | 270 | 270 | 260 | 250 | 250 | 230 | 220 | 220 | 220 | 220 | 220 |  | 210 | 210 | 200 | 195 | 195 | 195 | 195 | 5567328
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 159 | 159 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 179 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4174700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 151 | 151 | 155 | 156 | 157 | 161 | 164 | 165 | 157 | 166 | 170 | 191 | 205 | 183 | 183 | 175 | 168 | 181 |  | 190 | 187 | 190 | 188 | 189 | 179 | 181 | 4431382
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 136 | 136 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 141 | 140 | 162 | 179 | 141 | 141 | 141 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 146 | 3629564
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | [24 empty] | 0
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 182 | 183 | 181 | 182 | 183 | 183 | 184 | 190 | 190 | 190 | 192 | 197 | 181 | 175 | 183 | 182 | 180 | 191 |  | 200 | 201 | 201 | 199 | 200 | 187 | 180 | 4732945
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 343 | 343 | 342 | 343 | 343 | 344 | 343 | 344 | 308 | 304 | 343 | 344 | 336 | 331 | 344 | 325 | 296 | 433 |  | 397 | 409 | 430 | 374 | 386 | 432 | 375 | 8658454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [6 empty] | 0 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 341760
163 | Bogura 20 MW PP (Energyprima) | [6 empty] | 0 | 14 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 205272
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 500808
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 24 | 24 | 12 | 0 |  |  | 135680
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 10 | 100 |  | 113 | 113 | 113 | 113 |  |  | 0 | 528672
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 4 | 35 |  | 35 | 0 | 0 |  |  |  |  | 79872
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 109 | 109 |  | 113 | 75 | 55 | 35 |  |  |  | 383040
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.1 | 0 | 3 | 4.2 | 5.2 | 5.2 | 4.8 | 4.2 | 2.6 | 1 | 0.1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 31284
178
178