## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-15 | Sunday
|  | Date (day): | 2019-12-15 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11211.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13923 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-14 | 2019-12-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 134 | 169 | 170 | 170
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under shut down
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 109 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 371 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 360 | 330 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 70 | 97 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 68 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 145 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1889 | 2402 | 3606 | 4206 | 598 | 819
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 84 | 81 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 211 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 5 | 60 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 8 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 506.2 | 649 | 1335 | 1495 | 210 | 428
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 120 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 130 | 140 | 120 | 120
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 360 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 345 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 112 | 100 | 112 | 83 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 31 | 90 | 90 | 90 |  | 73 | ST under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 70 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 11 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 102 | 97 | 121
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1219 | 1494 | 1693 | 2193 | 118 | 444
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 144 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 180 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 174.9 | 346 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 63 | 65 | 65 | 65
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 50 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 79 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 33 | 38 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 325 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 377 | 381 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1224 | 1337 | 1371 | 1371 | 0 | 489
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 205 | 534 | 305 | 651
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 4 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 295 | 200 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 1 | 35 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 501 | 813 | 775 | 1746 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 25 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 115 | 115 | 120 | 120 |  | 74 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 127 | 188 | 305 | 375 | 0 | 87
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 202 | 214 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 210 | 210 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 208 | 216 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 433 | 0 | 0 |  |  | Under maint
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 15 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 909 | 1021 | 1312 | 1578 | 121 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 200 | 220
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 161.2 | 273 | 321 | 367 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6711.3 | 8523 | 11211.6 | 13923 | 1089 | 2555
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6322.3076 | 8029 | 10561.7666 | 13116.0116
A. |  | 2019-12-14 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8523 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4782 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8523 | MW
3 | Day peak Generation : |  |  | 6711.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8029 | MW
4 | Evening peak Generation : |  |  | 8523 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 156.6176 | MKWHr | By Solar | 0.065686 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 136.1719 | MKWHr |  | By Oil: | 6.6349 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.9328 | MKWHr |  | By Hydro: | 1.8697 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1089 | MW | Dhaka | 3018 | 3018 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2555 | MW | Chittagong | 886 | 886 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3644 | MW | Khulna | 968 | 968 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1120.7 | MMCFD |  |  | Rajshahi | 804 | 804 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 127218679.34 | ii) Oil : | Taka | 64467473.72 | Comilla | 691 | 691 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16085152 | Total | Taka | 207771305.06 | Mymensingh | 636 | 636 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.283 | MKWHr. | Sylhet | 318 | 318 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -365 | MW (E to W) at | 19:00 | hrs | Barisal | 228 | 228 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -485 | MW at | 23:00 | hrs | Rangpur | 480 | 480 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.7° C |  |  | Total | 8029 | 8029 |  | 0
B. |  | 2019-12-15 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 27.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13923 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6900 | MW
4 | Reserve(Generation end) |  |  |  | 5223 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 159.8701 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5307 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 6.1004 | MKWHr. | ii) HVDC Flow at Peak Time |  | 534 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8422 | MKWHr. | iii) Maximum HVDC Flow : |  | 535 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.96 |  | (b) Today: | 97.84 |  | (c) Rule Curve: |  | 104.7
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 94 | 0 | 0 | 0 | 12 | 0 | 344 | 262 |  | 0 | 350 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 80 | 130 | 0 | 275 | 275 | 0 | 8 | 80 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 64 | 159 | 0 | 0 | 0 | 60 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 180 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3923 | 1450 | 5373 | 3528 | 137 | 1384 | 0 | 180 | 80 | 0 | 64 | 0 | 0 | 97.98
2:00 | 35 | 94 | 0 | 0 | 0 | 7 | 0 | 350 | 262 |  | 0 | 300 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 130 | 0 | 275 | 275 | 0 | 8 | 81 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 62 | 110 | 0 | 0 | 0 | 60 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 180 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3687 | 1487 | 5174 | 3343 | 137 | 1372 | 0 | 180 | 80 | 0 | 62 | 0 | 0 | 97.98
3:00 | 35 | 95 | 0 | 0 | 0 | 7 | 0 | 346 | 248 |  | 0 | 280 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 176 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 130 | 0 | 278 | 275 | 0 | 8 | 70 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 110 | 0 | 0 | 0 | 60 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3591 | 1429 | 5020 | 3246 | 137 | 1337 | 0 | 160 | 80 | 0 | 60 | 0 | 0 | 97.97
4:00 | 35 | 94 | 0 | 0 | 0 | 7 | 0 | 345 | 248 |  | 0 | 270 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 176 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 130 | 0 | 274 | 270 | 0 | 8 | 50 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 112 | 0 | 0 | 0 | 60 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3487 | 1322 | 4809 | 3145 | 136 | 1228 | 0 | 160 | 80 | 0 | 60 | 0 | 0 | 97.97
5:00 | 35 | 94 | 0 | 0 | 0 | 7 | 0 | 345 | 248 |  | 0 | 270 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 177 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 130 | 0 | 273 | 270 | 0 | 8 | 50 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 110 | 0 | 0 | 0 | 35 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3461 | 1321 | 4782 | 3117 | 137 | 1228 | 0 | 160 | 80 | 0 | 60 | 0 | 0 | 97.96
6:00 | 35 | 94 | 0 | 0 | 0 | 7 | 0 | 362 | 277 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 130 | 0 | 302 | 300 | 0 | 8 | 52 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 62 | 113 | 0 | 0 | 0 | 35 | 65 | 5 | 2 | 100 | 0 | 41 | 5 | 0 | 0 | 0 | 4 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3759 | 1369 | 5128 | 3333 | 136 | 1357 | 0 | 160 | 80 | 0 | 62 | 0 | 0 | 97.96
7:00 | 35 | 93 | 0 | 0 | 0 | 7 | 0 | 369 | 288 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 80 | 130 | 0 | 300 | 300 | 0 | 8 | 50 | 25 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 160 | 0 | 0 | 0.1 | 35 | 65 | 5 | 2 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 4 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  | 135 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 3936.5 | 1460.1 | 5396.6 | 3497 | 135 | 1462 | 0 | 160 | 80 | 0 | 60 | 2.6 | 0 | 97.95
8:00 | 35 | 95 | 0 | 0 | 0 | 7 | 0 | 375 | 344 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 16 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 130 | 0 | 350 | 360 | 0 | 45 | 50 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68 | 161 | 0 | 0 | 0.5 | 58 | 65 | 5 | 4 | 130 | 0 | 69 | 5 | 0 | 0 | 0 | 4 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 141 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 0 | 0 | 159 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4405.8 | 1610.5 | 6016.3 | 3856 | 141 | 1701 | 0 | 159 | 82 | 0 | 68 | 9.3 | 0 | 97.95
9:00 | 35 | 95 | 0 | 0 | 0 | 43 | 0 | 367 | 364 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 17 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 80 | 130 | 0 | 335 | 320 | 0 | 83 | 50 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 161 | 0 | 0 | 1.2 | 60 | 65 | 5 | 50 | 130 | 0 | 67 | 74 | 0 | 0 | 0 | 26 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 |  | 205 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 11 | 0 | 0 | 160 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4594.8 | 1697.2 | 6292 | 3809 | 205 | 1960 | 0 | 160 | 84 | 0 | 70 | 4 | 0 | 97.94
10:00 | 35 | 95 | 0 | 0 | 0 | 43 | 0 | 346 | 330 |  | 0 | 370 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 33 | 17 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 3 | 80 | 130 | 0 | 340 | 325 | 0 | 83 | 50 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 10 | 72 | 156 | 0 | 0 | 1.7 | 60 | 65 | 5 | 50 | 130 | 0 | 67 | 76 | 0 | 0 | 0 | 27 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 7 | 3.6 | 0 | 0 | 0 | 0 |  | 205 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4495.3 | 1661.4 | 6156.7 | 3761 | 205 | 1861 | 7 | 160 | 84 | 0 | 72 | 6.7 | 0 | 97.94
11:00 | 35 | 95 | 0 | 0 | 0 | 43 | 0 | 355 | 320 |  | 0 | 370 | 0 | 0 | 0 | 0 | 300 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 33 | 17 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 80 | 130 | 0 | 295 | 340 | 0 | 83 | 30 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 0 | 10 | 76 | 155 | 0 | 22 | 1.8 | 60 | 65 | 5 | 50 | 130 | 0 | 65 | 76 | 0 | 0 | 0 | 30 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 51 | 4.1 | 0 | 0 | 0 | 0 |  | 205 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4582.9 | 1663.5 | 6246.4 | 3791 | 205 | 1873 | 51 | 160 | 84 | 0 | 76 | 6.4 | 0 | 97.93
12:00 | 35 | 134 | 0 | 0 | 0 | 95 | 0 | 371 | 360 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 33 | 17 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 8 | 100 | 130 | 0 | 350 | 345 | 0 | 83 | 31 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 30 | 12 | 80 | 151 | 0 | 22 | 1.9 | 60 | 63 | 25 | 50 | 130 | 0 | 65 | 79 | 0 | 0 | 17 | 33 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 51 | 4.2 | 0 | 0 | 0 | 0 |  | 205 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 409 | 0 | 0 | 0 | 1 | 0 | 0 | 1.2 | 0 |  | 5013.1 | 1698.2 | 6711.3 | 4047 | 205 | 2071 | 57 | 160 | 84 | 0 | 80 | 7.3 | 0 | 97.93
13:00 | 35 | 135 | 0 | 0 | 0 | 101 | 0 | 368 | 363 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 33 | 17 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 14 | 100 | 130 | 0 | 325 | 320 | 0 | 112 | 30 | 37 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 80 | 151 | 0 | 22 | 1.8 | 58 | 65 | 50 | 50 | 130 | 0 | 65 | 79 | 0 | 0 | 17 | 33 | 10 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 66 | 3.7 | 0 | 0 | 0 | 0 |  | 205 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 114 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 384 | 0 | 0 | 0 | 1 | 0 | 0 | 4.6 | 0 |  | 5068.5 | 1682.6 | 6751.1 | 3994 | 205 | 2134 | 84 | 160 | 82 | 2 | 80 | 10.1 | 0 | 0
14:00 | 35 | 135 | 0 | 0 | 0 | 105 | 0 | 348 | 300 |  | 0 | 370 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 33 | 17 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 10 | 100 | 140 | 0 | 285 | 290 | 0 | 112 | 31 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 10 | 84 | 151 | 0 | 22 | 1.4 | 60 | 65 | 50 | 50 | 100 | 0 | 64 | 79 | 0 | 0 | 17 | 34 | 10 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 86 | 3.159 | 0 | 0 | 0 | 0 |  | 206 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 115 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 409 | 0 | 0 | 0 | 5 | 0 | 0 | 1.6 | 0 |  | 4807.559 | 1651.6 | 6459.159 | 3784 | 206 | 2024 | 108 | 160 | 82 | 5 | 84 | 6.159 | 0 | 97.92
15:00 | 35 | 134 | 0 | 0 | 0 | 104 | 0 | 356 | 300 |  | 0 | 370 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 33 | 17 | 0 | 0 | 41 | 40 | 120 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 6 | 100 | 140 | 0 | 295 | 305 | 0 | 112 | 31 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 0 | 80 | 151 | 0 | 20 | 1 | 60 | 65 | 50 | 50 | 130 | 0 | 63 | 79 | 0 | 0 | 17 | 34 | 10 | 315 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 105 | 2.046 | 0 | 0 | 0 | 0 |  | 205 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 370 | 0 | 0 | 0 | 4 | 0 | 0 | 2.4 | 0 |  | 4894.046 | 1568.4 | 6462.446 | 3785 | 205 | 2020 | 126 | 160 | 81 | 0 | 80 | 5.446 | 0 | 0
16:00 | 35 | 134 | 0 | 0 | 0 | 105 | 0 | 358 | 300 |  | 0 | 370 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 9 | 33 | 17 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 8 | 100 | 140 | 0 | 300 | 305 | 0 | 112 | 31 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 3 | 80 | 151 | 0 | 20 | 0.2 | 60 | 65 | 50 | 50 | 130 | 0 | 64 | 79 | 0 | 0 | 17 | 35 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 68 | 0.826 | 0 | 0 | 0 | 0 |  | 192 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 369 | 0 | 0 | 0 | 7 | 0 | 0 | 1.1 | 0 |  | 4859.026 | 1566.1 | 6425.126 | 3807 | 192 | 2012 | 92 | 160 | 80 | 0 | 80 | 2.126 | 0 | 97.91
17:00 | 35 | 134 | 0 | 0 | 0 | 108 | 0 | 380 | 300 |  | 0 | 370 | 0 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 16 | 0 | 26 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 9 | 33 | 17 | 6 | 0 | 40 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 6 | 0 | 18 | 8 | 100 | 140 | 0 | 300 | 305 | 0 | 112 | 31 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 10 | 11 | 33 | 12 | 88 | 154 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 130 | 0 | 65 | 79 | 0 | 0 | 17 | 36 | 10 | 315 | 24 | 0 | 0 | 11 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 7 | 0 | 367 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 192 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 16 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 370 | 0 | 0 | 1 | 14 | 35 | 0 | 0.1 | 0 |  | 5050 | 1646.1 | 6696.1 | 3850 | 192 | 2033 | 277 | 160 | 80 | 16 | 88 | 0.1 | 0 | 97.9
18:00 | 35 | 158 | 0 | 0 | 0 | 109 | 0 | 376 | 340 |  | 0 | 450 | 0 | 0 | 0 | 0 | 340 | 0 | 95 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 30 | 0 | 17 | 17 | 22 | 25 | 15 | 33 | 17 | 38 | 0 | 40 | 40 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 34 | 60 | 12 | 0 | 18 | 8 | 110 | 140 | 0 | 335 | 360 | 0 | 112 | 91 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 102 | 153 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 38 | 10 | 320 | 24 | 8 | 0 | 130 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 60 | 0 | 419 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 21 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 431 | 0 | 0 | 32 | 35 | 85 | 0 | 0 | 0 |  | 6113 | 2249 | 8362 | 4253 | 534 | 2261 | 918 | 160 | 80 | 54 | 102 | 0 | 0 | 97.9
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 169 | 0 | 0 | 0 | 109 | 0 | 371 | 330 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 97 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 47 | 0 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 41 | 40 | 120 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 60 | 12 | 0 | 18 | 8 | 120 | 140 | 0 | 360 | 345 | 0 | 112 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 102 | 144 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 38 | 10 | 325 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 381 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 433 | 0 | 0 | 35 | 35 | 113 | 0 | 0 | 0 |  | 6228 | 2295 | 8523 | 4261 | 534 | 2262 | 1069 | 160 | 81 | 54 | 102 | 0 | 0 | 97.89
19:30 | 35 | 169 | 0 | 0 | 0 | 110 | 0 | 350 | 320 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 97 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 47 | 0 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 41 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 34 | 60 | 12 | 0 | 18 | 13 | 120 | 140 | 0 | 345 | 335 | 0 | 112 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 102 | 145 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 39 | 10 | 320 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 368 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 433 | 0 | 0 | 35 | 36 | 113 | 0 | 0 | 0 |  | 6148 | 2269 | 8417 | 4159 | 534 | 2253 | 1074 | 160 | 81 | 54 | 102 | 0 | 0 | 0
20:00 | 35 | 168 | 0 | 0 | 0 | 110 | 0 | 349 | 323 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 97 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 47 | 0 | 15 | 17 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 41 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 60 | 10 | 0 | 18 | 13 | 120 | 140 | 0 | 340 | 330 | 0 | 112 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 102 | 145 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 68 | 79 | 0 | 0 | 17 | 30 | 10 | 310 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 535 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 27 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 160 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 431 | 0 | 0 | 35 | 36 | 113 | 0 | 0 | 0 |  | 6080 | 2262 | 8342 | 4136 | 535 | 2238 | 1070 | 160 | 81 | 20 | 102 | 0 | 0 | 97.89
21:00 | 35 | 168 | 0 | 0 | 0 | 110 | 0 | 349 | 322 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 93 | 0 | 0 | 0 | 16 | 0 | 40 | 0 | 30 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 60 | 0 | 0 | 18 | 33 | 100 | 140 | 0 | 340 | 330 | 0 | 112 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 98 | 145 | 0 | 22 | 0 | 58 | 65 | 50 | 50 | 163 | 0 | 69 | 79 | 0 | 0 | 17 | 38 | 10 | 300 | 24 | 10 | 0 | 68 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 364 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 398 | 0 | 0 | 35 | 36 | 70 | 0 | 0 | 0 |  | 5904 | 2165 | 8069 | 4097 | 534 | 2219 | 859 | 160 | 82 | 20 | 98 | 0 | 0 | 97.88
22:00 | 35 | 164 | 0 | 0 | 0 | 110 | 0 | 343 | 313 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 34 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 140 | 0 | 340 | 330 | 0 | 112 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 92 | 147 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 69 | 79 | 0 | 0 | 17 | 39 | 10 | 280 | 24 | 10 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 535 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 115 | 26 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 376 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 |  | 5582 | 1940 | 7522 | 4060 | 535 | 2175 | 414 | 160 | 82 | 4 | 92 | 0 | 0 | 0
23:00 | 35 | 126 | 0 | 0 | 0 | 110 | 0 | 359 | 319 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 34 | 0 | 42 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 39 | 100 | 140 | 0 | 310 | 305 | 0 | 112 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 82 | 147 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 130 | 0 | 68 | 79 | 0 | 0 | 17 | 38 | 10 | 275 | 24 | 10 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 |  | 202 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 24 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 359 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 5380 | 1519 | 6899 | 3971 | 202 | 2124 | 274 | 160 | 82 | 4 | 82 | 0 | 0 | 0
24:00 | 35 | 122 | 0 | 0 | 0 | 111 | 0 | 361 | 352 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 100 | 140 | 0 | 285 | 280 | 0 | 112 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 0 | 33 | 21 | 76 | 146 | 0 | 22 | 0 | 60 | 65 | 50 | 21 | 100 | 0 | 69 | 79 | 0 | 0 | 17 | 8 | 10 | 300 | 16 | 10 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 193 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4982 | 1420 | 6402 | 3815 | 193 | 2026 | 46 | 160 | 82 | 4 | 76 | 0 | 0 | 0
KWH | 441000 | 3070300 | 0 | 0 | 0 | 1500227 | 0 | 8723450 | 7398000 |  | 0 | 8763300 | 0 | 0 | 0 | 0 | 6856303 | 0 | 961000 | 0 | 0 | 0 | 69120 | 0 | 252480 | 0 | 217104 | 0 | 53219 | 703637 | 245844 | 600000 | 528120 | 810100 | 580100 | 278268 | 0 | 905700 | 964000 | 2800000 | 0 | 0 | 4774725 | 0 | 0 | 0 |  | 0 | 0 | 87210 | 291240 | 54720 | 0 | 300576 | 323040 | 2244122 | 3245560 | 0 | 7830400 | 7592500 | 0 | 1756363 | 1339465 | 663696 | 0 | 0 | 629972 | 0 | 0 | 0 | 92628 | 148140 | 401200 | 332870 | 1842240 | 3424760 | 0 | 279792 | 11200 | 1341000 | 1565880 | 666600 | 819000 | 3232775 | 0 | 1432032 | 1293120 | 0 | 0 | 235000 | 571600 | 159300 | 7524000 | 278856 | 57168 | 0 | 529417 | 0 | 0 | 1164000 | 0 | 0 | 14985 | 0 | 306720 | 0 | 8490000 | 0 | 0 | 1192654 | 25680 | 0 | 0 | 0 | 0 |  | 6100363 | 0 | 5810112 | 0 | 0 | 0 | 0 | 0 | 0 | 28416 | 169875 | 2719000 | 374500 | 264960 | 0 | 0 | 1195000 | 0 | 0 | 0 | 115900 | 0 | 0 | 0 | 0 | 255120 | 238932 | 223110 | 0 | 0 | 3932800 | 0 | 0 | 4814400 | 0 | 0 | 0 | 0 | 0 | 5007809 | 0 | 9210036 | 0 | 0 | 178464 | 268560 | 408960 | 0 | 13821 | 0 |  | 115287478 | 41330138 | 156617616 | 91456018 | 6100363 | 44715885 | 6450178 | 3932800 | 1869700 | 184746 | 1842240 | 65686 | 0
Fuel Cost | 493920 | 3315924 | 0 | 0 | 0 | 1455220.19 | 0 | 6280884 | 5622480 |  | 0 | 7010640 | 0 | 0 | 0 | 0 | 8501815.72 | 0 | 1201250 | 0 | 0 | 0 | 684979.2 | 0 | 2297568 | 0 | 2032093.44 | 0 | 507709.26 | 7008224.52 | 184383 | 450000 | 0 | 0 | 0 | 2665807.44 | 0 | 235482 | 250640 | 4284000 | 0 | 0 | 5013461.25 | 0 | 0 | 0 |  | 0 | 0 | 914832.9 | 2996859.6 | 520387.2 | 0 | 276529.92 | 898051.2 | 2356328.1 | 3407838 | 0 | 5794496 | 6377700 | 0 | 1721235.74 | 1781488.45 | 544230.72 | 0 | 0 | 900859.96 | 0 | 0 | 0 | 94480.56 | 111105 | 758268 | 249652.5 | 12711456 | 2808303.2 | 0 | 285387.84 | 183680 | 1823760 | 2129596.8 | 906576 | 1023750 | 4008641 | 0 | 2133727.68 | 2275891.2 | 0 | 0 | 373650 | 668772 | 374355 | 5342040 | 209142 | 43447.68 | 0 | 5542995.99 | 0 | 0 | 11197680 | 0 | 0 | 172926.9 | 0 | 2877033.6 | 0 | 7980600 | 0 | 0 | 11270580.3 | 0 | 0 | 0 | 0 | 0 |  | 16470980.1 | 0 | 4531887.36 | 0 | 0 | 0 | 0 | 0 | 0 | 372249.6 | 1680063.75 | 2175200 | 580475 | 2845670.4 | 0 | 0 | 2246600 | 0 | 0 | 0 | 1201883 | 0 | 0 | 0 | 0 | 280632 | 394237.8 | 168894.27 | 0 | 0 | 16085152 | 0 | 0 | 4236672 | 0 | 0 | 0 | 0 | 0 | 4406871.92 | 0 | 6723326.28 | 0 | 0 | 1638299.52 | 2392869.6 | 3819686.4 | 0 | 0 | 0 |  | 165544819.06 | 72251651 | 237796470.06 | 87031495.97 | 16470980.1 | 40187183.37 | 62495412.02 | 16085152 | 486122 | 1972061.7 | 12711456 | 356606.9 | 0
Yesterday Day Peak | 35 | 134 | 0 | 0 | 0 | 95 | 0 | 371 | 360 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 33 | 17 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 8 | 100 | 130 | 0 | 350 | 345 | 0 | 83 | 31 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 30 | 12 | 80 | 151 | 0 | 22 | 1.9 | 60 | 63 | 25 | 50 | 130 | 0 | 65 | 79 | 0 | 0 | 17 | 33 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 51 | 4.2 | 0 | 0 | 0 | 0 |  | 205 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 409 | 0 | 0 | 0 | 1 | 0 | 0 | 1.2 | 0 |  | 6711.3 | DayPeak
Yesterday Evening Peak | 35 | 169 | 0 | 0 | 0 | 109 | 0 | 371 | 330 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 97 | 0 | 0 | 0 | 16 | 0 | 68 | 0 | 47 | 0 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 41 | 40 | 120 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 60 | 12 | 0 | 18 | 8 | 120 | 140 | 0 | 360 | 345 | 0 | 112 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 11 | 11 | 33 | 20 | 102 | 144 | 0 | 22 | 0 | 60 | 65 | 50 | 50 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 38 | 10 | 325 | 24 | 8 | 0 | 145 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 381 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 534 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 15 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 433 | 0 | 0 | 35 | 35 | 113 | 0 | 0 | 0 |  | 8523 | EvPeak
Forecast for Evening | 35 | 170 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 15 | 100 | 120 | 0 | 360 | 360 | 0 | 112 | 90 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 121 | 160 | 95 | 22 | 0 | 60 | 65 | 51 | 44 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  | 651 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 120 | 20 | 110 | 30 | 0 | 50 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 220 | 17 | 17 | 210 | 0 | 210 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 170 |  | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 21 | 10 | 100 | 120 | 0 | 360 | 360 | 0 | 100 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 97 | 160 | 95 | 22 | 1.6 | 60 | 65 | 51 | 44 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  | 305 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 20 | 70 | 0 | 0 | 50 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 210 |  | 95 | 80 | 220 | 0 | 0 | 50 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 115 | 0 | 0 | 0 | 12 | 0 | 367 | 371 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 65 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 80 | 140 | 0 | 370 | 360 | 0 | 8 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 70 | 162 | 0 | 20 | 0.4 | 58 | 65 | 5 | 25 | 130 | 0 | 68 | 10 | 0 | 0 | 17 | 5 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 1.353 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 189 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0
199
| Minimum Generation |  | 4782 | 5:00
| Highest Generation |  | 8523 | 19:00
| Day Peak Generation |  | 6711.3 | 12:00
| Evening Peak Generation |  | 8523 | 19:00
| HVDC Max Flow |  | 535 | 20:00
| HVDC EvPeak Flow |  | 534 | 19:00
| Load factor L.F |  | 76.57%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-15
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6711.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5307 | MW
Evening Peak Generation : |  | 8523 | MW Hour : | 19:00 | Available Max Generation : |  | 13923 | MW
E.P. Demand (at gen end) : |  | 8523 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8700 | MW
Maximum Generation : |  | 8523 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5223 | MW
Total Gen. (MKWH) : |  | 156.6176 | System Load Factor : | 76.57% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -485 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-15
Actual : | 97.84 | Ft.(MSL) , | Rule curve : | 104.7 | Ft.( MSL )
Gas Consumed : | Total = | 1120.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 127218679.34
: |  | Coal : | 16085152 | Oil : | 64467473.72 | Total : | 207771305.06
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3064.5889 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1035.7255 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 926.8345 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 837.068 |  |  | 0 | 0%
) | 0 | 0:00 | 756.6697 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 610.5895 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 349.653 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 157.4285 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 470.8775 |  |  | 0 | 0%
Total | 0 |  | 8209.4351 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Sylhet-150 MW. | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-1,5,7 | 12) Bhola-225 MW ST
|  |  |  | 4) Chandpur CCPP ST | 13) Baghabari 100 MW
|  |  |  | 5) Sylhet 150 MW | 14) Summit Meghna 305 MW
6) Sikalbaha-150 MW
7) Ashuganj Precision
8) Raozan #2
9) Ashuganj unit-5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari 230/132 kV MT02 transformer was under shut down from 11:30 to 16:49 for A/M.
b) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 08:30 to 17:11 for A/M.
c) New Tongi 132/33 kV T1 transformer was under shut down from 09:06 to 16:03 for A/M.
d) Kishoreganj 132/33 kV T1 transformer was under shut down from 09:35 to 16:00 for A/M.
e) Netrokona 132/33 kV T1 transformer was under shut down from 09:15 to 16:36 for A/M.
f) Fenchuganj-Bibiyana 230 kV Ckt-2 was under shut down from 09:26 to 13:10 for A/M.
g) Sirajganj-Baghabari 230 kV Ckt-2 was under shut down from 08:54 to 16:10 for A/M.
h) Jashore capacitor bank(132 kV side) was under shut down from 07:40 to 15:40 for A/M.
i) Haripur-Bhulta 230 kV Ckt-2 was under shut down from 11:20 to 13:08 for A/M.
j) Baroirhat 132/33 kV T1 transformer was under shut down from 12:30 to 13:34 for protection work.
k) Sitalakkhya 132/33 kV T2 transformer was under shut down from 09:31 to 14:21 for A/M.
l) Khulna(C)-Noapara 132 kV Ckt-1 tripped from both ends at 15:34 showing dist. A-phase, Z2 at
Noapara end & dist. A-phase, E/F at Khulna(C) end and was switched on at 15:56.
m) Choddagran-Cumilla(N) 132 kV both Ckts tripped from Choddagram end at 14:42 showing protection
trip, L-1, L-2, L-3, DTT and were switched on at 15:56.
n) Madunaghat-Khulshi 132 kV Ckt-1 switched on at 17:15.
o) Sirajganj unit-2 GT was synchronized at 00:23(15/12/2019).
p) Fenchuganj S/S-Biyanibazar-Sylhet Ckt tripped from both ends at 23:15 showing dist. 3-phase, Z1 at |  |  |  |  | About 20 MW power interruption occurred under Biyanibazar S/S area
Fenchuganj end & dist. A-phase, Z3 at Sylhet end and was switched on at 23:32. |  |  |  |  | from 23:15 to 23:32.
q) Mongla 132/33 kV T1&T2 transformers tripped from both sides at 00:48(15/12/2019) showing lock out at |  |  |  |  | About 30 MW power interruption occurred under Mongla S/S area
132 kV side & E/F at 33 kV side and were switched on at 01:05(15/12/2019) & 01:07(15/12/2019) respectively. |  |  |  |  | from 00:48(15/12/2019) to 01:05(15/12/2019).
r) Sirajganj unit-4 CCPP was shut down at 01:47(15/12/2019) for gas booster maintenance.
s) Sirajganj unit-2 ST was synchronized at 02:11(15/12/2019).
t) Feni 132/33 kV T2 transformer was shut down at 07:04(15/12/2019) due to oil leakage from 132 kV R-phase, CT.
u) Sikalbaha 132/33 kV T3 transformer tripped from 132 kV side at 06:10(15/12/2019) showing O/C,
E/F and was switched on at 06:25(15/12/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 441000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 169 | 3070300
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under shut down.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 109 | 1500227
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 371 | 8723450 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 330 | 7398000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8763300
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 245844
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 961000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6856303
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 217104
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 69120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 53219 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 703637 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 68 | 252480
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1128120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 810100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 580100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 278268
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 145 | 529417 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2402 | 42580989
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 14985
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 1869700 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 211 | 4774725 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1192654
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 87210 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 60 | 291240 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 300576
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 323040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 54720 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25680
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 649 | 11734530
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2244122
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 140 | 3245560
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7830400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 7592500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 663696 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 112 | 1756363 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 629972 | Machine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1339465 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 70 | 306720 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 92628
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 148140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1842240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 401200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 332870 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1494 | 28425876
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3424760 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 279792
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 1164000 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 346 | 4879752
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1341000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 65 | 1565880
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3232775
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 666600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 819000
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 57168
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1432032 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1293120 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 235000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 38 | 571600 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 278856
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7524000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 381 | 8490000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 159300
| Sylhet Area Total |  |  |  | 1949 | 1337 | 27666331
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 534 | 6100363
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 28416 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 5810112 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 169875 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 35 | 268560 | Low demand
| Khulna Area Total |  |  |  | 2314 | 813 | 12377326
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 264960 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 374500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 115 | 2719000 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Cable fault
| Barisal Area Total |  |  |  | 462 | 188 | 3358460
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1195000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 115900 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4814400 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 216 | 5007809 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 433 | 9210036
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 255120
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 15 | 238932
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223110
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 178464 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1021 | 21238771
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3932800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 408960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 13821
| Rangpur Area Total |  |  |  | 605 | 273 | 4355581
| Total |  |  |  | 19047 | 8523 | 156617616
| Eastern Grid Total |  |  |  | 13483 | 6228 | 115287478
| Western Grid Total |  |  |  | 5564 | 2295 | 41330138
| National Grid Total |  |  |  | 19047 | 8523 | 156617616
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-14
(a) ENTIRE EASTERN GRID : |  | 5549 | MW | (b) ENTIRE WESTERN GRID : |  | 2480 | MW
i) Dhaka area |  | 3018 | MW | i) Khulna area |  | 968 | MW
ii) Chittagong area |  | 886 | MW | ii) Rajshahi area |  | 804 | MW
iii) Comilla area |  | 691 | MW | iii) Barisal area |  | 228 | MW
iv) Mymensingh area |  | 636 | MW | iv) Rangpur area |  | 480 | MW
v) Sylhet area |  | 318 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8029 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 13:00 | Shahjibazar | 77 | 19:30 | Bottail | 100 | 18:00
Munsiganj | 74 | 19:00 | Fenchuganj | 22 | 18:00 | G.K Project | 25 | 18:00
Sonargaon | 57 | 18:30 | Kulawara | 30 | 18:30 | Faridpur | 120 | 18:00
Shyampur | 168 | 10:00 | Sylhet | 94 | 20:00 | Madaripur | 59 | 20:00
Bhulta | 160 | 19:30 | Chatak | 18 | 18:00 | Sariatpur | 36 | 18:30
Madanganj | 47 | 13:00 | Sunamganj | 27 | 18:00 | Gopalganj | 62 | 18:30
Shitalakhya | 97 | 16:00 | Biani Bazar | 31 | 18:00 | Bagerhat | 62 | 19:00
Rahim steel | 23 | 15:00 | Comilla (S) | 104 | 18:30 | Mongla | 34 | 0.45833
Matuail | 78 | 9:00 | Comilla(N) | 67 | 18:30 | Satkhira | 64 | 18:30
Ghorasal | 58 | 18:00 | Chandpur | 59 | 19:00 | Gallamari | 36 | 14:00
Narsingdi | 108 | 20:00 | Feni | 88 | 18:30 | Magura | 36 | 18:30
Haripur (SBU) | 85 | 18:00 | Chowmuhani | 108 | 21:00 | Norail | 25 | 21:00
Ullon | 50 | 18:00 | Ashuganj | 32 | 11:00 | Chuadanga | 57 | 18:30
Hasnabad | 125 | 19:00 | Daudkandi | 88 | 20:00 | Barisal(N) | 32 | 20:00
Magbazar | 72 | 12:00 | B.Baria | 86 | 19:30 | Barisal (S) | 72 | 20:00
Maniknagar | 70 | 18:00 | Ramganj | 60 | 18:00 | Patuakhali | 76 | 20:00
Bangabhaban | 14 | 12:00 | Chaddagram | 14 | 18:00 | Bhandaria | 47 | 1:00
Narinda | 72 | 13:00 | PHP | 1 | 18:00 | Borhan Uddin | 21 | 18:00
Dhanmondi | 102 | 13:00 | Madunaghat | 41 | 18:00 | Ishurdi | 43 | 18:00
Lalbag | 58 | 18:00 | Hathazari | 69 | 18:30 | Ruppur Paromanobik | 1 | 20:00
Madartek | 46 | 20:00 | Khulshi | 160 | 12:00 | Natore | 82 | 18:00
Mirpur | 72 | 18:00 | Halishahar | 87 | 18:30 | Bogra | 135 | 18:30
Kalyanpur | 63 | 18:00 | Baraulia | 134 | 19:00 | Noagaon | 78 | 18:30
Gulshan | 90 | 18:00 | Sikalbaha | 26 | 18:00 | Rajshahi | 84 | 19:00
Uttara | 41 | 18:00 | Dohazari | 64 | 18:30 | Rajshahi New | 8 | 20:00
Uttara New | 26 | 18:00 | Cox'sbazar | 78 | 18:00 | C.Nawabganj | 49 | 20:00
Kamrangirchar | 81 | 18:00 | Chandraghona | 22 | 18:00 | Amnura | 22 | 20:00
Savar | 98 | 18:00 | Kaptai | 3.2 | 18:30 | Pabna | 68 | 18:00
Bhasantec | 106 | 13:00 | A. Khaer Stl. | 8 | 5:00 | Shahjadpur | 70 | 19:00
Agargaon | 33 | 18:00 | Bakulia | 72 | 18:00 | Serajganj | 58 | 18:30
Satmosjid | 75 | 18:00 | Julda | 17 | 12:00 | Niyamatpur | 42 | 19:00
Tongi | 116 | 18:00 | TK chemical | 11.1 | 18:30 | Joypurhat | 45 | 18:30
Kabirpur | 133 | 12:00 | Modern Steel | 14 | 15:00 | Sherpur(Bogura) | 33 | 18:00
Basundhara | 81 | 13:00 | Shahmirpur | 19.5 | 17:00 | Mohastangor | 6 | 18:00
Manikganj | 56 | 18:00 | Khagrachhari | 16 | 18:00 | Rangpur | 102 | 18:00
Joydevpur | 155 | 18:00 | Matarbari | 21 | 18:00 | Lalmonirhat | 35 | 18:00
New Tongi | 66 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 83 | 18:00
Korda | 193 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 58 | 19:30
Dhamrai | 48 | 18:00 | Abul Khair 230 | 123 | 12:00 | Thakurgaon | 36 | 1:00
Valuka | 74 | 19:00 | BSRM | 102 | 9:00 | Palashbari | 82 | 18:30
Tangail | 130 | 19:30 | GPH Ispat | 7 | 16:00 | Barapukuria | 39 | 19:00
Mymensing | 149 | 18:00 | Goalpara | 17 | 18:30 | Panchagar | 25 | 9:00
Kishorganj | 72 | 20:00 | Central s/s | 60 | 18:00 | Joldhaka | 20 | 18:30
Netrokona | 69 | 18:30 | Noapara | 50 | 20:00 | Kurigram | 41 | 18:30
Jamalpur | 85 | 18:30 | Jessore | 65 | 19:00
Sherpur | 68 | 18:00 | Benapol | 32 | 18:00
Srimongal | 25 | 18:00 | Jhenida | 74 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-14 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 392 | 0.041667 | 382 | 0.5 | Kaliakoir | 379 | 0.16667 | 364 | 0.5
Bheramara | 408 | 0.125 | 396 | 0.77083 | Bhulta | 388 | 0.16667 | 378 | 0.45833
Ashuganj(N) | 393 | 0.16667 | 385 | 0.45833
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 0.29167 | 228 | 0.041667 | Hathazari | 221 | 0.083333 | 213 | 0.625
Ishurdi | 243 | 0.16667 | 226 | 0.75 | Megnaghat | 230 | 0.16667 | 223 | 0.79167
Ashuganj | 236 | 0.875 | 232 | 0.5 | Fenchuganj | 237 | 0.91667 | 233 | 0.33333
Serajganj | 235 | 0.041667 | 229 | 0.77083 | Siddhirganj | 229 | 0.16667 | 223 | 0.41667
Baghabari | 241 | 0.083333 | 232 | 0.79167 | Maniknagar | 228 | 0.16667 | 220 | 0.5
Barapukuria | 240 | 0.70833 | 226 | 0.45833 | Old Airport | 228 | 0.20833 | 217 | 0.5
Bogra | 232 | 0.041667 | 224 | 0.75 | Barisal | 232 | 0.125 | 221 | 0.5
Khulna South | 237 | 0.20833 | 214 | 0.75 | AKSML | 218 | 0.25 | 212 | 0.5
Rampura | 228 | 0.041667 | 222 | 0.45833 | BSRM | 222 | 0.20833 | 214 | 0.5
Haripur | 227 | 0.16667 | 220 | 0.5 | Bibiyana | 234 | 0.125 | 228 | 0.5
Hasnabad | 226 | 0.083333 | 220 | 0.41667 | Bhulta | 236 | 0.77083 | 223 | 0.45833
Aminbazar | 228 | 0.125 | 219 | 0.5 | Ashuganj (S) | 235 | 0.125 | 229 | 0.5
Tongi | 222 | 0.041667 | 212 | 0.45833 | Kaliakoir | 231 | 0.16667 | 222 | 0.45833
Comilla (N) | 232 | 0.16667 | 225 | 0.5 | GPH | 219 | 0.041667 | 211 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 0.041667 | 133 | 0.66667 | Halishahar | 131 | 0.125 | 126 | 0.625
Munsiganj | 136 | 0.125 | 131 | 0.5 | Baraulia | 130 | 0.83333 | 126 | 0.625
Sonargaon | 135 | 0.041667 | 131 | 0.5 | Sikalbaha | 130 | 0.041667 | 126 | 0.5
Shyampur | 136 | 0.041667 | 131 | 0.5 | Dohazari | 130 | 0.125 | 126 | 0.625
Bhulta | 131 | 0.041667 | 128 | 0.45833 | Cox'sbazar | 127 | 0.45833 | 119 | 0.75
Madanganj | 139 | 0.20833 | 130 | 0.41667 | Chandraghona | 132 | 0.20833 | 127 | 0.625
Shitalakhya | 140 | 0.20833 | 131 | 0.5 | Kaptai | 132 | 0.041667 | 128 | 0.29167
Rahim steal | 138 | 2:00 | 133 | 0.5 | A. Khaer Stl. | 130 | 0.16667 | 125 | 0.45833
Matuail | 136 | 0.041667 | 132 | 0.5 | Bakulia | 129 | 0.16667 | 124 | 0.5
Ghorasal | 136 | 0.29167 | 135 | 0.041667 | Julda | 129 | 0.20833 | 125 | 0.625
Narsinghdi | 129 | 0.25 | 122 | 0.5 | TK Chemical | 130 | 0.041667 | 126 | 0.5
Haripur (SBU) | 137 | 0.125 | 133 | 0.5 | Modern Steel | 129 | 0.041667 | 125 | 0.41667
Ullon | 136 | 0.041667 | 132 | 0.5 | Shahmirpur | 129 | 0.16667 | 125 | 0.5
Hasnabad | 139 | 0.29167 | 133 | 0.625 | Khagrachhari | 132 | 0.16667 | 127 | 0.625
Magbazar | 138 | 0.083333 | 132 | 0.5 | Matarbari | 128 | 0.16667 | 122 | 0.70833
Maniknagar | 137 | 0.25 | 132 | 0.5 | Baroiar Hat | 131 | 0.041667 | 127 | 0.5
Bangabhaban | 137 | 0.25 | 132 | 0.5 | Rangamati | 131 | 0.16667 | 127 | 0.5
Narinda | 137 | 0.25 | 132 | 0.5 | Goalpara | 138 | 0.20833 | 124 | 12:00
Dhanmondi | 136 | 0.041667 | 132 | 0.5 | Central s/s | 138 | 0.20833 | 124 | 12:00
Lalbag | 140 | 0.25 | 131 | 0.5 | Noapara | 132 | 0.20833 | 121 | 0.5
Madartek | 138 | 0.29167 | 132 | 0.5 | Jessore | 134 | 0.16667 | 120 | 0.5
Mirpur | 138 | 0.25 | 131 | 0.5 | Benapol | 136 | 0.125 | 122 | 0.5
Kalyanpur | 141 | 0.25 | 134 | 0.5 | Jhenida | 135 | 0.125 | 119 | 0.75
Gulshan | 136 | 0.25 | 131 | 0.5 | Bottail | 136 | 0.20833 | 125 | 0.75
Uttara | 138 | 0.25 | 130 | 0.5 | G.K Project | 141 | 0.16667 | 132 | 0.75
Uttara New | 137 | 0.25 | 131 | 0.5 | Faridpur | 135 | 0.20833 | 124 | 0.77083
Kamrangirchar | 138 | 0.25 | 129 | 0.5 | Madaripur | 132 | 0.25 | 126 | 0.75
Savar | 137 | 0.25 | 129 | 0.5 | Sariatpur | 132 | 0.16667 | 124 | 0.54167
Bhasantec | 139 | 0.20833 | 131 | 0.5 | Gopalganj | 139 | 0.875 | 125 | 0.58333
Agargaon | 139 | 0.25 | 131 | 0.5 | Bagerhat | 136 | 0.16667 | 124 | 0.5
Satmosjid | 139 | 0.25 | 131 | 0.5 | Mongla | 131 | 0.083333 | 118 | 0.5
Tongi | 136 | 0.95833 | 130 | 0.45833 | Satkhira | 136 | 0.20833 | 124 | 0.5
Kabirpur | 134 | 0.125 | 128 | 0.5 | Gallamari | 139 | 0.20833 | 125 | 0.75
Basundhara | 136 | 1:00 | 128 | 0.54167 | Magura | 135 | 0.25 | 120 | 0.75
Manikganj | 140 | 5:00 | 133 | 0.625 | Norail | 134 | 0.20833 | 121 | 0.54167
Joydevpur | 138 | 0.125 | 130 | 0.625 | Chuadanga | 132 | 0.125 | 116 | 0.75
New Tongi | 135 | 1904-01-02 | 129 | 0.5 | Barisal(N) | 136 | 0.125 | 127 | 0.54167
Kodda | 135 | 0.875 | 127 | 0.66667 | Barisal (S) | 134 | 0.125 | 124 | 0.54167
Dhamrai | 134 | 0.16667 | 128 | 0.66667 | Patuakhali | 134 | 0.16667 | 124 | 0.5
Valuka | 131 | 0.91667 | 124 | 0.75 | Bhandaria | 134 | 0.083333 | 125 | 0.5
Tangail | 133 | 0.25 | 129 | 0.5 | Ishurdi | 138 | 0.20833 | 129 | 0.75
Mymensing | 132 | 0.91667 | 125 | 0.33333 | Ruppur Paromanobik | 136 | 0.25 | 129 | 0.77083
Kishorganj | 132 | 0.25 | 126 | 0.75 | Natore | 135 | 0.25 | 127 | 0.75
Netrokona | 131 | 0.91667 | 124 | 0.33333 | Bogra | 137 | 0.20833 | 131 | 0.75
Jamalpur | 137 | 0.91667 | 123 | 0.29167 | Noagaon | 135 | 0.20833 | 127 | 0.75
Sherpur | 136 | 0.875 | 122 | 0.33333 | Rajshahi | 133 | 0.25 | 124 | 0.54167
Srimongal | 136 | 24:00 | 135 | 0.041667 | Rajshahi New | 134 | 0.25 | 124 | 0.54167
Shahjibazar | 134 | 0.95833 | 130 | 0.75 | C.Nawabganj | 131 | 0.20833 | 121 | 0.5
Fenchuganj | 136 | 0.95833 | 133 | 0.29167 | Amnura | 130 | 0.70833 | 120 | 0.5
Khulawara | 135 | 0.125 | 134 | 1:00 | Pabna | 138 | 0.25 | 130 | 0.75
Sylhet | 134 | 0.875 | 132 | 0.041667 | Shahjadpur | 142 | 0.25 | 136 | 0.5
Chatak | 134 | 0.91667 | 131 | 0.75 | Serajganj | 138 | 0.25 | 131 | 0.75
Sunamganj | 134 | 0.95833 | 131 | 0.041667 | Niyamatpur | 134 | 0.16667 | 124 | 0.75
Biani Bazar | 134 | 0.041667 | 131 | 0.33333 | Joypurhat | 135 | 0.25 | 126 | 0.75
Comilla(s) | 132 | 1904-01-02 | 127 | 0.41667 | Sherpur(Bogura) | 138 | 0.20833 | 131 | 0.75
Comilla(n) | 138 | 0.33333 | 134 | 0.66667 | Mohastangor | 136 | 0.20833 | 129 | 0.75
Chandpur | 135 | 8:00 | 130 | 0.625 | Rangpur | 130 | 0.125 | 124 | 0.5
Feni | 131 | 0.29167 | 122 | 0.625 | Lalmonirhat | 127 | 0.25 | 120 | 0.54167
Chowmuhani | 129 | 0.29167 | 125 | 0.91667 | Saidpur | 129 | 0.25 | 122 | 0.75
Ashuganj | 134 | 0.125 | 130 | 0.5 | Purbasadipur | 125 | 0.79167 | 116 | 0.75
Daudkandi | 135 | 0.29167 | 131 | 0.5 | Thakurgaon | 122 | 0.25 | 115 | 0.5
B.Baria | 130 | 0.91667 | 126 | 0.75 | Palashbari | 135 | 0.20833 | 125 | 0.54167
Ramganj | 130 | 0.375 | 126 | 0.875 | Barapukuria | 131 | 0.25 | 126 | 0.75
Chaddagram | 133 | 0.29167 | 129 | 0.5 | Panchagar | 120 | 0.25 | 111 | 0.5
PHP | 133 | 0.70833 | 127 | 0.5 | Joldhaka | 127 | 0.20833 | 119 | 0.5
Madanhat | 133 | 0.041667 | 130 | 0.41667 | Kurigram | 130 | 0.20833 | 121 | 0.33333
Hathazari | 132 | 0.041667 | 126 | 0.625
Khulshi | 128 | 0.20833 | 123 | 0.5

## L-Curve
Date | 2019-12-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 440 | 4982 | 1420 | 6402 |  |  |  | QF-LDC-12
0:30 | 305.5 | 4452.5 | 1435 | 5887.5 | Date: | 2019-12-14
1:00 | 171 | 3923 | 1450 | 5373
1:30 | 129 | 3805 | 1468.5 | 5273.5
2:00 | 87 | 3687 | 1487 | 5174
2:30 | 96 | 3639 | 1458 | 5097 | [5 empty] | Gen. at Eve. Peak | 8523 | 8523 MW (19:00 )
3:00 | 105 | 3591 | 1429 | 5020 | [6 empty] | 19:00
3:30 | 97.5 | 3539 | 1375.5 | 4914.5 | [5 empty] | Gen. at Day Peak | 6711.3 | 6711.3 MW (12:00 )
4:00 | 90 | 3487 | 1322 | 4809 | [6 empty] | 12:00
4:30 | 97.5 | 3474 | 1321.5 | 4795.5 | [5 empty] | Highest Generation | 8523
5:00 | 105 | 3461 | 1321 | 4782 | [6 empty] | 19:00
5:30 | 123 | 3610 | 1345 | 4955
6:00 | 141 | 3759 | 1369 | 5128
6:30 | 181.5 | 3847.75 | 1414.55 | 5262.3
7:00 | 222 | 3936.5 | 1460.1 | 5396.6
7:30 | 255 | 4171.15 | 1535.3 | 5706.45
8:00 | 288 | 4405.8 | 1610.5 | 6016.3
8:30 | 202.5 | 4500.3 | 1653.85 | 6154.15
9:00 | 117 | 4594.8 | 1697.2 | 6292
9:30 | 76.5 | 4545.05 | 1679.3 | 6224.35
10:00 | 36 | 4495.3 | 1661.4 | 6156.7
10:30 | 37 | 4539.1 | 1662.45 | 6201.55
11:00 | 38 | 4582.9 | 1663.5 | 6246.4
11:30 | 84 | 4798 | 1680.85 | 6478.85
12:00 | 130 | 5013.1 | 1698.2 | 6711.3
12:30 | 153.5 | 5040.8 | 1690.4 | 6731.2
13:00 | 177 | 5068.5 | 1682.6 | 6751.1
13:30 | 146.5 | 4938.0295 | 1667.1 | 6605.1295
14:00 | 116 | 4807.559 | 1651.6 | 6459.159
14:30 | 93 | 4850.8025 | 1610 | 6460.8025
15:00 | 70 | 4894.046 | 1568.4 | 6462.446
15:30 | 76 | 4876.536 | 1567.25 | 6443.786
16:00 | 82 | 4859.026 | 1566.1 | 6425.126
16:30 | 136 | 4954.513 | 1606.1 | 6560.613
17:00 | 190 | 5050 | 1646.1 | 6696.1
17:30 | 277 | 5581.5 | 1947.55 | 7529.05
18:00 | 364 | 6113 | 2249 | 8362
18:30 | 364.5 | 6170.5 | 2272 | 8442.5
19:00 | 365 | 6228 | 2295 | 8523
19:30 | 365 | 6148 | 2269 | 8417
20:00 | 345 | 6080 | 2262 | 8342 |  |  |  | Executive Engineer
20:30 | 327.5 | 5992 | 2213.5 | 8205.5 |  |  |  | Network Operation Division
21:00 | 310 | 5904 | 2165 | 8069
21:30 | 294 | 5743 | 2052.5 | 7795.5
22:00 | 278 | 5582 | 1940 | 7522 |  |  |  |  | Page 6 of 7
22:30 | 381.5 | 5481 | 1729.5 | 7210.5
23:00 | 485 | 5380 | 1519 | 6899
23:30 | 462.5 | 5181 | 1469.5 | 6650.5
24:00 | 440 | 4982 | 1420 | 6402
8523 MW (19:00 )
6711.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-14 |  | Energy | 156617616
[10 empty] | 2019-12-14 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3815 | 193 | 2026 | 274 | 160 | 82 | 4 | 0 | 76
0:30 | 3671.5 | 165 | 1705 | 137 | 170 | 81 | 2 | 0 | 70 | Date: | 2019-12-14
1:00 | 3528 | 137 | 1384 | 0 | 180 | 80 | 0 | 0 | 64
1:30 | 3435.5 | 137 | 1378 | 0 | 180 | 80 | 0 | 0 | 63 | [7 empty] | Total Energy | 156.6176 | Total Energy Gen 156.618 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.618 MKWHr
2:00 | 3343 | 137 | 1372 | 0 | 180 | 80 | 0 | 0 | 62 | [7 empty] | Energy not Served | 0
2:30 | 3294.5 | 137 | 1354.5 | 0 | 170 | 80 | 0 | 0 | 61 | [7 empty] | Energy Requirement | 156.6176
3:00 | 3246 | 137 | 1337 | 0 | 160 | 80 | 0 | 0 | 60
3:30 | 3195.5 | 136.5 | 1282.5 | 0 | 160 | 80 | 0 | 0 | 60 | [6 empty] | Shortage
4:00 | 3145 | 136 | 1228 | 0 | 160 | 80 | 0 | 0 | 60
4:30 | 3131 | 136.5 | 1228 | 0 | 160 | 80 | 0 | 0 | 60
5:00 | 3117 | 137 | 1228 | 0 | 160 | 80 | 0 | 0 | 60
5:30 | 3225 | 136.5 | 1292.5 | 0 | 160 | 80 | 0 | 0 | 61
6:00 | 3333 | 136 | 1357 | 0 | 160 | 80 | 0 | 0 | 62
6:30 | 3415 | 135.5 | 1409.5 | 0 | 160 | 80 | 0 | 0 | 61 |  |  |  |  | Coal
7:00 | 3497 | 135 | 1462 | 0 | 160 | 80 | 0 | 0 | 60
7:30 | 3676.5 | 138 | 1581.5 | 0 | 159.5 | 81 | 0 | 0 | 64 |  |  |  | Oil |  |  |  | ,
8:00 | 3856 | 141 | 1701 | 0 | 159 | 82 | 0 | 0 | 68
8:30 | 3832.5 | 173 | 1830.5 | 0 | 159.5 | 83 | 0 | 0 | 69
9:00 | 3809 | 205 | 1960 | 0 | 160 | 84 | 0 | 0 | 70
9:30 | 3785 | 205 | 1910.5 | 3.5 | 160 | 84 | 0 | 0 | 71
10:00 | 3761 | 205 | 1861 | 7 | 160 | 84 | 0 | 0 | 72
10:30 | 3776 | 205 | 1867 | 29 | 160 | 84 | 0 | 0 | 74
11:00 | 3791 | 205 | 1873 | 51 | 160 | 84 | 0 | 0 | 76
11:30 | 3919 | 205 | 1972 | 54 | 160 | 84 | 0 | 0 | 78
12:00 | 4047 | 205 | 2071 | 57 | 160 | 84 | 0 | 0 | 80
12:30 | 4020.5 | 205 | 2102.5 | 70.5 | 160 | 83 | 1 | 0 | 80
13:00 | 3994 | 205 | 2134 | 84 | 160 | 82 | 2 | 0 | 80
13:30 | 3994 | 205 | 2134 | 84 | 160 | 82 | 2 | 0 | 80
14:00 | 3994 | 205 | 2134 | 84 | 160 | 82 | 2 | 0 | 80
14:30 | 3889.5 | 205 | 2077 | 105 | 160 | 81.5 | 1 | 0 | 80
15:00 | 3785 | 205 | 2020 | 126 | 160 | 81 | 0 | 0 | 80
15:30 | 3796 | 198.5 | 2016 | 109 | 160 | 80.5 | 0 | 0 | 80
16:00 | 3807 | 192 | 2012 | 92 | 160 | 80 | 0 | 0 | 80
16:30 | 3828.5 | 192 | 2022.5 | 184.5 | 160 | 80 | 8 | 0 | 84
17:00 | 3850 | 192 | 2033 | 277 | 160 | 80 | 16 | 0 | 88
17:30 | 4051.5 | 363 | 2147 | 597.5 | 160 | 80 | 35 | 0 | 95
18:00 | 4253 | 534 | 2261 | 918 | 160 | 80 | 54 | 0 | 102
18:30 | 4257 | 534 | 2261.5 | 993.5 | 160 | 80.5 | 54 | 0 | 102
19:00 | 4261 | 534 | 2262 | 1069 | 160 | 81 | 54 | 0 | 102
19:30 | 4159 | 534 | 2253 | 1074 | 160 | 81 | 54 | 0 | 102
20:00 | 4136 | 535 | 2238 | 1070 | 160 | 81 | 20 | 0 | 102
20:30 | 4116.5 | 534.5 | 2228.5 | 964.5 | 160 | 81.5 | 20 | 0 | 100
21:00 | 4097 | 534 | 2219 | 859 | 160 | 82 | 20 | 0 | 98
21:30 | 4078.5 | 534.5 | 2197 | 636.5 | 160 | 82 | 12 | 0 | 95
22:00 | 4060 | 535 | 2175 | 414 | 160 | 82 | 4 | 0 | 92
22:30 | 4015.5 | 368.5 | 2149.5 | 344 | 160 | 82 | 4 | 0 | 87
23:00 | 3971 | 202 | 2124 | 274 | 160 | 82 | 4 | 0 | 82
23:30 | 3893 | 197.5 | 2075 | 274 | 160 | 82 | 4 | 0 | 79 | Max Temp. in Dhaka |  | 27.7° C
24:00 | 3815 | 193 | 2026 | 274 | 160 | 82 | 4 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 156.618 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 156.618 MKWHr
Note on W13: Author:

## Generation
2019-12-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 44 | 44 | 44 | 44 | 42 | 42 | 41 | 40 | 40 | 40 |  | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 905700
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2.3 | 7.3 | 0 | [17 empty] | 14985
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 175 | 176 | 176 | 177 | 205 | 216 | 218 | 204 | 207 | 212 | 216 | 212 | 205 | 210 | 213 | 204 | 219 |  | 211 | 203 | 203 | 204 | 203 | 205 | 202 | 4774725
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 34 |  | 34 | 34 | 0 |  |  |  |  | 87210
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 0 | 7 | 51 | 51 | 66 | 86 | 105 | 68 | 68 | 97 |  | 105 | 105 | 105 | 105 | 105 | 68 | 0 | 1192654
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 0 | [8 empty] | 0 | 40 | 70 | 68 | 40 | 40 | 40 | 40 | 95 |  | 97 | 97 | 97 | 93 | 90 | 67 | 41 | 961000
17 | Siddhirganj 335 MW CCPP | 305 | 252 | 216 | 164 | 160 | 230 | 230 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 340 |  | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 6856303
18 | Kodda 300 MW PP Unit-2 (Summit) | [15 empty] | 0 | 11 | 130 |  | 145 | 145 | 145 | 68 | 0 |  |  | 529417
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 83 | 83 | 83 | 83 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 1756363
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 441000
21 | Ghorasal Repowered CCPP Unit-3 | 94 | 94 | 95 | 94 | 94 | 94 | 93 | 95 | 95 | 95 | 95 | 134 | 135 | 135 | 134 | 134 | 134 | 158 |  | 169 | 169 | 168 | 168 | 164 | 126 | 122 | 3070300
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 110 |  | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 2244122
29 | Ashuganj TPP Unit- 4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3245560
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 663696
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 270 | 270 | 300 | 300 | 360 | 320 | 325 | 340 | 345 | 320 | 290 | 305 | 305 | 305 | 360 |  | 345 | 335 | 330 | 330 | 330 | 305 | 280 | 7592500
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 278 | 274 | 273 | 302 | 300 | 350 | 335 | 340 | 295 | 350 | 325 | 285 | 295 | 300 | 300 | 335 |  | 360 | 345 | 340 | 340 | 340 | 310 | 285 | 7830400
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 80 | 81 | 70 | 50 | 50 | 52 | 50 | 50 | 50 | 50 | 30 | 31 | 30 | 31 | 31 | 31 | 31 | 91 |  | 90 | 80 | 80 | 81 | 81 | 90 | 90 | 1339465
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 344 | 350 | 346 | 345 | 345 | 362 | 369 | 375 | 367 | 346 | 355 | 371 | 368 | 348 | 356 | 358 | 380 | 376 |  | 371 | 350 | 349 | 349 | 343 | 359 | 361 | 8723450
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 300 | 280 | 270 | 270 | 300 | 330 | 400 | 420 | 370 | 370 | 420 | 420 | 370 | 370 | 370 | 370 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 8763300
41 | Haripur 360MW CCPP(HPL) | 262 | 262 | 248 | 248 | 248 | 277 | 288 | 344 | 364 | 330 | 320 | 360 | 363 | 300 | 300 | 300 | 300 | 340 |  | 330 | 320 | 323 | 322 | 313 | 319 | 352 | 7398000
42 | RPCL 210MW CCPP | 159 | 110 | 110 | 112 | 110 | 113 | 160 | 161 | 161 | 156 | 155 | 151 | 151 | 151 | 151 | 151 | 154 | 153 |  | 144 | 145 | 145 | 145 | 147 | 147 | 146 | 3424760
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 35 | 35 | 35 | 58 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 1341000
45 | Fenchugonj CCPP Phase-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 63 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1565880
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 41 | 40 | 69 | 67 | 67 | 65 | 65 | 65 | 64 | 63 | 64 | 65 | 67 |  | 67 | 67 | 68 | 69 | 69 | 68 | 69 | 1432032
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 74 | 76 | 76 | 79 | 79 | 79 | 79 | 79 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1293120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 235000
52 | Sylhet 50MW PP (EPL) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 26 | 27 | 30 | 33 | 33 | 34 | 34 | 35 | 36 | 38 |  | 38 | 39 | 30 | 38 | 39 | 38 | 8 | 571600
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 159300
54 | Hobiganj 11MW PP Cofidence-E | [16 empty] | 0 | 8 |  | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 57168
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 666600
56 | Shahjahanulla 25 MW PP | [11 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 278856
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 280 | 270 | 270 | 300 | 305 | 325 | 315 | 300 | 315 | 315 | 305 | 305 | 315 | 300 | 315 | 320 |  | 325 | 320 | 310 | 300 | 280 | 275 | 300 | 7524000
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 0 | 17 | 17 |  | 17 | 17 | 17 | 0 |  |  |  | 703637
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 0 | [5 empty] | 0 | 18 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 300576
61 | Narshingdi 22 MW PP (Doreen) | [10 empty] | 0 | 19 | 19 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 245844
62 | Tangail 22 MW PP (Doreen) | [9 empty] | 0 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 279792
63 | Impoprt (Tripura) | 64 | 62 | 60 | 60 | 60 | 62 | 60 | 68 | 70 | 72 | 76 | 80 | 80 | 84 | 80 | 80 | 88 | 102 |  | 102 | 102 | 102 | 98 | 92 | 82 | 76 | 1842240
64 | Malancha, Ctg. EPZ (United) | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 4 | 3 | 3 | 8 | 14 | 10 | 6 | 8 | 8 | 8 |  | 8 | 13 | 13 | 33 | 38 | 39 | 12 | 323040
65 | Feni 22MW PP (Doreen) | [15 empty] | 0 | 10 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 92628
66 | Feni 11 MW PP (Doreen) | [8 empty] | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 148140
67 | Jangalia 33MW PP (Summit) | [10 empty] | 0 | 30 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 401200
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 12 | 12 | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 12 | 15 | 10 | 0 | 3 | 12 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 332870
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 15 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 528120
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810100
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 580100
73 | Ghorashal 108MW PP (Regent) | 12 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 43 | 43 | 43 | 95 | 101 | 105 | 104 | 105 | 108 | 109 |  | 109 | 110 | 110 | 110 | 110 | 110 | 111 | 1500227
| Feni Lanka Power | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [15 empty] | 0 | 6 | 38 |  | 52 | 52 | 52 | 52 | 34 | 34 | 0 | 278268
79 | Kodda 150MW PP | [15 empty] | 0 | 16 | 16 |  | 16 | 16 | 16 | 16 |  |  | 0 | 69120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.1 | 1 | 2.6 | 3.6 | 4.1 | 4.2 | 3.7 | 3.159 | 2.046 | 0.826 | 0 | [9 empty] | 25680
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 0 | 5 | 10 | 10 | 10 | 10 | 30 | 60 |  | 60 | 60 | 60 | 60 | 0 |  |  | 291240
92 | Fenchuganj 44MW (Energyprima) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 21 | 819000
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 36 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 629972
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 0 | 6 | 12 |  | 12 | 12 | 10 | 0 |  |  | 0 | 54720
97 | Katpotti 52 MW PP (Sinha) | [16 empty] | 0 | 30 |  | 47 | 47 | 47 | 30 | 18 | 12 | 6 | 217104
98 | Bosila 108MW PP(CLC) | [15 empty] | 0 | 26 | 68 |  | 68 | 72 | 72 | 40 |  |  | 0 | 252480
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 0 | 17 |  | 17 | 17 | 15 | 0 |  |  | 0 | 53219
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 130 | 130 | 130 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 3232775
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.5 | 1.2 | 1.7 | 1.8 | 1.9 | 1.8 | 1.4 | 1 | 0.2 | 0 | [9 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 0 | 7 | 7 | 7 | 7 | 24 | 124 |  | 180 | 180 | 180 | 180 | 180 | 120 | 40 | 1164000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn)
116 | Chandpur 200MW (Desh energy) | [15 empty] | 0 | 7 | 60 |  | 70 | 70 | 70 | 70 | 0 |  |  | 306720
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 335 | 291 | 293 | 290 | 292 | 319 | 359 | 353 | 351 | 360 | 366 | 377 | 352 | 352 | 367 | 369 | 367 | 419 |  | 381 | 368 | 365 | 364 | 365 | 398 | 372 | 8490000
| Jamalpur 115 MW PP (United) | [25 empty] | 0 | 0
Anwara 300 MW PP (United)
120 | Eastern Zone Total | 3923 | 3687 | 3591 | 3487 | 3461 | 3759 | 3936.5 | 4405.8 | 4594.8 | 4495.3 | 4582.9 | 5013.1 | 5068.5 | 4807.559 | 4894.046 | 4859.026 | 5050 | 6113 |  | 6228 | 6148 | 6080 | 5904 | 5582 | 5380 | 4982 | 115287478
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [15 empty] | 0 | 32 | 48 |  | 48 | 48 | 48 | 48 | 32 | 32 | 0 | 264960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 115 | 115 | 115 | 115 | 100 | 100 | 100 | 115 | 115 | 115 | 115 | 115 | 114 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2719000
140 | Bhola 33 MW PP (Venture) | 15 | 14 | 13 | 13 | 11 | 13 | 12 | 12 | 11 | 11 | 10 | 12 | 12 | 12 | 11 | 15 | 16 | 21 |  | 25 | 25 | 27 | 25 | 26 | 24 | 24 | 374500
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 40 |  | 40 | 40 | 40 | 40 | 8 | 0 |  | 169875
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 0 | 2 | 5 | 0 |  | 0 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 28416
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [10 empty] | 0 | 1 | 1 | 5 | 4 | 7 | 14 | 35 |  | 35 | 36 | 36 | 36 | 37 | 8 | 0 | 268560
146 | Bheramara HVDC | 137 | 137 | 137 | 136 | 137 | 136 | 135 | 141 | 205 | 205 | 205 | 205 | 205 | 206 | 205 | 192 | 192 | 534 |  | 534 | 534 | 535 | 534 | 535 | 202 | 193 | 6100363
147 | Bheramara 360 MW CCPP | 250 | 250 | 220 | 200 | 200 | 200 | 230 | 310 | 305 | 300 | 299 | 295 | 295 | 250 | 250 | 250 | 250 | 225 |  | 200 | 185 | 180 | 160 | 140 | 145 | 140 | 5810112
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3932800
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1195000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 169 | 176 | 171 | 170 | 171 | 180 | 185 | 202 | 205 | 190 | 195 | 202 | 204 | 199 | 176 | 183 | 181 | 190 |  | 214 | 204 | 199 | 202 | 195 | 182 | 179 | 4814400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 182 | 180 | 184 | 196 | 196 | 196 | 200 | 215 | 203 | 198 | 208 | 208 | 196 | 181 | 180 | 186 | 206 |  | 216 | 215 | 216 | 216 | 215 | 191 | 190 | 5007809
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 338 | 372 | 372 | 283 | 285 | 323 | 381 | 407 | 408 | 404 | 409 | 409 | 384 | 409 | 370 | 369 | 370 | 431 |  | 433 | 433 | 431 | 398 | 376 | 359 | 318 | 9210036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [10 empty] | 0 | 18 | 21 | 21 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 255120
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 |  | 15 | 14 | 15 | 14 | 14 | 14 | 14 | 238932
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223110
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 0 |  |  | 115900
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [15 empty] | 0 | 1 | 32 |  | 35 | 35 | 35 | 35 |  |  | 0 | 178464
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [15 empty] | 0 | 35 | 85 |  | 113 | 113 | 113 | 70 | 0 |  |  | 408960
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.5 | 0.2 | 1.4 | 0.5 | 1.2 | 4.6 | 1.6 | 2.4 | 1.1 | 0.1 | 0 | [8 empty] | 13821
178
178