## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-16 | Monday
|  | Date (day): | 2019-12-16 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10747.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13443 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-15 | 2019-12-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 115 | 114 | 170 | 170
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Under shut down
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 107 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 355 | 355 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 347 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 22 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 67 | 40 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 0 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 46 | 46 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 32 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 49 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 300 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1976 | 2573 | 3606 | 4206 | 598 | 819
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.39 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 81 | 82 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 215 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 68 | 105 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 25 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 98 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.291 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 587.681 | 763 | 1335 | 1495 | 210 | 428
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 90 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 140 | 140 | 140 | 140
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 365 | 325 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 340 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 167 | 100 | 185 | 28 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 90 | 90 | 90 |  | 73 | ST under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 54 | 102 | 86 | 109
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1321 | 1481 | 1702 | 2274 | 63 | 444
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 143 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 36 | 192 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 213.9 | 365 | 493.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 65 | 65 | 65 | 65
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 79 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 10 | 37 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 340 | 320 | 0 | 0 |  |  | Under maint. |  | 28/12/2019
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 395 | 362 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1255 | 1208 | 1036 | 1036 | 0 | 489
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 290 | 616 | 167 | 425
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 7 | 4 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 265 | 240 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 15 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 562 | 915 | 637 | 1520 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 25 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 115 | 115 | 120 | 120 |  | 74 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 132 | 188 | 305 | 375 | 0 | 87
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 204 | 184 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 217 | 202 | 210 | 210 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 190 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  |  | Under maint
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 726 | 798 | 1312 | 1578 | 121 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 200 | 220
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 66 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 164.8 | 226 | 321 | 367 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6938.381 | 8517 | 10747.6 | 13443 | 1034 | 2555
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6512.3186 | 7994 | 10087.6264 | 12617.5111
A. |  | 2019-12-15 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 8517 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5307 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8517 | MW
3 | Day peak Generation : |  |  | 6938.381 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7994 | MW
4 | Evening peak Generation : |  |  | 8517 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 162.9041 | MKWHr | By Solar | 0.18928 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 136.8722 | MKWHr |  | By Oil: | 10.9132 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.9023 | MKWHr |  | By Hydro: | 1.9357 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1034 | MW | Dhaka | 2997 | 2997 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2555 | MW | Chittagong | 888 | 888 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3589 | MW | Khulna | 973 | 973 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1099.14 | MMCFD |  |  | Rajshahi | 814 | 814 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 130514848.478 | ii) Oil : | Taka | 105504171.42 | Comilla | 711 | 711 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15960407 | Total | Taka | 251979426.898 | Mymensingh | 604 | 604 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6.0675 | MKWHr. | Sylhet | 324 | 324 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -512 | MW (E to W) at | 19:30 | hrs | Barisal | 215 | 215 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -556 | MW at | 2:00 | hrs | Rangpur | 468 | 468 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.8° C |  |  | Total | 7994 | 7994 |  | 0
B. |  | 2019-12-16 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 24.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13443 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6200 | MW
4 | Reserve(Generation end) |  |  |  | 5443 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 153.0154 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5134 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.3825 | MKWHr. | ii) HVDC Flow at Peak Time |  | 616 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7088 | MKWHr. | iii) Maximum HVDC Flow : |  | 616 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.84 |  | (b) Today: | 97.71 |  | (c) Rule Curve: |  | 104.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 124 | 0 | 0 | 0 | 52 | 0 | 356 | 367 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 140 | 0 | 315 | 310 | 0 | 55 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 70 | 158 | 0 | 0 | 0 | 60 | 65 | 5 | 5 | 100 | 0 | 40 | 79 | 0 | 0 | 0 | 5 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 23 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 5 | 0 | 0 | 0 | 190 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4610 | 1161 | 5771 | 3764 | 136 | 1555 | 0 | 160 | 82 | 4 | 70 | 0 | 0 | 97.86
2:00 | 35 | 123 | 0 | 0 | 0 | 52 | 0 | 378 | 370 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 28 | 33 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 100 | 140 | 0 | 320 | 320 | 0 | 55 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 66 | 158 | 0 | 0 | 0 | 60 | 65 | 5 | 5 | 100 | 0 | 40 | 40 | 0 | 0 | 0 | 5 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 186 | 0 | 12 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4652 | 1041 | 5693 | 3846 | 137 | 1398 | 0 | 160 | 82 | 4 | 66 | 0 | 0 | 97.86
3:00 | 35 | 124 | 0 | 0 | 0 | 52 | 0 | 357 | 373 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 28 | 33 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 100 | 140 | 0 | 275 | 270 | 0 | 55 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 64 | 160 | 0 | 0 | 0 | 60 | 65 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 41 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4420 | 1091 | 5511 | 3706 | 137 | 1360 | 0 | 160 | 80 | 4 | 64 | 0 | 0 | 97.85
4:00 | 35 | 125 | 0 | 0 | 0 | 12 | 0 | 352 | 306 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 28 | 33 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 80 | 140 | 0 | 310 | 305 | 0 | 8 | 90 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 64 | 161 | 0 | 0 | 0 | 60 | 65 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 175 | 0 | 86 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4168 | 1145 | 5313 | 3703 | 137 | 1165 | 0 | 160 | 80 | 4 | 64 | 0 | 0 | 97.85
5:00 | 35 | 123 | 0 | 0 | 0 | 12 | 0 | 337 | 306 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 184 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 80 | 140 | 0 | 285 | 280 | 0 | 8 | 90 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 66 | 162 | 0 | 0 | 0 | 60 | 65 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 133 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4088 | 1219 | 5307 | 3676 | 136 | 1185 | 0 | 160 | 80 | 4 | 66 | 0 | 0 | 97.84
6:00 | 35 | 125 | 0 | 0 | 0 | 12 | 0 | 325 | 305 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 195 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 140 | 0 | 295 | 290 | 0 | 8 | 90 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 66 | 162 | 0 | 0 | 0 | 59 | 65 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 169 | 0 | 143 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4199 | 1228 | 5427 | 3795 | 137 | 1185 | 0 | 160 | 80 | 4 | 66 | 0 | 0 | 97.84
7:00 | 35 | 113 | 0 | 0 | 0 | 12 | 0 | 364 | 338 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 32 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 140 | 0 | 368 | 360 | 0 | 8 | 90 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 14 | 64 | 161 | 0 | 0 | 0.1 | 58 | 65 | 5 | 5 | 100 | 0 | 40 | 10 | 0 | 0 | 0 | 5 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0.29 | 0 | 0 | 0 | 0 |  | 136 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 143 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4516.39 | 1318.1 | 5834.49 | 4124 | 136 | 1262 | 0 | 160 | 82 | 4 | 64 | 2.49 | 0 | 97.84
8:00 | 35 | 115 | 0 | 0 | 0 | 12 | 0 | 367 | 371 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 65 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 25 | 31 | 33 | 32 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 80 | 140 | 0 | 370 | 360 | 0 | 8 | 90 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 70 | 162 | 0 | 20 | 0.4 | 58 | 65 | 5 | 25 | 130 | 0 | 68 | 10 | 0 | 0 | 17 | 5 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 1.353 | 0 | 0 | 0 | 0 |  | 137 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 189 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 |  | 4846.953 | 1395.3 | 6242.253 | 4352 | 137 | 1396 | 30 | 160 | 82 | 4 | 70 | 11.253 | 0 | 97.83
9:00 | 35 | 115 | 0 | 0 | 0 | 12 | 0 | 350 | 364 |  | 0 | 450 | 0 | 0 | 0 | 4 | 300 | 0 | 69 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 32 | 11 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 80 | 140 | 0 | 330 | 325 | 0 | 83 | 81 | 33 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 11 | 33 | 14 | 66 | 162 | 0 | 22 | 1.1 | 60 | 65 | 50 | 50 | 130 | 0 | 68 | 74 | 0 | 0 | 17 | 12 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.19 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 2.617 | 0 | 0 | 0 | 0 |  | 284 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 199 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5005.907 | 1577 | 6582.907 | 4270 | 284 | 1607 | 93 | 160 | 82 | 4 | 66 | 16.907 | 0 | 97.82
10:00 | 35 | 115 | 0 | 0 | 0 | 12 | 0 | 348 | 330 |  | 0 | 400 | 0 | 0 | 0 | 15 | 300 | 0 | 69 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 32 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 80 | 140 | 0 | 380 | 320 | 0 | 83 | 81 | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 5 | 11 | 33 | 10 | 50 | 160 | 0 | 22 | 1.5 | 60 | 65 | 47 | 50 | 130 | 0 | 67 | 74 | 0 | 0 | 17 | 12 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.85 | 0 | 0 | 0 | 374 | 0 | 0 | 1 | 3.714 | 0 | 0 | 0 | 0 |  | 290 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 197 | 0 | 206 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 |  | 4953.064 | 1564.4 | 6517.464 | 4294 | 290 | 1526 | 86 | 160 | 81 | 4 | 50 | 26.464 | 0 | 97.82
11:00 | 35 | 115 | 0 | 0 | 0 | 12 | 0 | 340 | 330 |  | 0 | 400 | 0 | 0 | 0 | 15 | 300 | 0 | 69 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 16 | 7 | 80 | 140 | 0 | 330 | 330 | 0 | 83 | 91 | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 50 | 155 | 0 | 22 | 1.9 | 58 | 65 | 47 | 50 | 130 | 0 | 65 | 76 | 0 | 0 | 17 | 19 | 10 | 295 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.87 | 0 | 0 | 0 | 370 | 0 | 0 | 66 | 4.154 | 0 | 0 | 0 | 0 |  | 290 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 115 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 213 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 |  | 4997.924 | 1571 | 6568.924 | 4264 | 290 | 1536 | 152 | 160 | 81 | 6 | 50 | 29.924 | 0 | 97.81
12:00 | 35 | 115 | 0 | 0 | 0 | 101 | 0 | 355 | 348 |  | 0 | 400 | 0 | 0 | 0 | 22 | 300 | 0 | 67 | 0 | 0 | 7 | 0 | 0 | 32 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 16 | 12 | 90 | 140 | 0 | 365 | 360 | 0 | 83 | 91 | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 54 | 154 | 0 | 22 | 1.9 | 60 | 65 | 47 | 50 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 10 | 10 | 340 | 24 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 19.39 | 0 | 0 | 0 | 395 | 0 | 0 | 68 | 4.291 | 0 | 0 | 0 | 0 |  | 290 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 217 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 5353.581 | 1584.8 | 6938.381 | 4362 | 290 | 1685 | 269 | 160 | 81 | 7 | 54 | 30.381 | 0 | 97.81
13:00 | 35 | 115 | 0 | 0 | 0 | 101 | 0 | 361 | 320 |  | 0 | 420 | 0 | 0 | 0 | 30 | 335 | 0 | 97 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 15 | 100 | 140 | 0 | 330 | 325 | 0 | 102 | 82 | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 50 | 154 | 0 | 20 | 2 | 58 | 65 | 47 | 50 | 163 | 0 | 31 | 76 | 0 | 0 | 17 | 26 | 10 | 315 | 24 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 18.23 | 0 | 0 | 0 | 369 | 0 | 0 | 86 | 3.916 | 0 | 0 | 0 | 0 |  | 290 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 199 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 4.3 | 0 |  | 5424.146 | 1583.3 | 7007.446 | 4293 | 290 | 1722 | 375 | 160 | 81 | 8 | 50 | 28.446 | 0 | 97.8
14:00 | 35 | 115 | 0 | 0 | 0 | 98 | 0 | 348 | 320 |  | 0 | 380 | 0 | 0 | 0 | 48 | 300 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 41 | 0 | 0 | 0 | 22 | 25 | 28 | 33 | 29 | 8 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 10 | 100 | 140 | 0 | 290 | 290 | 0 | 102 | 88 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 56 | 149 | 0 | 20 | 1.5 | 58 | 65 | 47 | 50 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 30 | 10 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 15 | 0 | 0 | 0 | 366 | 0 | 0 | 86 | 3.19 | 0 | 0 | 0 | 0 |  | 274 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 199 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 4.2 | 0 |  | 5186.69 | 1536.2 | 6722.89 | 4091 | 274 | 1635 | 395 | 160 | 82 | 6 | 56 | 23.89 | 0 | 0
15:00 | 35 | 115 | 0 | 0 | 0 | 98 | 0 | 345 | 320 |  | 0 | 380 | 0 | 0 | 0 | 55 | 300 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 29 | 8 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 10 | 100 | 140 | 0 | 290 | 290 | 0 | 102 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 54 | 140 | 0 | 20 | 1 | 58 | 65 | 44 | 50 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 30 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 10.7 | 0 | 0 | 0 | 366 | 0 | 0 | 88 | 2.1 | 0 | 0 | 0 | 0 |  | 274 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 179 | 0 | 205 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 |  | 5187.8 | 1511 | 6698.8 | 4050 | 274 | 1647 | 410 | 160 | 82 | 7 | 54 | 14.8 | 0 | 0
16:00 | 35 | 115 | 0 | 0 | 0 | 98 | 0 | 344 | 330 |  | 0 | 340 | 0 | 0 | 0 | 55 | 300 | 0 | 40 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 29 | 8 | 0 | 42 | 40 | 120 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 12 | 100 | 140 | 0 | 290 | 290 | 0 | 63 | 90 | 37 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 56 | 139 | 0 | 20 | 0.4 | 58 | 65 | 10 | 50 | 100 | 0 | 31 | 79 | 0 | 0 | 17 | 30 | 10 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 5.2 | 0 | 0 | 0 | 374 | 0 | 0 | 105 | 0.9 | 0 | 0 | 0 | 0 |  | 275 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 115 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 178 | 0 | 202 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0.4 | 0 |  | 5039.5 | 1508.4 | 6547.9 | 4055 | 275 | 1479 | 427 | 160 | 82 | 7 | 56 | 6.9 | 0 | 0
17:00 | 35 | 115 | 0 | 0 | 0 | 72 | 0 | 342 | 300 |  | 0 | 340 | 0 | 0 | 0 | 55 | 270 | 0 | 40 | 0 | 0 | 7 | 48 | 0 | 40 | 0 | 46 | 5 | 0 | 0 | 22 | 25 | 32 | 33 | 29 | 10 | 0 | 42 | 40 | 120 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 1 | 0 | 18 | 10 | 100 | 140 | 0 | 260 | 290 | 0 | 63 | 80 | 37 | 0 | 0 | 15 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 62 | 154 | 0 | 22 | 0 | 60 | 65 | 11 | 5 | 100 | 0 | 20 | 73 | 0 | 0 | 17 | 14 | 10 | 270 | 24 | 0 | 0 | 34 | 0 | 0 | 80 | 0 | 0 | 0.3 | 10 | 70 | 0 | 340 | 0 | 0 | 105 | 0 | 0 | 27 | 0 | 0 |  | 420 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 202 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 35 | 3 | 102 | 0 | 0.1 | 0 |  | 4953.3 | 1818.1 | 6771.4 | 3969 | 420 | 1338 | 688 | 160 | 82 | 52 | 62 | 0.4 | 0 | 0
18:00 | 35 | 112 | 0 | 0 | 0 | 76 | 0 | 340 | 300 |  | 0 | 340 | 0 | 0 | 0 | 55 | 275 | 0 | 40 | 0 | 0 | 7 | 100 | 0 | 68 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 29 | 45 | 0 | 42 | 40 | 120 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 34 | 70 | 50 | 27 | 18 | 14 | 100 | 140 | 0 | 280 | 290 | 0 | 102 | 81 | 37 | 0 | 0 | 22 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 106 | 154 | 8 | 22 | 0 | 60 | 65 | 20 | 28 | 100 | 0 | 32 | 79 | 0 | 0 | 17 | 31 | 8 | 275 | 24 | 0 | 0 | 253 | 0 | 0 | 158 | 0 | 0 | 0 | 30 | 190 | 99 | 341 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 0 |  | 616 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 24 | 115 | 24 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 22 | 15 | 11 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 202 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 80 | 15 | 108 | 0 | 0 | 0 |  | 6132 | 2183 | 8315 | 3992 | 616 | 1456 | 1765 | 160 | 82 | 138 | 106 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 113 | 0 | 0 | 0 | 107 | 0 | 340 | 356 |  | 0 | 340 | 0 | 0 | 0 | 55 | 270 | 0 | 65 | 0 | 0 | 0 | 100 | 0 | 68 | 0 | 46 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 34 | 100 | 98 | 8 | 18 | 17 | 100 | 140 | 0 | 300 | 310 | 0 | 167 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 144 | 8 | 22 | 0 | 60 | 65 | 47 | 50 | 100 | 0 | 32 | 79 | 0 | 0 | 17 | 35 | 10 | 300 | 24 | 5 | 0 | 298 | 0 | 0 | 190 | 0 | 0 | 0 | 20 | 70 | 50 | 343 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 615 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 182 | 0 | 202 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 113 | 15 | 100 | 0 | 0 | 0 |  | 6326 | 2176 | 8502 | 4052 | 615 | 1712 | 1639 | 160 | 82 | 138 | 104 | 0 | 0 | 0
19:30 | 35 | 114 | 0 | 0 | 0 | 107 | 0 | 355 | 347 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 46 | 35 | 17 | 35 | 22 | 25 | 24 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 18 | 25 | 100 | 140 | 0 | 325 | 340 | 0 | 167 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 143 | 8 | 22 | 0 | 60 | 65 | 47 | 50 | 100 | 0 | 32 | 79 | 0 | 0 | 17 | 37 | 10 | 320 | 24 | 5 | 0 | 300 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 50 | 362 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 616 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 202 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 113 | 15 | 66 | 0 | 0 | 0 |  | 6390 | 2127 | 8517 | 4206 | 616 | 1843 | 1404 | 160 | 82 | 104 | 102 | 0 | 0 | 0
20:00 | 35 | 116 | 0 | 0 | 0 | 107 | 0 | 343 | 332 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 24 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 100 | 98 | 0 | 18 | 28 | 100 | 140 | 0 | 315 | 320 | 0 | 167 | 85 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 143 | 8 | 22 | 0 | 58 | 65 | 47 | 50 | 100 | 0 | 32 | 79 | 0 | 0 | 17 | 37 | 10 | 305 | 24 | 8 | 0 | 300 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 50 | 350 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 615 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 33 | 115 | 26 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 202 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 113 | 32 | 44 | 0 | 0 | 0 |  | 6189 | 2115 | 8304 | 4141 | 615 | 1817 | 1283 | 160 | 82 | 104 | 102 | 0 | 0 | 0
21:00 | 35 | 116 | 0 | 0 | 0 | 107 | 0 | 340 | 333 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 35 | 0 | 0 | 0 | 70 | 0 | 72 | 0 | 26 | 0 | 0 | 0 | 22 | 25 | 25 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 28 | 100 | 140 | 0 | 300 | 310 | 0 | 181 | 87 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 143 | 8 | 22 | 0 | 60 | 65 | 47 | 50 | 163 | 0 | 32 | 79 | 0 | 0 | 17 | 39 | 10 | 305 | 24 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 50 | 343 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 616 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 201 | 0 | 202 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 113 | 32 | 30 | 0 | 0 | 0 |  | 6034 | 2072 | 8106 | 4124 | 616 | 1896 | 1056 | 160 | 82 | 74 | 98 | 0 | 0 | 0
22:00 | 35 | 116 | 0 | 0 | 0 | 107 | 0 | 342 | 321 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 97 | 0 | 0 | 0 | 5 | 0 | 32 | 0 | 26 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 100 | 140 | 0 | 300 | 315 | 0 | 181 | 85 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 92 | 140 | 0 | 22 | 0 | 60 | 65 | 47 | 50 | 163 | 0 | 33 | 79 | 0 | 0 | 17 | 39 | 10 | 295 | 24 | 11 | 0 | 70 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 40 | 365 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 519 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 202 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 |  | 5704 | 1861 | 7565 | 4244 | 519 | 1884 | 575 | 160 | 82 | 9 | 92 | 0 | 0 | 0
23:00 | 35 | 116 | 0 | 0 | 0 | 107 | 0 | 341 | 319 |  | 0 | 450 | 0 | 0 | 0 | 0 | 336 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 100 | 140 | 0 | 305 | 315 | 0 | 185 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 82 | 139 | 0 | 22 | 0 | 59 | 65 | 47 | 50 | 163 | 0 | 31 | 79 | 0 | 0 | 17 | 37 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 40 | 360 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 356 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 24 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 197 | 0 | 204 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 5485 | 1652 | 7137 | 4227 | 356 | 1880 | 346 | 160 | 82 | 4 | 82 | 0 | 0 | 0
24:00 | 35 | 116 | 0 | 0 | 0 | 107 | 0 | 342 | 368 |  | 0 | 420 | 0 | 0 | 0 | 0 | 336 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 8 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 100 | 140 | 0 | 300 | 310 | 0 | 181 | 81 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 76 | 147 | 0 | 22 | 0 | 57 | 65 | 47 | 50 | 130 | 0 | 33 | 79 | 0 | 0 | 17 | 37 | 10 | 190 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 |  | 179 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 204 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5167 | 1409 | 6576 | 4198 | 179 | 1760 | 117 | 160 | 82 | 4 | 76 | 0 | 0 | 0
KWH | 851000 | 2960000 | 0 | 0 | 0 | 1504409 | 0 | 8459270 | 8013000 |  | 0 | 9102750 | 0 | 0 | 0 | 436565 | 7682003 | 0 | 1459000 | 0 | 0 | 143280 | 386880 | 0 | 504960 | 0 | 683904 | 126360 | 98035 | 99168 | 315036 | 600000 | 670680 | 804200 | 776200 | 420108 | 0 | 975703 | 960000 | 2900000 | 0 | 0 | 4901611 | 0 | 0 | 0 |  | 0 | 0 | 73281 | 590280 | 290880 | 36000 | 301248 | 387840 | 2283666 | 3393985 | 0 | 7776400 | 7609500 | 0 | 2141090 | 2066270 | 727776 | 0 | 0 | 648352 | 0 | 0 | 0 | 305964 | 165780 | 622700 | 375890 | 1708800 | 3577720 | 38400 | 345528 | 11200 | 1402000 | 1569119 | 695400 | 842040 | 3123442 | 0 | 976032 | 1437120 | 0 | 0 | 380000 | 464100 | 172800 | 7533500 | 387696 | 24096 | 0 | 1332326 | 0 | 0 | 1572000 | 0 | 0 | 127305 | 63360 | 405120 | 449963 | 8793000 | 0 | 0 | 1232799 | 26520 | 0 | 98159 | 0 | 0 |  | 7382545 | 0 | 5682240 | 0 | 0 | 0 | 0 | 0 | 0 | 103680 | 106875 | 2761000 | 464800 | 285120 | 0 | 0 | 1190000 | 0 | 0 | 0 | 124490 | 0 | 0 | 42240 | 0 | 361680 | 264888 | 224784 | 0 | 0 | 3902300 | 0 | 0 | 4857409 | 0 | 4255991 | 0 | 0 | 0 | 4968655 | 0 | 311545 | 0 | 0 | 660576 | 144576 | 363840 | 0 | 24252 | 0 |  | 124420569 | 38483486 | 162904055 | 99403449 | 7382545 | 37468756 | 10349384 | 3902300 | 1935703 | 563841 | 1708800 | 189277 | 0
Fuel Cost | 953120 | 3196800 | 0 | 0 | 0 | 1459276.73 | 0 | 6090674.4 | 6089880 |  | 0 | 7282200 | 0 | 0 | 0 | 4479156.9 | 9525683.72 | 0 | 1823750 | 0 | 0 | 1455724.8 | 3833980.8 | 0 | 4595136 | 0 | 6401341.44 | 1211792.4 | 935253.9 | 987713.28 | 236277 | 450000 | 0 | 0 | 0 | 4024634.64 | 0 | 253682.78 | 249600 | 4437000 | 0 | 0 | 5146691.55 | 0 | 0 | 0 |  | 0 | 0 | 768717.69 | 6073981.2 | 2766268.8 | 336960 | 277148.16 | 1078195.2 | 2397849.3 | 3563684.25 | 0 | 5754536 | 6391980 | 0 | 2098268.2 | 2748139.1 | 596776.32 | 0 | 0 | 927143.36 | 0 | 0 | 0 | 312083.28 | 124335 | 1176903 | 281917.5 | 11790720 | 2933730.4 | 365184 | 352438.56 | 183680 | 1906720 | 2134001.84 | 945744 | 1052550 | 3873068.08 | 0 | 1454287.68 | 2529331.2 | 0 | 0 | 604200 | 542997 | 406080 | 5348785 | 290772 | 18312.96 | 0 | 13949453.22 | 0 | 0 | 15122640 | 0 | 0 | 1469099.7 | 590515.2 | 3800025.6 | 4216153.31 | 8265420 | 0 | 0 | 11649950.55 | 0 | 0 | 0 | 0 | 0 |  | 19932871.5 | 0 | 4432147.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1358208 | 1056993.75 | 2208800 | 720440 | 3062188.8 | 0 | 0 | 2237200 | 0 | 0 | 0 | 1290961.3 | 0 | 0 | 420710.4 | 0 | 397848 | 437065.2 | 170161.488 | 0 | 0 | 15960407 | 0 | 0 | 4274519.92 | 0 | 3958071.63 | 0 | 0 | 0 | 4372416.4 | 0 | 227427.85 | 0 | 0 | 6064087.68 | 1288172.16 | 3398265.6 | 0 | 0 | 0 |  | 208590117 | 77268963.878 | 285859080.878 | 95098548.658 | 19932871.5 | 35416299.82 | 99543264.93 | 15960407 | 503282.78 | 5960906.49 | 11790720 | 1652779.7 | 0
Yesterday Day Peak | 35 | 115 | 0 | 0 | 0 | 101 | 0 | 355 | 348 |  | 0 | 400 | 0 | 0 | 0 | 22 | 300 | 0 | 67 | 0 | 0 | 7 | 0 | 0 | 32 | 0 | 46 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 29 | 8 | 0 | 41 | 40 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 16 | 12 | 90 | 140 | 0 | 365 | 360 | 0 | 83 | 91 | 37 | 0 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 10 | 54 | 154 | 0 | 22 | 1.9 | 60 | 65 | 47 | 50 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 10 | 10 | 340 | 24 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 19.39 | 0 | 0 | 0 | 395 | 0 | 0 | 68 | 4.291 | 0 | 0 | 0 | 0 |  | 290 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 217 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 0 |  | 6938.381 | DayPeak
Yesterday Evening Peak | 35 | 114 | 0 | 0 | 0 | 107 | 0 | 355 | 347 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 100 | 0 | 72 | 0 | 46 | 35 | 17 | 35 | 22 | 25 | 24 | 33 | 29 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 98 | 0 | 18 | 25 | 100 | 140 | 0 | 325 | 340 | 0 | 167 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 143 | 8 | 22 | 0 | 60 | 65 | 47 | 50 | 100 | 0 | 32 | 79 | 0 | 0 | 17 | 37 | 10 | 320 | 24 | 5 | 0 | 300 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 50 | 362 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 |  | 616 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 25 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 184 | 0 | 202 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 113 | 15 | 66 | 0 | 0 | 0 |  | 8517 | EvPeak
Forecast for Evening | 35 | 170 | 0 | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 15 | 100 | 140 | 0 | 360 | 360 | 0 | 185 | 90 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 109 | 160 | 95 | 22 | 0 | 60 | 65 | 51 | 50 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  | 425 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 120 | 20 | 110 | 30 | 0 | 50 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 220 | 17 | 17 | 210 | 0 | 210 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 170 |  | 0 | 0 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 0 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 21 | 10 | 100 | 140 | 0 | 360 | 360 | 0 | 100 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 86 | 160 | 95 | 22 | 1.6 | 60 | 65 | 51 | 50 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  | 167 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 20 | 70 | 0 | 0 | 50 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 210 |  | 95 | 80 | 220 | 0 | 0 | 50 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 99 | 0 | 0 | 0 | 6 | 0 | 342 | 373 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 40 | 40 | 120 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 140 | 0 | 265 | 270 | 0 | 8 | 82 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 60 | 161 | 0 | 0 | 0.2 | 55 | 65 | 45 | 50 | 100 | 0 | 33 | 10 | 0 | 0 | 17 | 36 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.05 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 206 | 0 | 202 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0
199
| Minimum Generation |  | 5307 | 5:00
| Highest Generation |  | 8517 | 19:30
| Day Peak Generation |  | 6938.381 | 12:00
| Evening Peak Generation |  | 8517 | 19:30
| HVDC Max Flow |  | 616 | 18:00
| HVDC EvPeak Flow |  | 616 | 19:30
| Load factor L.F |  | 79.7%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-16
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6938.381 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5134 | MW
Evening Peak Generation : |  | 8517 | MW Hour : | 19:30 | Available Max Generation : |  | 13443 | MW
E.P. Demand (at gen end) : |  | 8517 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8000 | MW
Maximum Generation : |  | 8517 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5443 | MW
Total Gen. (MKWH) : |  | 162.9041 | System Load Factor : | 79.7% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -556 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-16
Actual : | 97.71 | Ft.(MSL) , | Rule curve : | 104.6 | Ft.( MSL )
Gas Consumed : | Total = | 1099.14 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 130514848.478
: |  | Coal : | 15960407 | Oil : | 105504171.42 | Total : | 251979426.898
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2812.5039 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 948.175 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 848.0665 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 765.7789 |  |  | 0 | 0%
) | 0 | 0:00 | 692.3105 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 558.6493 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 322.9624 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 144.1175 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 430.8074 |  |  | 0 | 0%
Total | 0 |  | 7523.3715 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Sylhet-150 MW. | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-1,5,7 | 12) Bhola-225 MW ST
|  |  |  | 4) Chandpur CCPP ST | 13) Baghabari 100 MW
|  |  |  | 5) Sylhet 150 MW | 14) Summit Meghna 305 MW
|  |  |  | 6) Sikalbaha-150 MW | 15) Sirajganj unit-4
7) Ashuganj Precision
8) Raozan #2
9) Ashuganj unit-5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi 230/132 kV T02 transformer was under shut down from 08:02 to 12:42 for A/M.
b) Sirajganj-Ashuganj 230 kV Ckt-1 was under shut down from 08:10 to 17:08 for A/M.
c) Bhulta-Ghorashal 230 kV Ckt-1 was under shut down from 09:33 to 17:22 for A/M.
d) Haripur-Maniknagar-Ullon 132 kV Ckt-2 was under shut down from 09:35 to 15:54 for A/M.
e) Daudkandi-Sonargaon 132 kV Ckt-2 was under shut down from 08:10 to 17:06 for A/M.
f) Hasnabad-Sitalakkhya 132 kV Ckt was under shut down from 08:18 to 16:06 for A/M.
g) Hasnabad-Brahmangaon-Shympur 132 kV Ckt was under shut down from 08:16 to 15:27 for A/M.
h) Mymensingh 132/33 kV T1 transformer was under shut down from 08:54 to 16:44 for A/M.
i) Kishoreganj 132/33 kV T1 transformer was under shut down from 09:30 to 14:30 for A/M.
j) Fenchuganj-Bibiyana 230 kV Ckt-2 was under shut down from 09:14 to 13:07 for A/M.
k) Shahjibazar 132/33 kV T2 transformer was under shut down from 11:43 to 16:38 for A/M.
l) Netrokona 132/33 kV T3 transformer was under shut down from 09:14 to 14:32 for A/M.
m) Amnura 132/33 kV T3 transformer was under shut down from 08:03 to 13:25 for A/M.
n) Sirajganj-Baghabari 230 kV Ckt-2 was under shut down from 09:20 to 16:12 for A/M.
o) Gopalganj-Faridpur 132 kV Ckt-2 was under shut down from 08:12 to 16:19 for A/M.
p) Madunaghat-Khulshi 132 kV Ckt-1 tripped from both ends at 09:02 showing dist. B-phase, E,F at
Madunaghat end & dist. Trip, CAD, CD at Khulshi end and was switched on at 10:58.
q) Khulna(C) 132/33 kV T1 transformer was under shut down from 13:20 to 15:05 for maintenance.
r) Bheramara HVDC-Bheramara S/S line was under shut down from 13:21 to 15:49 for relay changing.
s) Siddhirganj GT-1 was shut down at 19:05.
t) Siddhirganj GT-2 was synchronized at 18:55.
u) Madunaghat-Khulshi 132 kV Ckt-1 tripped from both ends at 06:30(16/12/2019) showing dist. B-phase,
SOTF at Madunaghat end & dist. T-phase, lockout at Khulshi end.
v) Bibiyana-2 was shut down at 06:53 for maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 851000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 114 | 2960000
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1504409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8459270 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 347 | 8013000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9102750
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 436565 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 315036
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 40 | 1459000 | Low demand
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7682003
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 143280 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 683904
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 126360 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 386880 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 98035 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 99168 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 504960 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1270680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 776200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 420108
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 1332326
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2573 | 47429134
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127305
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 36000 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1935703 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 215 | 4901611 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1232799
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 73281 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 590280
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 63360 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 301248
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 387840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 98 | 290880
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26520
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 98159 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 763 | 12964986
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2283666
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 140 | 3393985
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7776400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 340 | 7609500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 727776 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 167 | 2141090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 648352 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 449963 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2066270 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 405120 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 305964
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 165780
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1708800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 622700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 375890 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1481 | 30681256
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 143 | 3577720 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 345528
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 38400 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 1572000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 365 | 5544848
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1402000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 65 | 1569119
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3123442 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 695400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 842040
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 24096 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 976032 | # 8 Under maint
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1437120
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 380000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 37 | 464100 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 387696
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7533500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 362 | 8793000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 172800
| Sylhet Area Total |  |  |  | 1949 | 1208 | 27800345
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 616 | 7382545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 103680 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 240 | 5682240 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 106875
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 15 | 144576 | Low demand
| Khulna Area Total |  |  |  | 2314 | 915 | 13419916
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 285120 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 464800 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 115 | 2761000 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Cable fault
| Barisal Area Total |  |  |  | 462 | 188 | 3510920
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1190000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 124490 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4857409 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 202 | 4255991 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4968655 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 311545 | Under maint.
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 361680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 264888
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224784
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 42240 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 660576
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 798 | 17262258
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3902300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 66 | 363840 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24252
| Rangpur Area Total |  |  |  | 605 | 226 | 4290392
| Total |  |  |  | 19047 | 8517 | 162904055
| Eastern Grid Total |  |  |  | 13483 | 6390 | 124420569
| Western Grid Total |  |  |  | 5564 | 2127 | 38483486
| National Grid Total |  |  |  | 19047 | 8517 | 162904055
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-15
(a) ENTIRE EASTERN GRID : |  | 5524 | MW | (b) ENTIRE WESTERN GRID : |  | 2470 | MW
i) Dhaka area |  | 2997 | MW | i) Khulna area |  | 973 | MW
ii) Chittagong area |  | 888 | MW | ii) Rajshahi area |  | 814 | MW
iii) Comilla area |  | 711 | MW | iii) Barisal area |  | 215 | MW
iv) Mymensingh area |  | 604 | MW | iv) Rangpur area |  | 468 | MW
v) Sylhet area |  | 324 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7994 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 12:00 | Shahjibazar | 82 | 19:30 | Bottail | 100 | 18:00
Munsiganj | 86 | 19:30 | Fenchuganj | 24 | 18:00 | G.K Project | 24 | 18:00
Sonargaon | 70 | 18:00 | Kulawara | 27 | 18:00 | Faridpur | 120 | 18:30
Shyampur | 176 | 12:00 | Sylhet | 97 | 18:00 | Madaripur | 59 | 20:00
Bhulta | 153 | 18:00 | Chatak | 19 | 19:30 | Sariatpur | 36 | 19:00
Madanganj | 54 | 17:00 | Sunamganj | 27 | 19:00 | Gopalganj | 62 | 18:30
Shitalakhya | 96 | 16:00 | Biani Bazar | 31 | 19:30 | Bagerhat | 63 | 19:00
Rahim steel | 23 | 1:00 | Comilla (S) | 106 | 18:00 | Mongla | 36 | 0.5
Matuail | 78 | 9:00 | Comilla(N) | 73 | 13:00 | Satkhira | 64 | 19:00
Ghorasal | 66 | 18:00 | Chandpur | 63 | 19:00 | Gallamari | 36 | 13:00
Narsingdi | 100 | 20:00 | Feni | 93 | 18:00 | Magura | 36 | 18:30
Haripur (SBU) | 86 | 18:30 | Chowmuhani | 108 | 19:30 | Norail | 25 | 18:00
Ullon | 50 | 18:30 | Ashuganj | 33 | 13:00 | Chuadanga | 56 | 18:00
Hasnabad | 131 | 19:00 | Daudkandi | 86 | 19:30 | Barisal(N) | 28 | 19:30
Magbazar | 78 | 18:00 | B.Baria | 90 | 19:30 | Barisal (S) | 68 | 18:00
Maniknagar | 74 | 18:00 | Ramganj | 56 | 18:00 | Patuakhali | 75 | 21:00
Bangabhaban | 18 | 11:00 | Chaddagram | 14 | 18:00 | Bhandaria | 36 | 18:30
Narinda | 72 | 18:00 | PHP | 1 | 11:00 | Borhan Uddin | 25 | 23:00
Dhanmondi | 100 | 13:00 | Madunaghat | 42 | 18:00 | Ishurdi | 47 | 18:30
Lalbag | 58 | 18:00 | Hathazari | 70 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 46 | 18:00 | Khulshi | 158 | 12:00 | Natore | 85 | 18:30
Mirpur | 70 | 18:00 | Halishahar | 95 | 18:30 | Bogra | 137 | 18:00
Kalyanpur | 72 | 18:00 | Baraulia | 129 | 14:00 | Noagaon | 80 | 18:30
Gulshan | 100 | 13:00 | Sikalbaha | 19 | 18:30 | Rajshahi | 91 | 18:00
Uttara | 41 | 18:00 | Dohazari | 64 | 19:00 | Rajshahi New | 6 | 18:00
Uttara New | 29 | 12:00 | Cox'sbazar | 70 | 18:00 | C.Nawabganj | 50 | 19:30
Kamrangirchar | 86 | 18:30 | Chandraghona | 22 | 18:00 | Amnura | 23 | 18:00
Savar | 96 | 15:00 | Kaptai | 3.3 | 18:00 | Pabna | 86 | 18:00
Bhasantec | 105 | 18:00 | A. Khaer Stl. | 9 | 11:00 | Shahjadpur | 63 | 18:30
Agargaon | 33 | 13:00 | Bakulia | 75 | 18:00 | Serajganj | 65 | 18:30
Satmosjid | 68 | 13:00 | Julda | 18 | 17:00 | Niyamatpur | 42 | 18:30
Tongi | 128 | 11:00 | TK chemical | 10 | 18:00 | Joypurhat | 46 | 18:30
Kabirpur | 137 | 12:00 | Modern Steel | 13 | 5:00 | Sherpur(Bogura) | 31 | 8:00
Basundhara | 69 | 18:00 | Shahmirpur | 21 | 18:00 | Mohastangor | 6 | 18:00
Manikganj | 54 | 21:00 | Khagrachhari | 16 | 18:00 | Rangpur | 99 | 18:00
Joydevpur | 148 | 20:00 | Matarbari | 21 | 18:00 | Lalmonirhat | 38 | 18:00
New Tongi | 66 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 81 | 18:00
Korda | 191 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 55 | 17:00
Dhamrai | 48 | 18:30 | Abul Khair 230 | 152 | 9:00 | Thakurgaon | 37 | 12:00
Valuka | 68 | 18:00 | BSRM | 109 | 22:00 | Palashbari | 80 | 18:00
Tangail | 130 | 18:00 | GPH Ispat | 10 | 13:00 | Barapukuria | 41 | 18:00
Mymensing | 151 | 18:00 | Goalpara | 18 | 13:00 | Panchagar | 25 | 17:00
Kishorganj | 68 | 19:30 | Central s/s | 60 | 18:00 | Joldhaka | 20 | 19:00
Netrokona | 67 | 18:00 | Noapara | 46 | 18:00 | Kurigram | 40 | 18:00
Jamalpur | 89 | 20:00 | Jessore | 72 | 18:00
Sherpur | 72 | 18:00 | Benapol | 32 | 18:00
Srimongal | 25 | 18:00 | Jhenida | 76 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-15 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 391 | 24:00 | 384 | 0.41667 | Kaliakoir | 377 | 0.20833 | 366 | 0.45833
Bheramara | 408 | 0.083333 | 396 | 0.75 | Bhulta | 389 | 24:00 | 379 | 0.45833
Ashuganj(N) | 394 | 24:00 | 385 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 0.041667 | 230 | 0.041667 | Hathazari | 221 | 0.77083 | 215 | 0.41667
Ishurdi | 242 | 0.125 | 225 | 0.75 | Megnaghat | 227 | 0.16667 | 222 | 0.45833
Ashuganj | 240 | 0.77083 | 232 | 0.33333 | Fenchuganj | 237 | 0.79167 | 233 | 0.041667
Serajganj | 233 | 0.041667 | 228 | 0.5 | Siddhirganj | 229 | 0.083333 | 223 | 0.5
Baghabari | 242 | 0.70833 | 232 | 0.5 | Maniknagar | 227 | 0.16667 | 221 | 0.5
Barapukuria | 231 | 0.125 | 225 | 0.5 | Old Airport | 226 | 0.125 | 219 | 0.5
Bogra | 232 | 0.041667 | 223 | 0.5 | Barisal | 235 | 0.625 | 222 | 0.5
Khulna South | 240 | 0.125 | 213 | 0.75 | AKSML | 218 | 0.625 | 210 | 0.5
Rampura | 228 | 0.125 | 222 | 0.5 | BSRM | 221 | 0.75 | 213 | 0.5
Haripur | 226 | 0.041667 | 220 | 0.45833 | Bibiyana | 236 | 24:00 | 228 | 0.66667
Hasnabad | 225 | 0.041667 | 220 | 0.5 | Bhulta | 236 | 24:00 | 223 | 0.5
Aminbazar | 226 | 0.083333 | 221 | 0.5 | Ashuganj (S) | 236 | 0.77083 | 230 | 0.5
Tongi | 225 | 0.8125 | 214 | 0.41667 | Kaliakoir | 230 | 0.70833 | 220 | 0.375
Comilla (N) | 233 | 0.125 | 227 | 0.45833 | GPH | 218 | 0.66667 | 211 | 0.375
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 0.041667 | 133 | 0.5 | Halishahar | 133 | 0.83333 | 123 | 0.041667
Munsiganj | 137 | 0.79167 | 131 | 0.5 | Baraulia | 130 | 0.79167 | 126 | 0.5
Sonargaon | 134 | 0.83333 | 132 | 0.5 | Sikalbaha | 132 | 0.75 | 126 | 0.5
Shyampur | 136 | 0.83333 | 131 | 0.5 | Dohazari | 131 | 0.77083 | 126 | 0.5
Bhulta | 131 | 0.125 | 127 | 0.5 | Cox'sbazar | 126 | 0.25 | 123 | 0.5
Madanganj | 134 | 0.75 | 130 | 0.5 | Chandraghona | 133 | 0.79167 | 128 | 0.41667
Shitalakhya | 139 | 0.33333 | 131 | 0.5 | Kaptai | 133 | 0.75 | 128 | 0.54167
Rahim steal | 138 | 6:00 | 134 | 0.5 | A. Khaer Stl. | 130 | 0.75 | 125 | 0.41667
Matuail | 136 | 0.041667 | 132 | 0.5 | Bakulia | 131 | 0.79167 | 124 | 0.41667
Ghorasal | 136 | 0.75 | 135 | 0.041667 | Julda | 131 | 0.75 | 124 | 0.41667
Narsinghdi | 129 | 0.70833 | 126 | 0.29167 | TK Chemical | 132 | 0.77083 | 126 | 0.33333
Haripur (SBU) | 137 | 0.041667 | 134 | 0.5 | Modern Steel | 131 | 0.75 | 125 | 0.5
Ullon | 137 | 1904-01-02 | 132 | 0.5 | Shahmirpur | 133 | 0.77083 | 124 | 0.375
Hasnabad | 138 | 0.375 | 136 | 0.58333 | Khagrachhari | 131 | 0.75 | 126 | 0.5
Magbazar | 138 | 0.20833 | 132 | 0.45833 | Matarbari | 128 | 0.79167 | 122 | 0.375
Maniknagar | 137 | 0.29167 | 132 | 0.5 | Baroiar Hat | 132 | 0.75 | 128 | 0.41667
Bangabhaban | 137 | 0.29167 | 132 | 0.5 | Rangamati | 131 | 0.75 | 127 | 0.45833
Narinda | 137 | 0.29167 | 132 | 0.5 | Goalpara | 139 | 0.25 | 125 | 18:30
Dhanmondi | 137 | 1904-01-02 | 132 | 0.5 | Central s/s | 139 | 0.125 | 123 | 18:00
Lalbag | 139 | 0.20833 | 136 | 0.5 | Noapara | 135 | 0.16667 | 120 | 0.75
Madartek | 137 | 0.25 | 131 | 0.5 | Jessore | 132 | 0.25 | 118 | 0.77083
Mirpur | 140 | 0.29167 | 134 | 0.45833 | Benapol | 135 | 0.125 | 120 | 0.77083
Kalyanpur | 141 | 0.16667 | 136 | 0.5 | Jhenida | 133 | 0.041667 | 118 | 0.75
Gulshan | 136 | 0.20833 | 131 | 0.5 | Bottail | 136 | 0.125 | 126 | 0.75
Uttara | 138 | 0.16667 | 132 | 0.45833 | G.K Project | 140 | 0.16667 | 133 | 0.75
Uttara New | 137 | 0.041667 | 133 | 0.375 | Faridpur | 134 | 0.16667 | 122 | 0.8125
Kamrangirchar | 137 | 0.29167 | 132 | 0.45833 | Madaripur | 136 | 0.083333 | 124 | 0.8125
Savar | 137 | 0.20833 | 132 | 0.45833 | Sariatpur | 134 | 0.625 | 123 | 0.77083
Bhasantec | 137 | 0.16667 | 132 | 0.5 | Gopalganj | 139 | 0.91667 | 126 | 0.33333
Agargaon | 137 | 0.125 | 133 | 0.54167 | Bagerhat | 138 | 0.16667 | 120 | 0.75
Satmosjid | 137 | 0.16667 | 133 | 0.41667 | Mongla | 135 | 0.041667 | 120 | 0.8125
Tongi | 136 | 0.875 | 128 | 0.5 | Satkhira | 139 | 0.125 | 121 | 0.75
Kabirpur | 134 | 1904-01-02 | 128 | 0.5 | Gallamari | 140 | 0.125 | 125 | 0.75
Basundhara | 136 | 4:00 | 126 | 0.5 | Magura | 135 | 0.041667 | 116 | 0.77083
Manikganj | 139 | 5:00 | 131 | 0.5 | Norail | 133 | 0.16667 | 116 | 0.77083
Joydevpur | 142 | 0.83333 | 130 | 0.5 | Chuadanga | 133 | 0.125 | 113 | 0.75
New Tongi | 136 | 0.875 | 126 | 0.5 | Barisal(N) | 136 | 0.083333 | 128 | 0.77083
Kodda | 141 | 0.83333 | 127 | 0.5 | Barisal (S) | 135 | 0.70833 | 127 | 0.5
Dhamrai | 133 | 0.875 | 129 | 0.41667 | Patuakhali | 134 | 0.16667 | 123 | 0.45833
Valuka | 132 | 0.875 | 126 | 0.375 | Bhandaria | 135 | 0.625 | 121 | 0.8125
Tangail | 134 | 0.95833 | 129 | 0.29167 | Ishurdi | 138 | 0.125 | 129 | 0.75
Mymensing | 133 | 0.91667 | 125 | 0.33333 | Ruppur Paromanobik | 137 | 0.20833 | 130 | 0.5
Kishorganj | 132 | 0.875 | 126 | 0.33333 | Natore | 136 | 0.20833 | 126 | 0.5
Netrokona | 132 | 0.95833 | 125 | 0.33333 | Bogra | 138 | 0.20833 | 129 | 0.5
Jamalpur | 139 | 0.8125 | 124 | 0.41667 | Noagaon | 135 | 0.20833 | 126 | 0.5
Sherpur | 136 | 0.75 | 123 | 0.29167 | Rajshahi | 132 | 0.083333 | 123 | 0.5
Srimongal | 137 | 24:00 | 134 | 0.29167 | Rajshahi New | 133 | 0.16667 | 121 | 0.5
Shahjibazar | 134 | 0.20833 | 131 | 0.5 | C.Nawabganj | 131 | 0.041667 | 120 | 0.5
Fenchuganj | 137 | 1904-01-02 | 134 | 0.41667 | Amnura | 130 | 0.70833 | 120 | 0.41667
Khulawara | 136 | 0.95833 | 133 | 17:00 | Pabna | 139 | 0.16667 | 129 | 0.5
Sylhet | 136 | 1904-01-02 | 131 | 0.66667 | Shahjadpur | 142 | 0.041667 | 136 | 0.45833
Chatak | 135 | 1904-01-02 | 130 | 0.70833 | Serajganj | 137 | 0.041667 | 130 | 0.5
Sunamganj | 135 | 1904-01-02 | 130 | 0.70833 | Niyamatpur | 135 | 0.16667 | 123 | 0.5
Biani Bazar | 136 | 1904-01-02 | 131 | 0.70833 | Joypurhat | 135 | 0.041667 | 124 | 0.5
Comilla(s) | 132 | 0.125 | 128 | 0.33333 | Sherpur(Bogura) | 138 | 0.16667 | 129 | 0.5
Comilla(n) | 138 | 0.70833 | 135 | 0.41667 | Mohastangor | 137 | 0.70833 | 127 | 0.5
Chandpur | 142 | 17:00 | 134 | 0.58333 | Rangpur | 131 | 0.70833 | 122 | 0.5
Feni | 133 | 0.75 | 127 | 0.41667 | Lalmonirhat | 126 | 0.125 | 119 | 0.5
Chowmuhani | 130 | 0.70833 | 126 | 0.8125 | Saidpur | 129 | 0.20833 | 122 | 0.33333
Ashuganj | 134 | 0.33333 | 131 | 0.5 | Purbasadipur | 125 | 0.041667 | 118 | 0.5
Daudkandi | 134 | 0.29167 | 131 | 0.5 | Thakurgaon | 122 | 0.16667 | 112 | 0.5
B.Baria | 131 | 0.91667 | 128 | 0.29167 | Palashbari | 133 | 0.70833 | 124 | 0.5
Ramganj | 133 | 0.75 | 128 | 0.45833 | Barapukuria | 131 | 0.125 | 125 | 0.5
Chaddagram | 134 | 0.75 | 131 | 0.33333 | Panchagar | 121 | 0.20833 | 108 | 0.5
PHP | 139 | 0.29167 | 128 | 0.33333 | Joldhaka | 129 | 0.25 | 119 | 0.5
Madanhat | 132 | 0.77083 | 129 | 0.5 | Kurigram | 130 | 0.16667 | 121 | 0.33333
Hathazari | 132 | 0.083333 | 129 | 0.29167
Khulshi | 130 | 0.75 | 124 | 0.41667

## L-Curve
Date | 2019-12-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 448 | 5167 | 1409 | 6576 |  |  |  | QF-LDC-12
0:30 | 474 | 4888.5 | 1285 | 6173.5 | Date: | 2019-12-15
1:00 | 500 | 4610 | 1161 | 5771
1:30 | 528 | 4631 | 1101 | 5732
2:00 | 556 | 4652 | 1041 | 5693
2:30 | 476 | 4536 | 1066 | 5602 | [5 empty] | Gen. at Eve. Peak | 8517 | 8517 MW (19:30 )
3:00 | 396 | 4420 | 1091 | 5511 | [6 empty] | 19:30
3:30 | 358 | 4294 | 1118 | 5412 | [5 empty] | Gen. at Day Peak | 6938.381 | 6938.381 MW (12:00 )
4:00 | 320 | 4168 | 1145 | 5313 | [6 empty] | 12:00
4:30 | 295 | 4128 | 1182 | 5310 | [5 empty] | Highest Generation | 8517
5:00 | 270 | 4088 | 1219 | 5307 | [6 empty] | 19:30
5:30 | 278.5 | 4143.5 | 1223.5 | 5367
6:00 | 287 | 4199 | 1228 | 5427
6:30 | 348.5 | 4357.695 | 1273.05 | 5630.745
7:00 | 410 | 4516.39 | 1318.1 | 5834.49
7:30 | 450 | 4681.6715 | 1356.7 | 6038.3715
8:00 | 490 | 4846.953 | 1395.3 | 6242.253
8:30 | 379.5 | 4926.43 | 1486.15 | 6412.58
9:00 | 269 | 5005.907 | 1577 | 6582.907
9:30 | 210.5 | 4979.4855 | 1570.7 | 6550.1855
10:00 | 152 | 4953.064 | 1564.4 | 6517.464
10:30 | 166.5 | 4975.494 | 1567.7 | 6543.194
11:00 | 181 | 4997.924 | 1571 | 6568.924
11:30 | 225.5 | 5175.7525 | 1577.9 | 6753.6525
12:00 | 270 | 5353.581 | 1584.8 | 6938.381
12:30 | 322.5 | 5388.8635 | 1584.05 | 6972.9135
13:00 | 375 | 5424.146 | 1583.3 | 7007.446
13:30 | 314.5 | 5305.418 | 1559.75 | 6865.168
14:00 | 254 | 5186.69 | 1536.2 | 6722.89
14:30 | 228 | 5187.245 | 1523.6 | 6710.845
15:00 | 202 | 5187.8 | 1511 | 6698.8
15:30 | 178.5 | 5113.65 | 1509.7 | 6623.35
16:00 | 155 | 5039.5 | 1508.4 | 6547.9
16:30 | 118.5 | 4996.4 | 1663.25 | 6659.65
17:00 | 82 | 4953.3 | 1818.1 | 6771.4
17:30 | 266 | 5542.65 | 2000.55 | 7543.2
18:00 | 450 | 6132 | 2183 | 8315
18:30 | 450 | 6229 | 2179.5 | 8408.5
19:00 | 450 | 6326 | 2176 | 8502
19:30 | 512 | 6390 | 2127 | 8517
20:00 | 500 | 6189 | 2115 | 8304 |  |  |  | Executive Engineer
20:30 | 455 | 6111.5 | 2093.5 | 8205 |  |  |  | Network Operation Division
21:00 | 410 | 6034 | 2072 | 8106
21:30 | 400 | 5869 | 1966.5 | 7835.5
22:00 | 390 | 5704 | 1861 | 7565 |  |  |  |  | Page 6 of 7
22:30 | 431 | 5594.5 | 1756.5 | 7351
23:00 | 472 | 5485 | 1652 | 7137
23:30 | 460 | 5326 | 1530.5 | 6856.5
24:00 | 448 | 5167 | 1409 | 6576
8517 MW (19:30 )
6938.381 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-15 |  | Energy | 162904055
[10 empty] | 2019-12-15 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4198 | 179 | 1760 | 346 | 160 | 82 | 4 | 0 | 76
0:30 | 3981 | 157.5 | 1657.5 | 173 | 160 | 82 | 4 | 0 | 73 | Date: | 2019-12-15
1:00 | 3764 | 136 | 1555 | 0 | 160 | 82 | 4 | 0 | 70
1:30 | 3805 | 136.5 | 1476.5 | 0 | 160 | 82 | 4 | 0 | 68 | [7 empty] | Total Energy | 162.9041 | Total Energy Gen 162.904 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.904 MKWHr
2:00 | 3846 | 137 | 1398 | 0 | 160 | 82 | 4 | 0 | 66 | [7 empty] | Energy not Served | 0
2:30 | 3776 | 137 | 1379 | 0 | 160 | 81 | 4 | 0 | 65 | [7 empty] | Energy Requirement | 162.9041
3:00 | 3706 | 137 | 1360 | 0 | 160 | 80 | 4 | 0 | 64
3:30 | 3704.5 | 137 | 1262.5 | 0 | 160 | 80 | 4 | 0 | 64 | [6 empty] | Shortage
4:00 | 3703 | 137 | 1165 | 0 | 160 | 80 | 4 | 0 | 64
4:30 | 3689.5 | 136.5 | 1175 | 0 | 160 | 80 | 4 | 0 | 65
5:00 | 3676 | 136 | 1185 | 0 | 160 | 80 | 4 | 0 | 66
5:30 | 3735.5 | 136.5 | 1185 | 0 | 160 | 80 | 4 | 0 | 66
6:00 | 3795 | 137 | 1185 | 0 | 160 | 80 | 4 | 0 | 66
6:30 | 3959.5 | 136.5 | 1223.5 | 0 | 160 | 81 | 4 | 0 | 65 |  |  |  |  | Coal
7:00 | 4124 | 136 | 1262 | 0 | 160 | 82 | 4 | 0 | 64
7:30 | 4238 | 136.5 | 1329 | 15 | 160 | 82 | 4 | 0 | 67 |  |  |  | Oil |  |  |  | ,
8:00 | 4352 | 137 | 1396 | 30 | 160 | 82 | 4 | 0 | 70
8:30 | 4311 | 210.5 | 1501.5 | 61.5 | 160 | 82 | 4 | 0 | 68
9:00 | 4270 | 284 | 1607 | 93 | 160 | 82 | 4 | 0 | 66
9:30 | 4282 | 287 | 1566.5 | 89.5 | 160 | 81.5 | 4 | 0 | 58
10:00 | 4294 | 290 | 1526 | 86 | 160 | 81 | 4 | 0 | 50
10:30 | 4279 | 290 | 1531 | 119 | 160 | 81 | 5 | 0 | 50
11:00 | 4264 | 290 | 1536 | 152 | 160 | 81 | 6 | 0 | 50
11:30 | 4313 | 290 | 1610.5 | 210.5 | 160 | 81 | 6.5 | 0 | 52
12:00 | 4362 | 290 | 1685 | 269 | 160 | 81 | 7 | 0 | 54
12:30 | 4327.5 | 290 | 1703.5 | 322 | 160 | 81 | 7.5 | 0 | 52
13:00 | 4293 | 290 | 1722 | 375 | 160 | 81 | 8 | 0 | 50
13:30 | 4293 | 290 | 1722 | 375 | 160 | 81 | 8 | 0 | 50
14:00 | 4293 | 290 | 1722 | 375 | 160 | 81 | 8 | 0 | 50
14:30 | 4171.5 | 282 | 1684.5 | 392.5 | 160 | 81.5 | 7.5 | 0 | 52
15:00 | 4050 | 274 | 1647 | 410 | 160 | 82 | 7 | 0 | 54
15:30 | 4052.5 | 274.5 | 1563 | 418.5 | 160 | 82 | 7 | 0 | 55
16:00 | 4055 | 275 | 1479 | 427 | 160 | 82 | 7 | 0 | 56
16:30 | 4012 | 347.5 | 1408.5 | 557.5 | 160 | 82 | 29.5 | 0 | 59
17:00 | 3969 | 420 | 1338 | 688 | 160 | 82 | 52 | 0 | 62
17:30 | 3980.5 | 518 | 1397 | 1226.5 | 160 | 82 | 95 | 0 | 84
18:00 | 3992 | 616 | 1456 | 1765 | 160 | 82 | 138 | 0 | 106
18:30 | 4022 | 615.5 | 1584 | 1702 | 160 | 82 | 138 | 0 | 105
19:00 | 4052 | 615 | 1712 | 1639 | 160 | 82 | 138 | 0 | 104
19:30 | 4206 | 616 | 1843 | 1404 | 160 | 82 | 104 | 0 | 102
20:00 | 4141 | 615 | 1817 | 1283 | 160 | 82 | 104 | 0 | 102
20:30 | 4132.5 | 615.5 | 1856.5 | 1169.5 | 160 | 82 | 89 | 0 | 100
21:00 | 4124 | 616 | 1896 | 1056 | 160 | 82 | 74 | 0 | 98
21:30 | 4184 | 567.5 | 1890 | 815.5 | 160 | 82 | 41.5 | 0 | 95
22:00 | 4244 | 519 | 1884 | 575 | 160 | 82 | 9 | 0 | 92
22:30 | 4235.5 | 437.5 | 1882 | 460.5 | 160 | 82 | 6.5 | 0 | 87
23:00 | 4227 | 356 | 1880 | 346 | 160 | 82 | 4 | 0 | 82
23:30 | 4212.5 | 267.5 | 1820 | 346 | 160 | 82 | 4 | 0 | 79 | Max Temp. in Dhaka |  | 27.8° C
24:00 | 4198 | 179 | 1760 | 346 | 160 | 82 | 4 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 162.904 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.904 MKWHr
Note on W13: Author:

## Generation
2019-12-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 975703
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 8.2 | 13.19 | 16.85 | 18.87 | 19.39 | 18.23 | 15 | 10.7 | 5.2 | 0.3 | [9 empty] | 127305
6 | Sikalbaha 225MW CCPP (Gas) | 216 | 219 | 202 | 195 | 184 | 195 | 216 | 226 | 204 | 202 | 206 | 217 | 203 | 204 | 204 | 214 | 206 | 204 |  | 202 | 215 | 207 | 205 | 203 | 203 | 203 | 4901611
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 34 | 0 | [5 empty] | 73281
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 0 | 1 | 66 | 68 | 86 | 86 | 88 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 51 | 17 | 1232799
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 38 | 40 | 37 | 40 | 42 | 65 | 69 | 69 | 69 | 67 | 97 | 60 | 60 | 40 | 40 | 40 |  | 65 | 40 | 39 | 35 | 97 | 100 | 90 | 1459000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 300 | 300 | 300 | 335 | 335 | 300 | 300 | 300 | 300 | 335 | 300 | 300 | 300 | 270 | 275 |  | 270 | 335 | 335 | 335 | 335 | 336 | 336 | 7682003
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 34 | 253 |  | 298 | 300 | 300 | 300 | 70 | 0 |  | 1332326
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 8 | 8 | 8 | 8 | 8 | 83 | 83 | 83 | 83 | 102 | 102 | 102 | 63 | 63 | 102 |  | 167 | 167 | 167 | 181 | 181 | 185 | 181 | 2141090
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 851000
21 | Ghorasal Repowered CCPP Unit-3 | 124 | 123 | 124 | 125 | 123 | 125 | 113 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 112 |  | 113 | 114 | 116 | 116 | 116 | 116 | 116 | 2960000
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2283666
29 | Ashuganj TPP Unit- 4 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3393985
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 10 | 10 | 10 | 10 | 37 | 33 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 33 | 727776
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 310 | 320 | 270 | 305 | 280 | 290 | 360 | 360 | 325 | 320 | 330 | 360 | 325 | 290 | 290 | 290 | 290 | 290 |  | 310 | 340 | 320 | 310 | 315 | 315 | 310 | 7609500
| Ashuganj 450 MW CCPP(North) | 315 | 320 | 275 | 310 | 285 | 295 | 368 | 370 | 330 | 380 | 330 | 365 | 330 | 290 | 290 | 290 | 260 | 280 |  | 300 | 325 | 315 | 300 | 300 | 305 | 300 | 7776400
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 81 | 81 | 91 | 91 | 82 | 88 | 80 | 90 | 80 | 81 |  | 80 | 90 | 85 | 87 | 85 | 81 | 81 | 2066270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 356 | 378 | 357 | 352 | 337 | 325 | 364 | 367 | 350 | 348 | 340 | 355 | 361 | 348 | 345 | 344 | 342 | 340 |  | 340 | 355 | 343 | 340 | 342 | 341 | 342 | 8459270
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 400 | 400 | 400 | 420 | 450 | 450 | 400 | 400 | 400 | 420 | 380 | 380 | 340 | 340 | 340 |  | 340 | 450 | 450 | 450 | 450 | 450 | 420 | 9102750
41 | Haripur 360MW CCPP(HPL) | 367 | 370 | 373 | 306 | 306 | 305 | 338 | 371 | 364 | 330 | 330 | 348 | 320 | 320 | 320 | 330 | 300 | 300 |  | 356 | 347 | 332 | 333 | 321 | 319 | 368 | 8013000
42 | RPCL 210MW CCPP | 158 | 158 | 160 | 161 | 162 | 162 | 161 | 162 | 162 | 160 | 155 | 154 | 154 | 149 | 140 | 139 | 154 | 154 |  | 144 | 143 | 143 | 143 | 140 | 139 | 147 | 3577720
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 59 | 58 | 58 | 60 | 60 | 58 | 60 | 58 | 58 | 58 | 58 | 60 | 60 |  | 60 | 60 | 58 | 60 | 60 | 59 | 57 | 1402000
45 | Fenchugonj CCPP Phase-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1569119
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 68 | 68 | 67 | 65 | 31 | 31 | 31 | 31 | 31 | 20 | 32 |  | 32 | 32 | 32 | 32 | 33 | 31 | 33 | 976032
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 74 | 74 | 76 | 76 | 76 | 76 | 76 | 79 | 73 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1437120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [5 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 380000
52 | Sylhet 50MW PP (EPL) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 12 | 19 | 10 | 26 | 30 | 30 | 30 | 14 | 31 |  | 35 | 37 | 37 | 39 | 39 | 37 | 37 | 464100
53 | Sylhet 10MW PP (Desh) | 0 | [5 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 172800
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 0 | 11 | 5 | 5 | 0 |  | 0 | [5 empty] | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 24096
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 47 | 47 | 47 | 47 | 47 | 44 | 10 | 11 | 20 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 695400
56 | Shahjahanulla 25 MW PP | [7 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 387696
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 310 | 300 | 280 | 300 | 300 | 320 | 325 | 300 | 290 | 295 | 340 | 315 | 285 | 300 | 270 | 270 | 275 |  | 300 | 320 | 305 | 305 | 295 | 290 | 190 | 7533500
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 35 |  | 35 | 35 | [5 empty] | 99168
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [6 empty] | 0 | 18 | 18 | 18 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 301248
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 0 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 315036
62 | Tangail 22 MW PP (Doreen) | [6 empty] | 0 | 20 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 345528
63 | Impoprt (Tripura) | 70 | 66 | 64 | 64 | 66 | 66 | 64 | 70 | 66 | 50 | 50 | 54 | 50 | 56 | 54 | 56 | 62 | 106 |  | 104 | 102 | 102 | 98 | 92 | 82 | 76 | 1708800
64 | Malancha, Ctg. EPZ (United) | 5 | 5 | 4 | 4 | 4 | 5 | 10 | 7 | 10 | 10 | 7 | 12 | 15 | 10 | 10 | 12 | 10 | 14 |  | 17 | 25 | 28 | 28 | 38 | 40 | 40 | 387840
65 | Feni 22MW PP (Doreen) | [8 empty] | 0 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 305964
66 | Feni 11 MW PP (Doreen) | [7 empty] | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 165780
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 622700
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 16 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 375890
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 22 | 25 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 30 | 30 | 32 | 24 |  | 24 | 24 | 24 | 25 | 31 | 31 | 31 | 670680
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 776200
73 | Ghorashal 108MW PP (Regent) | 52 | 52 | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 101 | 101 | 98 | 98 | 98 | 72 | 76 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1504409
| Feni Lanka Power | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [7 empty] | 0 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 45 |  | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 420108
79 | Kodda 150MW PP | [16 empty] | 48 | 100 |  | 100 | 100 | 100 | 70 | 5 |  |  | 386880
80 | Jamalpur 95 MW PP(Powerpac) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 0 | 0 |  | 38400
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.29 | 1.353 | 2.617 | 3.714 | 4.154 | 4.291 | 3.916 | 3.19 | 2.1 | 0.9 | [10 empty] | 26520
| Jodiac Power | [16 empty] | 27 | 54 | [8 empty] | 98159
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 0 | 10 | 50 | 50 | 50 | 50 | 50 | 10 | 70 |  | 100 | 100 | 100 | 50 | 0 | 0 |  | 590280
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 5 | 28 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 842040
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 25 | 25 | 25 | 25 | 43 | 43 | 35 | 15 | 22 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 648352
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 0 | 16 | 32 | 16 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 0 | [6 empty] | 143280
95 | Patenga 50MW PP (Baraka) | [17 empty] | 27 |  | 8 | [6 empty] | 36000
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 1 | 50 |  | 98 | 98 | 98 |  |  |  |  | 290880
97 | Katpotti 52 MW PP (Sinha) | [6 empty] | 0 | 14 | 46 | 46 | 46 | 46 | 46 | 41 | 47 | 47 | 46 | 46 |  | 46 | 46 | 46 | 26 | 26 | 26 | 12 | 683904
98 | Bosila 108MW PP(CLC) | [10 empty] | 0 | 32 | 40 | 40 | 40 | 40 | 40 | 68 |  | 68 | 72 | 72 | 72 | 32 |  |  | 504960
99 | Madanganj-55 MW PP(Summit) | [7 empty] | 0 | 4 | 15 | 15 | 22 | 30 | 48 | 55 | 55 | 55 | 55 |  | 55 | 0 | [5 empty] | 436565
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 55 | 17 | [5 empty] | 98035
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 100 | 100 | 100 |  | 100 | 100 | 100 | 163 | 163 | 163 | 130 | 3123442
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.4 | 1.1 | 1.5 | 1.9 | 1.9 | 2 | 1.5 | 1 | 0.4 | [10 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 5 | 53 |  | 35 | 35 | [5 empty] | 126360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [10 empty] | 0 | 36 | 80 | 80 | 80 | 80 | 80 | 158 |  | 190 | 192 | 170 | 170 | 170 | 130 | 80 | 1572000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 30 |  | 20 | 0 | [5 empty] | 63360
116 | Chandpur 200MW (Desh energy) | [16 empty] | 70 | 190 |  | 70 | 0 | [5 empty] | 405120
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 99 |  | 50 | 50 | 50 | 50 | 40 | 40 |  | 449963
118 | Bibiyana-III 400 MW CCPP | 396 | 409 | 364 | 323 | 298 | 386 | 398 | 399 | 366 | 374 | 370 | 395 | 369 | 366 | 366 | 374 | 340 | 341 |  | 343 | 362 | 350 | 343 | 365 | 360 | 363 | 8793000
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | [26 empty] | 0
120 | Eastern Zone Total | 4610 | 4652 | 4420 | 4168 | 4088 | 4199 | 4516.39 | 4846.953 | 5005.907 | 4953.064 | 4997.924 | 5353.581 | 5424.146 | 5186.69 | 5187.8 | 5039.5 | 4953.3 | 6132 |  | 6326 | 6390 | 6189 | 6034 | 5704 | 5485 | 5167 | 124420569
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 20 | 48 |  | 48 | 48 | 48 | 48 | 48 | 32 | 0 | 285120
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2761000
140 | Bhola 33 MW PP (Venture) | 23 | 20 | 20 | 19 | 19 | 19 | 18 | 16 | 16 | 17 | 16 | 17 | 17 | 18 | 18 | 16 | 19 | 24 |  | 25 | 25 | 26 | 25 | 25 | 24 | 22 | 464800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 24 |  | 40 | 40 | 33 | 0 |  |  |  | 106875
143 | Gopalganj 100 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 7 | 8 | 6 | 7 | 7 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 103680
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 3 | 15 |  | 15 | 15 | 32 | 32 | 32 | 15 | 0 | 144576
146 | Bheramara HVDC | 136 | 137 | 137 | 137 | 136 | 137 | 136 | 137 | 284 | 290 | 290 | 290 | 290 | 274 | 274 | 275 | 420 | 616 |  | 615 | 616 | 615 | 616 | 519 | 356 | 179 | 7382545
147 | Bheramara 360 MW CCPP | 140 | 155 | 185 | 200 | 220 | 240 | 265 | 278 | 278 | 270 | 263 | 265 | 244 | 243 | 235 | 235 | 240 | 235 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5682240
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3902300
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1190000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 176 | 186 | 179 | 175 | 179 | 169 | 202 | 204 | 214 | 197 | 194 | 204 | 214 | 202 | 179 | 178 | 185 | 181 |  | 182 | 184 | 184 | 201 | 214 | 197 | 181 | 4857409
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 5 | 12 | 41 | 86 | 133 | 143 | 143 | 189 | 199 | 206 | 213 | 217 | 199 | 199 | 205 | 202 | 202 | 202 |  | 202 | 202 | 202 | 202 | 202 | 204 | 204 | 4255991
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 190 | 188 | 186 | 185 | 189 | 177 | 211 | 213 | 210 | 207 | 215 | 211 | 211 | 186 | 188 | 191 | 191 | 191 |  | 190 | 190 | 190 | 189 | 205 | 208 | 207 | 4968655
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 148 | 0 | [24 empty] | 311545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 361680
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 264888
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224784
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 20 | 50 |  | 30 | 12 | 12 | 0 | 0 |  |  | 124490
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 8 | 32 |  | 0 | [6 empty] | 42240
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 0 | 28 | 35 | 35 | 35 | 35 | 80 |  | 113 | 113 | 113 | 113 |  |  |  | 660576
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 102 | 108 |  | 100 | 66 | 44 | 30 | 0 |  |  | 363840
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.1 | 1.3 | 0 | 4.4 | 5 | 4.8 | 4.3 | 4.2 | 1 | 0.4 | 0.1 | [9 empty] | 24252
178
178