## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-18 | Wednesday
|  | Date (day): | 2019-12-18 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10922.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13784 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-17 | 2019-12-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 99 | 99 | 100 | 100
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 107 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 17 | 307 | 307 |  | 105 | ST Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 365 | 368 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 45 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 36 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 91 | 97 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 40 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 345 | 344 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 94 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 40 | 47 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 65 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 15 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 52 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 30 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1841 | 2219 | 3431 | 4031 | 598 | 1104
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 83 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 216 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 134 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 50 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 90 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 15 | 7 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.14 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 50 | 172 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 663.84 | 937 | 1582 | 1745 | 290 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 120 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 60 | 135 | 135
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 345 | 240 | 240 |  |  | ST under maint.
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 285 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Under Maint.
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 187 | 8 | 100 | 185 | 10 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 0 | 0 | 0 |  | 163 | under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 52 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 86 | 102 | 90 | 105
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 25 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 18 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 50 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1198 | 1178 | 1511 | 2075 | 25 | 400
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 145 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 94 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.8 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 7 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 253.8 | 381 | 543.6 | 642 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 62 | 89 | 65 | 65
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 47 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 79 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 34 | 35 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  |  | Under maint. |  | 28/12/2019
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 321 | 363 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 891 | 1012 | 1036 | 1036 | 0 | 489
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 299 | 640 | 301 | 650
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 16 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 4 | 4 | 30 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 170 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 669 | 920 | 801 | 1745 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 12 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 115 | 115 | 120 | 120 |  | 74 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 126 | 191 | 305 | 375 | 0 | 87
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 192 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 173 | 0 | 0 | 220 |  | Gas shortage.
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 195 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 125 | 419 | 290 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 796 | 1234 | 1392 | 1768 | 341 | 8
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 260 | 200 | 220
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 262.6 | 373 | 321 | 367 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6701.24 | 8445 | 10922.6 | 13784 | 1254 | 2466
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6365.5829 | 8022 | 10375.5 | 13093.5758
A. |  | 2019-12-17 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8445 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4671 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8445 | MW
3 | Day peak Generation : |  |  | 6701.24 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8022 | MW
4 | Evening peak Generation : |  |  | 8445 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 154.6151 | MKWHr | By Solar | 0.17202 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 124.7475 | MKWHr |  | By Oil: | 12.8169 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 5.3186 | MKWHr |  | By Hydro: | 1.9529 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1254 | MW | Dhaka | 3024 | 3024 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2466 | MW | Chittagong | 783 | 783 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3720 | MW | Khulna | 991 | 991 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1056.7 | MMCFD |  |  | Rajshahi | 828 | 828 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 120778952.398 | ii) Oil : | Taka | 118220907.89 | Comilla | 721 | 721 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 21753074 | Total | Taka | 260752934.288 | Mymensingh | 629 | 629 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.1535 | MKWHr. | Sylhet | 318 | 318 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 60 | MW (E to W) at | 19:00 | hrs | Barisal | 221 | 221 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -335 | MW at | 8:00 | hrs | Rangpur | 507 | 507 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.7° C |  |  | Total | 8022 | 8022 |  | 0
B. |  | 2019-12-18 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 24.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13784 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6800 | MW
4 | Reserve(Generation end) |  |  |  | 5184 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 157.4529 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5179 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.6785 | MKWHr. | ii) HVDC Flow at Peak Time |  | 640 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9286 | MKWHr. | iii) Maximum HVDC Flow : |  | 640 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.59 |  | (b) Today: | 97.47 |  | (c) Rule Curve: |  | 104.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 315 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 105 | 80 | 0 | 275 | 335 | 0 | 8 | 82 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 66 | 215 | 0 | 0 | 0 | 60 | 65 | 5 | 0 | 100 | 0 | 32 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 21 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 196 | 0 | 188 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3872 | 1394 | 5266 | 3949 | 137 | 868 | 0 | 160 | 82 | 4 | 66 | 0 | 0 | 97.61
2:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 315 | 300 |  | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 80 | 0 | 250 | 270 | 0 | 8 | 87 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 201 | 0 | 0 | 0 | 60 | 65 | 5 | 0 | 100 | 0 | 20 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 181 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3669 | 1379 | 5048 | 3757 | 137 | 844 | 0 | 160 | 82 | 4 | 64 | 0 | 0 | 97.61
3:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 315 | 280 |  | 0 | 350 | 0 | 0 | 0 | 0 | 230 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 178 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 80 | 0 | 260 | 290 | 0 | 8 | 87 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 62 | 166 | 0 | 0 | 0 | 60 | 65 | 5 | 0 | 100 | 0 | 20 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 20 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 183 | 0 | 184 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3537 | 1350 | 4887 | 3657 | 137 | 795 | 0 | 150 | 82 | 4 | 62 | 0 | 0 | 97.6
4:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 290 | 280 |  | 0 | 350 | 0 | 0 | 0 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 176 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 80 | 0 | 255 | 275 | 0 | 8 | 84 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 60 | 167 | 0 | 0 | 0 | 60 | 65 | 5 | 0 | 100 | 0 | 20 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 185 | 0 | 184 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3455 | 1300 | 4755 | 3528 | 137 | 794 | 0 | 150 | 82 | 4 | 60 | 0 | 0 | 97.6
5:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 256 | 220 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 191 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 80 | 0 | 255 | 310 | 0 | 8 | 90 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 56 | 151 | 0 | 0 | 0 | 20 | 65 | 5 | 0 | 100 | 0 | 20 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 193 | 0 | 152 | 0 | 0 | 0 | 183 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3343 | 1328 | 4671 | 3441 | 137 | 802 | 0 | 149 | 82 | 4 | 56 | 0 | 0 | 97.59
6:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 246 | 320 |  | 0 | 400 | 0 | 0 | 0 | 0 | 230 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 80 | 80 | 0 | 255 | 310 | 0 | 8 | 90 | 20 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 60 | 215 | 0 | 0 | 0 | 20 | 65 | 5 | 0 | 100 | 0 | 20 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 19 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 143 | 0 | 0 | 0 | 194 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3647 | 1366 | 5013 | 3570 | 137 | 1010 | 0 | 150 | 82 | 4 | 60 | 0 | 0 | 97.59
7:00 | 35 | 99 | 0 | 0 | 0 | 52 | 0 | 0 | 340 |  | 0 | 380 | 0 | 0 | 0 | 0 | 270 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 41 | 40 | 120 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 100 | 80 | 0 | 240 | 345 | 0 | 80 | 90 | 27 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 62 | 215 | 0 | 0 | 0 | 60 | 65 | 34 | 30 | 130 | 0 | 20 | 76 | 0 | 0 | 0 | 30 | 10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  | 137 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 8 | 0 | 0 | 150 | 0 | 0 | 205 | 0 | 186 | 0 | 0 | 0 | 213 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 3920.6 | 1470.1 | 5390.7 | 3604 | 137 | 1351 | 0 | 150 | 81 | 4 | 62 | 1.7 | 0 | 97.58
8:00 | 35 | 99 | 0 | 0 | 0 | 98 | 0 | 0 | 370 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 25 | 25 | 0 | 0 | 41 | 40 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 120 | 80 | 0 | 250 | 340 | 0 | 180 | 90 | 27 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 70 | 217 | 0 | 0 | 0.2 | 60 | 65 | 47 | 50 | 163 | 0 | 32 | 76 | 0 | 0 | 17 | 29 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 |  | 148 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 150 | 0 | 0 | 225 | 0 | 198 | 0 | 0 | 0 | 216 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 4324.6 | 1510.2 | 5834.8 | 3776 | 148 | 1597 | 0 | 150 | 81 | 4 | 70 | 8.8 | 0 | 0
9:00 | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 370 |  | 0 | 435 | 0 | 1 | 0 | 0 | 335 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 18 | 2 | 120 | 80 | 0 | 245 | 365 | 0 | 187 | 90 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 14 | 68 | 186 | 22 | 20 | 0.5 | 60 | 65 | 47 | 50 | 100 | 0 | 32 | 76 | 0 | 0 | 17 | 29 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12.8 | 46 | 0 | 0 | 395 | 0 | 0 | 11 | 2.5 | 32 | 0 | 0 | 0 |  | 299 | 0 | 305 | 0 | 6 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 200 | 0 | 0 | 224 | 0 | 206 | 0 | 0 | 0 | 214 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4634.8 | 1696.5 | 6331.3 | 3903 | 299 | 1516 | 243 | 200 | 82 | 4 | 68 | 16.3 | 0 | 0
10:00 | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 332 |  | 0 | 420 | 0 | 15 | 0 | 0 | 335 | 0 | 35 | 0 | 0 | 16 | 0 | 0 | 72 | 0 | 0 | 53 | 35 | 0 | 22 | 0 | 32 | 33 | 25 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 34 | 18 | 4 | 120 | 80 | 0 | 220 | 315 | 0 | 187 | 86 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 10 | 11 | 20 | 14 | 82 | 170 | 50 | 20 | 0.5 | 60 | 65 | 44 | 50 | 100 | 0 | 31 | 76 | 0 | 0 | 17 | 30 | 10 | 0 | 16 | 1 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 16.3 | 50 | 0 | 0 | 350 | 0 | 0 | 34 | 3.5 | 66 | 0 | 0 | 0 |  | 299 | 0 | 290 | 0 | 49 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 14 | 10 | 0 | 0 | 242 | 0 | 0 | 195 | 0 | 187 | 0 | 0 | 0 | 213 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 36 |  | 4678.3 | 1749.8 | 6428.1 | 3669 | 299 | 1459 | 570 | 242 | 82 | 4 | 82 | 21.1 | 0 | 0
11:00 | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 285 |  | 0 | 370 | 0 | 44 | 0 | 0 | 347 | 0 | 63 | 0 | 0 | 64 | 0 | 0 | 24 | 0 | 25 | 53 | 55 | 0 | 0 | 25 | 32 | 33 | 30 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 181 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 41 | 18 | 7 | 120 | 80 | 0 | 280 | 285 | 0 | 187 | 91 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 16 | 14 | 80 | 149 | 50 | 20 | 1.5 | 60 | 65 | 47 | 50 | 100 | 0 | 31 | 76 | 0 | 0 | 17 | 31 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 18.4 | 50 | 0 | 0 | 325 | 0 | 0 | 50 | 4.05 | 50 | 0 | 0 | 0 |  | 299 | 0 | 300 | 0 | 40 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 175 | 0 | 159 | 0 | 0 | 0 | 193 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 |  | 4656.95 | 1742.6 | 6399.55 | 3616 | 299 | 1447 | 586 | 260 | 82 | 4 | 80 | 25.55 | 0 | 0
12:00 | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 365 |  | 0 | 400 | 0 | 45 | 0 | 0 | 345 | 0 | 91 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 47 | 19 | 7 | 120 | 0 | 0 | 295 | 285 | 0 | 187 | 86 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 86 | 142 | 50 | 20 | 1.8 | 60 | 62 | 47 | 50 | 163 | 0 | 31 | 73 | 0 | 0 | 17 | 34 | 10 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 18.7 | 50 | 0 | 0 | 321 | 0 | 0 | 50 | 4.14 | 50 | 0 | 0 | 0 |  | 299 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 180 | 0 | 0 | 0 | 196 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 |  | 4847.64 | 1853.6 | 6701.24 | 3678 | 299 | 1655 | 610 | 260 | 82 | 4 | 86 | 27.24 | 0 | 0
13:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 0 | 368 |  | 0 | 400 | 0 | 45 | 0 | 0 | 350 | 0 | 63 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 43 | 40 | 120 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 10 | 120 | 0 | 0 | 277 | 270 | 0 | 187 | 88 | 37 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 88 | 142 | 50 | 20 | 1.5 | 60 | 63 | 47 | 50 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 33 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 17.6 | 50 | 0 | 0 | 294 | 0 | 0 | 50 | 3.8 | 70 | 0 | 0 | 0 |  | 297 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 214 | 0 | 213 | 0 | 0 | 0 | 213 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 |  | 4773.9 | 2108.6 | 6882.5 | 3657 | 297 | 1827 | 640 | 260 | 83 | 4 | 88 | 26.5 | 0 | 0
14:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 0 | 314 |  | 0 | 320 | 0 | 47 | 0 | 0 | 240 | 0 | 37 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 43 | 40 | 120 | 0 | 0 | 194 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 8 | 120 | 0 | 0 | 290 | 285 | 0 | 187 | 86 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 16 | 14 | 90 | 125 | 50 | 20 | 0.6 | 60 | 52 | 47 | 47 | 100 | 0 | 31 | 76 | 0 | 0 | 17 | 35 | 10 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 14.8 | 50 | 0 | 0 | 303 | 0 | 0 | 50 | 3 | 124 | 0 | 0 | 0 |  | 296 | 0 | 200 | 0 | 66 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 188 | 0 | 184 | 0 | 0 | 0 | 185 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 |  | 4498.4 | 1975.8 | 6474.2 | 3314 | 296 | 1709 | 696 | 260 | 83 | 4 | 90 | 22.2 | 0 | 0
15:00 | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 367 |  | 0 | 320 | 0 | 0 | 0 | 0 | 240 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 2 | 110 | 0 | 0 | 230 | 285 | 0 | 187 | 84 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 16 | 14 | 82 | 128 | 50 | 20 | 0.8 | 60 | 55 | 47 | 44 | 130 | 0 | 31 | 76 | 0 | 0 | 17 | 36 | 10 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10.7 | 50 | 0 | 0 | 303 | 0 | 0 | 50 | 2 | 133 | 0 | 0 | 0 |  | 296 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 185 | 0 | 181 | 0 | 0 | 0 | 184 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 4427.5 | 1939 | 6366.5 | 3312 | 296 | 1768 | 544 | 260 | 84 | 4 | 82 | 16.5 | 0 | 0
16:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 0 | 364 |  | 0 | 380 | 0 | 0 | 0 | 0 | 240 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 42 | 53 | 55 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 44 | 40 | 120 | 0 | 0 | 219 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 5 | 100 | 0 | 23 | 240 | 320 | 0 | 73 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 16 | 14 | 84 | 140 | 50 | 20 | 0.3 | 60 | 89 | 47 | 44 | 163 | 0 | 30 | 76 | 0 | 0 | 17 | 35 | 10 | 0 | 23 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 4.6 | 20 | 0 | 0 | 334 | 0 | 0 | 50 | 0.8 | 82 | 0 | 0 | 0 |  | 297 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 116 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 181 | 0 | 197 | 0 | 0 | 0 | 186 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4582.7 | 1976 | 6558.7 | 3588 | 297 | 1777 | 458 | 260 | 84 | 4 | 84 | 6.7 | 0 | 0
17:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 0 | 367 |  | 0 | 380 | 0 | 15 | 0 | 0 | 260 | 0 | 90 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 46 | 53 | 55 | 13 | 22 | 25 | 28 | 33 | 33 | 8 | 0 | 43 | 40 | 120 | 0 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 18 | 8 | 100 | 0 | 60 | 260 | 270 | 0 | 73 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 86 | 145 | 63 | 20 | 0 | 58 | 89 | 44 | 44 | 163 | 0 | 37 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 23 | 8 | 0 | 2 | 0 | 0 | 16 | 0 | 0 | 0.2 | 20 | 0 | 0 | 290 | 11 | 0 | 50 | 0 | 86 | 0 | 0 | 0 |  | 441 | 0 | 215 | 0 | 6 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 24 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 182 | 0 | 185 | 0 | 0 | 0 | 191 | 0 | 348 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 2 |  | 4688.2 | 2094.1 | 6782.3 | 3527 | 441 | 1751 | 595 | 260 | 83 | 39 | 86 | 0.3 | 0 | 0
18:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 0 | 365 |  | 0 | 420 | 0 | 78 | 0 | 15 | 344 | 0 | 97 | 0 | 2 | 80 | 48 | 0 | 8 | 0 | 47 | 53 | 55 | 17 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 43 | 40 | 120 | 0 | 0 | 217 | 0 | 134 | 0 |  | 0 | 0 | 34 | 10 | 0 | 50 | 18 | 8 | 110 | 0 | 60 | 355 | 310 | 0 | 73 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 18 | 102 | 145 | 94 | 20 | 0 | 58 | 89 | 47 | 44 | 130 | 0 | 67 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 0 | 397 | 70 | 0 | 17 | 0 | 159 | 0 | 0 | 27 |  | 640 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 11 | 61 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 186 | 0 | 176 | 0 | 0 | 0 | 193 | 0 | 434 | 0 | 0 | 0 | 42 | 108 | 0 | 0 | 76 |  | 5573 | 2699 | 8272 | 3889 | 640 | 1845 | 1367 | 260 | 83 | 86 | 102 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 17 | 368 |  | 0 | 420 | 0 | 100 | 0 | 36 | 344 | 0 | 97 | 0 | 40 | 94 | 65 | 0 | 0 | 0 | 47 | 53 | 55 | 15 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 40 | 120 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 34 | 0 | 0 | 50 | 18 | 15 | 120 | 0 | 60 | 345 | 285 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 18 | 102 | 145 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 11 | 0 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 90 | 52 | 0 | 363 | 115 | 0 | 17 | 0 | 172 | 0 | 0 | 50 |  | 640 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 12 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 192 | 0 | 173 | 0 | 0 | 0 | 195 | 0 | 419 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 108 |  | 5727 | 2718 | 8445 | 3838 | 640 | 1809 | 1610 | 260 | 83 | 103 | 102 | 0 | 0 | 97.64
19:30 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 17 | 369 |  | 0 | 420 | 0 | 100 | 0 | 55 | 342 | 0 | 40 | 0 | 60 | 94 | 65 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 40 | 120 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 18 | 120 | 0 | 80 | 360 | 305 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 18 | 102 | 146 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 130 | 0 | 67 | 79 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 11 | 0 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 52 | 0 | 379 | 115 | 0 | 17 | 0 | 179 | 0 | 0 | 50 |  | 640 | 0 | 155 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 12 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 170 | 0 | 166 | 0 | 0 | 0 | 170 | 0 | 409 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 108 |  | 5718 | 2639 | 8357 | 3782 | 640 | 1770 | 1651 | 260 | 83 | 69 | 102 | 0 | 0 | 0
20:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 18 | 368 |  | 0 | 420 | 0 | 100 | 0 | 55 | 346 | 0 | 41 | 0 | 90 | 94 | 65 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 23 | 120 | 0 | 80 | 340 | 275 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 100 | 147 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 130 | 0 | 68 | 79 | 0 | 0 | 17 | 37 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 50 | 0 | 362 | 115 | 0 | 17 | 0 | 195 | 0 | 0 | 40 |  | 640 | 0 | 150 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 12 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 165 | 0 | 163 | 0 | 0 | 0 | 178 | 0 | 403 | 0 | 0 | 0 | 50 | 88 | 0 | 0 | 108 |  | 5673 | 2603 | 8276 | 3725 | 640 | 1770 | 1630 | 260 | 82 | 69 | 100 | 0 | 0 | 97.64
21:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 165 | 367 |  | 0 | 420 | 0 | 100 | 0 | 0 | 340 | 0 | 41 | 0 | 0 | 94 | 51 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 42 | 40 | 120 | 0 | 0 | 210 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 32 | 120 | 0 | 80 | 360 | 305 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 98 | 146 | 94 | 20 | 0 | 59 | 89 | 47 | 47 | 130 | 0 | 67 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 381 | 70 | 0 | 17 | 0 | 205 | 0 | 0 | 0 |  | 640 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 115 | 12 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 171 | 0 | 396 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 |  | 5503 | 2327 | 7830 | 3909 | 640 | 1774 | 1012 | 260 | 82 | 55 | 98 | 0 | 0 | 97.63
22:00 | 35 | 98 | 0 | 0 | 0 | 107 | 0 | 290 | 353 |  | 0 | 420 | 0 | 100 | 18 | 0 | 350 | 0 | 41 | 0 | 0 | 94 | 40 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 40 | 120 | 0 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 18 | 36 | 120 | 0 | 80 | 360 | 285 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 90 | 146 | 94 | 20 | 0 | 58 | 89 | 47 | 47 | 130 | 0 | 67 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 40 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 542 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 116 | 12 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 158 | 0 | 135 | 0 | 0 | 0 | 166 | 0 | 371 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 |  | 5432 | 2065 | 7497 | 3975 | 542 | 1739 | 764 | 260 | 83 | 44 | 90 | 0 | 0 | 97.51
23:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 304 | 358 |  | 0 | 420 | 0 | 65 | 0 | 0 | 349 | 0 | 40 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 43 | 40 | 120 | 0 | 0 | 209 | 0 | 137 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 120 | 0 | 80 | 350 | 275 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 86 | 145 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 130 | 0 | 69 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 299 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5195 | 1669 | 6864 | 3840 | 299 | 1748 | 544 | 260 | 83 | 4 | 86 | 0 | 0 | 97.5
24:00 | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 304 | 360 |  | 0 | 420 | 0 | 14 | 0 | 0 | 349 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 43 | 40 | 120 | 10 | 0 | 203 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 120 | 0 | 80 | 340 | 305 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 76 | 161 | 27 | 20 | 0 | 60 | 89 | 47 | 47 | 130 | 0 | 69 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 |  | 202 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 0 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4912 | 1564 | 6476 | 3910 | 202 | 1726 | 215 | 260 | 83 | 4 | 76 | 0 | 0 | 97.5
KWH | 791000 | 2532800 | 0 | 0 | 0 | 1849409 | 0 | 2918400 | 8005000 |  | 0 | 8644250 | 0 | 855360 | 34800 | 123787 | 7259640 | 0 | 1510000 | 0 | 189120 | 926064 | 278400 | 0 | 129600 | 0 | 472656 | 842040 | 598609 | 43932 | 319392 | 600000 | 693900 | 745800 | 753200 | 307944 | 0 | 980880 | 972000 | 2900000 | 0 | 0 | 4820854 | 0 | 1076525 | 0 |  | 0 | 0 | 62428 | 22200 | 0 | 136320 | 324576 | 430080 | 2679106 | 910340 | 550990 | 7162100 | 7272000 | 0 | 1856727 | 1363360 | 644472 | 0 | 0 | 813764 | 0 | 0 | 0 | 294624 | 143100 | 372500 | 373020 | 1928640 | 3817760 | 1074240 | 313848 | 7100 | 1350000 | 1734360 | 835800 | 841320 | 3243313 | 0 | 923520 | 1407360 | 0 | 0 | 322000 | 706740 | 181980 | 0 | 341016 | 108144 | 0 | 85309 | 0 | 0 | 470400 | 0 | 0 | 122175 | 752640 | 165120 | 0 | 8514000 | 520800 | 0 | 513527 | 25560 | 1884327 | 0 | 0 | 126540 |  | 7678545 | 0 | 5793408 | 0 | 344640 | 0 | 0 | 0 | 0 | 84736 | 155625 | 2755000 | 0 | 391968 | 0 | 0 | 1200000 | 0 | 0 | 0 | 155180 | 0 | 0 | 0 | 0 | 361920 | 246564 | 232074 | 0 | 0 | 5318600 | 0 | 0 | 4833573 | 0 | 4095082 | 0 | 0 | 0 | 4867164 | 0 | 5110600 | 0 | 0 | 0 | 257616 | 382080 | 0 | 17183 | 428928 |  | 109904608 | 44710486 | 154615094 | 90212648 | 7678545 | 34534827 | 12391372 | 5318600 | 1952880 | 425564 | 1928640 | 172018 | 0
Fuel Cost | 885920 | 2735424 | 0 | 0 | 0 | 1793926.73 | 0 | 2101248 | 6083800 |  | 0 | 6915400 | 0 | 8724672 | 376884 | 1270054.62 | 9001953.6 | 0 | 1887500 | 0 | 2099232 | 9408810.24 | 2758944 | 0 | 1179360 | 0 | 4424060.16 | 8075163.6 | 5710729.86 | 437562.72 | 239544 | 450000 | 0 | 0 | 0 | 2950103.52 | 0 | 255028.8 | 252720 | 4437000 | 0 | 0 | 5061896.7 | 0 | 1367186.75 | 0 |  | 0 | 0 | 654869.72 | 228438 | 0 | 1275955.2 | 298609.92 | 1195622.4 | 2813061.3 | 955857 | 578539.5 | 5299954 | 6108480 | 0 | 1819592.46 | 1813268.8 | 528467.04 | 0 | 0 | 1163682.52 | 0 | 0 | 0 | 300516.48 | 107325 | 704025 | 279765 | 13307616 | 3130563.2 | 10216022.4 | 320124.96 | 116440 | 1836000 | 2358729.6 | 1136688 | 1051650 | 4021708.12 | 0 | 1376044.8 | 2476953.6 | 0 | 0 | 511980 | 826885.8 | 427653 | 0 | 255762 | 82189.44 | 0 | 893185.23 | 0 | 0 | 4525248 | 0 | 0 | 1409899.5 | 7014604.8 | 1548825.6 | 0 | 8003160 | 4567416 | 0 | 4852830.15 | 0 | 17373494.94 | 0 | 0 | 0 |  | 20732071.5 | 0 | 4518858.24 | 0 | 3322329.6 | 0 | 0 | 0 | 0 | 1110041.6 | 1539131.25 | 2204000 | 0 | 4209736.32 | 0 | 0 | 2256000 | 0 | 0 | 0 | 1609216.6 | 0 | 0 | 0 | 0 | 398112 | 406830.6 | 175680.018 | 0 | 0 | 21753074 | 0 | 0 | 4253544.24 | 0 | 3808426.26 | 0 | 0 | 0 | 4283104.32 | 0 | 3730738 | 0 | 0 | 0 | 2295358.56 | 3568627.2 | 0 | 0 | 0 |  | 210651829.78 | 86174880.308 | 296826710.088 | 87329709.168 | 20732071.5 | 33449243.23 | 113697052.57 | 21753074 | 507748.8 | 4523855.32 | 13307616 | 1526339.5 | 0
Yesterday Day Peak | 35 | 99 | 0 | 0 | 0 | 104 | 0 | 0 | 365 |  | 0 | 400 | 0 | 45 | 0 | 0 | 345 | 0 | 91 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 40 | 120 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 47 | 19 | 7 | 120 | 0 | 0 | 295 | 285 | 0 | 187 | 86 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 86 | 142 | 50 | 20 | 1.8 | 60 | 62 | 47 | 50 | 163 | 0 | 31 | 73 | 0 | 0 | 17 | 34 | 10 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 18.7 | 50 | 0 | 0 | 321 | 0 | 0 | 50 | 4.14 | 50 | 0 | 0 | 0 |  | 299 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 4 | 0 | 115 | 11 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 180 | 0 | 0 | 0 | 196 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 |  | 6701.24 | DayPeak
Yesterday Evening Peak | 35 | 99 | 0 | 0 | 0 | 107 | 0 | 17 | 368 | 0 | 0 | 420 | 0 | 100 | 0 | 36 | 344 | 0 | 97 | 0 | 40 | 94 | 65 | 0 | 0 | 0 | 47 | 53 | 55 | 15 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 40 | 120 | 0 | 0 | 204 | 0 | 134 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 50 | 18 | 15 | 120 | 0 | 60 | 345 | 285 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 18 | 102 | 145 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 163 | 0 | 67 | 79 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 11 | 0 | 30 | 0 | 0 | 7 | 0 | 0 | 0 | 90 | 52 | 0 | 363 | 115 | 0 | 17 | 0 | 172 | 0 | 0 | 50 |  | 640 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 40 | 115 | 12 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 192 | 0 | 173 | 0 | 0 | 0 | 195 | 0 | 419 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 108 |  | 8445 | EvPeak
Forecast for Evening | 35 | 100 | 0 | 0 | 0 | 108 | 0 | 307 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 100 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 15 | 120 | 0 | 135 | 240 | 360 | 0 | 185 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 105 | 210 | 95 | 22 | 0 | 60 | 65 | 51 | 50 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  | 650 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 120 | 20 | 110 | 30 | 0 | 50 | 50 | 45 | 100 | 50 | 42 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 220 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 100 | 0 | 0 | 0 | 108 | 0 | 307 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 100 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 21 | 7 | 120 | 0 | 135 | 240 | 360 | 0 | 100 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 210 | 95 | 22 | 1.6 | 60 | 65 | 51 | 50 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  | 301 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 120 | 20 | 70 | 0 | 0 | 50 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 290 | 50 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 90 | 0 | 0 | 0 | 32 | 0 | 307 | 300 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 352 | 0 | 42 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 25 | 28 | 34 | 33 | 0 | 0 | 43 | 40 | 120 | 100 | 0 | 216 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 12 | 120 | 0 | 80 | 0 | 345 | 0 | 141 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 14 | 74 | 161 | 0 | 20 | 0.1 | 60 | 89 | 45 | 47 | 130 | 0 | 53 | 30 | 0 | 0 | 17 | 30 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0 | 0 | 0 | 395 | 0 | 12 | 0 | 1.1 | 50 | 0 | 0 | 0 | 0 | 136 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0
199
| Minimum Generation |  | 4671 | 5:00
| Highest Generation |  | 8445 | 19:00
| Day Peak Generation |  | 6701.24 | 12:00
| Evening Peak Generation |  | 8445 | 19:00
| HVDC Max Flow |  | 640 | 18:00
| HVDC EvPeak Flow |  | 640 | 19:00
| Load factor L.F |  | 76.29%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6701.24 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5179 | MW
Evening Peak Generation : |  | 8445 | MW Hour : | 19:00 | Available Max Generation : |  | 13784 | MW
E.P. Demand (at gen end) : |  | 8445 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8600 | MW
Maximum Generation : |  | 8445 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5184 | MW
Total Gen. (MKWH) : |  | 154.6151 | System Load Factor : | 76.29% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -335 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-18
Actual : | 97.47 | Ft.(MSL) , | Rule curve : | 104.4 | Ft.( MSL )
Gas Consumed : | Total = | 1056.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120778952.398
: |  | Coal : | 21753074 | Oil : | 118220907.89 | Total : | 260752934.288
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3054.128 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1032.0924 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 923.5659 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 834.1097 |  |  | 0 | 0%
) | 0 | 0:00 | 753.9989 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 608.4341 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 348.5454 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 156.8761 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 469.2147 |  |  | 0 | 0%
Total | 0 |  | 8180.9653 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Summit Meghna 305 MW | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-1,4,5,7 | 12) Baghabari 100 MW
|  |  |  | 4) Chandpur CCPP | 13) Ashuganj North ST
|  |  |  | 5) Sylhet 150 MW | 14) Haripur 412 ST
|  |  |  | 6) Bhola-225 MW ST | 15) Sirajganj unit-2
7) Ashuganj Precision
8) Ashuganj 225 MW CCPP
9) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sirajganj unit-4 ST was synchronized at 11:45.
b) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 08:30 to 16:46 for A/M.
c) Tongi 230/132 kV T-2 transformer was under shut down from 08:02 to 14:08 for A/M.
d) AKSML-BSRM 230 kV CKT was under shut down from 08:52 to 15:16 for A/M.
e) Aminbazar-Agargaon 230 kV Ckt-2 was under shut down from 09:40 to 14:29 for A/M.
f) Dohazari-Sikalbaha 132 kV Ckt-2 was under shut down from 09:52 to 14:34 for A/M.
g) Haripur-Shyampur GIS 132 kV Ckt was under shut down from 09:45 to 17:31 for A/M.
h) Madanganj-Sitalakkhya 132 kV Ckt was under shut down from 09:45 to 15:30 for A/M.
i) Mymensingh 132/33 kV T-1 transformer was under shut down from 09:06 to 16:59 for A/M.
j) Bogura-Sherpur 132 kV Ckt-1 was shut down at 08:02 for A/M.
k) Bogura-Sherpur 132 kV Ckt-2 was shut down at 08:04 for A/M.
l) Daudkandi-Sonargaon 132 kV Ckt-2 was under shut down from 08:10 to 16:18 for A/M.
m) Fenchuganj-Bibiyana 132 kV Ckt-2 was under shut down from 09:04 to 17:06 for A/M.
n) Amnura 132/33 kV T-1 transformer was shut down at 08:13 for A/M.
o) Ashuganj unit-4 was shut down at 11:16 for condenser tube leakage.
p) B.Baria 132/33 kV T-2 transformer was under shut down from 11:11 to 14:05 for A/M.
q) Bogura-CPL(1) 132 kV Ckt was under shut down from 11:17 to 13:45 for A/M.
r) Tangail 132/33 kV T-4 transformer was switched on at 14:12.
s) Bogura 230/132 kV T-3 transformer was under shut down from 15:15 to 17:12 for SCADA test.
t) B.Baria 132/33 kV T-3 transformer was under shut down from 14:12 to 16:48 for SCADA test.
u) Sikalbaha 150 MW synchronized at 15:14.
v) Chandpur 150 MW shut down at 15:55.
w) Ashuganj unit-5 synchronized at 15:36.
x) Haripur EGCB 412 MW GT synchronized at 18:01 .
y) Sirajganj unit-2 was shut down at 22:04 due to gas Shortage.
z) Raozan unit-2 was synchronized at 23:56 and tripped at 00:44(17/12/2019) due to protection relay problem
and again synchronized at 01:27(17/12/2019).
aa) Bhola 225 MW GT-1 tripped at 00:20(17/12/2019).
ab) Ashuganj 450 MW (North) tripped at 02:28(17/12/2019) due to GBC problem.
ac) Ghorashal-Bhulta 230 kV Ckt-1 tripped from both ends at 02:28(17/12/2019) showing dist. B, C, Z2 at Ghorashal
end & dist. B, Y, Z1 at Bhulta end and was switched on at 03:20(17/12/2019).
ad) Haripur-Bhulta 230 kV Ckt-1 tripped from Bhulta end at 02:28(17/12/2019) showing dist. B, Y, 67 and was
switched on at 03:14(17/12/2019).
ae) Hasnabad-Aminbazar 230 kV Ckt-2 was shut down at 07:30(17/12/2019) for A/M.
af) Kaliakoir-Aminbazar 230 kV Ckt-2 was shut down at 07:51(17/12/2019) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 791000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 99 | 2532800 | Ghorasal transformer over load.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1849409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 17 | 2918400 | Machine problem
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 368 | 8005000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8644250 | Gas shortage.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 855360
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 34800 | Machine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 36 | 123787 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 319392
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 1510000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 40 | 189120 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 344 | 7259640
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 926064 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 472656
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 842040
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 65 | 278400 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 598609
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 15 | 43932 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 129600 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1293900 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 745800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 753200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 52 | 307944
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 85309 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2219 | 41510412
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122175
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 136320
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 83 | 1952880 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4820854 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 1076525
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 513527 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 62428 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 22200 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 752640
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 324576
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 430080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25560
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 172 | 1884327 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 937 | 15024092
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2679106
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 910340 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 60 | 550990 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7162100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 7272000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 644472 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1856727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 813764 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1363360 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 52 | 165120 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 294624
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 143100
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 1928640
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 372500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 373020 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 126540 | Low demand
| Cumilla Area Total |  |  |  | 2920 | 1178 | 26656403
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3817760 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 313848
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 94 | 1074240
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 7 | 470400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 520800
| Mymensingh Area Total |  |  |  | 637 | 381 | 6204148
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1350000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 89 | 1734360
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3243313
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 835800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 841320
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 108144
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 923520
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1407360
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 322000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 35 | 706740 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 341016
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 363 | 8514000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 181980
| Sylhet Area Total |  |  |  | 1949 | 1012 | 20509553
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 640 | 7678545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 344640 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 84736 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 170 | 5793408 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 155625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 257616 | Low demand
| Khulna Area Total |  |  |  | 2314 | 920 | 14314570
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 391968 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 12 | 0 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 115 | 2755000 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Cable fault
| Barisal Area Total |  |  |  | 462 | 191 | 3146968
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1200000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 155180
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 192 | 4833573 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 173 | 4095082 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 195 | 4867164 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 5110600 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 361920
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 246564
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232074
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 108 | 428928
| Rajshahi Area Total |  |  |  | 2183 | 1234 | 21531085
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 5318600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 382080
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 17183
| Rangpur Area Total |  |  |  | 605 | 373 | 5717863
| Total |  |  |  | 19047 | 8445 | 154615094
| Eastern Grid Total |  |  |  | 13483 | 5727 | 109904608
| Western Grid Total |  |  |  | 5564 | 2718 | 44710486
| National Grid Total |  |  |  | 19047 | 8445 | 154615094
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-17
(a) ENTIRE EASTERN GRID : |  | 5475 | MW | (b) ENTIRE WESTERN GRID : |  | 2547 | MW
i) Dhaka area |  | 3024 | MW | i) Khulna area |  | 991 | MW
ii) Chittagong area |  | 783 | MW | ii) Rajshahi area |  | 828 | MW
iii) Comilla area |  | 721 | MW | iii) Barisal area |  | 221 | MW
iv) Mymensingh area |  | 629 | MW | iv) Rangpur area |  | 507 | MW
v) Sylhet area |  | 318 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8022 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 16:00 | Shahjibazar | 76 | 19:00 | Bottail | 100 | 18:00
Munsiganj | 87 | 19:30 | Fenchuganj | 24 | 18:00 | G.K Project | 25 | 18:00
Sonargaon | 72 | 20:00 | Kulawara | 28 | 18:30 | Faridpur | 126 | 19:30
Shyampur | 168 | 10:00 | Sylhet | 92 | 18:00 | Madaripur | 57 | 20:00
Bhulta | 149 | 18:30 | Chatak | 17 | 19:00 | Sariatpur | 38 | 19:30
Madanganj | 42 | 1:00 | Sunamganj | 27 | 18:00 | Gopalganj | 64 | 18:30
Shitalakhya | 91 | 11:00 | Biani Bazar | 34 | 18:00 | Bagerhat | 63 | 18:00
Rahim steel | 20 | 19:00 | Comilla (S) | 102 | 18:00 | Mongla | 36 | 0.625
Matuail | 78 | 13:00 | Comilla(N) | 83 | 18:30 | Satkhira | 66 | 20:00
Ghorasal | 73 | 19:30 | Chandpur | 61 | 18:00 | Gallamari | 36 | 13:00
Narsingdi | 100 | 20:00 | Feni | 92 | 18:30 | Magura | 36 | 18:30
Haripur (SBU) | 95 | 12:00 | Chowmuhani | 110 | 18:30 | Norail | 25 | 19:00
Ullon | 44 | 18:00 | Ashuganj | 33 | 18:00 | Chuadanga | 57 | 18:00
Hasnabad | 138 | 19:30 | Daudkandi | 90 | 19:00 | Barisal(N) | 28 | 20:00
Magbazar | 75 | 18:00 | B.Baria | 88 | 19:30 | Barisal (S) | 70 | 19:00
Maniknagar | 72 | 17:00 | Ramganj | 56 | 18:00 | Patuakhali | 68 | 20:00
Bangabhaban | 16 | 16:00 | Chaddagram | 16 | 18:30 | Bhandaria | 37 | 19:30
Narinda | 72 | 15:00 | PHP | 1 | 13:00 | Borhan Uddin | 30 | 19:30
Dhanmondi | 87 | 13:00 | Madunaghat | 42 | 18:00 | Ishurdi | 43 | 18:00
Lalbag | 59 | 19:00 | Hathazari | 68 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 44 | 18:30 | Khulshi | 127 | 13:00 | Natore | 86 | 18:30
Mirpur | 64 | 12:00 | Halishahar | 95 | 10:00 | Bogra | 142 | 18:30
Kalyanpur | 63 | 13:00 | Baraulia | 140 | 13:00 | Noagaon | 80 | 19:30
Gulshan | 98 | 13:00 | Sikalbaha | 17 | 18:30 | Rajshahi | 90 | 18:30
Uttara | 38 | 13:00 | Dohazari | 64 | 18:00 | Rajshahi New | 8 | 18:30
Uttara New | 26 | 18:00 | Cox'sbazar | 71 | 19:00 | C.Nawabganj | 51 | 19:00
Kamrangirchar | 75 | 13:00 | Chandraghona | 22 | 18:00 | Amnura | 23 | 18:30
Savar | 97 | 18:30 | Kaptai | 3.8 | 18:00 | Pabna | 73 | 18:30
Bhasantec | 110 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 75 | 18:30
Agargaon | 33 | 13:00 | Bakulia | 72 | 18:30 | Serajganj | 65 | 19:00
Satmosjid | 60 | 18:00 | Julda | 17 | 9:00 | Niyamatpur | 43 | 18:30
Tongi | 118 | 14:00 | TK chemical | 10.5 | 23:00 | Joypurhat | 46 | 19:00
Kabirpur | 127 | 10:00 | Modern Steel | 12 | 15:00 | Sherpur(Bogura) | 34 | 18:30
Basundhara | 63 | 18:00 | Shahmirpur | 23 | 12:00 | Mohastangor | 6 | 18:00
Manikganj | 58 | 19:00 | Khagrachhari | 16 | 18:00 | Rangpur | 104 | 18:30
Joydevpur | 157 | 21:00 | Matarbari | 20.5 | 20:00 | Lalmonirhat | 38 | 18:00
New Tongi | 73 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 87 | 18:30
Korda | 199 | 21:00 | Rangamati | 8 | 18:00 | Purbasadipur | 60 | 19:00
Dhamrai | 48 | 18:00 | Abul Khair 230 | 143 | 23:00 | Thakurgaon | 35 | 19:30
Valuka | 72 | 18:30 | BSRM | 59 | 24:00 | Palashbari | 83 | 18:00
Tangail | 126 | 18:00 | GPH Ispat | 14 | 11:00 | Barapukuria | 43 | 19:00
Mymensing | 152 | 18:30 | Goalpara | 18 | 18:30 | Panchagar | 23 | 19:00
Kishorganj | 78 | 20:00 | Central s/s | 60 | 18:30 | Joldhaka | 19 | 19:00
Netrokona | 70 | 18:00 | Noapara | 49 | 18:30 | Kurigram | 40 | 18:00
Jamalpur | 84 | 19:30 | Jessore | 74 | 18:30
Sherpur | 70 | 19:00 | Benapol | 34 | 18:30
Srimongal | 25 | 19:30 | Jhenida | 74 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-17 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 391 | 0.083333 | 382 | 0.66667 | Kaliakoir | 381 | 0.125 | 369 | 0.5
Bheramara | 408 | 0.083333 | 390 | 0.75 | Bhulta | 391 | 0.16667 | 379 | 0.66667
Ashuganj(N) | 395 | 0.16667 | 383 | 0.66667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 0.041667 | 224 | 0.375 | Hathazari | 224 | 0.25 | 220 | 0.375
Ishurdi | 244 | 0.16667 | 227 | 0.75 | Megnaghat | 232 | 0.041667 | 225 | 0.41667
Ashuganj | 240 | 0.33333 | 232 | 0.66667 | Fenchuganj | 237 | 0.41667 | 234 | 0.083333
Serajganj | 235 | 0.083333 | 230 | 0.33333 | Siddhirganj | 231 | 0.16667 | 224 | 0.66667
Baghabari | 245 | 0.16667 | 240 | 0.77083 | Maniknagar | 230 | 0.083333 | 222 | 0.66667
Barapukuria | 232 | 0.125 | 227 | 0.875 | Old Airport | 230 | 0.16667 | 221 | 0.66667
Bogra | 233 | 0.20833 | 227 | 0.375 | Barisal | 234 | 0.16667 | 224 | 0.54167
Khulna South | 238 | 0.20833 | 214 | 0.75 | AKSML | 222 | 0.25 | 214 | 0.5
Rampura | 230 | 0.16667 | 224 | 0.66667 | BSRM | 226 | 0.16667 | 212 | 0.5
Haripur | 230 | 0.041667 | 223 | 0.625 | Bibiyana | 234 | 0.083333 | 227 | 0.45833
Hasnabad | 230 | 0.041667 | 222 | 0.5 | Bhulta | 236 | 0.16667 | 223 | 0.29167
Aminbazar | 230 | 0.125 | 223 | 0.5 | Ashuganj (S) | 236 | 0.16667 | 230 | 0.66667
Tongi | 227 | 0.16667 | 216 | 0.625 | Kaliakoir | 233 | 0.16667 | 220 | 0.33333
Comilla (N) | 235 | 0.041667 | 228 | 0.66667 | GPH | 223 | 0.79167 | 218 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 139 | 0.041667 | 133 | 0.66667 | Halishahar | 134 | 0.77083 | 131 | 0.33333
Munsiganj | 140 | 0.83333 | 135 | 0.33333 | Baraulia | 132 | 0.75 | 128 | 0.41667
Sonargaon | 136 | 0.875 | 135 | 0.041667 | Sikalbaha | 133 | 0.77083 | 130 | 0.33333
Shyampur | 137 | 0.20833 | 131 | 0.625 | Dohazari | 131 | 0.125 | 128 | 0.5
Bhulta | 133 | 0.16667 | 129 | 0.5 | Cox'sbazar | 128 | 0.125 | 124 | 0.5
Madanganj | 136 | 0.79167 | 130 | 0.66667 | Chandraghona | 133 | 0.041667 | 131 | 0.375
Shitalakhya | 139 | 0.83333 | 130 | 0.41667 | Kaptai | 132 | 0.041667 | 132 | 0.041667
Rahim steal | 139 | 19:30 | 135 | 0.375 | A. Khaer Stl. | 131 | 0.41667 | 129 | 0.33333
Matuail | 139 | 0.125 | 133 | 0.54167 | Bakulia | 132 | 0.77083 | 129 | 0.375
Ghorasal | 138 | 0.041667 | 135 | 0.45833 | Julda | 133 | 0.83333 | 129 | 0.33333
Narsinghdi | 131 | 0.375 | 126 | 0.77083 | TK Chemical | 133 | 0.20833 | 130 | 0.375
Haripur (SBU) | 139 | 0.083333 | 135 | 0.375 | Modern Steel | 132 | 0.79167 | 129 | 0.375
Ullon | 135 | 0.25 | 130 | 0.5 | Shahmirpur | 132 | 0.77083 | 128 | 0.29167
Hasnabad | 135 | 0.20833 | 128 | 0.70833 | Khagrachhari | 133 | 0.125 | 130 | 0.375
Magbazar | 135 | 0.29167 | 130 | 0.70833 | Matarbari | 130 | 0.625 | 126 | 0.45833
Maniknagar | 138 | 0.25 | 133 | 0.66667 | Baroiar Hat | 133 | 0.041667 | 131 | 0.375
Bangabhaban | 138 | 0.25 | 133 | 0.66667 | Rangamati | 133 | 0.20833 | 130 | 0.33333
Narinda | 138 | 0.25 | 133 | 0.66667 | Goalpara | 138 | 0.16667 | 124 | 18:00
Dhanmondi | 135 | 0.25 | 130 | 0.5 | Central s/s | 138 | 0.20833 | 128 | 8:00
Lalbag | 136 | 0.25 | 128 | 0.5 | Noapara | 136 | 0.125 | 122 | 0.75
Madartek | 135 | 0.25 | 129 | 0.66667 | Jessore | 133 | 0.20833 | 121 | 0.75
Mirpur | 137 | 0.083333 | 130 | 0.5 | Benapol | 135 | 0.16667 | 122 | 0.75
Kalyanpur | 136 | 0.083333 | 131 | 0.5 | Jhenida | 133 | 0.25 | 121 | 0.77083
Gulshan | 134 | 0.083333 | 129 | 0.5 | Bottail | 138 | 0.20833 | 125 | 0.75
Uttara | 134 | 0.20833 | 126 | 0.66667 | G. K. Project | 141 | 0.25 | 132 | 0.75
Uttara New | 133 | 0.083333 | 126 | 0.5 | Faridpur | 135 | 0.20833 | 125 | 0.75
Kamrangirchar | 134 | 0.083333 | 126 | 0.625 | Madaripur | 133 | 0.95833 | 125 | 0.66667
Savar | 133 | 0.083333 | 127 | 0.5 | Sariatpur | 135 | 0.16667 | 127 | 0.375
Bhasantec | 137 | 0.083333 | 130 | 0.5 | Gopalganj | 139 | 0.8125 | 129 | 0.5
Agargaon | 136 | 0.083333 | 131 | 0.5 | Bagerhat | 135 | 0.25 | 120 | 0.75
Satmosjid | 136 | 0.083333 | 131 | 0.66667 | Mongla | 132 | 0.125 | 118 | 0.75
Tongi | 140 | 0.16667 | 131 | 0.45833 | Satkhira | 138 | 0.16667 | 125 | 0.75
Kabirpur | 136 | 0.083333 | 130 | 0.5 | Gallamari | 138 | 0.16667 | 125 | 0.75
Basundhara | 137 | 24:00 | 128 | 0.5 | Magura | 135 | 0.16667 | 120 | 0.75
Manikganj | 141 | 4:00 | 132 | 0.45833 | Norail | 134 | 0.20833 | 115 | 0.75
Joydevpur | 142 | 0.83333 | 132 | 0.54167 | Chuadanga | 132 | 0.25 | 115 | 0.75
New Tongi | 138 | 0.041667 | 129 | 0.5 | Barisal(N) | 136 | 0.20833 | 130 | 0.5
Kodda | 140 | 0.79167 | 130 | 0.5 | Barisal (S) | 135 | 0.25 | 129 | 0.5
Dhamrai | 135 | 0.083333 | 130 | 0.79167 | Patuakhali | 133 | 0.25 | 126 | 0.54167
Valuka | 133 | 0.375 | 127 | 0.75 | Bhandaria | 135 | 0.25 | 124 | 0.75
Tangail | 135 | 0.041667 | 130 | 0.75 | Ishurdi | 139 | 0.16667 | 130 | 0.75
Mymensing | 136 | 0.375 | 129 | 0.75 | Ruppur Paromanobik | 138 | 0.16667 | 131 | 0.75
Kishorganj | 134 | 0.41667 | 129 | 0.75 | Natore | 136 | 0.20833 | 129 | 0.5
Netrokona | 134 | 0.375 | 128 | 0.75 | Bogra | 137 | 0.16667 | 132 | 0.33333
Jamalpur | 140 | 0.375 | 127 | 0.29167 | Noagaon | 135 | 0.20833 | 128 | 0.5
Sherpur | 139 | 0.375 | 125 | 0.33333 | Rajshahi | 133 | 0.083333 | 124 | 0.58333
Srimongal | 138 | 0.16667 | 135 | 0.66667 | Rajshahi New | 135 | 0.16667 | 124 | 0.33333
Shahjibazar | 135 | 0.33333 | 131 | 0.77083 | C.Nawabganj | 133 | 0.20833 | 122 | 0.5
Fenchuganj | 137 | 0.41667 | 134 | 0.041667 | Amnura | 130 | 0.16667 | 122 | 0.45833
Khulawara | 137 | 0.20833 | 133 | 18:00 | Pabna | 139 | 0.083333 | 131 | 0.75
Sylhet | 136 | 0.29167 | 133 | 0.041667 | Shahjadpur | 144 | 0.125 | 137 | 0.54167
Chatak | 135 | 0.33333 | 132 | 0.041667 | Serajganj | 138 | 0.083333 | 131 | 0.77083
Sunamganj | 136 | 0.375 | 131 | 0.041667 | Niyamatpur | 134 | 0.125 | 125 | 0.33333
Biani Bazar | 136 | 0.25 | 132 | 0.75 | Joypurhat | 136 | 0.125 | 129 | 0.66667
Comilla(s) | 132 | 0.16667 | 127 | 0.75 | Sherpur(Bogura) | 138 | 0.125 | 131 | 0.75
Comilla(n) | 140 | 0.33333 | 135 | 0.66667 | Mohastangor | 136 | 0.125 | 130 | 0.375
Chandpur | 137 | 18:30 | 135 | 0.33333 | Rangpur | 130 | 0.79167 | 124 | 0.54167
Feni | 133 | 0.79167 | 128 | 0.875 | Lalmonirhat | 126 | 0.83333 | 120 | 0.375
Chowmuhani | 131 | 0.29167 | 126 | 0.66667 | Saidpur | 130 | 0.125 | 123 | 0.45833
Ashuganj | 136 | 0.20833 | 133 | 0.75 | Purbasadipur | 130 | 0.20833 | 119 | 0.66667
Daudkandi | 137 | 0.33333 | 132 | 0.625 | Thakurgaon | 125 | 0.20833 | 116 | 0.5
B.Baria | 133 | 0.375 | 129 | 0.79167 | Palashbari | 134 | 0.125 | 125 | 0.45833
Ramganj | 132 | 0.29167 | 126 | 0.66667 | Barapukuria | 132 | 0.125 | 128 | 0.45833
Chaddagram | 136 | 0.95833 | 133 | 0.375 | Panchagar | 124 | 0.16667 | 114 | 0.66667
PHP | 133 | 0.8125 | 128 | 0.875 | Joldhaka | 130 | 0.20833 | 122 | 0.375
Madanhat | 135 | 0.58333 | 132 | 0.375 | Kurigram | 129 | 0.79167 | 124 | 0.33333
Hathazari | 133 | 0.041667 | 131 | 0.375
Khulshi | 131 | 0.77083 | 128 | 0.29167

## L-Curve
Date | 2019-12-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 272 | 4912 | 1564 | 6476 |  |  |  | QF-LDC-12
0:30 | 261 | 4392 | 1479 | 5871 | Date: | 2019-12-17
1:00 | 250 | 3872 | 1394 | 5266
1:30 | 241 | 3770.5 | 1386.5 | 5157
2:00 | 232 | 3669 | 1379 | 5048
2:30 | 209.5 | 3603 | 1364.5 | 4967.5 | [5 empty] | Gen. at Eve. Peak | 8445 | 8095 MW (19:00 )
3:00 | 187 | 3537 | 1350 | 4887 | [6 empty] | 19:00
3:30 | 172 | 3496 | 1325 | 4821 | [5 empty] | Gen. at Day Peak | 6701.24 | 6206.6 MW (12:00 )
4:00 | 157 | 3455 | 1300 | 4755 | [6 empty] | 12:00
4:30 | 131.5 | 3399 | 1314 | 4713 | [5 empty] | Highest Generation | 8445
5:00 | 106 | 3343 | 1328 | 4671 | [6 empty] | 19:00
5:30 | 113 | 3495 | 1347 | 4842
6:00 | 120 | 3647 | 1366 | 5013
6:30 | 158 | 3783.8 | 1418.05 | 5201.85
7:00 | 196 | 3920.6 | 1470.1 | 5390.7
7:30 | 265.5 | 4122.6 | 1490.15 | 5612.75
8:00 | 335 | 4324.6 | 1510.2 | 5834.8
8:30 | 265 | 4479.7 | 1603.35 | 6083.05
9:00 | 195 | 4634.8 | 1696.5 | 6331.3
9:30 | 152 | 4656.55 | 1723.15 | 6379.7
10:00 | 109 | 4678.3 | 1749.8 | 6428.1
10:30 | 70 | 4667.625 | 1746.2 | 6413.825
11:00 | 31 | 4656.95 | 1742.6 | 6399.55
11:30 | 25.5 | 4752.295 | 1798.1 | 6550.395
12:00 | 20 | 4847.64 | 1853.6 | 6701.24
12:30 | 35 | 4810.77 | 1981.1 | 6791.87
13:00 | 50 | 4773.9 | 2108.6 | 6882.5
13:30 | 130 | 4636.15 | 2042.2 | 6678.35
14:00 | 210 | 4498.4 | 1975.8 | 6474.2
14:30 | 242.5 | 4462.95 | 1957.4 | 6420.35
15:00 | 275 | 4427.5 | 1939 | 6366.5
15:30 | 277.5 | 4505.1 | 1957.5 | 6462.6
16:00 | 280 | 4582.7 | 1976 | 6558.7
16:30 | 235 | 4635.45 | 2035.05 | 6670.5
17:00 | 190 | 4688.2 | 2094.1 | 6782.3
17:30 | 108.5 | 5130.6 | 2396.55 | 7527.15
18:00 | 27 | 5573 | 2699 | 8272
18:30 | 43.5 | 5650 | 2708.5 | 8358.5
19:00 | 60 | 5727 | 2718 | 8445
19:30 | 0 | 5718 | 2639 | 8357
20:00 | 20 | 5673 | 2603 | 8276 |  |  |  | Executive Engineer
20:30 | 92 | 5588 | 2465 | 8053 |  |  |  | Network Operation Division
21:00 | 164 | 5503 | 2327 | 7830
21:30 | 217 | 5467.5 | 2196 | 7663.5
22:00 | 270 | 5432 | 2065 | 7497 |  |  |  |  | Page 6 of 7
22:30 | 295 | 5313.5 | 1867 | 7180.5
23:00 | 320 | 5195 | 1669 | 6864
23:30 | 296 | 5053.5 | 1616.5 | 6670
24:00 | 272 | 4912 | 1564 | 6476
8095 MW (19:00 )
6206.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-17 |  | Energy | 154615094
[10 empty] | 2019-12-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3910 | 202 | 1726 | 544 | 260 | 83 | 4 | 0 | 76
0:30 | 3929.5 | 169.5 | 1297 | 272 | 210 | 82.5 | 4 | 0 | 71 | Date: | 2019-12-17
1:00 | 3949 | 137 | 868 | 0 | 160 | 82 | 4 | 0 | 66
1:30 | 3853 | 137 | 856 | 0 | 160 | 82 | 4 | 0 | 65 | [7 empty] | Total Energy | 154.6151 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3757 | 137 | 844 | 0 | 160 | 82 | 4 | 0 | 64 | [7 empty] | Energy not Served | 0
2:30 | 3707 | 137 | 819.5 | 0 | 155 | 82 | 4 | 0 | 63 | [7 empty] | Energy Requirement | 154.6151
3:00 | 3657 | 137 | 795 | 0 | 150 | 82 | 4 | 0 | 62
3:30 | 3592.5 | 137 | 794.5 | 0 | 150 | 82 | 4 | 0 | 61 | [6 empty] | Shortage
4:00 | 3528 | 137 | 794 | 0 | 150 | 82 | 4 | 0 | 60
4:30 | 3484.5 | 137 | 798 | 0 | 149.5 | 82 | 4 | 0 | 58
5:00 | 3441 | 137 | 802 | 0 | 149 | 82 | 4 | 0 | 56
5:30 | 3505.5 | 137 | 906 | 0 | 149.5 | 82 | 4 | 0 | 58
6:00 | 3570 | 137 | 1010 | 0 | 150 | 82 | 4 | 0 | 60
6:30 | 3587 | 137 | 1180.5 | 0 | 150 | 81.5 | 4 | 0 | 61 |  |  |  |  | Coal
7:00 | 3604 | 137 | 1351 | 0 | 150 | 81 | 4 | 0 | 62
7:30 | 3690 | 142.5 | 1474 | 0 | 150 | 81 | 4 | 0 | 66 |  |  |  | Oil |  |  |  | ,
8:00 | 3776 | 148 | 1597 | 0 | 150 | 81 | 4 | 0 | 70
8:30 | 3839.5 | 223.5 | 1556.5 | 121.5 | 175 | 81.5 | 4 | 0 | 69
9:00 | 3903 | 299 | 1516 | 243 | 200 | 82 | 4 | 0 | 68
9:30 | 3786 | 299 | 1487.5 | 406.5 | 221 | 82 | 4 | 0 | 75
10:00 | 3669 | 299 | 1459 | 570 | 242 | 82 | 4 | 0 | 82
10:30 | 3642.5 | 299 | 1453 | 578 | 251 | 82 | 4 | 0 | 81
11:00 | 3616 | 299 | 1447 | 586 | 260 | 82 | 4 | 0 | 80
11:30 | 3647 | 299 | 1551 | 598 | 260 | 82 | 4 | 0 | 83
12:00 | 3678 | 299 | 1655 | 610 | 260 | 82 | 4 | 0 | 86
12:30 | 3667.5 | 298 | 1741 | 625 | 260 | 82.5 | 4 | 0 | 87
13:00 | 3657 | 297 | 1827 | 640 | 260 | 83 | 4 | 0 | 88
13:30 | 3657 | 297 | 1827 | 640 | 260 | 83 | 4 | 0 | 88
14:00 | 3657 | 297 | 1827 | 640 | 260 | 83 | 4 | 0 | 88
14:30 | 3484.5 | 296.5 | 1797.5 | 592 | 260 | 83.5 | 4 | 0 | 85
15:00 | 3312 | 296 | 1768 | 544 | 260 | 84 | 4 | 0 | 82
15:30 | 3450 | 296.5 | 1772.5 | 501 | 260 | 84 | 4 | 0 | 83
16:00 | 3588 | 297 | 1777 | 458 | 260 | 84 | 4 | 0 | 84
16:30 | 3557.5 | 369 | 1764 | 526.5 | 260 | 83.5 | 21.5 | 0 | 85
17:00 | 3527 | 441 | 1751 | 595 | 260 | 83 | 39 | 0 | 86
17:30 | 3708 | 540.5 | 1798 | 981 | 260 | 83 | 62.5 | 0 | 94
18:00 | 3889 | 640 | 1845 | 1367 | 260 | 83 | 86 | 0 | 102
18:30 | 3863.5 | 640 | 1827 | 1488.5 | 260 | 83 | 94.5 | 0 | 102
19:00 | 3838 | 640 | 1809 | 1610 | 260 | 83 | 103 | 0 | 102
19:30 | 3782 | 640 | 1770 | 1651 | 260 | 83 | 69 | 0 | 102
20:00 | 3725 | 640 | 1770 | 1630 | 260 | 82 | 69 | 0 | 100
20:30 | 3817 | 640 | 1772 | 1321 | 260 | 82 | 62 | 0 | 99
21:00 | 3909 | 640 | 1774 | 1012 | 260 | 82 | 55 | 0 | 98
21:30 | 3942 | 591 | 1756.5 | 888 | 260 | 82.5 | 49.5 | 0 | 94
22:00 | 3975 | 542 | 1739 | 764 | 260 | 83 | 44 | 0 | 90
22:30 | 3907.5 | 420.5 | 1743.5 | 654 | 260 | 83 | 24 | 0 | 88
23:00 | 3840 | 299 | 1748 | 544 | 260 | 83 | 4 | 0 | 86
23:30 | 3875 | 250.5 | 1737 | 544 | 260 | 83 | 4 | 0 | 81 | Max Temp. in Dhaka |  | 25.7° C
24:00 | 3910 | 202 | 1726 | 544 | 260 | 83 | 4 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-12-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 42 | 42 | 42 | 42 | 43 | 43 | 44 | 44 | 43 | 43 |  | 43 | 43 | 42 | 42 | 43 | 43 | 43 | 980880
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2 | [24 empty] | 0 | 10
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.4 | 7.1 | 12.8 | 16.3 | 18.4 | 18.7 | 17.6 | 14.8 | 10.7 | 4.6 | 0.2 | [9 empty] | 122175
6 | Sikalbaha 225MW CCPP (Gas) | 213 | 205 | 178 | 176 | 191 | 220 | 215 | 228 | 211 | 216 | 181 | 216 | 207 | 194 | 205 | 219 | 205 | 217 |  | 204 | 204 | 203 | 210 | 204 | 209 | 203 | 4820854
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | [15 empty] | 141 | 135 | 134 |  | 134 | 134 | 134 | 134 | 135 | 137 | 135 | 1076525
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 0 | 34 |  | 34 | 0 | 0 |  |  |  |  | 62428
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 11 | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 513527
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 60 | 34 | 37 | 32 | 37 | 37 | 97 | 100 | 65 | 35 | 63 | 91 | 63 | 37 | 40 | 90 | 90 | 97 |  | 97 | 40 | 41 | 41 | 41 | 40 | 40 | 1510000
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 230 | 230 | 230 | 230 | 270 | 300 | 335 | 335 | 347 | 345 | 350 | 240 | 240 | 240 | 260 | 344 |  | 344 | 342 | 346 | 340 | 350 | 349 | 349 | 7259640
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 2 | 30 |  | 30 | 30 | 0 | 0 |  |  |  | 85309
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 80 | 180 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 73 | 73 | 73 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1856727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 791000
21 | Ghorasal Repowered CCPP Unit-3 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 98 | 99 | 99 | 2532800
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 105 | 80 | 80 | 80 | 80 | 80 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 100 | 100 | 110 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2679106
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | [14 empty] | 910340
30 | Ashuganj TPP Unit- 5 | [15 empty] | 23 | 60 | 60 |  | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 550990
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 20 | 27 | 27 | 30 | 33 | 33 | 33 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 644472
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 335 | 270 | 290 | 275 | 310 | 310 | 345 | 340 | 365 | 315 | 285 | 285 | 270 | 285 | 285 | 320 | 270 | 310 |  | 285 | 305 | 275 | 305 | 285 | 275 | 305 | 7272000
| Ashuganj 450 MW CCPP(North) | 275 | 250 | 260 | 255 | 255 | 255 | 240 | 250 | 245 | 220 | 280 | 295 | 277 | 290 | 230 | 240 | 260 | 355 |  | 345 | 360 | 340 | 360 | 360 | 350 | 340 | 7162100
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 82 | 87 | 87 | 84 | 90 | 90 | 90 | 90 | 90 | 86 | 91 | 86 | 88 | 86 | 84 | 0 | 0 | [9 empty] | 1363360
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 315 | 315 | 315 | 290 | 256 | 246 | 0 | [10 empty] | 0 |  | 17 | 17 | 18 | 165 | 290 | 304 | 304 | 2918400
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 380 | 350 | 350 | 300 | 400 | 380 | 400 | 435 | 420 | 370 | 400 | 400 | 320 | 320 | 380 | 380 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 8644250
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 280 | 280 | 220 | 320 | 340 | 370 | 370 | 332 | 285 | 365 | 368 | 314 | 367 | 364 | 367 | 365 |  | 368 | 369 | 368 | 367 | 353 | 358 | 360 | 8005000
42 | RPCL 210MW CCPP | 215 | 201 | 166 | 167 | 151 | 215 | 215 | 217 | 186 | 170 | 149 | 142 | 142 | 125 | 128 | 140 | 145 | 145 |  | 145 | 146 | 147 | 146 | 146 | 145 | 161 | 3817760
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 20 | 20 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 |  | 60 | 60 | 60 | 59 | 58 | 60 | 60 | 1350000
45 | Fenchugonj CCPP Phase-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 62 | 63 | 52 | 55 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1734360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 20 | 20 | 20 | 20 | 20 | 20 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 37 | 67 |  | 67 | 67 | 68 | 67 | 67 | 69 | 69 | 923520
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 76 | 76 | 76 | 76 | 76 | 73 | 76 | 76 | 76 | 76 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1407360
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 322000
52 | Sylhet 50MW PP (EPL) | 7 | 7 | 7 | 8 | 8 | 8 | 30 | 29 | 29 | 30 | 31 | 34 | 33 | 35 | 36 | 35 | 38 | 38 |  | 35 | 35 | 37 | 40 | 40 | 40 | 40 | 706740
53 | Sylhet 10MW PP (Desh) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 181980
54 | Hobiganj 11MW PP Cofidence-E | [6 empty] | 2 |  |  | 1 |  | 7 | 8 | 5 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 108144
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 34 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 835800
56 | Shahjahanulla 25 MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 23 | 23 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 341016
57 | Bibiana-II 341 MW CCPP (Summit)
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 13 | 17 |  | 15 | [6 empty] | 43932
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [6 empty] | 18 | 18 | 18 | 18 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 324576
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 319392
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 313848
63 | Impoprt (Tripura) | 66 | 64 | 62 | 60 | 56 | 60 | 62 | 70 | 68 | 82 | 80 | 86 | 88 | 90 | 82 | 84 | 86 | 102 |  | 102 | 102 | 100 | 98 | 90 | 86 | 76 | 1928640
64 | Malancha, Ctg. EPZ (United) | 8 | 5 | 6 | 5 | 5 | 15 | 13 | 7 | 2 | 4 | 7 | 7 | 10 | 8 | 2 | 5 | 8 | 8 |  | 15 | 18 | 23 | 32 | 36 | 38 | 42 | 430080
65 | Feni 22MW PP (Doreen) | [9 empty] | 10 | 19 | 22 | 22 | 22 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 294624
66 | Feni 11 MW PP (Doreen) | [9 empty] | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 143100
67 | Jangalia 33MW PP (Summit) | [8 empty] | 33 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 372500
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 373020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 21 | 31 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 693900
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 745800
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 753200
73 | Ghorashal 108MW PP (Regent) | 7 | 7 | 7 | 7 | 7 | 7 | 52 | 98 | 104 | 104 | 104 | 104 | 107 | 107 | 104 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 1849409
| Feni Lanka Power | [17 empty] | 27 |  | 50 | 50 | 40 |  |  |  |  | 126540
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 2 |  | 40 | 60 | 90 |  |  |  |  | 189120
78 | Gazipur 52 MW PP | [16 empty] | 8 | 52 |  | 52 | 52 | 52 | 52 | 52 | 25 | 0 | 307944
79 | Kodda 150MW PP | [16 empty] | 35 | 48 |  | 65 | 65 | 65 | 51 | 40 | 0 |  | 278400
80 | Jamalpur 95 MW PP(Powerpac) | [8 empty] | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 63 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 27 | 1074240
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [6 empty] | 0.2 | 1.3 | 2.5 | 3.5 | 4.05 | 4.14 | 3.8 | 3 | 2 | 0.8 | 0 | [9 empty] | 25560
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [21 empty] | 0 |  | 18 | 0 |  | 34800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 1 | 15 | 44 | 45 | 45 | 47 |  |  | 15 | 78 |  | 100 | 100 | 100 | 100 | 100 | 65 | 14 | 855360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 10 | 10 |  | 0 | 0 | [5 empty] | 22200
92 | Fenchuganj 44MW (Energyprima) | [6 empty] | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 44 | 44 | 44 | 44 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 841320
93 | Ashuganj 51 MW PP (Midland) | 7 | 7 | 7 | 7 | 7 | 7 | 14 | 43 | 43 | 43 | 43 | 43 | 45 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 813764
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 16 | 64 | 64 | 64 | 64 | 16 | 16 | 50 | 80 |  | 94 | 94 | 94 | 94 | 94 | 50 | 0 | 926064
95 | Patenga 50MW PP (Baraka) | [8 empty] | 4 | 34 | 41 | 47 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 30 | 0 |  | 136320
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | Katpotti 52 MW PP (Sinha) | [10 empty] | 25 | 40 | 47 | 47 | 47 | 42 | 46 | 47 |  | 47 | 47 | 47 |  |  |  |  | 472656
98 | Bosila 108MW PP(CLC) | [8 empty] | 18 | 72 | 24 | 0 | [5 empty] | 8 | [8 empty] | 129600
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 0 | 15 |  | 36 | 55 | 55 | 0 |  |  |  | 123787
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 |  |  |  |  | 598609
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 100 | 100 | 100 | 163 | 130 | 100 | 130 | 163 | 163 | 130 |  | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 3243313
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.2 | 0.5 | 0.5 | 1.5 | 1.8 | 1.5 | 0.6 | 0.8 | 0.3 | 0 | [9 empty] | 7100
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 842040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 50 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 16 |  |  | 7 | 7 | 7 |  |  |  |  | 470400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 46 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 60 |  | 90 | 100 | 100 | 100 | 0 |  |  | 752640
116 | Chandpur 200MW (Desh energy) | [16 empty] | 0 | 50 |  | 52 | 52 | 50 | 0 |  |  |  | 165120
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 380 | 372 | 370 | 348 | 379 | 371 | 372 | 368 | 395 | 350 | 325 | 321 | 294 | 303 | 303 | 334 | 290 | 397 |  | 363 | 379 | 362 | 381 | 375 | 366 | 343 | 8514000
| Jamalpur 115 MW PP (United) | [16 empty] | 11 | 70 |  | 115 | 115 | 115 | 70 | 40 | 0 |  | 520800
| Anwara 300 MW PP (United) | [8 empty] | 32 | 66 | 50 | 50 | 70 | 124 | 133 | 82 | 86 | 159 |  | 172 | 179 | 195 | 205 | 209 | 209 | 105 | 1884327
120 | Eastern Zone Total | 3872 | 3669 | 3537 | 3455 | 3343 | 3647 | 3920.6 | 4324.6 | 4634.8 | 4678.3 | 4656.95 | 4847.64 | 4773.9 | 4498.4 | 4427.5 | 4582.7 | 4688.2 | 5573 |  | 5727 | 5718 | 5673 | 5503 | 5432 | 5195 | 4912 | 109904608
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [8 empty] | 6 | 49 | 40 | 66 | 66 | 66 | 0 |  | 6 | 16 |  | 16 | 16 | 16 | 0 |  |  |  | 344640
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [15 empty] | 0 | 24 | 61 |  | 64 | 64 | 64 | 64 | 48 | 48 | 16 | 391968
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 116 | 115 | 115 |  | 115 | 115 | 115 | 115 | 116 | 115 | 115 | 2755000
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 19 | 18 | 19 | 18 | 18 | 17 | 14 | 11 | 11 | 10 | 10 | 11 | 11 | 11 | 11 |  | 12 | 12 | 12 | 12 | 12 | 11 | 0
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 40 |  | 40 | 40 | 40 | 16 | 0 |  |  | 155625
143 | Gopalganj 100 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 84736
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 15 | 42 |  | 50 | 50 | 50 | 50 | 26 | 0 |  | 257616
146 | Bheramara HVDC | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 148 | 299 | 299 | 299 | 299 | 297 | 296 | 296 | 297 | 441 | 640 |  | 640 | 640 | 640 | 640 | 542 | 299 | 202 | 7678545
147 | Bheramara 360 MW CCPP | 305 | 310 | 310 | 260 | 200 | 240 | 240 | 270 | 305 | 290 | 300 | 300 | 300 | 200 | 250 | 245 | 215 | 190 |  | 170 | 155 | 150 | 135 | 130 | 130 | 147 | 5793408
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 150 | 150 | 149 | 150 | 150 | 150 | 200 | 242 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5318600
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 196 | 200 | 183 | 185 | 193 | 190 | 205 | 225 | 224 | 195 | 175 | 200 | 214 | 188 | 185 | 181 | 182 | 186 |  | 192 | 170 | 165 | 160 | 158 | 162 | 185 | 4833573
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 181 | 184 | 184 | 152 | 143 | 186 | 198 | 206 | 187 | 159 | 180 | 213 | 184 | 181 | 197 | 185 | 176 |  | 173 | 166 | 163 | 160 | 135 | 0 |  | 4095082
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | [12 empty] | 0 | 0
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 210 | 194 | 189 | 188 | 183 | 194 | 213 | 216 | 214 | 213 | 193 | 196 | 213 | 185 | 184 | 186 | 191 | 193 |  | 195 | 170 | 178 | 171 | 166 | 169 | 181 | 4867164
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 |  |  |  |  | 119 | 116 | 120 | 70 | 10 | 10 | 90 | 125 | 318 | 369 | 355 | 383 | 348 | 434 |  | 419 | 409 | 403 | 396 | 371 | 374 | 357 | 5110600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [6 empty] | 12 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 361920
163 | Bogura 20 MW PP (Energyprima) | [6 empty] | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 246564
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232074
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 50 |  | 50 | 50 | 50 | 12 | 0 |  |  | 155180
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 36 | 0 | [5 empty] | 2 | 76 |  | 108 | 108 | 108 | 35 | 0 |  |  | 428928
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 108 |  | 113 | 113 | 88 | 0 |  |  |  | 382080
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.2 | 0.5 | 0.8 | 1.6 | 2.6 | 3.6 | 3.8 | 3 | 1 | 0.1 | [9 empty] | 17183
178
178