## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-19 | Thursday
|  | Date (day): | 2019-12-19 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10809.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13605 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-18 | 2019-12-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 98 | 113 | 110 | 110
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 107 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 301 | 244 | 300 | 300 |  | 139 | ST Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 354 | 291 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 75 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 42 | 42 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 70 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 349 | 357 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 93 | 93 | 93 |  | 9 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 45 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 70 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1894 | 2253 | 3427 | 4027 | 598 | 1147
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.1 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 83 | 83 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 208 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 144 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 2 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 21 | 14 | 14
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 52 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 86 | 212 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 801.1 | 1147 | 1609 | 1764 | 270 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 125 | 125 | 125 | 125
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 45 | 350 | 240 | 240 |  | 120 | ST under maint.
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 345 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 150 | 150 | 150 | 185
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 5 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 100 | 90 | 105
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 873 | 1258 | 1431 | 1945 | 134 | 704
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 129 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 23 | 94 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.4 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 7 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 187.4 | 365 | 483.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 89 | 89 | 85 | 89
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 44 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 52 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 79 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 32 | 40 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 28/12/2019
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 388 | 377 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1003 | 950 | 1050 | 1054 | 0 | 830
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 299 | 639 | 301 | 650
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 4 | 4 | 30 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 295 | 240 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 16 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 0 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 598 | 981 | 801 | 1745 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 10 | 7 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 56 | 60 | 60 |  | 130 | GT-1 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 75 | 173 | 245 | 315 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 203 | 196 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage.
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 206 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 453 | 431 | 290 | 400 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 72 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 952 | 1052 | 1392 | 1766 | 341 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 260 | 250 | 260
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 40 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 260.6 | 300 | 371 | 407 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6644.1 | 8479 | 10809.6 | 13605 | 1395 | 3212
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6277.3777 | 8011 | 10212.9621 | 12854.0695
A. |  | 2019-12-18 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 8479 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5179 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8479 | MW
3 | Day peak Generation : |  |  | 6644.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8011 | MW
4 | Evening peak Generation : |  |  | 8479 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 159.1218 | MKWHr | By Solar | 0.15219 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.4008 | MKWHr |  | By Oil: | 9.837 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.2686 | MKWHr |  | By Hydro: | 1.9499 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1395 | MW | Dhaka | 2943 | 2943 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3212 | MW | Chittagong | 905 | 905 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4607 | MW | Khulna | 977 | 977 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1080.23 | MMCFD |  |  | Rajshahi | 824 | 824 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 128178868.296 | ii) Oil : | Taka | 90868097.57 | Comilla | 686 | 686 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 25638574 | Total | Taka | 244685539.866 | Mymensingh | 626 | 626 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.1075 | MKWHr. | Sylhet | 319 | 319 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -185 | MW (E to W) at | 19:00 | hrs | Barisal | 222 | 222 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -327 | MW at | 1:00 | hrs | Rangpur | 509 | 509 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 20° C |  |  | Total | 8011 | 8011 |  | 0
B. |  | 2019-12-19 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 24.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13605 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6900 | MW
4 | Reserve(Generation end) |  |  |  | 5005 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 161.3926 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4989 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.6058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 639 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9075 | MKWHr. | iii) Maximum HVDC Flow : |  | 641 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.47 |  | (b) Today: | 97.32 |  | (c) Rule Curve: |  | 104.3
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 304 | 370 |  | 0 | 390 | 0 | 0 | 0 | 0 | 320 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 43 | 40 | 120 | 0 | 0 | 204 | 0 | 136 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 120 | 0 | 80 | 358 | 360 | 0 | 8 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 0 | 14 | 72 | 158 | 0 | 20 | 0 | 60 | 90 | 5 | 47 | 130 | 0 | 68 | 40 | 0 | 0 | 0 | 8 | 0 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4531 | 1413 | 5944 | 3928 | 137 | 1460 | 0 | 260 | 83 | 4 | 72 | 0 | 0 | 97.49
2:00 | 35 | 99 | 0 | 0 | 0 | 7 | 0 | 304 | 370 |  | 0 | 360 | 0 | 0 | 0 | 0 | 240 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 0 | 33 | 0 | 0 | 42 | 40 | 120 | 50 | 0 | 214 | 0 | 137 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 120 | 0 | 80 | 345 | 355 | 0 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 161 | 0 | 0 | 0 | 60 | 90 | 5 | 47 | 130 | 0 | 40 | 40 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4171 | 1465 | 5636 | 3718 | 137 | 1367 | 0 | 260 | 82 | 4 | 68 | 0 | 0 | 97.49
3:00 | 35 | 99 | 0 | 0 | 0 | 6 | 0 | 304 | 370 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 40 | 120 | 80 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 120 | 0 | 80 | 0 | 320 | 0 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 66 | 161 | 0 | 0 | 0 | 60 | 90 | 5 | 47 | 130 | 0 | 40 | 20 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3879 | 1494 | 5373 | 3442 | 137 | 1382 | 0 | 260 | 82 | 4 | 66 | 0 | 0 | 97.48
4:00 | 35 | 99 | 0 | 0 | 0 | 6 | 0 | 304 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 42 | 40 | 120 | 100 | 0 | 203 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 80 | 0 | 320 | 0 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 161 | 0 | 0 | 0 | 60 | 90 | 5 | 5 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3702 | 1480 | 5182 | 3437 | 137 | 1198 | 0 | 260 | 82 | 4 | 64 | 0 | 0 | 97.48
5:00 | 35 | 99 | 0 | 0 | 0 | 6 | 0 | 304 | 260 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 43 | 40 | 120 | 100 | 0 | 184 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 120 | 0 | 80 | 0 | 320 | 0 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 161 | 0 | 0 | 0 | 60 | 89 | 5 | 5 | 100 | 0 | 40 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3644 | 1535 | 5179 | 3431 | 137 | 1200 | 0 | 260 | 83 | 4 | 64 | 0 | 0 | 97.47
6:00 | 35 | 95 | 0 | 0 | 0 | 31 | 0 | 304 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 0 | 33 | 0 | 0 | 43 | 40 | 120 | 100 | 0 | 186 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 17 | 120 | 0 | 80 | 0 | 325 | 0 | 75 | 0 | 37 | 0 | 0 | 8 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 66 | 161 | 0 | 20 | 0 | 60 | 89 | 5 | 8 | 130 | 0 | 40 | 5 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 260 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3892 | 1554 | 5446 | 3486 | 136 | 1411 | 0 | 260 | 83 | 4 | 66 | 0 | 0 | 97.47
7:00 | 35 | 90 | 0 | 0 | 0 | 32 | 0 | 309 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 43 | 40 | 120 | 100 | 0 | 192 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 120 | 0 | 80 | 0 | 360 | 0 | 112 | 0 | 37 | 0 | 0 | 20 | 0 | 0 | 0 | 22 | 0 | 33 | 14 | 64 | 161 | 0 | 20 | 0 | 60 | 89 | 45 | 47 | 130 | 0 | 40 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.31 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0.234 | 0 | 0 | 0 | 0 |  | 136 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4158.544 | 1592.1 | 5750.644 | 3630 | 136 | 1572 | 0 | 260 | 83 | 4 | 64 | 1.644 | 0 | 97.46
8:00 | 35 | 90 | 0 | 0 | 0 | 32 | 0 | 307 | 300 |  | 0 | 450 | 0 | 0 | 0 | 0 | 352 | 0 | 42 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 25 | 28 | 34 | 33 | 0 | 0 | 43 | 40 | 120 | 100 | 0 | 216 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 12 | 120 | 0 | 80 | 0 | 345 | 0 | 141 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 14 | 74 | 161 | 0 | 20 | 0.1 | 60 | 89 | 45 | 47 | 130 | 0 | 53 | 30 | 0 | 0 | 17 | 30 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 0 | 0 | 0 | 395 | 0 | 12 | 0 | 1.1 | 50 | 0 | 0 | 0 |  | 136 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4554.7 | 1609.1 | 6163.8 | 3766 | 136 | 1710 | 123 | 260 | 83 | 4 | 74 | 7.8 | 0 | 97.46
9:00 | 35 | 90 | 0 | 0 | 0 | 32 | 0 | 304 | 311 |  | 0 | 450 | 0 | 5 | 0 | 0 | 351 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 42 | 40 | 120 | 100 | 0 | 216 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 5 | 120 | 0 | 80 | 0 | 320 | 0 | 187 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 78 | 160 | 5 | 20 | 0.2 | 58 | 89 | 45 | 47 | 130 | 0 | 53 | 30 | 0 | 0 | 17 | 29 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.48 | 0 | 0 | 0 | 366 | 0 | 35 | 0 | 2.4 | 83 | 0 | 0 | 0 |  | 299 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 |  | 4645.08 | 1752.4 | 6397.48 | 3707 | 299 | 1747 | 206 | 260 | 82 | 4 | 78 | 14.48 | 0 | 97.45
10:00 | 35 | 94 | 0 | 0 | 0 | 32 | 0 | 305 | 312 |  | 0 | 400 | 0 | 7 | 0 | 0 | 352 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 40 | 120 | 100 | 0 | 202 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 4 | 125 | 0 | 80 | 10 | 330 | 0 | 187 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 80 | 160 | 8 | 20 | 0.2 | 59 | 89 | 45 | 47 | 130 | 0 | 52 | 30 | 0 | 0 | 17 | 29 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4 | 0 | 0 | 0 | 352 | 0 | 35 | 0 | 3.3 | 84 | 0 | 0 | 0 |  | 299 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 |  | 4590.9 | 1820.4 | 6411.3 | 3716 | 299 | 1738 | 213 | 260 | 82 | 4 | 80 | 19.3 | 0 | 97.45
11:00 | 35 | 94 | 0 | 0 | 0 | 32 | 0 | 302 | 364 |  | 0 | 400 | 0 | 7 | 0 | 0 | 358 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 40 | 115 | 100 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 3 | 125 | 0 | 0 | 40 | 320 | 0 | 187 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 16 | 14 | 80 | 159 | 8 | 20 | 0.4 | 60 | 89 | 45 | 47 | 130 | 0 | 52 | 30 | 0 | 0 | 17 | 32 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.83 | 0 | 0 | 0 | 367 | 0 | 35 | 0 | 3.9 | 86 | 0 | 0 | 0 |  | 299 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | 4609.13 | 1853.5 | 6462.63 | 3676 | 299 | 1824 | 215 | 260 | 82 | 4 | 80 | 22.63 | 0 | 97.44
12:00 | 35 | 98 | 0 | 0 | 0 | 104 | 0 | 301 | 354 |  | 0 | 400 | 0 | 7 | 0 | 0 | 349 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 0 | 0 | 0 | 43 | 40 | 115 | 100 | 0 | 209 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 6 | 125 | 0 | 0 | 45 | 330 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 80 | 144 | 23 | 20 | 0.4 | 60 | 89 | 44 | 44 | 163 | 0 | 51 | 76 | 0 | 0 | 17 | 32 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1 | 0 | 0 | 0 | 388 | 0 | 35 | 0 | 4 | 86 | 0 | 0 | 0 |  | 299 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 4758.5 | 1885.6 | 6644.1 | 3740 | 299 | 1925 | 230 | 260 | 83 | 4 | 80 | 23.1 | 0 | 97.44
13:00 | 35 | 114 | 0 | 0 | 0 | 107 | 0 | 300 | 323 |  | 0 | 450 | 0 | 7 | 0 | 0 | 270 | 0 | 87 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 23 | 0 | 0 | 44 | 40 | 115 | 100 | 0 | 205 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 14 | 125 | 0 | 0 | 75 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 78 | 144 | 47 | 20 | 0.5 | 58 | 89 | 47 | 44 | 163 | 0 | 52 | 79 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 361 | 0 | 105 | 0 | 3.7 | 150 | 0 | 0 | 0 |  | 299 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 |  | 4947.2 | 1876.7 | 6823.9 | 3730 | 299 | 1958 | 388 | 260 | 84 | 4 | 78 | 22.9 | 0 | 97.43
14:00 | 35 | 112 | 0 | 0 | 0 | 107 | 0 | 265 | 282 |  | 0 | 450 | 0 | 8 | 0 | 0 | 270 | 0 | 62 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 82 | 40 | 115 | 140 | 0 | 205 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 10 | 125 | 0 | 0 | 145 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 84 | 130 | 65 | 20 | 0 | 57 | 89 | 47 | 44 | 100 | 0 | 51 | 79 | 0 | 0 | 17 | 37 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 366 | 0 | 70 | 0 | 2.93 | 156 | 0 | 0 | 0 |  | 299 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 54 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 |  | 4871.93 | 1733.2 | 6605.13 | 3640 | 299 | 1799 | 378 | 260 | 122 | 4 | 84 | 19.13 | 0 | 97.43
15:00 | 35 | 112 | 0 | 0 | 0 | 107 | 0 | 256 | 282 |  | 0 | 400 | 0 | 7 | 0 | 0 | 270 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 40 | 115 | 180 | 0 | 204 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 5 | 125 | 0 | 0 | 240 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 84 | 132 | 65 | 20 | 0.4 | 60 | 89 | 47 | 47 | 100 | 0 | 51 | 76 | 0 | 0 | 17 | 36 | 10 | 0 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 366 | 0 | 69 | 0 | 1.91 | 155 | 0 | 0 | 0 |  | 299 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 51 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4897.31 | 1669.8 | 6567.11 | 3756 | 299 | 1694 | 375 | 260 | 80 | 5 | 84 | 14.11 | 0 | 97.42
16:00 | 35 | 112 | 0 | 0 | 0 | 107 | 0 | 239 | 282 |  | 0 | 400 | 0 | 7 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 40 | 40 | 115 | 180 | 0 | 177 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 7 | 125 | 0 | 0 | 365 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 16 | 14 | 78 | 129 | 65 | 20 | 0.2 | 60 | 89 | 14 | 44 | 100 | 0 | 40 | 40 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 328 | 0 | 69 | 0 | 0.732 | 158 | 0 | 0 | 0 |  | 297 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 53 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4815.932 | 1689.1 | 6505.032 | 3745 | 297 | 1655 | 378 | 260 | 80 | 6 | 78 | 6.032 | 0 | 97.42
17:00 | 35 | 112 | 0 | 0 | 0 | 107 | 0 | 256 | 312 |  | 0 | 400 | 0 | 9 | 0 | 0 | 270 | 0 | 35 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 5 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 40 | 115 | 120 | 0 | 178 | 0 | 105 | 0 |  | 0 | 0 | 13 | 0 | 0 | 22 | 18 | 7 | 125 | 0 | 0 | 365 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 14 | 88 | 129 | 70 | 20 | 0 | 58 | 89 | 14 | 44 | 100 | 0 | 40 | 40 | 0 | 0 | 17 | 39 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 30 | 0 | 0 | 278 | 0 | 80 | 3 | 0 | 158 | 0 | 0 | 0 |  | 443 | 0 | 240 | 0 | 12 | 0 | 0 | 0 | 0 | 4 | 0 | 55 | 8 | 9 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 9 | 0 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 380 | 0 | 0 | 0 | 15 | 8 | 0 | 0.1 | 0 |  | 4846 | 1899.1 | 6745.1 | 3681 | 443 | 1690 | 484 | 260 | 82 | 17 | 88 | 0.1 | 0 | 97.41
18:00 | 35 | 112 | 0 | 0 | 0 | 107 | 0 | 250 | 312 |  | 0 | 420 | 0 | 60 | 20 | 15 | 270 | 0 | 42 | 0 | 45 | 68 | 0 | 0 | 0 | 0 | 36 | 53 | 25 | 0 | 19 | 25 | 20 | 33 | 33 | 34 | 0 | 43 | 40 | 120 | 120 | 0 | 204 | 0 | 151 | 0 |  | 0 | 0 | 17 | 0 | 40 | 50 | 18 | 5 | 125 | 0 | 0 | 365 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 102 | 130 | 94 | 20 | 0 | 59 | 89 | 41 | 44 | 100 | 0 | 52 | 79 | 0 | 0 | 17 | 44 | 10 | 0 | 24 | 11 | 0 | 8 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 17 | 10 | 291 | 71 | 105 | 17 | 0 | 212 | 0 | 0 | 37 |  | 639 | 0 | 240 | 0 | 40 | 0 | 0 | 0 | 0 | 4 | 0 | 57 | 7 | 74 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 379 | 0 | 0 | 0 | 50 | 109 | 0 | 0 | 60 |  | 5759 | 2416 | 8175 | 3786 | 639 | 1777 | 1507 | 260 | 83 | 21 | 102 | 0 | 0 | 97.41
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 113 | 0 | 0 | 0 | 107 | 0 | 244 | 291 |  | 0 | 420 | 0 | 75 | 0 | 0 | 357 | 0 | 42 | 0 | 70 | 93 | 32 | 0 | 0 | 0 | 47 | 53 | 17 | 0 | 19 | 25 | 32 | 33 | 33 | 45 | 0 | 43 | 40 | 120 | 120 | 0 | 208 | 0 | 144 | 0 |  | 0 | 0 | 2 | 0 | 52 | 50 | 18 | 21 | 125 | 0 | 0 | 350 | 345 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 100 | 129 | 94 | 20 | 0 | 60 | 89 | 44 | 47 | 100 | 0 | 52 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 0 | 5 | 377 | 115 | 70 | 17 | 0 | 212 | 0 | 0 | 17 |  | 639 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 16 | 56 | 7 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 431 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 72 |  | 5973 | 2506 | 8479 | 4024 | 639 | 1826 | 1509 | 260 | 83 | 38 | 100 | 0 | 0 | 97.4
19:30 | 35 | 113 | 0 | 0 | 0 | 107 | 0 | 257 | 282 |  | 0 | 420 | 0 | 50 | 0 | 0 | 354 | 0 | 65 | 0 | 7 | 93 | 48 | 0 | 0 | 0 | 12 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 42 | 40 | 120 | 120 | 0 | 215 | 0 | 154 | 0 |  | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 22 | 125 | 0 | 0 | 360 | 345 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 100 | 129 | 94 | 20 | 0 | 60 | 89 | 47 | 47 | 130 | 0 | 52 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 392 | 115 | 70 | 17 | 0 | 216 | 0 | 0 | 0 |  | 640 | 0 | 235 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 16 | 60 | 6 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 433 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 |  | 5816 | 2440 | 8256 | 4108 | 640 | 1852 | 1162 | 260 | 82 | 52 | 100 | 0 | 0 | 0
20:00 | 35 | 110 | 0 | 0 | 0 | 107 | 0 | 264 | 285 |  | 0 | 420 | 0 | 50 | 0 | 0 | 355 | 0 | 65 | 0 | 0 | 93 | 48 | 0 | 0 | 0 | 12 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 41 | 40 | 120 | 120 | 0 | 211 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 27 | 125 | 0 | 0 | 350 | 340 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 102 | 130 | 94 | 20 | 0 | 59 | 89 | 47 | 47 | 130 | 0 | 52 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 375 | 115 | 70 | 17 | 0 | 216 | 0 | 0 | 0 |  | 640 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 16 | 60 | 7 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 432 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 35 |  | 5783 | 2435 | 8218 | 4062 | 640 | 1858 | 1163 | 260 | 81 | 52 | 102 | 0 | 0 | 97.4
21:00 | 35 | 117 | 0 | 0 | 0 | 107 | 0 | 244 | 284 |  | 0 | 420 | 0 | 50 | 0 | 0 | 350 | 0 | 65 | 0 | 0 | 93 | 48 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 35 | 125 | 0 | 0 | 330 | 320 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 96 | 128 | 94 | 20 | 0 | 58 | 89 | 47 | 47 | 130 | 0 | 53 | 79 | 0 | 0 | 19 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 363 | 40 | 70 | 0 | 0 | 216 | 0 | 0 | 0 |  | 641 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 4 | 16 | 54 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 433 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 5525 | 2363 | 7888 | 3960 | 641 | 1870 | 928 | 260 | 81 | 52 | 96 | 0 | 0 | 97.39
22:00 | 35 | 117 | 0 | 0 | 0 | 107 | 0 | 117 | 295 |  | 0 | 420 | 0 | 10 | 0 | 0 | 359 | 0 | 62 | 0 | 0 | 16 | 25 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 125 | 0 | 0 | 330 | 320 | 0 | 150 | 0 | 36 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 86 | 114 | 94 | 20 | 0 | 60 | 89 | 47 | 50 | 130 | 0 | 53 | 79 | 0 | 0 | 17 | 41 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 363 | 40 | 17 | 0 | 0 | 203 | 0 | 0 | 0 |  | 541 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 16 | 50 | 8 | 114 | 0 | 0 | 50 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 392 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 |  | 5161 | 2157 | 7318 | 3815 | 541 | 1846 | 660 | 260 | 81 | 29 | 86 | 0 | 0 | 97.39
23:00 | 35 | 117 | 0 | 0 | 0 | 107 | 0 | 104 | 316 |  | 0 | 420 | 0 | 0 | 0 | 0 | 360 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 32 | 28 | 33 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 125 | 0 | 0 | 330 | 320 | 0 | 150 | 0 | 36 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 82 | 114 | 9 | 20 | 0 | 60 | 89 | 47 | 50 | 130 | 0 | 53 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 |  | 299 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 53 | 6 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 431 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 4764 | 1807 | 6571 | 3765 | 299 | 1906 | 173 | 260 | 82 | 4 | 82 | 0 | 0 | 97.38
24:00 | 35 | 115 | 0 | 0 | 0 | 14 | 0 | 301 | 314 |  | 0 | 390 | 0 | 0 | 0 | 0 | 365 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 28 | 33 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 206 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 125 | 0 | 0 | 330 | 320 | 0 | 112 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 12 | 74 | 132 | 0 | 20 | 0 | 58 | 89 | 45 | 0 | 130 | 0 | 53 | 79 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 52 | 7 | 48 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 416 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 4524 | 1641 | 6165 | 3849 | 201 | 1632 | 63 | 260 | 82 | 4 | 74 | 0 | 0 | 97.38
KWH | 775000 | 2661200 | 0 | 0 | 0 | 1539954 | 0 | 6609480 | 7516000 |  | 0 | 9237000 | 0 | 336960 | 42768 | 23036 | 7702285 | 0 | 1538000 | 0 | 126691 | 486720 | 136320 | 0 | 0 | 0 | 115104 | 849240 | 55282 | 0 | 292068 | 600000 | 713340 | 736700 | 803200 | 120396 | 0 | 977869 | 972000 | 2800000 | 2600000 | 0 | 4810837 | 0 | 2939216 | 0 |  | 0 | 0 | 34833 | 0 | 97920 | 313440 | 355776 | 455520 | 3015230 | 0 | 831494 | 4527200 | 8185500 | 0 | 2810181 | 0 | 841320 | 0 | 0 | 876628 | 0 | 0 | 0 | 404352 | 160560 | 458000 | 363710 | 1907520 | 3366200 | 906240 | 376992 | 2950 | 1418000 | 2134920 | 781200 | 969408 | 3100671 | 0 | 1188192 | 1222080 | 0 | 0 | 318000 | 693800 | 162000 | 0 | 386472 | 159312 | 0 | 12545 | 0 | 0 | 21600 | 0 | 0 | 116640 | 419520 | 26400 | 25090 | 8811000 | 456000 | 870828 | 67745 | 23400 | 2318400 | 0 | 0 | 86640 |  | 7605818 | 0 | 5987808 | 0 | 130560 | 0 | 0 | 0 | 0 | 88320 | 63750 | 1478000 | 504051 | 638688 | 0 | 0 | 1190000 | 0 | 0 | 0 | 214610 | 0 | 0 | 0 | 0 | 361680 | 247788 | 221598 | 0 | 0 | 6268600 | 0 | 0 | 4714264 | 0 | 0 | 0 | 0 | 0 | 4779673 | 0 | 9667945 | 0 | 0 | 0 | 294480 | 216000 | 0 | 9203 | 240864 |  | 114198095 | 44923700 | 159121795 | 91254899 | 7605818 | 40145906 | 9577517 | 6268600 | 1949869 | 259473 | 1907520 | 152193 | 0
Fuel Cost | 868000 | 2874096 | 0 | 0 | 0 | 1493755.38 | 0 | 4758825.6 | 5712160 |  | 0 | 7389600 | 0 | 3436992 | 463177.44 | 236349.36 | 9550833.4 | 0 | 1922500 | 0 | 1406270.1 | 4945075.2 | 1350931.2 | 0 | 0 | 0 | 1077373.44 | 8144211.6 | 527390.28 | 0 | 219051 | 450000 | 0 | 0 | 0 | 1153393.68 | 0 | 254245.94 | 252720 | 4284000 | 3978000 | 0 | 5051378.85 | 0 | 3732804.32 | 0 |  | 0 | 0 | 365398.17 | 0 | 931219.2 | 2933798.4 | 327313.92 | 1266345.6 | 3165991.5 | 0 | 873068.7 | 3350128 | 6875820 | 0 | 2753977.38 | 0 | 689882.4 | 0 | 0 | 1253578.04 | 0 | 0 | 0 | 412439.04 | 120420 | 865620 | 272782.5 | 13161888 | 2760284 | 8618342.4 | 384531.84 | 48380 | 1928480 | 2903491.2 | 1062432 | 1211760 | 3844832.04 | 0 | 1770406.08 | 2150860.8 | 0 | 0 | 505620 | 811746 | 380700 | 0 | 289854 | 121077.12 | 0 | 131346.15 | 0 | 0 | 207792 | 0 | 0 | 1346025.6 | 3909926.4 | 247632 | 235093.3 | 8282340 | 3999120 | 7759077.48 | 640190.25 | 0 | 21375648 | 0 | 0 | 0 |  | 20535708.6 | 0 | 4670490.24 | 0 | 1258598.4 | 0 | 0 | 0 | 0 | 1156992 | 630487.5 | 1182400 | 781279.05 | 6859509.12 | 0 | 0 | 2237200 | 0 | 0 | 0 | 2225505.7 | 0 | 0 | 0 | 0 | 397848 | 408850.2 | 167749.686 | 0 | 0 | 25638574 | 0 | 0 | 4148552.32 | 0 | 0 | 0 | 0 | 0 | 4206112.24 | 0 | 7057599.85 | 0 | 0 | 0 | 2623816.8 | 2017440 | 0 | 0 | 0 |  | 192079794.3 | 88204713.706 | 280284508.006 | 90201543.956 | 20535708.6 | 37977324.34 | 87994776.2 | 25638574 | 506965.94 | 2873321.37 | 13161888 | 1394405.6 | 0
Yesterday Day Peak | 35 | 98 | 0 | 0 | 0 | 104 | 0 | 301 | 354 |  | 0 | 400 | 0 | 7 | 0 | 0 | 349 | 0 | 42 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 0 | 0 | 0 | 43 | 40 | 115 | 100 | 0 | 209 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 6 | 125 | 0 | 0 | 45 | 330 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 16 | 14 | 80 | 144 | 23 | 20 | 0.4 | 60 | 89 | 44 | 44 | 163 | 0 | 51 | 76 | 0 | 0 | 17 | 32 | 10 | 0 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1 | 0 | 0 | 0 | 388 | 0 | 35 | 0 | 4 | 86 | 0 | 0 | 0 |  | 299 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 260 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 453 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 |  | 6644.1 | DayPeak
Yesterday Evening Peak | 35 | 113 | 0 | 0 | 0 | 107 | 0 | 244 | 291 | 0 | 0 | 420 | 0 | 75 | 0 | 0 | 357 | 0 | 42 | 0 | 70 | 93 | 32 | 0 | 0 | 0 | 47 | 53 | 17 | 0 | 19 | 25 | 32 | 33 | 33 | 45 | 0 | 43 | 40 | 120 | 120 | 0 | 208 | 0 | 144 | 0 | 0 | 0 | 0 | 2 | 0 | 52 | 50 | 18 | 21 | 125 | 0 | 0 | 350 | 345 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 100 | 129 | 94 | 20 | 0 | 60 | 89 | 44 | 47 | 100 | 0 | 52 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 0 | 5 | 377 | 115 | 70 | 17 | 0 | 212 | 0 | 0 | 17 |  | 639 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 16 | 56 | 7 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 431 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 72 |  | 8479 | EvPeak
Forecast for Evening | 35 | 110 | 0 | 0 | 0 | 108 | 0 | 300 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 14 | 125 | 0 | 0 | 240 | 360 | 0 | 185 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 105 | 150 | 95 | 22 | 0 | 60 | 89 | 51 | 44 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  | 650 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 60 | 20 | 110 | 30 | 0 | 50 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 260 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 110 | 0 | 0 | 0 | 108 | 0 | 300 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 50 | 50 | 21 | 14 | 125 | 0 | 0 | 240 | 360 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 150 | 95 | 22 | 1.6 | 60 | 85 | 51 | 44 | 163 | 0 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 150 | 150 | 400 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  | 301 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 20 | 70 | 0 | 0 | 50 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 290 | 50 | 100 | 0 | 0 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 95 | 0 | 0 | 0 | 94 | 0 | 311 | 374 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 365 | 0 | 76 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 43 | 40 | 120 | 120 | 0 | 206 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 125 | 0 | 0 | 320 | 320 | 0 | 150 | 0 | 30 | 0 | 0 | 15 | 0 | 0 | 0 | 22 | 11 | 21 | 12 | 72 | 161 | 2 | 20 | 0.1 | 60 | 89 | 37 | 0 | 130 | 0 | 53 | 73 | 0 | 0 | 17 | 27 | 9 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0.837 | 15 | 0 | 0 | 0 | 0 | 136 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 52 | 5 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 8 | 0 | 0 | 180 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0
199
| Minimum Generation |  | 5179 | 5:00
| Highest Generation |  | 8479 | 19:00
| Day Peak Generation |  | 6644.1 | 12:00
| Evening Peak Generation |  | 8479 | 19:00
| HVDC Max Flow |  | 641 | 21:00
| HVDC EvPeak Flow |  | 639 | 19:00
| Load factor L.F |  | 78.19%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6644.1 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4989 | MW
Evening Peak Generation : |  | 8479 | MW Hour : | 19:00 | Available Max Generation : |  | 13605 | MW
E.P. Demand (at gen end) : |  | 8479 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8600 | MW
Maximum Generation : |  | 8479 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5005 | MW
Total Gen. (MKWH) : |  | 159.1218 | System Load Factor : | 78.19% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -327 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-19
Actual : | 97.32 | Ft.(MSL) , | Rule curve : | 104.3 | Ft.( MSL )
Gas Consumed : | Total = | 1080.23 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 128178868.296
: |  | Coal : | 25638574 | Oil : | 90868097.57 | Total : | 244685539.866
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3038.4628 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1026.6517 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 918.671 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 829.6796 |  |  | 0 | 0%
) | 0 | 0:00 | 749.9995 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 605.2064 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 346.8868 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 156.0489 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 466.7246 |  |  | 0 | 0%
Total | 0 |  | 8138.3313 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Summit Meghna 305 MW | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-1,4,5,7 | 12) Baghabari 100 MW
|  |  |  | 4) Chandpur CCPP | 13) Ashuganj North ST
|  |  |  | 5) Sylhet 150 MW | 14) Haripur 412 ST
|  |  |  | 6) Bhola-225 MW GT-1 & ST | 15) Sirajganj unit-2
7) Ashuganj Precision
8) Ashuganj 225 MW CCPP
9) Ashuganj unit-4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) New Tongi-Tongi 132 kV Ckt-1 was under shut down from 08:55 to 13:40 for A/M.
b) Kallyanpur 132 kV main bus was shut down at 08:38 for A/M.
c) Agargaon 132/33 kV T-2 transformer was under shut down from 08:37 to 14:50 for A/M.
d) Aminbazar-Mirpur 132 kV Ckt-1 was under shut down from 08:20 to 17:45 for A/M.
e) Hathazari-Madunaghat 132 kV Ckt-1 was under shut down from 10:47 to 12:09 for A/M.
f) AKSML-BSRM 230 kV Ckt was under shut down from 08:23 for 15:00 for A/M.
g) Fenchuganj-Bibiyana 132 kV Ckt-2 was under shut down from 09:05 to 16:56 for A/M.
h) Cumilla (N) -BSRM(2) 132 kV Ckt was under shut down from 08:31 to 15:59 for A/M.
i) Bheramara-Ishurdi 132 kV Ckt-2 was under shut down from 08:38 to 16:20 for A/M.
j) Noapara-Jessore 132 kV Ckt-1 was under shut down from 08:10 to 14:25 for A/M.
k) Barishal (N)-Barishal (S) 132 kV Ckt-1 was under shut down from 11:15 to 13:44 for D/W.
l) Benapole 132/33 kV T-2 transformer was under shut down from 10:00 to 13:33 for D/W.
m) Ashuganj unit-5 tripped at 10:10.
n) Ashuganj (N) ST was synchronized at 12:47
p) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 08:30 to 16:30 for A/M.
q) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 11:37 to 12:51 for SCADA testing.
r) Juldah-Shahmirpur 132 kV Ckt-1 was under shut down from 08:34 to 15:01 for A/M.
s) Hasnabad-Aminbazar 132 kV Ckt-1 was under shut down from 13:08 to 16:52 for A/M.
t) Hasnabad-Shyampur GIS 132 kV Ckt-1 was under shut down from 10:26 to 15:27 for A/M.
u) Joydevpur-Kodda 132 kV Ckt-1 & 2 were under shut down from 08:52 to 17:55 for D/W.
v) Ishurdi-Bheramara HVDC 230 kV Ckt-1 & 2 were shut down at 09:16 for C/M.
w) Ishurdi 230 kV bus-1 was shut down at 09:14 for C/M.
x) Shahzibazar 132/33 kV T-6 transformer was under shut down from 08:09 to 13:22 for A/M.
y) Cumilla (N) 132/33 kV T-3 transformer tripped at 15:12 from both sides showing E/F relay at 132 kV side and
L/O at 33 kV side for 33 kV Burichong feeder fault and was switched on at 15:35.
z) Tongi-Bashundhara 132 kV Ckt-1 tripped at 02:17(19/12/2019) showing dist. Z2 relay at B-phase from Tongi side and
dist. Relay from Bashundhara side and was switched on at 02:48.
aa) Rampura-Bhulta 230 kV Ckt-4 was shut down at 07:19(19/12/2019) for A/M.
ab) Maniknagar 132 kV main bus was shut down at 07:03(19/12/209) for A/M.
ac) Bhola-Barisal 230 kV Ckt-2 was shut down at 07:37(19/12/2019) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 775000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 113 | 2661200 | Ghorasal transformer over load.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1539954
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 244 | 6609480 | Machine problem
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 291 | 7516000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9237000 | Gas shortage.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 75 | 336960 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 42768 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 23036 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 292068
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 42 | 1538000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 126691 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 357 | 7702285
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 486720 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 115104
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 849240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 136320 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 55282 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1313340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 736700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 45 | 120396
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 12545 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 870828 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2253 | 43900117
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2600000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 116640
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 313440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 83 | 1949869 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 208 | 4810837 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 2939216
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 67745 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 2 | 34833 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 419520
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 355776
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 455520
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 52 | 97920 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23400
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 212 | 2318400 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1147 | 19303116
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 3015230
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 831494 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 350 | 4527200 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 345 | 8185500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 841320 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 150 | 2810181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 876628 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 25090 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 26400 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 404352
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 160560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 1907520
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 458000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 363710 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 86640 | Low demand
| Cumilla Area Total |  |  |  | 2920 | 1258 | 24519825
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 129 | 3366200 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 376992
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 94 | 906240
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 2950
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 7 | 21600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 456000
| Mymensingh Area Total |  |  |  | 637 | 365 | 5129982
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1418000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 89 | 2134920
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3100671 | frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 781200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 47 | 969408
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 159312
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1188192
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1222080
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 318000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 40 | 693800 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 386472
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 377 | 8811000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 162000
| Sylhet Area Total |  |  |  | 1949 | 950 | 21345055
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 639 | 7605818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 130560 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 88320 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 240 | 5987808 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 16 | 63750 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 294480 | Low demand
| Khulna Area Total |  |  |  | 2314 | 981 | 14170736
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 638688
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 7 | 504051 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 56 | 1478000 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Cable fault
| Barisal Area Total |  |  |  | 462 | 173 | 2620739
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1190000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 214610
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 196 | 4714264 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 206 | 4779673 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 431 | 9667945 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 361680
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 247788
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 221598
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 72 | 240864
| Rajshahi Area Total |  |  |  | 2183 | 1052 | 21638422
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 6268600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 40 | 216000
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 9203
| Rangpur Area Total |  |  |  | 605 | 300 | 6493803
| Total |  |  |  | 19047 | 8479 | 159121795
| Eastern Grid Total |  |  |  | 13483 | 5973 | 114198095
| Western Grid Total |  |  |  | 5564 | 2506 | 44923700
| National Grid Total |  |  |  | 19047 | 8479 | 159121795
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-18
(a) ENTIRE EASTERN GRID : |  | 5479 | MW | (b) ENTIRE WESTERN GRID : |  | 2532 | MW
i) Dhaka area |  | 2943 | MW | i) Khulna area |  | 977 | MW
ii) Chittagong area |  | 905 | MW | ii) Rajshahi area |  | 824 | MW
iii) Comilla area |  | 686 | MW | iii) Barisal area |  | 222 | MW
iv) Mymensingh area |  | 626 | MW | iv) Rangpur area |  | 509 | MW
v) Sylhet area |  | 319 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8011 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 18:00 | Shahjibazar | 76 | 18:00 | Bottail | 94 | 18:00
Munsiganj | 84 | 19:00 | Fenchuganj | 24 | 18:00 | G.K Project | 24 | 18:00
Sonargaon | 67 | 19:00 | Kulawara | 29 | 18:00 | Faridpur | 126 | 19:00
Shyampur | 170 | 24:00 | Sylhet | 96 | 18:30 | Madaripur | 56 | 20:00
Bhulta | 145 | 10:00 | Chatak | 18 | 19:00 | Sariatpur | 38 | 19:00
Madanganj | 45 | 16:00 | Sunamganj | 27 | 18:00 | Gopalganj | 64 | 19:00
Shitalakhya | 91 | 11:00 | Biani Bazar | 31 | 18:30 | Bagerhat | 63 | 19:30
Rahim steel | 16 | 7:00 | Comilla (S) | 102 | 18:00 | Mongla | 38 | 0.5
Matuail | 72 | 9:00 | Comilla(N) | 67 | 18:00 | Satkhira | 65 | 18:30
Ghorasal | 70 | 18:30 | Chandpur | 70 | 19:30 | Gallamari | 34 | 13:00
Narsingdi | 97 | 19:30 | Feni | 85 | 18:00 | Magura | 36 | 18:30
Haripur (SBU) | 90 | 3:00 | Chowmuhani | 112 | 18:30 | Norail | 21 | 18:00
Ullon | 47 | 19:00 | Ashuganj | 34 | 18:30 | Chuadanga | 58 | 18:00
Hasnabad | 138 | 18:00 | Daudkandi | 76 | 18:00 | Barisal(N) | 29 | 20:00
Magbazar | 73 | 13:00 | B.Baria | 86 | 18:00 | Barisal (S) | 70 | 19:30
Maniknagar | 72 | 12:00 | Ramganj | 54 | 18:00 | Patuakhali | 62 | 21:00
Bangabhaban | 16 | 13:00 | Chaddagram | 16 | 18:00 | Bhandaria | 38 | 19:00
Narinda | 70 | 13:00 | PHP | 1 | 18:00 | Borhan Uddin | 35 | 21:00
Dhanmondi | 85 | 13:00 | Madunaghat | 43 | 18:00 | Ishurdi | 46 | 18:30
Lalbag | 58 | 12:00 | Hathazari | 70 | 18:30 | Ruppur Paromanobik | 1 | 1:00
Madartek | 43 | 18:00 | Khulshi | 122 | 12:00 | Natore | 83 | 18:30
Mirpur | 67 | 18:30 | Halishahar | 93 | 17:00 | Bogra | 131 | 18:30
Kalyanpur | 63 | 18:00 | Baraulia | 141 | 9:00 | Noagaon | 79 | 18:30
Gulshan | 92 | 13:00 | Sikalbaha | 28 | 18:00 | Rajshahi | 88 | 20:00
Uttara | 33 | 18:00 | Dohazari | 66 | 18:00 | Rajshahi New | 8 | 18:00
Uttara New | 25 | 18:00 | Cox'sbazar | 68 | 20:00 | C.Nawabganj | 53 | 18:30
Kamrangirchar | 59 | 18:00 | Chandraghona | 22 | 18:00 | Amnura | 23 | 18:30
Savar | 106 | 18:00 | Kaptai | 4 | 19:00 | Pabna | 72 | 18:30
Bhasantec | 106 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 74 | 18:30
Agargaon | 32 | 18:00 | Bakulia | 74 | 18:00 | Serajganj | 62 | 18:30
Satmosjid | 66 | 19:30 | Julda | 15 | 17:00 | Niyamatpur | 44 | 18:00
Tongi | 112 | 11:00 | TK chemical | 8 | 1:00 | Joypurhat | 41 | 18:00
Kabirpur | 132 | 18:00 | Modern Steel | 14 | 7:00 | Sherpur(Bogura) | 34 | 18:00
Basundhara | 59 | 18:00 | Shahmirpur | 22 | 18:00 | Mohastangor | 11 | 18:00
Manikganj | 70 | 19:00 | Khagrachhari | 16 | 18:00 | Rangpur | 99 | 18:30
Joydevpur | 160 | 18:00 | Matarbari | 22 | 18:00 | Lalmonirhat | 41 | 18:00
New Tongi | 73 | 18:30 | Baroiar Hat | 18 | 18:00 | Saidpur | 85 | 18:00
Korda | 184 | 18:00 | Rangamati | 8 | 18:00 | Purbasadipur | 59 | 6:00
Dhamrai | 32 | 18:00 | Abul Khair 230 | 135 | 7:00 | Thakurgaon | 35 | 11:00
Valuka | 70 | 18:00 | BSRM | 110 | 1:00 | Palashbari | 84 | 18:30
Tangail | 130 | 19:00 | GPH Ispat | 10 | 19:30 | Barapukuria | 41 | 18:00
Mymensing | 151 | 18:00 | Goalpara | 17 | 19:00 | Panchagar | 23 | 8:00
Kishorganj | 76 | 18:00 | Central s/s | 60 | 18:00 | Joldhaka | 20 | 18:00
Netrokona | 66 | 18:00 | Noapara | 60 | 18:00 | Kurigram | 43 | 18:00
Jamalpur | 88 | 18:30 | Jessore | 74 | 19:00
Sherpur | 70 | 18:00 | Benapol | 28 | 18:00
Srimongal | 26 | 18:30 | Jhenida | 70 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-18 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 389 | 0.16667 | 382 | 0.41667 | Kaliakoir | 378 | 0.20833 | 367 | 0.45833
Bheramara | 409 | 0.083333 | 390 | 0.75 | Bhulta | 390 | 0.95833 | 374 | 0.5
Ashuganj(N) | 397 | 0.91667 | 377 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 0.041667 | 226 | 0.41667 | Hathazari | 224 | 0.75 | 220 | 0.41667
Ishurdi | 243 | 0.125 | 228 | 0.79167 | Megnaghat | 231 | 0.95833 | 222 | 0.375
Ashuganj | 240 | 0.70833 | 234 | 0.41667 | Fenchuganj | 237 | 0.54167 | 233 | 0.79167
Serajganj | 235 | 0.20833 | 230 | 0.33333 | Siddhirganj | 230 | 0.041667 | 221 | 0.375
Baghabari | 247 | 0.20833 | 230 | 0.33333 | Maniknagar | 229 | 0.91667 | 222 | 0.45833
Barapukuria | 231 | 0.125 | 226 | 0.375 | Old Airport | 228 | 0.083333 | 218 | 0.5
Bogra | 233 | 0.20833 | 223 | 0.58333 | Barisal | 235 | 0.16667 | 221 | 0.375
Khulna South | 236 | 0.16667 | 215 | 0.77083 | AKSML | 221 | 0.95833 | 216 | 0.125
Rampura | 229 | 0.041667 | 223 | 0.41667 | BSRM | 224 | 0.91667 | 217 | 0.41667
Haripur | 229 | 0.25 | 222 | 0.45833 | Bibiyana | 235 | 0.25 | 226 | 0.45833
Hasnabad | 230 | 0.041667 | 220 | 0.41667 | Bhulta | 236 | 0.041667 | 222 | 0.5
Aminbazar | 229 | 0.083333 | 220 | 0.5 | Ashuganj (S) | 237 | 0.91667 | 230 | 0.45833
Tongi | 226 | 0.16667 | 214 | 0.45833 | Kaliakoir | 230 | 0.91667 | 222 | 0.66667
Comilla (N) | 236 | 0.083333 | 230 | 0.66667 | GPH | 220 | 0.16667 | 216 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 139 | 0.75 | 134 | 0.5 | Halishahar | 133 | 0.75 | 130 | 0.41667
Munsiganj | 141 | 0.75 | 134 | 0.5 | Baraulia | 132 | 0.70833 | 128 | 0.41667
Sonargaon | 136 | 0.041667 | 133 | 0.29167 | Sikalbaha | 133 | 0.75 | 129 | 0.5
Shyampur | 137 | 0.29167 | 130 | 0.5 | Dohazari | 131 | 0.041667 | 128 | 0.45833
Bhulta | 132 | 0.125 | 128 | 0.41667 | Cox'sbazar | 126 | 0.125 | 123 | 0.5
Madanganj | 133 | 0.20833 | 126 | 0.41667 | Chandraghona | 133 | 0.125 | 131 | 0.20833
Shitalakhya | 136 | 0.77083 | 126 | 0.5 | Kaptai | 133 | 0.77083 | 132 | 0.041667
Rahim steal | 139 | 18:00 | 135 | 0.41667 | A. Khaer Stl. | 131 | 0.041667 | 130 | 0.125
Matuail | 138 | 0.75 | 133 | 0.5 | Bakulia | 132 | 0.75 | 128 | 0.41667
Ghorasal | 138 | 0.041667 | 135 | 0.41667 | Julda | 133 | 0.75 | 129 | 0.45833
Narsinghdi | 129 | 0.16667 | 125 | 0.5 | TK Chemical | 133 | 0.8125 | 128 | 0.083333
Haripur (SBU) | 139 | 0.125 | 136 | 0.41667 | Modern Steel | 132 | 0.70833 | 128 | 0.5
Ullon | 134 | 0.041667 | 129 | 0.5 | Shahmirpur | 133 | 0.77083 | 126 | 0.625
Hasnabad | 134 | 0.041667 | 130 | 0.5 | Khagrachhari | 132 | 0.125 | 130 | 0.375
Magbazar | 135 | 0.16667 | 130 | 0.5 | Matarbari | 129 | 0.70833 | 126 | 0.25
Maniknagar | 137 | 0.041667 | 133 | 0.5 | Baroiar Hat | 132 | 0.041667 | 130 | 0.75
Bangabhaban | 137 | 0.041667 | 133 | 0.5 | Rangamati | 132 | 0.083333 | 130 | 0.45833
Narinda | 137 | 0.041667 | 133 | 0.5 | Goalpara | 137 | 0.91667 | 128 | 8:00
Dhanmondi | 134 | 0.041667 | 129 | 0.5 | Central s/s | 138 | 0.16667 | 126 | 18:00
Lalbag | 134 | 0.16667 | 125 |  | Noapara | 135 | 0.25 | 122 | 0.75
Madartek | 135 | 1904-01-02 | 129 | 0.5 | Jessore | 132 | 0.25 | 121 | 0.77083
Mirpur | 135 | 0.16667 | 127 | 0.54167 | Benapol | 135 | 0.91667 | 122 | 0.75
Kalyanpur | 136 | 0.20833 | 134 | 0.041667 | Jhenida | 133 | 0.25 | 120 | 0.75
Gulshan | 136 | 0.041667 | 128 | 0.5 | Bottail | 136 | 0.083333 | 126 | 0.77083
Uttara | 133 | 0.041667 | 124 | 0.5 | G.K Project | 140 | 0.25 | 133 | 0.77083
Uttara New | 132 | 0.125 | 123 | 0.5 | Faridpur | 135 | 0.25 | 125 | 0.77083
Kamrangirchar | 133 | 0.20833 | 126 | 0.5 | Madaripur | 137 | 0.16667 | 124 | 0.33333
Savar | 135 | 0.20833 | 123 | 0.5 | Sariatpur | 134 | 0.20833 | 125 | 0.41667
Bhasantec | 132 | 0.125 | 128 | 0.5 | Gopalganj | 141 | 0.875 | 129 | 0.33333
Agargaon | 136 | 0.125 | 129 | 0.5 | Bagerhat | 135 | 0.95833 | 121 | 0.75
Satmosjid | 135 | 0.083333 | 129 | 0.5 | Mongla | 133 | 0.20833 | 121 | 0.375
Tongi | 139 | 0.16667 | 130 | 0.45833 | Satkhira | 137 | 0.041667 | 124 | 0.77083
Kabirpur | 136 | 0.125 | 129 | 0.41667 | Gallamari | 137 | 0.25 | 128 | 0.375
Basundhara | 137 | 1:00 | 129 | 0.45833 | Magura | 135 | 0.125 | 120 | 0.77083
Manikganj | 140 | 1:00 | 131 | 0.45833 | Norail | 134 | 0.20833 | 118 | 0.75
Joydevpur | 140 | 0.041667 | 135 | 0.41667 | Chuadanga | 132 | 0.25 | 117 | 0.77083
New Tongi | 137 | 0.041667 | 129 | 0.5 | Barisal(N) | 138 | 0.16667 | 126 | 0.41667
Kodda | 135 | 0.25 | 122 | 0.5 | Barisal (S) | 135 | 0.083333 | 127 | 0.33333
Dhamrai | 134 | 0.16667 | 129 | 0.45833 | Patuakhali | 135 | 0.20833 | 126 | 0.5
Valuka | 132 | 0.91667 | 125 | 0.45833 | Bhandaria | 136 | 0.91667 | 125 | 0.33333
Tangail | 134 | 0.041667 | 130 | 0.45833 | Ishurdi | 137 | 0.083333 | 131 | 0.75
Mymensing | 133 | 0.91667 | 127 | 0.45833 | Ruppur Paromanobik | 136 | 0.083333 | 130 | 0.79167
Kishorganj | 132 | 0.20833 | 128 | 0.45833 | Natore | 136 | 0.083333 | 128 | 0.54167
Netrokona | 131 | 0.625 | 126 | 0.45833 | Bogra | 138 | 0.125 | 131 | 0.33333
Jamalpur | 139 | 0.77083 | 125 | 0.95833 | Noagaon | 135 | 0.16667 | 128 | 0.33333
Sherpur | 138 | 0.79167 | 125 | 0.45833 | Rajshahi | 134 | 0.25 | 125 | 0.5
Srimongal | 137 | 0.95833 | 135 | 0.29167 | Rajshahi New | 133 | 0.083333 | 123 | 0.54167
Shahjibazar | 136 | 0.16667 | 132 | 0.45833 | C.Nawabganj | 132 | 0.083333 | 122 | 0.375
Fenchuganj | 137 | 0.95833 | 133 | 0.70833 | Amnura | 132 | 0.25 | 122 | 0.375
Khulawara | 136 | 0.20833 | 134 | 17:00 | Pabna | 139 | 0.125 | 131 | 0.77083
Sylhet | 135 | 0.041667 | 133 | 0.70833 | Shahjadpur | 142 | 0.083333 | 137 | 0.75
Chatak | 135 | 0.041667 | 132 | 0.625 | Serajganj | 138 | 0.125 | 130 | 0.5
Sunamganj | 135 | 0.29167 | 132 | 0.041667 | Niyamatpur | 135 | 0.125 | 126 | 0.54167
Biani Bazar | 135 | 0.91667 | 132 | 0.70833 | Joypurhat | 136 | 0.25 | 127 | 0.375
Comilla(s) | 131 | 0.16667 | 127 | 0.375 | Sherpur(Bogura) | 141 | 0.16667 | 131 | 0.375
Comilla(n) | 139 | 0.375 | 135 | 0.41667 | Mohastangor | 136 | 0.16667 | 130 | 0.375
Chandpur | 135 | 7:00 | 132 | 0.79167 | Rangpur | 130 | 0.16667 | 124 | 0.375
Feni | 133 | 0.29167 | 127 | 0.8125 | Lalmonirhat | 126 | 0.16667 | 120 | 0.5
Chowmuhani | 130 | 0.29167 | 124 | 0.8125 | Saidpur | 130 | 0.25 | 123 | 0.375
Ashuganj | 135 | 0.041667 | 132 | 0.41667 | Purbasadipur | 128 | 0.16667 | 118 | 0.83333
Daudkandi | 137 | 0.95833 | 132 | 0.5 | Thakurgaon | 126 | 0.20833 | 118 | 0.5
B.Baria | 132 | 0.91667 | 129 | 0.75 | Palashbari | 132 | 0.20833 | 125 | 0.375
Ramganj | 130 | 0.66667 | 126 | 0.91667 | Barapukuria | 131 | 0.125 | 126 | 0.83333
Chaddagram | 134 | 0.79167 | 131 | 0.83333 | Panchagar | 124 | 0.16667 | 112 | 0.41667
PHP | 133 | 0.33333 | 128 | 0.79167 | Joldhaka | 129 | 0.25 | 120 | 0.83333
Madanhat | 135 | 0.33333 | 132 | 0.5 | Kurigram | 131 | 0.25 | 119 | 0.83333
Hathazari | 133 | 0.75 | 131 | 0.041667
Khulshi | 131 | 0.75 | 127 | 0.45833

## L-Curve
Date | 2019-12-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 175 | 4524 | 1641 | 6165 |  |  |  | QF-LDC-12
0:30 | 251 | 4527.5 | 1527 | 6054.5 | Date: | 2019-12-18
1:00 | 327 | 4531 | 1413 | 5944
1:30 | 288.5 | 4351 | 1439 | 5790
2:00 | 250 | 4171 | 1465 | 5636
2:30 | 235 | 4025 | 1479.5 | 5504.5 | [5 empty] | Gen. at Eve. Peak | 8479 | 8479 MW (19:00 )
3:00 | 220 | 3879 | 1494 | 5373 | [6 empty] | 19:00
3:30 | 190 | 3790.5 | 1487 | 5277.5 | [5 empty] | Gen. at Day Peak | 6644.1 | 6644.1 MW (12:00 )
4:00 | 160 | 3702 | 1480 | 5182 | [6 empty] | 12:00
4:30 | 80 | 3673 | 1507.5 | 5180.5 | [5 empty] | Highest Generation | 8479
5:00 | 0 | 3644 | 1535 | 5179 | [6 empty] | 19:00
5:30 | 30.5 | 3768 | 1544.5 | 5312.5
6:00 | 61 | 3892 | 1554 | 5446
6:30 | 104.5 | 4025.272 | 1573.05 | 5598.322
7:00 | 148 | 4158.544 | 1592.1 | 5750.644
7:30 | 234 | 4356.622 | 1600.6 | 5957.222
8:00 | 320 | 4554.7 | 1609.1 | 6163.8
8:30 | 219 | 4599.89 | 1680.75 | 6280.64
9:00 | 118 | 4645.08 | 1752.4 | 6397.48
9:30 | 86 | 4617.99 | 1786.4 | 6404.39
10:00 | 54 | 4590.9 | 1820.4 | 6411.3
10:30 | 66 | 4600.015 | 1836.95 | 6436.965
11:00 | 78 | 4609.13 | 1853.5 | 6462.63
11:30 | 46.5 | 4683.815 | 1869.55 | 6553.365
12:00 | 15 | 4758.5 | 1885.6 | 6644.1
12:30 | 83 | 4852.85 | 1881.15 | 6734
13:00 | 151 | 4947.2 | 1876.7 | 6823.9
13:30 | 130.5 | 4909.565 | 1804.95 | 6714.515
14:00 | 110 | 4871.93 | 1733.2 | 6605.13
14:30 | 79.5 | 4884.62 | 1701.5 | 6586.12
15:00 | 49 | 4897.31 | 1669.8 | 6567.11
15:30 | 35.5 | 4856.621 | 1679.45 | 6536.071
16:00 | 22 | 4815.932 | 1689.1 | 6505.032
16:30 | 27 | 4830.966 | 1794.1 | 6625.066
17:00 | 32 | 4846 | 1899.1 | 6745.1
17:30 | 97.5 | 5302.5 | 2157.55 | 7460.05
18:00 | 163 | 5759 | 2416 | 8175
18:30 | 174 | 5866 | 2461 | 8327
19:00 | 185 | 5973 | 2506 | 8479
19:30 | 211 | 5816 | 2440 | 8256
20:00 | 201 | 5783 | 2435 | 8218 |  |  |  | Executive Engineer
20:30 | 176 | 5654 | 2399 | 8053 |  |  |  | Network Operation Division
21:00 | 151 | 5525 | 2363 | 7888
21:30 | 92.5 | 5343 | 2260 | 7603
22:00 | 34 | 5161 | 2157 | 7318 |  |  |  |  | Page 6 of 7
22:30 | 111 | 4962.5 | 1982 | 6944.5
23:00 | 188 | 4764 | 1807 | 6571
23:30 | 181.5 | 4644 | 1724 | 6368
24:00 | 175 | 4524 | 1641 | 6165
8479 MW (19:00 )
6644.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-18 |  | Energy | 159121795
[10 empty] | 2019-12-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3849 | 201 | 1632 | 173 | 260 | 82 | 4 | 0 | 74
0:30 | 3888.5 | 169 | 1546 | 86.5 | 260 | 82.5 | 4 | 0 | 73 | Date: | 2019-12-18
1:00 | 3928 | 137 | 1460 | 0 | 260 | 83 | 4 | 0 | 72
1:30 | 3823 | 137 | 1413.5 | 0 | 260 | 82.5 | 4 | 0 | 70 | [7 empty] | Total Energy | 159.1218 | Total Energy Gen 159.122 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.122 MKWHr
2:00 | 3718 | 137 | 1367 | 0 | 260 | 82 | 4 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 3580 | 137 | 1374.5 | 0 | 260 | 82 | 4 | 0 | 67 | [7 empty] | Energy Requirement | 159.1218
3:00 | 3442 | 137 | 1382 | 0 | 260 | 82 | 4 | 0 | 66
3:30 | 3439.5 | 137 | 1290 | 0 | 260 | 82 | 4 | 0 | 65 | [6 empty] | Shortage
4:00 | 3437 | 137 | 1198 | 0 | 260 | 82 | 4 | 0 | 64
4:30 | 3434 | 137 | 1199 | 0 | 260 | 82.5 | 4 | 0 | 64
5:00 | 3431 | 137 | 1200 | 0 | 260 | 83 | 4 | 0 | 64
5:30 | 3458.5 | 136.5 | 1305.5 | 0 | 260 | 83 | 4 | 0 | 65
6:00 | 3486 | 136 | 1411 | 0 | 260 | 83 | 4 | 0 | 66
6:30 | 3558 | 136 | 1491.5 | 0 | 260 | 83 | 4 | 0 | 65 |  |  |  |  | Coal
7:00 | 3630 | 136 | 1572 | 0 | 260 | 83 | 4 | 0 | 64
7:30 | 3698 | 136 | 1641 | 61.5 | 260 | 83 | 4 | 0 | 69 |  |  |  | Oil |  |  |  | ,
8:00 | 3766 | 136 | 1710 | 123 | 260 | 83 | 4 | 0 | 74
8:30 | 3736.5 | 217.5 | 1728.5 | 164.5 | 260 | 82.5 | 4 | 0 | 76
9:00 | 3707 | 299 | 1747 | 206 | 260 | 82 | 4 | 0 | 78
9:30 | 3711.5 | 299 | 1742.5 | 209.5 | 260 | 82 | 4 | 0 | 79
10:00 | 3716 | 299 | 1738 | 213 | 260 | 82 | 4 | 0 | 80
10:30 | 3696 | 299 | 1781 | 214 | 260 | 82 | 4 | 0 | 80
11:00 | 3676 | 299 | 1824 | 215 | 260 | 82 | 4 | 0 | 80
11:30 | 3708 | 299 | 1874.5 | 222.5 | 260 | 82.5 | 4 | 0 | 80
12:00 | 3740 | 299 | 1925 | 230 | 260 | 83 | 4 | 0 | 80
12:30 | 3735 | 299 | 1941.5 | 309 | 260 | 83.5 | 4 | 0 | 79
13:00 | 3730 | 299 | 1958 | 388 | 260 | 84 | 4 | 0 | 78
13:30 | 3730 | 299 | 1958 | 388 | 260 | 84 | 4 | 0 | 78
14:00 | 3730 | 299 | 1958 | 388 | 260 | 84 | 4 | 0 | 78
14:30 | 3743 | 299 | 1826 | 381.5 | 260 | 82 | 4.5 | 0 | 81
15:00 | 3756 | 299 | 1694 | 375 | 260 | 80 | 5 | 0 | 84
15:30 | 3750.5 | 298 | 1674.5 | 376.5 | 260 | 80 | 5.5 | 0 | 81
16:00 | 3745 | 297 | 1655 | 378 | 260 | 80 | 6 | 0 | 78
16:30 | 3713 | 370 | 1672.5 | 431 | 260 | 81 | 11.5 | 0 | 83
17:00 | 3681 | 443 | 1690 | 484 | 260 | 82 | 17 | 0 | 88
17:30 | 3733.5 | 541 | 1733.5 | 995.5 | 260 | 82.5 | 19 | 0 | 95
18:00 | 3786 | 639 | 1777 | 1507 | 260 | 83 | 21 | 0 | 102
18:30 | 3905 | 639 | 1801.5 | 1508 | 260 | 83 | 29.5 | 0 | 101
19:00 | 4024 | 639 | 1826 | 1509 | 260 | 83 | 38 | 0 | 100
19:30 | 4108 | 640 | 1852 | 1162 | 260 | 82 | 52 | 0 | 100
20:00 | 4062 | 640 | 1858 | 1163 | 260 | 81 | 52 | 0 | 102
20:30 | 4011 | 640.5 | 1864 | 1045.5 | 260 | 81 | 52 | 0 | 99
21:00 | 3960 | 641 | 1870 | 928 | 260 | 81 | 52 | 0 | 96
21:30 | 3887.5 | 591 | 1858 | 794 | 260 | 81 | 40.5 | 0 | 91
22:00 | 3815 | 541 | 1846 | 660 | 260 | 81 | 29 | 0 | 86
22:30 | 3790 | 420 | 1876 | 416.5 | 260 | 81.5 | 16.5 | 0 | 84
23:00 | 3765 | 299 | 1906 | 173 | 260 | 82 | 4 | 0 | 82
23:30 | 3807 | 250 | 1769 | 173 | 260 | 82 | 4 | 0 | 78 | Max Temp. in Dhaka |  | 20° C
24:00 | 3849 | 201 | 1632 | 173 | 260 | 82 | 4 | 0 | 74
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 159.122 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.122 MKWHr
Note on W13: Author:

## Generation
2019-12-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 43 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 43 | 44 | 82 | 40 | 40 | 42 | 43 |  | 43 | 42 | 41 | 41 | 41 | 42 | 42 | 977869
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2 | 0 | 50 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 180 | 180 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2600000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1.31 | 6.5 | 11.48 | 15.4 | 17.83 | 18.1 | 17 | 14 | 9 | 4 | 0 | [9 empty] | 116640
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 214 | 204 | 203 | 184 | 186 | 192 | 216 | 216 | 202 | 203 | 209 | 205 | 205 | 204 | 177 | 178 | 204 |  | 208 | 215 | 211 | 203 | 203 | 204 | 206 | 4810837
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 136 | 137 | 105 | 106 | 107 | 105 | 110 | 105 | 105 | 110 | 105 | 145 | 145 | 103 | 103 | 105 | 105 | 151 |  | 144 | 154 | 144 | 145 | 145 | 145 | 147 | 2939216
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 13 | 17 |  | 2 | 0 | [5 empty] | 34833
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 3 | 17 |  | 17 | 17 | 17 |  |  |  |  | 67745
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 100 | 42 | 100 | 67 | 67 | 67 | 42 | 42 | 42 | 42 | 42 | 42 | 87 | 62 | 60 | 40 | 35 | 42 |  | 42 | 65 | 65 | 65 | 62 | 65 | 40 | 1538000
17 | Siddhirganj 335 MW CCPP | 320 | 240 | 280 | 280 | 280 | 300 | 300 | 352 | 351 | 352 | 358 | 349 | 270 | 270 | 270 | 270 | 270 | 270 |  | 357 | 354 | 355 | 350 | 359 | 360 | 365 | 7702285
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 8 |  | 0 | [6 empty] | 12545
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 75 | 112 | 141 | 187 | 187 | 187 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 112 | 2810181
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 775000
21 | Ghorasal Repowered CCPP Unit-3 | 99 | 99 | 99 | 99 | 99 | 95 | 90 | 90 | 90 | 94 | 94 | 98 | 114 | 112 | 112 | 112 | 112 | 112 |  | 113 | 113 | 110 | 117 | 117 | 117 | 115 | 2661200
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 3015230
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 0 | [14 empty] | 831494
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 36 | 36 | 33 | 841320
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 360 | 355 | 320 | 320 | 320 | 325 | 360 | 345 | 320 | 330 | 320 | 330 | 320 | 320 | 320 | 320 | 320 | 320 |  | 345 | 345 | 340 | 320 | 320 | 320 | 320 | 8185500
| Ashuganj 450 MW CCPP(North) | 358 | 345 | 0 | [6 empty] | 10 | 40 | 45 | 75 | 145 | 240 | 365 | 365 | 365 |  | 350 | 360 | 350 | 330 | 330 | 330 | 330 | 4527200
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 304 | 304 | 304 | 304 | 304 | 304 | 309 | 307 | 304 | 305 | 302 | 301 | 300 | 265 | 256 | 239 | 256 | 250 |  | 244 | 257 | 264 | 244 | 117 | 104 | 301 | 6609480
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 360 | 400 | 400 | 400 | 400 | 400 | 450 | 450 | 400 | 400 | 400 | 450 | 450 | 400 | 400 | 400 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 390 | 9237000
41 | Haripur 360MW CCPP(HPL) | 370 | 370 | 370 | 300 | 260 | 300 | 300 | 300 | 311 | 312 | 364 | 354 | 323 | 282 | 282 | 282 | 312 | 312 |  | 291 | 282 | 285 | 284 | 295 | 316 | 314 | 7516000
42 | RPCL 210MW CCPP | 158 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 160 | 160 | 159 | 144 | 144 | 130 | 132 | 129 | 129 | 130 |  | 129 | 129 | 130 | 128 | 114 | 114 | 132 | 3366200
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 59 | 60 | 60 | 58 | 57 | 60 | 60 | 58 | 59 |  | 60 | 60 | 59 | 58 | 60 | 60 | 58 | 1418000
45 | Fenchugonj CCPP Phase-2 | 90 | 90 | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2134920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 68 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 53 | 52 | 52 | 51 | 52 | 51 | 51 | 40 | 40 | 52 |  | 52 | 52 | 52 | 53 | 53 | 53 | 53 | 1188192
48 | Shahjibazar 86MW PP (Shahjibazar) | 40 | 40 | 20 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 76 | 79 | 79 | 76 | 40 | 40 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1222080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 19 | 17 | 17 | 17 | 318000
52 | Sylhet 50MW PP (EPL) | 8 | 8 | 8 | 8 | 8 | 30 | 30 | 30 | 29 | 29 | 32 | 32 | 35 | 37 | 36 | 35 | 39 | 44 |  | 40 | 40 | 38 | 40 | 41 | 40 | 40 | 693800
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 162000
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 | [5 empty] | 11 | 11 | 0 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 159312
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 45 | 45 | 45 | 45 | 44 | 47 | 47 | 47 | 14 | 14 | 41 |  | 44 | 47 | 47 | 47 | 47 | 47 | 45 | 781200
56 | Shahjahanulla 25 MW PP | 23 | 0 | [5 empty] | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 386472
57 | Bibiana-II 341 MW CCPP (Summit)
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 0 |  | 0 | 14 | 18 | 18 | 18 | 16 | 16 | 16 | 18 | 18 | 19 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 355776
61 | Narshingdi 22 MW PP (Doreen) | 0 | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 292068
62 | Tangail 22 MW PP (Doreen) | 20 | 0 |  |  | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 376992
63 | Impoprt (Tripura) | 72 | 68 | 66 | 64 | 64 | 66 | 64 | 74 | 78 | 80 | 80 | 80 | 78 | 84 | 84 | 78 | 88 | 102 |  | 100 | 100 | 102 | 96 | 86 | 82 | 74 | 1907520
64 | Malancha, Ctg. EPZ (United) | 40 | 7 | 6 | 5 | 6 | 17 | 8 | 12 | 5 | 4 | 3 | 6 | 14 | 10 | 5 | 7 | 7 | 5 |  | 21 | 22 | 27 | 35 | 38 | 41 | 42 | 455520
65 | Feni 22MW PP (Doreen) | 22 | 0 |  |  | 0 | 14 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 404352
66 | Feni 11 MW PP (Doreen) | 11 | 0 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 160560
67 | Jangalia 33MW PP (Summit) | 0 |  |  |  |  | 0 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 458000
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 363710
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 30 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 713340
71 | Maona 33 MW PP(Summit) | 33 | 0 | 25 | 25 | 25 | 0 | 25 | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 736700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 23 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803200
73 | Ghorashal 108MW PP (Regent) | 7 | 7 | 6 | 6 | 6 | 31 | 32 | 32 | 32 | 32 | 32 | 104 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 14 | 1539954
| Feni Lanka Power | [16 empty] | 0 | 37 |  | 17 | [6 empty] | 86640
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 45 |  | 70 | 7 | [5 empty] | 126691
78 | Gazipur 52 MW PP | [16 empty] | 0 | 34 |  | 45 | 25 | 25 |  |  |  |  | 120396
79 | Kodda 150MW PP | [19 empty] | 32 | 48 | 48 | 48 | 25 |  |  | 136320
80 | Jamalpur 95 MW PP(Powerpac) | 0 | [7 empty] | 5 | 8 | 8 | 23 | 47 | 65 | 65 | 65 | 70 | 94 |  | 94 | 94 | 94 | 94 | 94 | 9 | 0 | 906240
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [7 empty] | 12 | 35 | 35 | 35 | 35 | 105 | 70 | 69 | 69 | 80 | 105 |  | 70 | 70 | 70 | 70 | 17 |  |  | 870828
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.234 | 1.1 | 2.4 | 3.3 | 3.9 | 4 | 3.7 | 2.93 | 1.91 | 0.732 | [10 empty] | 23400
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 20 |  | 0 | [6 empty] | 42768
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 5 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 9 | 60 |  | 75 | 50 | 50 | 50 | 10 |  |  | 336960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 47 | 5 | 5 | 8 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 47 | 44 | 44 | 44 |  | 47 | 47 | 47 | 47 | 50 | 50 |  | 969408
93 | Ashuganj 51 MW PP (Midland) | 43 | 5 | 5 | 5 | 5 | 8 | 20 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 876628
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 68 |  | 93 | 93 | 93 | 93 | 16 | 0 |  | 486720
95 | Patenga 50MW PP (Baraka) | [7 empty] | 6 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 50 |  | 50 | 17 | 25 |  |  |  |  | 313440
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 0 | 40 |  | 52 | [6 empty] | 97920
97 | Katpotti 52 MW PP (Sinha) | [16 empty] | 0 | 36 |  | 47 | 12 | 12 |  |  |  |  | 115104
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 15 |  | 0 | [6 empty] | 23036
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 5 | 25 |  | 17 | [6 empty] | 55282
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 100 |  | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 3100671
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 |  | 0.4 | 0.2 | [10 empty] | 2950
103 | Kamalaghat 54 MW PP(Banco Energy) | 0 | [6 empty] | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 17 |  | 849240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 3 | 7 |  | 7 | [6 empty] | 21600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 30 | 100 |  | 100 | 100 | 100 | 70 | 40 | 0 |  | 419520
116 | Chandpur 200MW (Desh energy) | [17 empty] | 17 |  | 0 | [6 empty] | 26400
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 0 | 10 |  | 5 | [6 empty] | 25090
118 | Bibiyana-III 400 MW CCPP | 397 | 383 | 362 | 362 | 361 | 362 | 393 | 395 | 366 | 352 | 367 | 388 | 361 | 366 | 366 | 328 | 278 | 291 |  | 377 | 392 | 375 | 363 | 363 | 363 | 363 | 8811000
| Jamalpur 115 MW PP (United) | [16 empty] | 0 | 71 |  | 115 | 115 | 115 | 40 | 40 |  |  | 456000
| Anwara 300 MW PP (United) | 0 | [6 empty] | 50 | 83 | 84 | 86 | 86 | 150 | 156 | 155 | 158 | 158 | 212 |  | 212 | 216 | 216 | 216 | 203 | 68 |  | 2318400
120 | Eastern Zone Total | 4531 | 4171 | 3879 | 3702 | 3644 | 3892 | 4158.544 | 4554.7 | 4645.08 | 4590.9 | 4609.13 | 4758.5 | 4947.2 | 4871.93 | 4897.31 | 4815.932 | 4846 | 5759 |  | 5973 | 5816 | 5783 | 5525 | 5161 | 4764 | 4524 | 114198095
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 12 | 40 |  | 32 | 32 | 32 | 16 | 0 |  |  | 130560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | 0 | [15 empty] | 9 | 74 |  | 110 | 110 | 110 | 110 | 114 | 64 | 48 | 638688
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 54 | 51 | 53 | 55 | 57 |  | 56 | 60 | 60 | 54 | 50 | 53 | 52 | 1478000
140 | Bhola 33 MW PP (Venture) | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 7 | 10 | 10 | 10 | 9 | 8 | 8 | 8 | 7 |  | 7 | 6 | 7 | 9 | 8 | 6 | 7 | 504051
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 0 |  | 63750
143 | Gopalganj 100 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 88320
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 15 | 50 |  | 50 | 50 | 50 | 50 | 32 | 15 | 15 | 294480
146 | Bheramara HVDC | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 136 | 299 | 299 | 299 | 299 | 299 | 299 | 299 | 297 | 443 | 639 |  | 639 | 640 | 640 | 641 | 541 | 299 | 201 | 7605818
147 | Bheramara 360 MW CCPP | 160 | 200 | 228 | 246 | 268 | 280 | 310 | 300 | 290 | 280 | 260 | 295 | 280 | 240 | 240 | 240 | 240 | 240 |  | 240 | 235 | 230 | 215 | 220 | 220 | 220 | 5987808
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6268600
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1190000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 178 | 180 | 179 | 181 | 175 | 173 | 169 | 174 | 178 | 205 | 205 | 203 | 205 | 178 | 178 | 168 | 180 | 179 |  | 196 | 200 | 202 | 196 | 188 | 174 | 178 | 4714264
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 179 | 181 | 186 | 178 | 176 | 176 | 172 | 172 | 170 | 180 | 201 | 202 | 211 | 198 | 184 | 182 | 190 | 171 |  | 206 | 212 | 210 | 212 | 210 | 184 | 179 | 4779673
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 372 | 371 | 368 | 342 | 383 | 393 | 395 | 395 | 384 | 426 | 455 | 453 | 447 | 395 | 347 | 379 | 380 | 379 |  | 431 | 433 | 432 | 433 | 392 | 431 | 416 | 9667945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 361680
163 | Bogura 20 MW PP (Energyprima) | 0 |  |  |  |  | 0 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 |  | 247788
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 221598
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 50 | 25 |  |  | 214610
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 0 | 60 |  | 72 | 35 | 35 | 0 |  |  |  | 240864
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 8 | 109 |  | 40 | 0 | [5 empty] | 216000
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0.1 | 0.1 | 0.4 | 0.4 | 0.5 | 0.6 | 1.7 | 2.2 | 2.8 | 1.1 | 0.1 | 0 | [8 empty] | 9203
178
178