## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-21 | Saturday
|  | Date (day): | 2019-12-21 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11014.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14070 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-20 | 2019-12-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 101 | 100 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 110 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 335 | 320 | 360 |  | 139
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 308 | 370 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 60 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 45 | 74 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 292 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 93 | 93 |  | 9 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 55 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 24 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1565 | 2065 | 3488 | 4177 | 598 | 967
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 82 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 189 | 179 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 116 | 109 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 51 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 70 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 25 | 40 | 14 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 2 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.3 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 104 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 691.8 | 962 | 1589 | 1790 | 270 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 125 | 125
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 295 | 335 | 360 |  | 120
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 285 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 33 | 37 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 54 | 167 | 150 | 185
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 40 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 80 | 0 | 0 |  | 163 | under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 90 | 90 | 105
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1051 | 1199 | 1476 | 2065 | 134 | 704
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 157 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 94 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.3 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 30 | 100 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 156.3 | 301 | 468.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 89 | 89 | 85 | 89
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 90 | 135 |  | 330 | GT-2 Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 45 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 57 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 79 | 79 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 28 | 38 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint. |  | 28/12/2019
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 319 | 300 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 847 | 943 | 1140 | 1189 | 0 | 830
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 176 | 443 | 203 | 649
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 13 | 4 | 30 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 275 | 255 | 300 | 300 |  | 110 | ST under maint
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 32 | 32 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 464 | 734 | 735 | 1744 | 0 | 110
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 80 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 5 | 9 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 60 | 65 |  | 130 | GT-1 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 150 | 184 | 245 | 320 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 18 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 198 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage.
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 182 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 306 | 445 | 400 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 14 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 25 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 721 | 979 | 1502 | 1796 | 341 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 250 | 260
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 50 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 181.2 | 230 | 371 | 407 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 5827.3 | 7597 | 11014.6 | 14070 | 1395 | 3032
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5475.9898 | 7139 | 10350.5633 | 13221.7625
A. |  | 2019-12-20 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 7597 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 5075 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7597 | MW
3 | Day peak Generation : |  |  | 5827.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7139 | MW
4 | Evening peak Generation : |  |  | 7597 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 144.1824 | MKWHr | By Solar | 0.14941 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 124.4172 | MKWHr |  | By Oil: | 6.3261 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.4406 | MKWHr |  | By Hydro: | 1.9334 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1395 | MW | Dhaka | 2384 | 2384 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3032 | MW | Chittagong | 785 | 785 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4427 | MW | Khulna | 908 | 908 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 995.34 | MMCFD |  |  | Rajshahi | 745 | 745 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 120164666.084 | ii) Oil : | Taka | 59481605.65 | Comilla | 671 | 671 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 18162054 | Total | Taka | 197808325.734 | Mymensingh | 601 | 601 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.704 | MKWHr. | Sylhet | 293 | 293 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -420 | MW (E to W) at | 20:00 | hrs | Barisal | 227 | 227 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -443 | MW at | 18:30 | hrs | Rangpur | 525 | 525 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 17.3° C |  |  | Total | 7139 | 7139 |  | 0
B. |  | 2019-12-21 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 23.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14070 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve(Generation end) |  |  |  | 5570 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 161.3204 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4596 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 5.228 | MKWHr. | ii) HVDC Flow at Peak Time |  | 443 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6877 | MKWHr. | iii) Maximum HVDC Flow : |  | 443 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.2 |  | (b) Today: | 97.05 |  | (c) Rule Curve: |  | 104.1
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4(gas) | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 355 | 314 |  | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 80 | 0 | 0 | 345 | 295 | 0 | 112 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 0 | 20 | 66 | 112 | 0 | 0 | 0 | 60 | 89 | 2 | 50 | 163 | 0 | 57 | 10 | 0 | 0 | 0 | 36 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 169 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 190 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4319 | 1463 | 5782 | 3608 | 169 | 1647 | 16 | 190 | 82 | 4 | 66 | 0 | 0 | 97.22
2:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 355 | 352 |  | 0 | 450 | 0 | 0 | 0 | 0 | 250 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 204 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 355 | 305 | 0 | 8 | 0 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 131 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 163 | 0 | 45 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 184 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4127 | 1373 | 5500 | 3594 | 133 | 1439 | 0 | 184 | 82 | 4 | 64 | 0 | 0 | 97.22
3:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 354 | 368 |  | 0 | 400 | 0 | 0 | 0 | 0 | 250 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 350 | 285 | 0 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 131 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 130 | 0 | 45 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 132 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3953 | 1297 | 5250 | 3473 | 132 | 1315 | 0 | 180 | 82 | 4 | 64 | 0 | 0 | 97.21
4:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 353 | 303 |  | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 184 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 290 | 290 | 0 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 147 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 130 | 0 | 45 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3766 | 1318 | 5084 | 3438 | 133 | 1187 | 0 | 180 | 82 | 4 | 60 | 0 | 0 | 97.21
5:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 357 | 288 |  | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 193 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 290 | 300 | 0 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 62 | 159 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 100 | 0 | 45 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3740 | 1335 | 5075 | 3511 | 133 | 1103 | 0 | 180 | 82 | 4 | 62 | 0 | 0 | 97.2
6:00 | 35 | 0 | 102 | 0 | 0 | 0 | 0 | 365 | 320 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 201 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 280 | 300 | 0 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 62 | 157 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 100 | 0 | 45 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3815 | 1345 | 5160 | 3513 | 133 | 1186 | 0 | 180 | 82 | 4 | 62 | 0 | 0 | 97.2
7:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 356 | 320 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 207 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 280 | 290 | 0 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 158 | 0 | 0 | 0 | 60 | 89 | 2 | 3 | 100 | 0 | 45 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0.162 | 0 | 0 | 0 | 0 |  | 132 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 3794.562 | 1441.1 | 5235.662 | 3571 | 132 | 1182 | 24 | 180 | 82 | 4 | 60 | 0.662 | 0 | 97.19
8:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 362 | 374 |  | 0 | 350 | 0 | 0 | 0 | 0 | 275 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 215 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21 | 80 | 0 | 0 | 280 | 295 | 0 | 8 | 0 | 13 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 158 | 0 | 0 | 0.1 | 60 | 89 | 2 | 5 | 130 | 0 | 45 | 5 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 132 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 371 | 0 | 0 | 0 | 32 | 0 | 0 | 0.2 | 0 |  | 4000.2 | 1498.2 | 5498.4 | 3671 | 132 | 1284 | 82 | 180 | 82 | 4 | 60 | 3.4 | 0 | 97.19
9:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 356 | 377 |  | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 28 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 28 | 80 | 0 | 0 | 260 | 275 | 0 | 8 | 0 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 66 | 159 | 0 | 0 | 0.1 | 60 | 89 | 39 | 50 | 130 | 0 | 58 | 76 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.66 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 |  | 132 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 5 | 8 | 0 | 0 | 50 | 0 | 0 | 15 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 347 | 0 | 0 | 0 | 54 | 0 | 0 | 0.7 | 0 |  | 4156.46 | 1522.7 | 5679.16 | 3655 | 132 | 1422 | 112 | 180 | 82 | 19 | 66 | 11.16 | 0 | 97.18
10:00 | 35 | 0 | 100 | 0 | 0 | 0 | 0 | 354 | 377 |  | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 25 | 31 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 196 | 0 | 119 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 26 | 80 | 0 | 0 | 300 | 310 | 0 | 8 | 0 | 33 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 66 | 158 | 0 | 0 | 0.2 | 60 | 89 | 39 | 50 | 100 | 0 | 57 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.64 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 |  | 132 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 65 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4137.64 | 1445.1 | 5582.74 | 3586 | 132 | 1364 | 130 | 180 | 81 | 24 | 66 | 19.74 | 0 | 97.18
11:00 | 35 | 0 | 101 | 0 | 0 | 52 | 0 | 369 | 326 |  | 0 | 320 | 0 | 0 | 0 | 0 | 285 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 25 | 28 | 0 | 0 | 40 | 40 | 120 | 120 | 0 | 176 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 80 | 0 | 0 | 265 | 280 | 0 | 54 | 0 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 68 | 160 | 0 | 0 | 0.4 | 60 | 89 | 42 | 50 | 100 | 0 | 57 | 76 | 0 | 0 | 17 | 22 | 10 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.93 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 |  | 131 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 62 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 |  | 4172.73 | 1444.7 | 5617.43 | 3556 | 131 | 1415 | 130 | 180 | 80 | 32 | 68 | 25.43 | 0 | 97.17
12:00 | 35 | 0 | 101 | 0 | 0 | 52 | 0 | 368 | 308 |  | 0 | 320 | 0 | 0 | 0 | 0 | 270 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 0 | 28 | 0 | 0 | 40 | 40 | 120 | 120 | 0 | 189 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 80 | 0 | 0 | 335 | 350 | 0 | 54 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 72 | 156 | 0 | 0 | 0.3 | 60 | 89 | 44 | 47 | 100 | 0 | 58 | 40 | 0 | 0 | 17 | 28 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.5 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 176 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 65 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4311.1 | 1516.2 | 5827.3 | 3714 | 176 | 1412 | 130 | 180 | 80 | 38 | 72 | 25.3 | 0 | 97.17
13:00 | 35 | 0 | 104 | 0 | 0 | 52 | 0 | 369 | 338 |  | 0 | 320 | 0 | 0 | 0 | 0 | 300 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 12 | 0 | 28 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 177 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 80 | 0 | 0 | 275 | 295 | 0 | 54 | 0 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 15 | 12 | 74 | 157 | 0 | 0 | 0.7 | 60 | 89 | 17 | 10 | 100 | 0 | 57 | 40 | 0 | 0 | 17 | 33 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 176 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 65 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 |  | 4199.8 | 1653.3 | 5853.1 | 3721 | 176 | 1435 | 130 | 180 | 81 | 32 | 74 | 24.1 | 0 | 97.16
14:00 | 35 | 0 | 104 | 0 | 0 | 12 | 0 | 330 | 308 |  | 0 | 300 | 0 | 0 | 0 | 0 | 270 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 12 | 0 | 28 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 177 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 80 | 0 | 0 | 280 | 285 | 0 | 8 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 8 | 12 | 68 | 111 | 0 | 0 | 0.5 | 60 | 89 | 11 | 10 | 100 | 0 | 45 | 10 | 0 | 0 | 17 | 36 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 |  | 173 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 65 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 180 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 |  | 3779.2 | 1621.3 | 5400.5 | 3478 | 173 | 1239 | 130 | 180 | 81 | 32 | 68 | 19.5 | 0 | 97.16
15:00 | 35 | 0 | 100 | 0 | 0 | 12 | 0 | 300 | 309 |  | 0 | 300 | 0 | 0 | 0 | 0 | 270 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 11 | 0 | 28 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 177 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 41 | 80 | 0 | 0 | 270 | 275 | 0 | 8 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 8 | 10 | 64 | 111 | 0 | 0 | 0.2 | 60 | 89 | 11 | 10 | 100 | 0 | 45 | 10 | 0 | 0 | 17 | 36 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 0 |  | 172 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 50 | 5 | 64 | 0 | 0 | 50 | 0 | 0 | 8 | 50 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 179 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 |  | 3711.7 | 1500.8 | 5212.5 | 3338 | 172 | 1236 | 114 | 179 | 81 | 15 | 64 | 13.5 | 0 | 97.15
16:00 | 35 | 0 | 100 | 0 | 0 | 12 | 0 | 300 | 310 |  | 0 | 300 | 0 | 0 | 0 | 0 | 270 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 11 | 0 | 31 | 0 | 0 | 41 | 40 | 120 | 120 | 0 | 179 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 31 | 80 | 0 | 0 | 280 | 280 | 0 | 8 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 0 | 21 | 11 | 8 | 15 | 62 | 111 | 0 | 0 | 0.1 | 60 | 89 | 11 | 10 | 100 | 0 | 45 | 10 | 0 | 0 | 17 | 35 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 |  | 172 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 50 | 5 | 48 | 0 | 0 | 50 | 0 | 0 | 8 | 50 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 0 | 0 | 180 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 |  | 3718.4 | 1487.2 | 5205.6 | 3367 | 172 | 1227 | 98 | 180 | 81 | 12 | 62 | 6.6 | 0 | 97.15
17:00 | 35 | 0 | 100 | 0 | 0 | 12 | 0 | 300 | 331 |  | 0 | 330 | 0 | 1 | 0 | 0 | 270 | 0 | 65 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 25 | 11 | 15 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 191 | 0 | 109 | 0 |  | 0 | 0 | 4 | 0 | 0 | 1 | 18 | 34 | 80 | 0 | 0 | 280 | 325 | 0 | 8 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 0 | 19 | 11 | 8 | 15 | 70 | 111 | 3 | 0 | 0 | 60 | 89 | 11 | 10 | 100 | 0 | 45 | 10 | 0 | 0 | 17 | 37 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0 | 0 | 334 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 172 | 0 | 200 | 0 | 10 | 0 | 0 | 0 | 0 | 4 | 0 | 50 | 6 | 48 | 0 | 0 | 50 | 0 | 0 | 8 | 50 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 438 | 0 | 0 | 0 | 0 | 14 | 0 | 0.1 | 0 |  | 3936.3 | 1602.1 | 5538.4 | 3524 | 172 | 1352 | 142 | 180 | 82 | 16 | 70 | 0.4 | 0 | 97.14
18:00 | 35 | 0 | 100 | 0 | 0 | 106 | 0 | 315 | 310 |  | 0 | 330 | 0 | 50 | 0 | 10 | 250 | 0 | 45 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 54 | 0 | 13 | 25 | 11 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 181 | 0 | 112 | 0 |  | 0 | 0 | 17 | 0 | 0 | 32 | 18 | 34 | 80 | 0 | 0 | 290 | 295 | 0 | 187 | 0 | 33 | 0 | 0 | 19 | 0 | 0 | 0 | 19 | 11 | 33 | 15 | 90 | 155 | 76 | 0 | 0 | 60 | 89 | 44 | 35 | 100 | 0 | 45 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 11 | 45 | 305 | 70 | 20 | 47 | 0 | 85 | 0 | 0 | 35 |  | 438 | 0 | 270 | 0 | 32 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 8 | 96 | 0 | 0 | 50 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 381 | 0 | 0 | 0 | 32 | 70 | 0 | 0 | 60 |  | 5079 | 2117 | 7196 | 3619 | 438 | 1719 | 1039 | 180 | 82 | 29 | 90 | 0 | 0 | 97.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 99 | 0 | 0 | 110 | 0 | 300 | 310 |  | 0 | 400 | 0 | 100 | 0 | 15 | 270 | 0 | 45 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 30 | 53 | 55 | 0 | 13 | 25 | 25 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 184 | 0 | 109 | 0 |  | 0 | 0 | 17 | 0 | 0 | 41 | 18 | 40 | 80 | 0 | 0 | 295 | 320 | 0 | 187 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 90 | 155 | 93 | 20 | 0 | 60 | 89 | 45 | 50 | 100 | 0 | 57 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40 | 321 | 50 | 17 | 51 | 0 | 100 | 0 | 0 | 0 |  | 438 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 423 | 0 | 0 | 0 | 32 | 70 | 0 | 0 | 70 |  | 5330 | 2144 | 7474 | 3728 | 438 | 1880 | 1055 | 180 | 82 | 21 | 90 | 0 | 0 | 97.13
19:30 | 35 | 0 | 99 | 0 | 0 | 110 | 0 | 328 | 311 |  | 0 | 420 | 0 | 62 | 0 | 15 | 290 | 0 | 75 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 13 | 25 | 32 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 17 | 0 | 0 | 50 | 18 | 40 | 80 | 0 | 0 | 340 | 290 | 0 | 178 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 155 | 93 | 20 | 0 | 60 | 89 | 45 | 50 | 163 | 0 | 57 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40 | 356 | 30 | 0 | 51 | 0 | 104 | 0 | 0 | 0 |  | 438 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 435 | 0 | 0 | 0 | 32 | 63 | 0 | 0 | 50 |  | 5473 | 2119 | 7592 | 3894 | 438 | 1967 | 920 | 180 | 82 | 21 | 90 | 0 | 0 | 0
20:00 | 35 | 0 | 100 | 0 | 0 | 110 | 0 | 335 | 370 |  | 0 | 450 | 0 | 60 | 0 | 0 | 292 | 0 | 74 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 16 | 25 | 30 | 24 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 179 | 0 | 109 | 0 |  | 0 | 0 | 17 | 0 | 2 | 50 | 18 | 40 | 80 | 0 | 0 | 295 | 285 | 0 | 167 | 80 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 157 | 94 | 20 | 0 | 60 | 89 | 45 | 50 | 163 | 0 | 57 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40 | 300 | 30 | 0 | 51 | 0 | 104 | 0 | 0 | 0 |  | 443 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 445 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 50 |  | 5470 | 2127 | 7597 | 3850 | 443 | 2055 | 876 | 180 | 82 | 21 | 90 | 0 | 0 | 97.13
21:00 | 35 | 0 | 98 | 0 | 0 | 110 | 0 | 351 | 367 |  | 0 | 450 | 0 | 0 | 0 | 0 | 290 | 0 | 74 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 32 | 24 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 177 | 0 | 109 | 0 |  | 0 | 0 | 17 | 0 | 10 | 34 | 18 | 40 | 80 | 0 | 0 | 270 | 265 | 0 | 167 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 86 | 158 | 94 | 20 | 0 | 60 | 89 | 45 | 50 | 163 | 21 | 58 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40 | 290 | 30 | 0 | 51 | 0 | 106 | 0 | 0 | 0 |  | 443 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 441 | 0 | 0 | 0 | 32 | 38 | 0 | 0 | 35 |  | 5300 | 2084 | 7384 | 3741 | 443 | 2048 | 783 | 180 | 82 | 21 | 86 | 0 | 0 | 97.12
22:00 | 35 | 0 | 100 | 0 | 0 | 110 | 0 | 351 | 331 |  | 0 | 450 | 0 | 0 | 0 | 0 | 290 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 25 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 176 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 40 | 80 | 0 | 0 | 280 | 290 | 0 | 167 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 82 | 158 | 60 | 22 | 0 | 60 | 89 | 45 | 50 | 163 | 74 | 58 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 303 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 |  | 443 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 8 | 80 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 357 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 5013 | 1828 | 6841 | 3817 | 443 | 1927 | 306 | 180 | 82 | 4 | 82 | 0 | 0 | 97.12
23:00 | 35 | 0 | 100 | 0 | 0 | 110 | 0 | 352 | 334 |  | 0 | 450 | 0 | 0 | 0 | 0 | 290 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 32 | 16 | 29 | 0 | 0 | 38 | 40 | 120 | 120 | 0 | 207 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 40 | 80 | 0 | 0 | 285 | 290 | 0 | 167 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 20 | 76 | 159 | 24 | 22 | 0 | 60 | 89 | 45 | 50 | 163 | 70 | 45 | 30 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 16 | 0 | 0 | 0 |  | 200 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 64 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4771 | 1531 | 6302 | 3728 | 200 | 1861 | 175 | 180 | 78 | 4 | 76 | 0 | 0 | 97.11
24:00 | 35 | 0 | 100 | 0 | 0 | 110 | 0 | 354 | 330 |  | 0 | 380 | 0 | 0 | 0 | 0 | 250 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 12 | 29 | 0 | 0 | 38 | 40 | 120 | 120 | 0 | 202 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 80 | 0 | 0 | 270 | 270 | 0 | 167 | 0 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 66 | 159 | 0 | 22 | 0 | 60 | 89 | 5 | 50 | 130 | 77 | 59 | 5 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 7 | 32 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4334 | 1453 | 5787 | 3572 | 200 | 1655 | 32 | 180 | 78 | 4 | 66 | 0 | 0 | 97.11
KWH | 817000 | 0 | 2398000 | 0 | 0 | 905363 | 0 | 8401920 | 7970000 |  | 0 | 8472250 | 0 | 241920 | 936 | 42627 | 6610830 | 0 | 1313000 | 0 | 9600 | 133200 | 0 | 0 | 0 | 0 | 50832 | 304560 | 230668 | 0 | 140832 | 600000 | 567180 | 529800 | 760000 | 0 | 0 | 961396 | 972000 | 2900000 | 2900000 | 0 | 4537119 | 0 | 2788008 | 0 |  | 0 | 0 | 79950 | 0 | 20160 | 206400 | 302832 | 659520 | 2026630 | 0 | 0 | 7393300 | 7144000 | 0 | 1605818 | 74136 | 582264 | 0 | 0 | 543656 | 0 | 0 | 0 | 290808 | 127800 | 323400 | 447020 | 1687680 | 3391840 | 501120 | 132300 | 2600 | 1422000 | 2121840 | 565200 | 733752 | 3205300 | 801000 | 1230720 | 840000 | 0 | 0 | 238000 | 568920 | 133740 | 0 | 284544 | 134976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114480 | 324480 | 27360 | 209090 | 8031000 | 228000 | 56988 | 265963 | 23760 | 454145 | 0 | 0 | 53580 |  | 5228000 | 0 | 5521248 | 0 | 40320 | 0 | 0 | 0 | 0 | 105984 | 0 | 1518000 | 155965 | 1222080 | 0 | 0 | 1195000 | 0 | 0 | 158808 | 598590 | 0 | 0 | 0 | 0 | 168240 | 156384 | 76122 | 0 | 0 | 4440600 | 0 | 0 | 4509455 | 0 | 0 | 0 | 0 | 0 | 4158691 | 0 | 8990490 | 0 | 0 | 0 | 239328 | 269760 | 0 | 8571 | 249696 |  | 105171113 | 39011332 | 144182445 | 88742615 | 5228000 | 35674598 | 5981403 | 4440600 | 1933396 | 344742 | 1687680 | 149411 | 0
Fuel Cost | 915040 | 0 | 2565860 | 0 | 0 | 878202.11 | 0 | 6049382.4 | 6057200 |  | 0 | 6777800 | 0 | 2467584 | 10136.88 | 437353.02 | 8197429.2 | 0 | 1641250 | 0 | 106560 | 1353312 | 0 | 0 | 0 | 0 | 475787.52 | 2920730.4 | 2200572.72 | 0 | 105624 | 450000 | 0 | 0 | 0 | 0 | 0 | 249962.96 | 252720 | 4437000 | 4437000 | 0 | 4763974.95 | 0 | 3540770.16 | 0 |  | 0 | 0 | 838675.5 | 0 | 191721.6 | 1931904 | 278605.44 | 1833465.6 | 2127961.5 | 0 | 0 | 5471042 | 6000960 | 0 | 1573701.64 | 98600.88 | 477456.48 | 0 | 0 | 777428.08 | 0 | 0 | 0 | 296624.16 | 95850 | 611226 | 335265 | 11644992 | 2781308.8 | 4765651.2 | 134946 | 42640 | 1933920 | 2885702.4 | 768672 | 917190 | 3974572 | 736920 | 1833772.8 | 1478400 | 0 | 0 | 378420 | 665636.4 | 314289 | 0 | 213408 | 102581.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1321099.2 | 3024153.6 | 256636.8 | 1959173.3 | 7549140 | 1999560 | 507763.08 | 2513350.35 | 0 | 4187216.9 | 0 | 0 | 0 |  | 14115600 | 0 | 4306573.44 | 0 | 388684.8 | 0 | 0 | 0 | 0 | 1388390.4 | 0 | 1214400 | 241745.75 | 13125139.2 | 0 | 0 | 2246600 | 0 | 0 | 1572199.2 | 6207378.3 | 0 | 0 | 0 | 0 | 185064 | 258033.6 | 57624.354 | 0 | 0 | 18162054 | 0 | 0 | 3968320.4 | 0 | 0 | 0 | 0 | 0 | 3659648.08 | 0 | 6563057.7 | 0 | 0 | 0 | 2132412.48 | 2519558.4 | 0 | 0 | 0 |  | 143122855.79 | 82312484.104 | 225435339.894 | 86900208.204 | 14115600 | 33264457.88 | 55682340.55 | 18162054 | 502682.96 | 3799265.1 | 11644992 | 1363739.2 | 0
Yesterday Day Peak | 35 | 0 | 101 | 0 | 0 | 52 | 0 | 368 | 308 |  | 0 | 320 | 0 | 0 | 0 | 0 | 270 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 0 | 28 | 0 | 0 | 40 | 40 | 120 | 120 | 0 | 189 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 80 | 0 | 0 | 335 | 350 | 0 | 54 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 72 | 156 | 0 | 0 | 0.3 | 60 | 89 | 44 | 47 | 100 | 0 | 58 | 40 | 0 | 0 | 17 | 28 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.5 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 |  | 176 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 65 | 5 | 80 | 0 | 0 | 50 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 5827.3 | DayPeak
Yesterday Evening Peak | 35 | 0 | 100 | 0 | 0 | 110 | 0 | 335 | 370 | 0 | 0 | 450 | 0 | 60 | 0 | 0 | 292 | 0 | 74 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 16 | 25 | 30 | 24 | 29 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 179 | 0 | 109 | 0 | 0 | 0 | 0 | 17 | 0 | 2 | 50 | 18 | 40 | 80 | 0 | 0 | 295 | 285 | 0 | 167 | 80 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 157 | 94 | 20 | 0 | 60 | 89 | 45 | 50 | 163 | 0 | 57 | 79 | 0 | 0 | 17 | 38 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 40 | 300 | 30 | 0 | 51 | 0 | 104 | 0 | 0 | 0 |  | 443 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 9 | 110 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 0 | 180 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 445 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 50 |  | 7597 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 0 | 108 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 40 | 125 | 0 | 0 | 360 | 360 | 0 | 185 | 0 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 105 | 150 | 95 | 22 | 0 | 60 | 89 | 51 | 44 | 163 | 135 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  | 649 | 40 | 300 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 65 | 20 | 110 | 30 | 0 | 50 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 260 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 200 | 0 | 0 | 108 | 0 | 320 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 100 | 0 | 100 | 93 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 40 | 120 | 120 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 50 | 21 | 14 | 125 | 0 | 0 | 335 | 360 | 0 | 150 | 0 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 90 | 150 | 95 | 22 | 1.6 | 60 | 85 | 51 | 44 | 163 | 90 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 0 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 150 | 100 | 400 | 100 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  | 203 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 20 | 70 | 0 | 0 | 50 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 50 | 100 | 0 | 32 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 0 | 80 | 0 | 320 | 305 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 210 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 12 | 17 | 0 | 0 | 42 | 40 | 120 | 120 | 0 | 216 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 80 | 0 | 0 | 335 | 320 | 0 | 45 | 0 | 33 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 66 | 170 | 0 | 22 | 0.1 | 59 | 89 | 16 | 5 | 163 | 100 | 58 | 5 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 180 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 0 | 0
199
| Minimum Generation |  | 5075 | 5:00
| Highest Generation |  | 7597 | 20:00
| Day Peak Generation |  | 5827.3 | 12:00
| Evening Peak Generation |  | 7597 | 20:00
| HVDC Max Flow |  | 443 | 20:00
| HVDC EvPeak Flow |  | 443 | 20:00
| Load factor L.F |  | 79.08%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-21
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5827.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4596 | MW
Evening Peak Generation : |  | 7597 | MW Hour : | 20:00 | Available Max Generation : |  | 14070 | MW
E.P. Demand (at gen end) : |  | 7597 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 7597 | MW Hour : | 20:00 | Reserve(Generation end) |  | 5570 | MW
Total Gen. (MKWH) : |  | 144.1824 | System Load Factor : | 79.08% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -443 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-21
Actual : | 97.05 | Ft.(MSL) , | Rule curve : | 104.1 | Ft.( MSL )
Gas Consumed : | Total = | 995.34 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120164666.084
: |  | Coal : | 18162054 | Oil : | 59481605.65 | Total : | 197808325.734
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2988.3172 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1009.2359 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 903.0022 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 815.4985 |  |  | 0 | 0%
) | 0 | 0:00 | 737.1969 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 594.8743 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 341.5774 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 153.4011 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 458.7537 |  |  | 0 | 0%
Total | 0 |  | 8001.8574 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 10) Ashuganj 225 MW CCPP
|  |  |  | 2) Summit Meghna 305 MW | 11) Bheramara-360 MW ST
|  |  |  | 3) Ghorasal Unit-1,3,5,7 | 12) Baghabari 100 MW
|  |  |  | 4) Chandpur CCPP | 13) Ashuganj North ST
|  |  |  | 5) Sylhet 150 MW | 14) Sirajganj unit-2
6) Bhola-225 MW GT-1 & ST
7) Ashuganj Precision
8) Ashuganj 225 MW CCPP
9) Ashuganj unit-4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Shyampur 132/33 kV GT-2 was shut down from 09:23 to 13:53 for A/M.
b) Siddhirganj 230/132 kV T-2 Transformer was shut down from 08:05 to 14:56 for A/M.
c) Joydevpur-Kodda 132 kV Ckt-1,2 were under shut down from 10:17 to 20:59 for A/M.
d) Mongla 132/33 kV T-1 Transformer was shut down from 09:39 to 16:27 for A/M.
e) Ishurdi-HVDC 230 kV Ckt-3 & 4 were under shut down since 10:30 to till now for C/M.
f) Ishurdi 230 kV bus-2 was under shut down since 10:25 to till now for C/M.
g) Ishurdi-Baghabari 230 kV Ckt-1 was under shut down since 10:25 to till now for C/M.
h) Ishurdi 132/33 kV T-3 was under shut down from 08:48 to 12:22 for maintenance by NESCO.
i) Shahjadpur 132/33 kV T-4 was under shut down since 09:55 for A/M.
j) Modhumoti-Gopalganj 132 kV Ckt was under shut down from 10:19 to 11:49 for C/M.
k) Barapukuria 230/132 kV T-3 Transformer was shut down from 10:40 to 13:04 for D/W.
l) Barapukuria P/S- Barapukuria S/S 230 kV Ckt-2 was under shut down from 09:30 to 10:06 for D/W.
m) Barapukuria P/S- Barapukuria S/S 230 kV Ckt-1 was under shut down from 10:08 to 10:33 for D/W.
n) Benapole 33 kV bus under T-1 transformer was shut down from 09:06 to 11:52 for A/M.
o) Joydevpur 132/33 kV T3 & T4 transformer tripped at 11:34 from 33 kV side showing O/C,E/F relay due to 33 kV |  |  |  |  | About 69 MW power interruption occurred under Joydevpur S/S area from
Sreepur feeder fault and was switched on at 11:37. |  |  |  |  | 11:34 to 11:37.
p) Chowmuhoni 132 kV bus was under shut down from 07:11 to 16:47 for bus arrangement of Hosaf P/P 132 kV line
q) Chowmuhoni S/S- Hosaf P/P 132 kV line charged on at 20:05.
r) After reconducting Saidpur-Purbasadipur 132 kV Ckt-2 switched on at 15:10 .
s) After maintenance Shahjibazar 330 MW GT-1 was synchronized at 20:04.
t) After maint Chandpur 150 MW GT was synchronized at 19:37 and tripped at 20:50 due to GBC problem.
u) After maintenance HVDC Bheramara tie breaker 10C01B switched on at 15:25.
v) Hosaf Power unit transformer 1 & 2 were switched on at 20:50,21:07 respectively.
w) Barapukuria T01 & T02 were shut down from 14:15 to 15:20 one after another for SCADA integration .
x) Ullon 132/33 kV T3 transformer tripped at 20:53 showing differential relay R & Y phase REF due to 33 kV cable
burst at DPDC GIS S/S.
y) Natore-Rajshahi 132 kV Ckt-2 is under shut down since at 06:28 for D/W.
z) Khulshi-Hathazari 132 kV Ckt is under shutdown since at 07:26 for A/M.
aa) Kulshi-madanaghat 132 kV Ckt is under shutdown since at 07:01 for A/M.
ab) Mymensing 33 kv bus under T2 transformer shutdown since at 07:11 for PBS maintenance work. |  |  |  |  | About 34 MW power interruption occurred under Mymensing S/S area from
07:11 to till now
ac) Sirajganj #03 tripped at 07:41 due to DP high.
ad) Faridpur- Bheramara 132 kV Ckt-1 is under shut down since at 07:29 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 817000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | DP high
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2398000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 905363
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8401920 | Friquency control
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 370 | 7970000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8472250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 60 | 241920 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 936 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 42627 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 140832 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 74 | 1313000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 9600 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 292 | 6610830 | Friquency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 7 | 133200 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 50832 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 304560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 230668
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1167180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 529800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 760000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 56988 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2065 | 40557506
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 114480 | Reserve
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 206400
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1933396 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 179 | 4537119 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 109 | 2788008 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 265963 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 79950 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 324480 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 302832
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 659520
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 2 | 20160 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23760
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 104 | 454145 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 962 | 17510213
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2026630 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7393300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 7144000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 582264 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 167 | 1605818 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 543656 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 209090 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 74136
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 27360 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 290808
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 127800
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1687680
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 323400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 447020
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 53580 | Reserve
| Cumilla Area Total |  |  |  | 2920 | 1199 | 22536542
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3391840 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 132300
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 94 | 501120
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 2600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 30 | 228000 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 301 | 4255860
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1422000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 89 | 2121840
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3205300
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 801000 | Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 45 | 565200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 733752
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 134976
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1230720 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 840000
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 238000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 38 | 568920 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 284544
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 300 | 8031000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 133740
| Sylhet Area Total |  |  |  | 1949 | 943 | 20310992
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 443 | 5228000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 40320 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 4 | 105984 | Low demand
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 255 | 5521248 | ST under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 32 | 239328 | Low demand
| Khulna Area Total |  |  |  | 2314 | 734 | 11134880
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1222080
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 155965 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1518000 | GT1 & ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Cable fault
| Barisal Area Total |  |  |  | 462 | 184 | 2896045
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1195000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 18 | 598590 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 198 | 4509455 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4158691 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 445 | 8990490 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 168240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 156384
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 76122 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 158808 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 249696 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 979 | 20261476
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4440600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 50 | 269760
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 8571
| Rangpur Area Total |  |  |  | 605 | 230 | 4718931
| Total |  |  |  | 19047 | 7597 | 144182445
| Eastern Grid Total |  |  |  | 13483 | 5470 | 105171113
| Western Grid Total |  |  |  | 5564 | 2127 | 39011332
| National Grid Total |  |  |  | 19047 | 7597 | 144182445
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-20
(a) ENTIRE EASTERN GRID : |  | 4734 | MW | (b) ENTIRE WESTERN GRID : |  | 2405 | MW
i) Dhaka area |  | 2384 | MW | i) Khulna area |  | 908 | MW
ii) Chittagong area |  | 785 | MW | ii) Rajshahi area |  | 745 | MW
iii) Comilla area |  | 671 | MW | iii) Barisal area |  | 227 | MW
iv) Mymensingh area |  | 601 | MW | iv) Rangpur area |  | 525 | MW
v) Sylhet area |  | 293 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7139 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 78 | 10:00 | Shahjibazar | 75 | 20:00 | Bottail | 82 | 18:00
Munsiganj | 74 | 19:30 | Fenchuganj | 24 | 18:30 | G.K Project | 24 | 18:30
Sonargaon | 64 | 2:00 | Kulawara | 27 | 18:00 | Faridpur | 118 | 19:30
Shyampur | 146 | 1:00 | Sylhet | 77 | 19:30 | Madaripur | 53 | 19:00
Bhulta | 145 | 1:00 | Chatak | 17 | 18:00 | Sariatpur | 38 | 19:30
Madanganj | 48 | 19:00 | Sunamganj | 26 | 20:00 | Gopalganj | 58 | 19:00
Shitalakhya | 61 | 10:00 | Biani Bazar | 35 | 19:00 | Bagerhat | 60 | 18:30
Rahim steel | 16 | 20:00 | Comilla (S) | 90 | 18:00 | Mongla | 26 | 1:00
Matuail | 60 | 10:00 | Comilla(N) | 65 | 19:30 | Satkhira | 62 | 19:00
Ghorasal | 57 | 19:30 | Chandpur | 55 | 18:30 | Gallamari | 36 | 13:00
Narsingdi | 77 | 20:00 | Feni | 87 | 20:00 | Magura | 34 | 18:00
Haripur (SBU) | 68 | 19:30 | Chowmuhani | 118 | 20:00 | Norail | 25 | 18:00
Ullon | 44 | 20:00 | Ashuganj | 32 | 19:30 | Chuadanga | 56 | 18:30
Hasnabad | 123 | 18:30 | Daudkandi | 78 | 18:00 | Barisal(N) | 28 | 20:00
Magbazar | 70 | 17:00 | B.Baria | 84 | 18:00 | Barisal (S) | 62 | 20:00
Maniknagar | 68 | 16:00 | Ramganj | 54 | 20:00 | Patuakhali | 63 | 20:00
Bangabhaban | 16 | 13:00 | Chaddagram | 14 | 19:00 | Bhandaria | 40 | 20:00
Narinda | 68 | 12:00 | PHP | 1 | 13:00 | Borhan Uddin | 34 | 20:00
Dhanmondi | 82 | 14:00 | Madunaghat | 36 | 19:30 | Ishurdi | 37 | 18:00
Lalbag | 75 | 18:00 | Hathazari | 61 | 19:30 | Ruppur Paromanobik | 1 | 1:00
Madartek | 38 | 13:00 | Khulshi | 106 | 17:00 | Natore | 79 | 18:30
Mirpur | 60 | 18:00 | Halishahar | 81 | 18:30 | Bogra | 120 | 19:30
Kalyanpur | 57 | 12:00 | Baraulia | 111 | 8:00 | Noagaon | 76 | 18:00
Gulshan | 74 | 13:00 | Sikalbaha | 22 | !9:00 | Rajshahi | 82 | 21:00
Uttara | 33 | 12:00 | Dohazari | 64 | 18:30 | Rajshahi New | 8 | 19:00
Uttara New | 27 | 12:00 | Cox'sbazar | 65 | 18:00 | C.Nawabganj | 54 | 19:00
Kamrangirchar | 44 | 12:00 | Chandraghona | 22 | 18:00 | Amnura | 23 | 18:00
Savar | 72 | 12:00 | Kaptai | 3.8 | 18:00 | Pabna | 62 | 18:30
Bhasantec | 76 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 64 | 18:30
Agargaon | 32 | 13:00 | Bakulia | 56 | 18:30 | Serajganj | 57 | 19:00
Satmosjid | 68 | 13:00 | Julda | 18 | 1:00 | Niyamatpur | 44 | 19:00
Tongi | 87 | 11:00 | TK chemical | 2.4 | 9:00 | Joypurhat | 40 | 18:30
Kabirpur | 113 | 12:00 | Modern Steel | 10 | 1:00 | Sherpur(Bogura) | 31 | 18:00
Basundhara | 65 | 12:00 | Shahmirpur | 19.5 | 1:00 | Mohastangor | 10 | 18:00
Manikganj | 60 | 18:30 | Khagrachhari | 16 | 18:30 | Rangpur | 95 | 18:00
Joydevpur | 116 | 19:30 | Matarbari | 15 | 17:00 | Lalmonirhat | 40 | 18:00
New Tongi | 58 | 11:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 73 | 18:30
Korda | 128 | 19:30 | Rangamati | 8 | 12:00 | Purbasadipur | 86 | 18:30
Dhamrai | 26 | 18:30 | Abul Khair 230 | 151 | 23:00 | Thakurgaon | 56 | 18:30
Valuka | 64 | 18:30 | BSRM | 109 | 19:30 | Palashbari | 76 | 18:30
Tangail | 125 | 18:30 | GPH Ispat | 8 | 18:00 | Barapukuria | 37 | 19:30
Mymensing | 146 | 19:00 | Goalpara | 21 | 20:00 | Panchagar | 35 | 18:00
Kishorganj | 76 | 20:00 | Central s/s | 54 | 19:30 | Joldhaka | 18 | 18:00
Netrokona | 64 | 18:00 | Noapara | 36 | 18:00 | Kurigram | 38 | 18:30
Jamalpur | 79 | 18:00 | Jessore | 66 | 19:00
Sherpur | 68 | 18:00 | Benapol | 32 | 18:00
Srimongal | 23 | 18:00 | Jhenida | 74 | 18:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-20 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 397 | 24:00 | 389 | 0.41667 | Kaliakoir | 385 | 0.875 | 377 | 0.41667
Bheramara | 410 | 0.125 | 395 | 0.75 | Bhulta | 399 | 24:00 | 390 | 0.375
Ashuganj(N) | 403 | 24:00 | 395 | 0.375
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 234 | 24:00 | 228 | 0.041667 | Hathazari | 227 | 0.75 | 223 | 0.29167
Ishurdi | 244 | 0.625 | 225 | 0.79167 | Megnaghat | 239 | 0.95833 | 230 | 0.29167
Ashuganj | 244 | 0.95833 | 240 | 0.083333 | Fenchuganj | 241 | 24:00 | 235 | 0.083333
Serajganj | 235 | 0.041667 | 230 | 0.77083 | Siddhirganj | 236 | 24:00 | 231 | 0.33333
Baghabari | 248 | 0.29167 | 232 | 0.8125 | Maniknagar | 234 | 0.91667 | 230 | 0.083333
Barapukuria | 231 | 0.16667 | 227 | 0.5 | Old Airport | 234 | 24:00 | 228 | 0.41667
Bogra | 234 | 0.20833 | 226 | 0.77083 | Barisal | 237 | 0.875 | 220 | 0.33333
Khulna South | 241 | 0.625 | 214 | 0.79167 | AKSML | 224 | 0.875 | 219 | 0.083333
Rampura | 232 | 0.95833 | 230 | 0.041667 | BSRM | 227 | 0.77083 | 222 | 0.083333
Haripur | 234 | 0.95833 | 230 | 0.041667 | Bibiyana | 238 | 0.875 | 232 | 0.66667
Hasnabad | 232 | 0.20833 | 229 | 0.83333 | Bhulta | 236 | 24:00 | 231 | 0.375
Aminbazar | 236 | 24:00 | 230 | 0.375 | Ashuganj (S) | 242 | 24:00 | 236 | 0.33333
Tongi | 230 | 0.95833 | 225 | 0.16667 | Kaliakoir | 235 | 0.125 | 228 | 0.5
Comilla (N) | 239 | 24:00 | 235 | 0.41667 | GPH | 224 | 0.95833 | 220 | 0.54167
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 142 | 0.75 | 139 | 0.29167 | Halishahar | 135 | 0.75 | 131 | 0.29167
Munsiganj | 142 | 0.75 | 138 | 0.45833 | Baraulia | 135 | 0.79167 | 129 | 0.375
Sonargaon | 140 | 0.75 | 136 | 0.41667 | Sikalbaha | 133 | 0.75 | 130 | 0.5
Shyampur | 139 | 0.75 | 136 | 0.41667 | Dohazari | 133 | 0.79167 | 130 | 0.125
Bhulta | 136 | 0.58333 | 132 | 0.125 | Cox'sbazar | 128 | 0.25 | 125 | 0.8125
Madanganj | 138 | 0.79167 | 133 | 0.041667 | Chandraghona | 135 | 0.77083 | 132 | 0.41667
Shitalakhya | 141 | 0.75 | 134 | 0.41667 | Kaptai | 135 | 0.8125 | 132 | 0.54167
Rahim steal | 142 | 18:00 | 140 | 0.041667 | A. Khaer Stl. | 132 | 0.25 | 130 | 0.041667
Matuail | 141 | 0.75 | 138 | 0.33333 | Bakulia | 133 | 0.75 | 129 | 0.45833
Ghorasal | 140 | 0.041667 | 138 | 0.77083 | Julda | 134 | 0.77083 | 129 | 0.5
Narsinghdi | 135 | 0.625 | 130 | 0.041667 | TK Chemical | 134 | 0.79167 | 130 | 0.041667
Haripur (SBU) | 142 | 0.75 | 139 | 0.25 | Modern Steel | 133 | 0.75 | 130 | 0.125
Ullon | 136 | 0.95833 | 132 | 0.625 | Shahmirpur | 133 | 0.77083 | 130 | 0.041667
Hasnabad | 135 | 0.77083 | 129 | 0.45833 | Khagrachhari | 134 | 0.79167 | 132 | 0.041667
Magbazar | 135 | 0.25 | 132 | 0.45833 | Matarbari | 130 | 0.375 | 128 | 0.041667
Maniknagar | 139 | 0.25 | 135 | 0.5 | Baroiar Hat | 136 | 0.625 | 132 | 0.41667
Bangabhaban | 139 | 0.25 | 135 | 0.5 | Rangamati | 134 | 0.75 | 132 | 0.16667
Narinda | 139 | 0.25 | 135 | 0.5 | Goalpara | 141 | 0.58333 | 123 | 19:30
Dhanmondi | 136 | 0.95833 | 132 | 0.625 | Central s/s | 140 | 0.58333 | 124 | 19:30
Lalbag | 136 | 0.25 | 128 | 0.66667 | Noapara | 135 | 0.29167 | 120 | 0.77083
Madartek | 136 | 0.25 | 131 | 0.66667 | Jessore | 136 | 0.625 | 118 | 0.77083
Mirpur | 137 | 0.125 | 132 | 0.45833 | Benapol | 136 | 0.125 | 123 | 0.77083
Kalyanpur | 138 | 0.16667 | 135 | 0.41667 | Jhenida | 137 | 0.625 | 120 | 0.77083
Gulshan | 136 | 0.041667 | 135 | 0.33333 | Bottail | 139 | 0.58333 | 126 | 0.77083
Uttara | 135 | 0.083333 | 131 | 0.5 | G.K Project | 144 | 0.625 | 133 | 0.8125
Uttara New | 135 | 0.083333 | 132 | 0.375 | Faridpur | 135 | 0.375 | 126 | 0.70833
Kamrangirchar | 136 | 0.75 | 133 | 0.5 | Madaripur | 137 | 0.625 | 125 | 0.29167
Savar | 135 | 0.75 | 131 | 0.5 | Sariatpur | 136 | 0.66667 | 128 | 0.33333
Bhasantec | 138 | 0.041667 | 134 | 0.41667 | Gopalganj | 141 | 0.875 | 131 | 0.33333
Agargaon | 138 | 0.041667 | 135 | 0.41667 | Bagerhat | 135 | 0.125 | 115 | 0.33333
Satmosjid | 138 | 0.16667 | 134 | 0.41667 | Mongla | 135 | 0.70833 | 115 | 0.33333
Tongi | 141 | 0.95833 | 137 | 0.79167 | Satkhira | 139 | 0.58333 | 121 | 0.8125
Kabirpur | 138 | 1904-01-02 | 133 | 0.41667 | Gallamari | 140 | 0.58333 | 124 | 0.8125
Basundhara | 140 | 24:00 | 135 | 0.375 | Magura | 136 | 0.625 | 118 | 0.77083
Manikganj | 142 | 24:00 | 137 | 0.8125 | Norail | 135 | 0.625 | 119 | 0.77083
Joydevpur | 142 | 0.83333 | 139 | 0.5 | Chuadanga | 135 | 0.625 | 117 | 0.79167
New Tongi | 140 | 0.95833 | 126 | 0.5 | Barisal(N) | 139 | 0.875 | 127 | 0.33333
Kodda | 137 | 0.125 | 131 | 0.33333 | Barisal (S) | 137 | 0.5 | 130 | 0.33333
Dhamrai | 137 | 0.95833 | 133 | 0.54167 | Patuakhali | 137 | 0.58333 | 128 | 0.33333
Valuka | 132 | 0.79167 | 128 | 0.41667 | Bhandaria | 135 | 0.29167 | 120 | 0.33333
Tangail | 135 | 0.16667 | 131 | 0.375 | Ishurdi | 139 | 0.16667 | 131 | 0.77083
Mymensing | 133 | 0.77083 | 128 | 0.375 | Ruppur Paromanobik | 138 | 0.25 | 130 | 0.79167
Kishorganj | 133 | 0.25 | 130 | 0.041667 | Natore | 138 | 0.58333 | 128 | 0.77083
Netrokona | 132 | 0.16667 | 128 | 0.375 | Bogra | 137 | 0.58333 | 132 | 0.8125
Jamalpur | 138 | 0.75 | 124 | 0.375 | Noagaon | 135 | 0.16667 | 128 | 0.8125
Sherpur | 136 | 0.75 | 123 | 0.29167 | Rajshahi | 135 | 0.58333 | 125 | 0.79167
Srimongal | 139 | 0.91667 | 136 | 0.375 | Rajshahi New | 135 | 0.58333 | 123 | 0.8125
Shahjibazar | 136 | 0.33333 | 134 | 0.20833 | C.Nawabganj | 133 | 0.54167 | 122 | 0.77083
Fenchuganj | 138 | 0.91667 | 135 | 0.083333 | Amnura | 136 | 0.54167 | 124 | 0.77083
Khulawara | 138 | 0.95833 | 136 | 3:00 | Pabna | 139 | 0.20833 | 132 | 0.75
Sylhet | 137 | 0.041667 | 134 | 0.45833 | Shahjadpur | 143 | 0.041667 | 138 | 0.79167
Chatak | 136 | 0.875 | 132 | 0.41667 | Serajganj | 140 | 0.083333 | 133 | 0.77083
Sunamganj | 136 | 0.95833 | 132 | 0.41667 | Niyamatpur | 135 | 0.125 | 126 | 0.8125
Biani Bazar | 136 | 0.041667 | 134 | 0.083333 | Joypurhat | 136 | 0.58333 | 130 | 0.77083
Comilla(s) | 132 | 0.16667 | 128 | 0.5 | Sherpur(Bogura) | 141 | 0.083333 | 133 | 0.77083
Comilla(n) | 142 | 0.29167 | 139 | 0.83333 | Mohastangor | 136 | 0.58333 | 131 | 0.77083
Chandpur | 138 | 9:00 | 135 | 0.875 | Rangpur | 130 | 0.125 | 125 | 0.5
Feni | 138 | 0.58333 | 130 | 0.875 | Lalmonirhat | 127 | 0.20833 | 121 | 0.8125
Chowmuhani | 132 | 0.29167 | 126 | 0.70833 | Saidpur | 130 | 0.125 | 124 | 0.5
Ashuganj | 137 | 0.625 | 135 | 0.041667 | Purbasadipur | 128 | 0.20833 | 119 | 0.77083
Daudkandi | 139 | 0.625 | 137 | 0.45833 | Thakurgaon | 124 | 0.20833 | 118 | 0.75
B.Baria | 135 | 0.70833 | 132 | 0.83333 | Palashbari | 136 | 0.125 | 127 | 0.77083
Ramganj | 134 | 0.625 | 128 | 0.83333 | Barapukuria | 131 | 0.16667 | 127 | 0.5
Chaddagram | 139 | 0.66667 | 134 | 0.83333 | Panchagar | 120 | 0.20833 | 112 | 0.75
PHP | 134 | 0.91667 | 132 | 0.5 | Joldhaka | 129 | 0.25 | 121 | 0.75
Madanhat | 136 | 0.75 | 134 | 0.125 | Kurigram | 130 | 0.16667 | 125 | 0.5
Hathazari | 135 | 0.75 | 132 | 0.29167
Khulshi | 133 | 0.75 | 128 | 0.375

## L-Curve
Date | 2019-12-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 322 | 4334 | 1453 | 5787 |  |  |  | QF-LDC-12
0:30 | 292.5 | 4326.5 | 1458 | 5784.5 | Date: | 2019-12-20
1:00 | 263 | 4319 | 1463 | 5782
1:30 | 231.5 | 4223 | 1418 | 5641
2:00 | 200 | 4127 | 1373 | 5500
2:30 | 211 | 4040 | 1335 | 5375 | [5 empty] | Gen. at Eve. Peak | 7597 | 8095 MW (19:00 )
3:00 | 222 | 3953 | 1297 | 5250 | [6 empty] | 20:00
3:30 | 201 | 3859.5 | 1307.5 | 5167 | [5 empty] | Gen. at Day Peak | 5827.3 | 6206.6 MW (12:00 )
4:00 | 180 | 3766 | 1318 | 5084 | [6 empty] | 12:00
4:30 | 166 | 3753 | 1326.5 | 5079.5 | [5 empty] | Highest Generation | 7597
5:00 | 152 | 3740 | 1335 | 5075 | [6 empty] | 20:00
5:30 | 179.5 | 3777.5 | 1340 | 5117.5
6:00 | 207 | 3815 | 1345 | 5160
6:30 | 172 | 3804.781 | 1393.05 | 5197.831
7:00 | 137 | 3794.562 | 1441.1 | 5235.662
7:30 | 204.5 | 3897.381 | 1469.65 | 5367.031
8:00 | 272 | 4000.2 | 1498.2 | 5498.4
8:30 | 238.5 | 4078.33 | 1510.45 | 5588.78
9:00 | 205 | 4156.46 | 1522.7 | 5679.16
9:30 | 166.5 | 4147.05 | 1483.9 | 5630.95
10:00 | 128 | 4137.64 | 1445.1 | 5582.74
10:30 | 97 | 4155.185 | 1444.9 | 5600.085
11:00 | 66 | 4172.73 | 1444.7 | 5617.43
11:30 | 96.5 | 4241.915 | 1480.45 | 5722.365
12:00 | 127 | 4311.1 | 1516.2 | 5827.3
12:30 | 75.5 | 4255.45 | 1584.75 | 5840.2
13:00 | 24 | 4199.8 | 1653.3 | 5853.1
13:30 | 64.5 | 3989.5 | 1637.3 | 5626.8
14:00 | 105 | 3779.2 | 1621.3 | 5400.5
14:30 | 96 | 3745.45 | 1561.05 | 5306.5
15:00 | 87 | 3711.7 | 1500.8 | 5212.5
15:30 | 79 | 3715.05 | 1494 | 5209.05
16:00 | 71 | 3718.4 | 1487.2 | 5205.6
16:30 | 39 | 3827.35 | 1544.65 | 5372
17:00 | 7 | 3936.3 | 1602.1 | 5538.4
17:30 | 193.5 | 4507.65 | 1859.55 | 6367.2
18:00 | 380 | 5079 | 2117 | 7196
18:30 | 397.5 | 5204.5 | 2130.5 | 7335
19:00 | 415 | 5330 | 2144 | 7474
19:30 | 415 | 5473 | 2119 | 7592
20:00 | 420 | 5470 | 2127 | 7597 |  |  |  | Executive Engineer
20:30 | 375 | 5385 | 2105.5 | 7490.5 |  |  |  | Network Operation Division
21:00 | 330 | 5300 | 2084 | 7384
21:30 | 309 | 5156.5 | 1956 | 7112.5
22:00 | 288 | 5013 | 1828 | 6841 |  |  |  |  | Page 6 of 7
22:30 | 326 | 4892 | 1679.5 | 6571.5
23:00 | 364 | 4771 | 1531 | 6302
23:30 | 343 | 4552.5 | 1492 | 6044.5
24:00 | 322 | 4334 | 1453 | 5787
8095 MW (19:00 )
6206.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-20 |  | Energy | 144182445
[10 empty] | 2019-12-20 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3572 | 200 | 1655 | 175 | 180 | 78 | 4 | 0 | 66
0:30 | 3590 | 184.5 | 1651 | 95.5 | 185 | 80 | 4 | 0 | 66 | Date: | 2019-12-20
1:00 | 3608 | 169 | 1647 | 16 | 190 | 82 | 4 | 0 | 66
1:30 | 3601 | 151 | 1543 | 8 | 187 | 82 | 4 | 0 | 65 | [7 empty] | Total Energy | 144.1824 | Total Energy Gen 144.182 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 144.182 MKWHr
2:00 | 3594 | 133 | 1439 | 0 | 184 | 82 | 4 | 0 | 64 | [7 empty] | Energy not Served | 0
2:30 | 3533.5 | 132.5 | 1377 | 0 | 182 | 82 | 4 | 0 | 64 | [7 empty] | Energy Requirement | 144.1824
3:00 | 3473 | 132 | 1315 | 0 | 180 | 82 | 4 | 0 | 64
3:30 | 3455.5 | 132.5 | 1251 | 0 | 180 | 82 | 4 | 0 | 62 | [6 empty] | Shortage
4:00 | 3438 | 133 | 1187 | 0 | 180 | 82 | 4 | 0 | 60
4:30 | 3474.5 | 133 | 1145 | 0 | 180 | 82 | 4 | 0 | 61
5:00 | 3511 | 133 | 1103 | 0 | 180 | 82 | 4 | 0 | 62
5:30 | 3512 | 133 | 1144.5 | 0 | 180 | 82 | 4 | 0 | 62
6:00 | 3513 | 133 | 1186 | 0 | 180 | 82 | 4 | 0 | 62
6:30 | 3542 | 132.5 | 1184 | 12 | 180 | 82 | 4 | 0 | 61 |  |  |  |  | Coal
7:00 | 3571 | 132 | 1182 | 24 | 180 | 82 | 4 | 0 | 60
7:30 | 3621 | 132 | 1233 | 53 | 180 | 82 | 4 | 0 | 60 |  |  |  | Oil |  |  |  | ,
8:00 | 3671 | 132 | 1284 | 82 | 180 | 82 | 4 | 0 | 60
8:30 | 3663 | 132 | 1353 | 97 | 180 | 82 | 11.5 | 0 | 63
9:00 | 3655 | 132 | 1422 | 112 | 180 | 82 | 19 | 0 | 66
9:30 | 3620.5 | 132 | 1393 | 121 | 180 | 81.5 | 21.5 | 0 | 66
10:00 | 3586 | 132 | 1364 | 130 | 180 | 81 | 24 | 0 | 66
10:30 | 3571 | 131.5 | 1389.5 | 130 | 180 | 80.5 | 28 | 0 | 67
11:00 | 3556 | 131 | 1415 | 130 | 180 | 80 | 32 | 0 | 68
11:30 | 3635 | 153.5 | 1413.5 | 130 | 180 | 80 | 35 | 0 | 70
12:00 | 3714 | 176 | 1412 | 130 | 180 | 80 | 38 | 0 | 72
12:30 | 3717.5 | 176 | 1423.5 | 130 | 180 | 80.5 | 35 | 0 | 73
13:00 | 3721 | 176 | 1435 | 130 | 180 | 81 | 32 | 0 | 74
13:30 | 3721 | 176 | 1435 | 130 | 180 | 81 | 32 | 0 | 74
14:00 | 3721 | 176 | 1435 | 130 | 180 | 81 | 32 | 0 | 74
14:30 | 3529.5 | 174 | 1335.5 | 122 | 179.5 | 81 | 23.5 | 0 | 69
15:00 | 3338 | 172 | 1236 | 114 | 179 | 81 | 15 | 0 | 64
15:30 | 3352.5 | 172 | 1231.5 | 106 | 179.5 | 81 | 13.5 | 0 | 63
16:00 | 3367 | 172 | 1227 | 98 | 180 | 81 | 12 | 0 | 62
16:30 | 3445.5 | 172 | 1289.5 | 120 | 180 | 81.5 | 14 | 0 | 66
17:00 | 3524 | 172 | 1352 | 142 | 180 | 82 | 16 | 0 | 70
17:30 | 3571.5 | 305 | 1535.5 | 590.5 | 180 | 82 | 22.5 | 0 | 80
18:00 | 3619 | 438 | 1719 | 1039 | 180 | 82 | 29 | 0 | 90
18:30 | 3673.5 | 438 | 1799.5 | 1047 | 180 | 82 | 25 | 0 | 90
19:00 | 3728 | 438 | 1880 | 1055 | 180 | 82 | 21 | 0 | 90
19:30 | 3894 | 438 | 1967 | 920 | 180 | 82 | 21 | 0 | 90
20:00 | 3850 | 443 | 2055 | 876 | 180 | 82 | 21 | 0 | 90
20:30 | 3795.5 | 443 | 2051.5 | 829.5 | 180 | 82 | 21 | 0 | 88
21:00 | 3741 | 443 | 2048 | 783 | 180 | 82 | 21 | 0 | 86
21:30 | 3779 | 443 | 1987.5 | 544.5 | 180 | 82 | 12.5 | 0 | 84
22:00 | 3817 | 443 | 1927 | 306 | 180 | 82 | 4 | 0 | 82
22:30 | 3772.5 | 321.5 | 1894 | 240.5 | 180 | 80 | 4 | 0 | 79
23:00 | 3728 | 200 | 1861 | 175 | 180 | 78 | 4 | 0 | 76
23:30 | 3650 | 200 | 1758 | 175 | 180 | 78 | 4 | 0 | 71 | Max Temp. in Dhaka |  | 17.3° C
24:00 | 3572 | 200 | 1655 | 175 | 180 | 78 | 4 | 0 | 66
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
HVDC
COAL
HYDRO
Total Energy Gen 144.182 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 144.182 MKWHr
Note on W13: Author:

## Generation
2019-12-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 40 | 41 | 41 | 41 | 41 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 38 | 38 | 961396
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.4 | 2.1 | 8.66 | 16.64 | 18.93 | 19.5 | 18.1 | 14.5 | 10.4 | 5.4 | 0.3 | [9 empty] | 114480
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 204 | 203 | 184 | 193 | 201 | 207 | 215 | 203 | 196 | 176 | 189 | 177 | 177 | 177 | 179 | 191 | 181 |  | 184 | 203 | 179 | 177 | 176 | 207 | 202 | 4537119
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 141 | 104 | 110 | 109 | 105 | 104 | 140 | 141 | 119 | 110 | 116 | 108 | 105 | 108 | 104 | 109 | 112 |  | 109 | 120 | 109 | 109 | 109 | 109 | 105 | 2788008
10 | Sikalbaha 150MW GTPP(Oil) | [8 empty] | 0
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 4 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 79950
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 47 |  | 51 | 51 | 51 | 51 | 17 | 17 | 0 | 265963
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 42 | 42 | 42 | 42 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 65 | 45 |  | 45 | 75 | 74 | 74 | 74 | 75 | 60 | 1313000
17 | Siddhirganj 335 MW CCPP | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 275 | 300 | 300 | 285 | 270 | 300 | 270 | 270 | 270 | 270 | 250 |  | 270 | 290 | 292 | 290 | 290 | 290 | 250 | 6610830
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 112 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 54 | 54 | 54 | 8 | 8 | 8 | 8 | 187 |  | 187 | 178 | 167 | 167 | 167 | 167 | 167 | 1605818
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 817000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 100 | 100 | 100 | 100 | 102 | 100 | 100 | 100 | 100 | 101 | 101 | 104 | 104 | 100 | 100 | 100 | 100 |  | 99 | 99 | 100 | 98 | 100 | 100 | 100 | 2398000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2026630
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 10 | 10 | 10 | 10 | 10 | 13 | 33 | 33 | 33 | 37 | 37 | 10 | 10 | 10 | 10 | 33 |  | 33 | 33 | 33 | 33 | 37 | 33 | 33 | 582264
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 295 | 305 | 285 | 290 | 300 | 300 | 290 | 295 | 275 | 310 | 280 | 350 | 295 | 285 | 275 | 280 | 325 | 295 |  | 320 | 290 | 285 | 265 | 290 | 290 | 270 | 7144000
| Ashuganj 450 MW CCPP(North) | 345 | 355 | 350 | 290 | 290 | 280 | 280 | 280 | 260 | 300 | 265 | 335 | 275 | 280 | 270 | 280 | 280 | 290 |  | 295 | 340 | 295 | 270 | 280 | 285 | 270 | 7393300
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | [21 empty] | 80 | 0 |  |  |  | 74136
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 355 | 355 | 354 | 353 | 357 | 365 | 356 | 362 | 356 | 354 | 369 | 368 | 369 | 330 | 300 | 300 | 300 | 315 |  | 300 | 328 | 335 | 351 | 351 | 352 | 354 | 8401920
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 340 | 300 | 350 | 350 | 350 | 350 | 350 | 320 | 320 | 320 | 300 | 300 | 300 | 330 | 330 |  | 400 | 420 | 450 | 450 | 450 | 450 | 380 | 8472250
41 | Haripur 360MW CCPP(HPL) | 314 | 352 | 368 | 303 | 288 | 320 | 320 | 374 | 377 | 377 | 326 | 308 | 338 | 308 | 309 | 310 | 331 | 310 |  | 310 | 311 | 370 | 367 | 331 | 334 | 330 | 7970000
42 | RPCL 210MW CCPP | 112 | 131 | 131 | 147 | 159 | 157 | 158 | 158 | 159 | 158 | 160 | 156 | 157 | 111 | 111 | 111 | 111 | 155 |  | 155 | 155 | 157 | 158 | 158 | 159 | 159 | 3391840
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1422000
45 | Fenchugonj CCPP Phase-2 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2121840
46 | Shajibazar 330 MW CCPP | [22 empty] | 21 | 74 | 70 | 77 | 801000
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 58 | 57 | 57 | 58 | 57 | 45 | 45 | 45 | 45 | 45 |  | 57 | 57 | 57 | 58 | 58 | 45 | 59 | 1230720
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 76 | 76 | 76 | 40 | 40 | 10 | 10 | 10 | 10 | 79 |  | 79 | 79 | 79 | 79 | 79 | 30 | 5 | 840000
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 238000
52 | Sylhet 50MW PP (EPL) | 36 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 0 | 22 | 28 | 33 | 36 | 36 | 35 | 37 | 40 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 568920
53 | Sylhet 10MW PP (Desh) | 8 | 0 | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 133740
54 | Hobiganj 11MW PP Cofidence-E | [10 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 0 |  | 134976
55 | Fenchugonj 51 MW PP (Barakatullah) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 39 | 39 | 42 | 44 | 17 | 11 | 11 | 11 | 11 | 44 |  | 45 | 45 | 45 | 45 | 45 | 45 | 5 | 565200
56 | Shahjahanulla 25 MW PP | [10 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 16 | 24 | 24 | 24 | 24 | 0 |  | 284544
57 | Bibiana-II 341 MW CCPP (Summit)
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | [6 empty] | 10 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 302832
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 16 | 19 | 19 | 0 |  | 140832
62 | Tangail 22 MW PP (Doreen) | [19 empty] | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 132300
63 | Impoprt (Tripura) | 66 | 64 | 64 | 60 | 62 | 62 | 60 | 60 | 66 | 66 | 68 | 72 | 74 | 68 | 64 | 62 | 70 | 90 |  | 90 | 90 | 90 | 86 | 82 | 76 | 66 | 1687680
64 | Malancha, Ctg. EPZ (United) | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 21 | 28 | 26 | 25 | 25 | 41 | 41 | 41 | 31 | 34 | 34 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 659520
65 | Feni 22MW PP (Doreen) | 19 | [9 empty] | 19 | 19 | 19 | 19 | 19 | 21 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 0 | 290808
66 | Feni 11 MW PP (Doreen) | [10 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 0 |  | 127800
67 | Jangalia 33MW PP (Summit) | [10 empty] | 33 | 33 | 15 | 8 | 8 | 8 | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 323400
68 | Cumilla 25 MW PP (Summit) | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 17 | 17 | 17 | 12 | 12 | 10 | 15 | 15 | 15 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 447020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 28 | 25 | 25 | 13 | 13 | 12 | 12 | 11 | 11 | 11 | 11 |  | 25 | 32 | 30 | 32 | 32 | 32 | 32 | 567180
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 15 | 25 |  | 25 | 25 | 24 | 24 | 25 | 16 | 12 | 529800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 31 | 28 | 28 | 28 | 28 | 28 | 31 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 760000
73 | Ghorashal 108MW PP (Regent) | 0 | [9 empty] | 52 | 52 | 52 | 12 | 12 | 12 | 12 | 106 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 905363
| Feni Lanka Power | [17 empty] | 35 | [8 empty] | 53580
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 0 | 7 | [8 empty] | 9600
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 3 | 76 |  | 93 | 93 | 94 | 94 | 60 | 24 | 0 | 501120
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 20 |  | 17 | [5 empty] | 0 | 56988
| Kaptai 7 MW Solar PP | [6 empty] | 0.162 | 1 | 1.7 | 1.8 | 4.4 | 4.3 | 4 | 3.2 | 2.1 | 0.9 | 0 | [9 empty] | 23760
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [26 empty] | 936
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 50 |  | 100 | 62 | 60 |  |  |  |  | 241920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 50 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 50 | 50 | 50 | 47 | 10 | 10 | 10 | 10 | 10 | 35 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 733752
93 | Ashuganj 51 MW PP (Midland) | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 43 | 7 | 7 | 7 | 7 | 7 | 19 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 543656
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 3 | 50 |  | 40 | 24 | 7 | 7 | 0 |  |  | 133200
95 | Patenga 50MW PP (Baraka) | [16 empty] | 1 | 32 |  | 41 | 50 | 50 | 34 | 19 | 19 | 0 | 206400
96 | Chattogram 108 MW PP (ECPV) | [21 empty] | 2 | 10 | 0 |  |  | 20160
97 | Katpotti 52 MW PP (Sinha) | [19 empty] | 30 | [6 empty] | 50832
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 10 |  | 15 | 15 | 0 |  |  |  |  | 42627
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 54 |  | 55 | 55 | 55 | 55 | 0 |  |  | 230668
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 163 | 163 | 163 | 163 | 163 | 130 | 3205300
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.7 | 0.5 | 0.2 | 0.1 | 0 | [9 empty] | 2600
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 53 |  | 53 | 53 | 53 | 53 | 53 | 35 | 0 | 304560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United)
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 70 |  | 70 | 70 | 70 | 70 | 10 | 0 |  | 324480
116 | Chandpur 200MW (Desh energy) | [17 empty] | 11 |  | 0 | [6 empty] | 27360
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 45 |  | 40 | 40 | 40 | 40 | 0 |  |  | 209090
118 | Bibiyana-III 400 MW CCPP | 365 | 378 | 368 | 363 | 383 | 374 | 374 | 385 | 361 | 324 | 299 | 319 | 367 | 295 | 290 | 295 | 334 | 305 |  | 321 | 356 | 300 | 290 | 303 | 300 | 291 | 8031000
| Jamalpur 115 MW PP (United) | [16 empty] | 2 | 70 |  | 50 | 30 | 30 | 30 | 0 |  |  | 228000
| Anwara 300 MW PP (United) | [17 empty] | 85 |  | 100 | 104 | 104 | 106 | 52 | 16 | 0 | 454145
120 | Eastern Zone Total | 4319 | 4127 | 3953 | 3766 | 3740 | 3815 | 3794.562 | 4000.2 | 4156.46 | 4137.64 | 4172.73 | 4311.1 | 4199.8 | 3779.2 | 3711.7 | 3718.4 | 3936.3 | 5079 |  | 5330 | 5473 | 5470 | 5300 | 5013 | 4771 | 4334 | 105171113
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 10 | 32 |  | 0 | [6 empty] | 40320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | 16 | 0 | [6 empty] | 8 | 80 | 80 | 80 | 80 | 80 | 64 | 48 | 48 | 96 |  | 110 | 110 | 110 | 110 | 80 | 64 | 32 | 1222080
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 62 | 65 | 65 | 65 | 50 | 50 | 50 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1518000
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 8 |  | 9 | 9 | 9 | 9 | 8 | 7 | 7 | 155965
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 7 | 13 | 7 | 7 | 7 | 4 | 4 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 105984
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [7 empty] | 32 | 54 | 0 | [7 empty] | 32 |  | 32 | 32 | 32 | 32 | 15 | 0 |  | 239328
146 | Bheramara HVDC | 169 | 133 | 132 | 133 | 133 | 133 | 132 | 132 | 132 | 132 | 131 | 176 | 176 | 173 | 172 | 172 | 172 | 438 |  | 438 | 438 | 443 | 443 | 443 | 200 | 200 | 5228000
147 | Bheramara 360 MW CCPP | 140 | 148 | 148 | 170 | 190 | 200 | 270 | 270 | 270 | 270 | 275 | 275 | 275 | 260 | 200 | 200 | 200 | 270 |  | 270 | 255 | 255 | 240 | 220 | 219 | 220 | 5521248
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 190 | 184 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 179 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4440600
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1195000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 198 | 195 | 179 | 177 | 173 | 172 | 175 | 174 | 177 | 130 | 130 | 130 | 175 | 174 | 168 | 169 | 181 | 183 |  | 195 | 196 | 198 | 200 | 192 | 181 | 178 | 4509455
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 151 | 153 | 156 | 156 | 156 | 156 | 156 | 157 | 130 | 130 | 130 | 156 | 170 | 170 | 173 | 183 | 170 |  | 174 | 178 | 182 | 183 | 178 | 177 | 167 | 4158691
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 432 | 428 | 371 | 369 | 370 | 371 | 371 | 371 | 347 | 328 | 306 | 306 | 372 | 368 | 371 | 372 | 438 | 381 |  | 423 | 435 | 445 | 441 | 357 | 370 | 350 | 8990490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [11 empty] | 18 | 22 | 3 | 3 | 3 | 5 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 168240
163 | Bogura 20 MW PP (Energyprima) | 14 | 0 | [8 empty] | 12 | 12 | 14 | 10 | 3 | 3 | 3 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 156384
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 76122
165 | Amnura 50 MW PP(Sinha) | [6 empty] | 24 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 34 |  | 18 | 18 | 18 | 18 | 0 |  |  | 598590
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 15 | 18 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 |  | 0 | [6 empty] | 158808
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 60 |  | 70 | 50 | 50 | 35 | 0 |  |  | 249696
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 14 | 70 |  | 70 | 63 | 50 | 38 | 0 |  |  | 269760
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.2 | 0.7 | 1.1 | 1.7 | 1.2 | 1.3 | 1.3 | 0.8 | 0.2 | 0.1 | [9 empty] | 8571
178
178