## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-12-27 | Friday
|  | Date (day): | 2019-12-27 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11223.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14261 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-26 | 2019-12-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 34 | 34 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 180 | 220 | 250 | 250
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 343 | 360 | 360 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 294 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 310 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 17 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1636 | 2132 | 3479 | 4128 | 806 | 624
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 150 | 30 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 43 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 44 | 84 | 84 | 146 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 196 | 204 | 0 | 215 |  |  | FGMO
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 134 | 0 | 0 |  |  | Under maint.
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 10 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 13 | 5 | 12
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 174 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 631.6 | 898 | 1219 | 1646 | 236 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under Maint.
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 315 | 335 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 37 | 30 | 37 |  | 8 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 63 | 73 | 150 | 180
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 81 | 90 | 90 |  | 73 | ST under shut down
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 104 | 87 | 101
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 34 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 14 | 14 | 14 |  | 11 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 0 | 0 | 9 | 116 | 0 | 0
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1085 | 1254 | 1525 | 2115 | 134 | 505
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 110 | 111 | 150 | 160 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 68 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 112 | 100 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 133.9 | 313 | 468.6 | 592 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 89 | 86 | 85 | 86
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 144 | 160 | 160 |  |  | GT-2 Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 17 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 76 | 75 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 12 | 39 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 310 | 341 | 341
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 333 | 365 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1287 | 1442 | 1547 | 1552 | 0 | 159
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 310 | 648 | 180 | 460
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 7 | 0 | 30 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 310 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 32 | 32 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 587 | 990 | 822 | 1665 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 26 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 96 | 96 | 95 | 95 |  | 100 | GT-2+ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 74 | 75 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 189 | 213 | 280 | 350 | 0 | 113
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 60 | 60 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 169 | 194 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage.
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 187 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 396 | 370 | 400 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 5 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 799 | 973 | 1512 | 1806 | 341 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 250 | 260
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 114 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 164.3 | 274 | 371 | 407 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6512.8 | 8489 | 11223.6 | 14261 | 1569 | 1679
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6092.5702 | 7941.2586 | 10499.4121 | 13340.8279
A. |  | 2019-12-26 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8555 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4984 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8555 | MW
3 | Day peak Generation : |  |  | 6512.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8003 | MW
4 | Evening peak Generation : |  |  | 8555 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 157.6554 | MKWHr | By Solar | 0.14606 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 137.2553 | MKWHr |  | By Oil: | 5.4159 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.0737 | MKWHr |  | By Hydro: | 0.9837 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1569 | MW | Dhaka | 2881 | 2881 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1679 | MW | Chittagong | 830 | 830 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3248 | MW | Khulna | 996 | 996 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1072.2 | MMCFD |  |  | Rajshahi | 840 | 840 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129163065.194 | ii) Oil : | Taka | 38241679.68 | Comilla | 716 | 716 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16661433 | Total | Taka | 184066177.874 | Mymensingh | 627 | 627 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.935 | MKWHr. | Sylhet | 320 | 320 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -276 | MW (E to W) at | 19:00 | hrs | Barisal | 217 | 217 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -396 | MW at | 6:00 | hrs | Rangpur | 576 | 576 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 21.8° C |  |  | Total | 8003 | 8003 |  | 0
B. |  | 2019-12-27 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 21.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14261 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 5900 | MW
4 | Reserve(Generation end) |  |  |  | 6561 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 141.899 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4418 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.8233 | MKWHr. | ii) HVDC Flow at Peak Time |  | 648 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9574 | MKWHr. | iii) Maximum HVDC Flow : |  | 649 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.39 |  | (b) Today: | 96.34 |  | (c) Rule Curve: |  | 103.5
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 34 | 0 | 99 | 0 | 215 | 0 | 0 | 342 | 250 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 30 | 0 | 0 | 44 | 0 | 100 | 100 | 0 | 202 | 0 | 104 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 270 | 0 | 8 | 52 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 72 | 113 | 0 | 0 | 0 | 60 | 86 | 5 | 5 | 100 | 144 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4193 | 1390 | 5583 | 3705 | 136 | 1439 | 0 | 180 | 44 | 7 | 72 | 0 | 0 | 96.39
2:00 | 34 | 0 | 99 | 0 | 215 | 0 | 0 | 341 | 230 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 30 | 0 | 0 | 44 | 0 | 100 | 100 | 0 | 182 | 0 | 75 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 270 | 0 | 8 | 50 | 37 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 70 | 113 | 0 | 0 | 0 | 35 | 86 | 5 | 5 | 100 | 145 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4067 | 1302 | 5369 | 3591 | 136 | 1341 | 0 | 180 | 44 | 7 | 70 | 0 | 0 | 96.39
3:00 | 34 | 0 | 102 | 0 | 215 | 0 | 0 | 329 | 200 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 30 | 0 | 0 | 44 | 0 | 100 | 100 | 0 | 182 | 0 | 75 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 250 | 0 | 8 | 50 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 66 | 135 | 0 | 0 | 0 | 30 | 86 | 5 | 5 | 100 | 144 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3938 | 1233 | 5171 | 3491 | 136 | 1247 | 0 | 180 | 44 | 7 | 66 | 0 | 0 | 96.39
4:00 | 34 | 0 | 102 | 0 | 150 | 0 | 0 | 280 | 200 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 30 | 0 | 0 | 42 | 0 | 100 | 100 | 0 | 182 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 260 | 0 | 8 | 50 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 113 | 0 | 0 | 0 | 30 | 86 | 5 | 5 | 100 | 143 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3772 | 1212 | 4984 | 3311 | 136 | 1251 | 0 | 180 | 42 | 0 | 64 | 0 | 0 | 96.39
5:00 | 34 | 0 | 102 | 0 | 150 | 0 | 0 | 280 | 200 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 30 | 0 | 0 | 42 | 0 | 100 | 100 | 0 | 182 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 80 | 0 | 0 | 260 | 260 | 0 | 8 | 51 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 112 | 0 | 0 | 0 | 30 | 86 | 5 | 5 | 100 | 143 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3785 | 1210 | 4995 | 3312 | 136 | 1261 | 0 | 180 | 42 | 0 | 64 | 0 | 0 | 96.39
6:00 | 34 | 0 | 101 | 0 | 150 | 0 | 0 | 307 | 200 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 30 | 0 | 0 | 42 | 0 | 100 | 100 | 0 | 195 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 80 | 0 | 0 | 290 | 260 | 0 | 8 | 49 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 112 | 0 | 0 | 0 | 30 | 86 | 5 | 5 | 100 | 159 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3938 | 1212 | 5150 | 3447 | 136 | 1281 | 0 | 180 | 42 | 0 | 64 | 0 | 0 | 96.39
7:00 | 34 | 0 | 102 | 0 | 150 | 0 | 0 | 374 | 290 |  | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 30 | 0 | 0 | 42 | 0 | 100 | 100 | 0 | 190 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 80 | 0 | 0 | 295 | 305 | 0 | 8 | 50 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 112 | 0 | 0 | 0 | 30 | 86 | 5 | 5 | 100 | 157 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 147 | 0 | 0 | 0 | 36 | 0 | 166 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 |  | 4202.1 | 1378.1 | 5580.2 | 3648 | 136 | 1509 | 0 | 180 | 42 | 0 | 64 | 1.2 | 0 | 96.38
8:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 371 | 300 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 43 | 0 | 100 | 100 | 0 | 196 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 300 | 320 | 0 | 8 | 90 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 33 | 14 | 70 | 161 | 0 | 0 | 0.3 | 30 | 88 | 5 | 5 | 100 | 160 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 184 | 0 | 0 | 0 | 83 | 0 | 184 | 0 | 395 | 0 | 0 | 0 | 32 | 0 | 0 | 0.8 | 0 |  | 4502.8 | 1566.8 | 6069.6 | 3971 | 136 | 1630 | 32 | 180 | 43 | 0 | 70 | 7.6 | 0 | 96.38
9:00 | 34 | 0 | 101 | 0 | 180 | 0 | 0 | 370 | 307 |  | 0 | 370 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 15 | 31 | 0 | 0 | 43 | 0 | 120 | 100 | 0 | 183 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 100 | 0 | 0 | 290 | 305 | 0 | 43 | 81 | 37 | 0 | 0 | 9 | 0 | 0 | 0 | 19 | 8 | 34 | 14 | 78 | 131 | 0 | 0 | 0.9 | 30 | 86 | 19 | 16 | 100 | 143 | 70 | 40 | 0 | 0 | 0 | 23 | 0 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 |  | 309 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 0 | 148 | 0 | 0 | 183 | 0 | 0 | 0 | 92 | 0 | 190 | 0 | 378 | 0 | 0 | 0 | 15 | 0 | 0 | 2.2 | 0 |  | 4674.6 | 1732.2 | 6406.8 | 4046 | 309 | 1752 | 15 | 148 | 43 | 0 | 78 | 15.8 | 0 | 96.38
10:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 342 | 283 |  | 0 | 370 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 15 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 183 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 125 | 0 | 0 | 290 | 305 | 0 | 61 | 80 | 37 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 76 | 109 | 0 | 22 | 0.1 | 35 | 86 | 45 | 50 | 100 | 145 | 70 | 60 | 0 | 0 | 17 | 25 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 307 | 0 | 5 | 0 | 2.3 | 0 | 0 | 0 | 0 | 49 |  | 309 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 158 | 0 | 0 | 168 | 0 | 0 | 0 | 96 | 0 | 188 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 |  | 4792.9 | 1704.4 | 6497.3 | 4016 | 309 | 1825 | 54 | 158 | 44 | 0 | 76 | 15.3 | 0 | 96.38
11:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 342 | 283 |  | 0 | 340 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 185 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 125 | 0 | 0 | 290 | 305 | 0 | 63 | 86 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 76 | 109 | 0 | 22 | 1.3 | 35 | 86 | 14 | 10 | 100 | 145 | 68 | 76 | 0 | 0 | 17 | 26 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 0 | 0 | 307 | 0 | 17 | 0 | 2.6 | 0 | 0 | 0 | 0 | 117 |  | 309 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 73 | 0 | 190 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 |  | 4795.1 | 1692.1 | 6487.2 | 4017 | 309 | 1735 | 134 | 160 | 44 | 0 | 76 | 12.2 | 0 | 96.37
12:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 344 | 252 |  | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 15 | 31 | 0 | 0 | 40 | 0 | 120 | 120 | 0 | 196 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 100 | 0 | 0 | 325 | 300 | 0 | 63 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 84 | 110 | 0 | 22 | 1.9 | 35 | 89 | 17 | 10 | 100 | 156 | 64 | 76 | 0 | 0 | 17 | 12 | 10 | 341 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 333 | 0 | 17 | 0 | 4.1 | 0 | 0 | 0 | 0 | 9 |  | 310 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 169 | 0 | 0 | 0 | 74 | 0 | 187 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 4773.5 | 1739.3 | 6512.8 | 4064 | 310 | 1794 | 26 | 160 | 40 | 7 | 84 | 27.8 | 0 | 96.37
13:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 380 | 332 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 40 | 0 | 120 | 120 | 0 | 182 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 100 | 0 | 0 | 315 | 275 | 0 | 73 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 88 | 112 | 0 | 22 | 1.6 | 35 | 86 | 14 | 10 | 100 | 156 | 65 | 76 | 0 | 0 | 17 | 13 | 10 | 330 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 17 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 |  | 309 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 97 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 95 | 0 | 189 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 |  | 4868.4 | 1811.8 | 6680.2 | 4108 | 309 | 1924 | 34 | 160 | 40 | 7 | 88 | 10.2 | 0 | 96.37
14:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 343 | 313 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 24 | 15 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 184 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 100 | 0 | 0 | 290 | 260 | 0 | 73 | 85 | 36 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 88 | 113 | 0 | 22 | 1.4 | 35 | 86 | 11 | 10 | 100 | 145 | 66 | 76 | 0 | 0 | 17 | 14 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 |  | 309 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 0 | 0 | 95 | 0 | 190 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4720.4 | 1756.4 | 6476.8 | 4009 | 309 | 1823 | 17 | 160 | 44 | 7 | 88 | 19.8 | 0 | 96.37
15:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 349 | 313 |  | 0 | 340 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 42 | 0 | 120 | 120 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 100 | 0 | 0 | 290 | 260 | 0 | 73 | 80 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 5 | 90 | 110 | 0 | 22 | 1 | 35 | 86 | 11 | 10 | 100 | 145 | 66 | 76 | 0 | 0 | 17 | 14 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 |  | 306 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 160 | 0 | 0 | 199 | 0 | 0 | 0 | 74 | 0 | 193 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 |  | 4685.1 | 1761.3 | 6446.4 | 4009 | 306 | 1802 | 17 | 160 | 42 | 7 | 90 | 13.4 | 0 | 96.36
16:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 342 | 282 |  | 0 | 340 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 42 | 0 | 120 | 120 | 0 | 182 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 100 | 0 | 0 | 260 | 270 | 0 | 73 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 86 | 110 | 0 | 22 | 0.3 | 33 | 86 | 14 | 10 | 100 | 143 | 66 | 76 | 0 | 0 | 17 | 14 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 112 |  | 306 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 10 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 73 | 0 | 216 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 |  | 4714.9 | 1743.8 | 6458.7 | 3991 | 306 | 1734 | 129 | 160 | 42 | 7 | 86 | 3.7 | 0 | 96.36
17:00 | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 347 | 282 |  | 0 | 340 | 0 | 1 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 15 | 31 | 0 | 0 | 43 | 0 | 120 | 120 | 0 | 192 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 100 | 0 | 0 | 280 | 290 | 0 | 73 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 98 | 110 | 3 | 22 | 0 | 35 | 86 | 14 | 10 | 100 | 151 | 66 | 76 | 0 | 0 | 17 | 13 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0 | 0 | 321 | 1 | 5 | 1 | 0 | 16 | 0 | 0 | 0 | 116 |  | 449 | 0 | 290 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 10 | 0 | 0 | 160 | 0 | 0 | 195 | 0 | 0 | 0 | 74 | 0 | 191 | 0 | 369 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 0 |  | 4856.3 | 1895.1 | 6751.4 | 4048 | 449 | 1757 | 196 | 160 | 43 | 0 | 98 | 0.4 | 0 | 96.36
18:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 353 | 302 |  | 0 | 380 | 0 | 58 | 4 | 15 | 280 | 0 | 0 | 0 | 7 | 32 | 16 | 0 | 0 | 0 | 6 | 53 | 35 | 0 | 22 | 25 | 16 | 15 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 4 | 100 | 0 | 0 | 310 | 280 | 0 | 73 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 14 | 106 | 110 | 50 | 22 | 0 | 60 | 86 | 50 | 28 | 100 | 150 | 66 | 76 | 0 | 0 | 17 | 36 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 345 | 40 | 17 | 17 | 0 | 140 | 0 | 0 | 0 | 116 |  | 649 | 0 | 320 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 17 | 32 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 202 | 0 | 0 | 0 | 74 | 0 | 191 | 0 | 386 | 0 | 0 | 0 | 67 | 109 | 0 | 0 | 55 |  | 5640 | 2528 | 8168 | 4259 | 649 | 1921 | 963 | 160 | 44 | 66 | 106 | 0 | 0 | 96.36
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 343 | 294 |  | 0 | 400 | 0 | 100 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 13 | 100 | 0 | 0 | 315 | 305 | 0 | 73 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 111 | 68 | 22 | 0 | 60 | 86 | 53 | 50 | 130 | 144 | 67 | 76 | 0 | 0 | 17 | 39 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 365 | 112 | 17 | 17 | 0 | 174 | 0 | 0 | 0 | 116 |  | 648 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 26 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 0 | 0 | 75 | 0 | 187 | 0 | 370 | 0 | 0 | 0 | 32 | 114 | 0 | 0 | 109 |  | 6039 | 2516 | 8555 | 4370 | 648 | 1989 | 1174 | 160 | 44 | 66 | 104 | 0 | 0 | 96.35
19:30 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 342 | 294 |  | 0 | 400 | 0 | 100 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 133 | 0 |  | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 17 | 100 | 0 | 0 | 315 | 305 | 0 | 73 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 111 | 68 | 22 | 0 | 60 | 86 | 53 | 50 | 130 | 145 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 115 | 17 | 0 | 0 | 180 | 0 | 0 | 0 | 116 |  | 649 | 0 | 310 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 26 | 16 | 0 | 0 | 30 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 75 | 0 | 186 | 0 | 386 | 0 | 0 | 0 | 32 | 92 | 0 | 0 | 71 |  | 6013 | 2481 | 8494 | 4390 | 649 | 2004 | 1079 | 160 | 44 | 66 | 102 | 0 | 0 | 0
20:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 341 | 285 |  | 0 | 400 | 0 | 65 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 25 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 18 | 100 | 0 | 0 | 315 | 305 | 0 | 78 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 107 | 68 | 22 | 0 | 60 | 86 | 53 | 50 | 130 | 146 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 115 | 17 | 0 | 0 | 184 | 0 | 0 | 0 | 116 |  | 649 | 0 | 310 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 25 | 16 | 0 | 0 | 30 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 0 | 0 | 75 | 0 | 187 | 0 | 382 | 0 | 0 | 0 | 32 | 72 | 0 | 0 | 35 |  | 5908 | 2420 | 8328 | 4384 | 649 | 1991 | 932 | 160 | 44 | 66 | 102 | 0 | 0 | 0
21:00 | 34 | 0 | 98 | 0 | 220 | 0 | 0 | 342 | 285 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 0 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 27 | 100 | 0 | 0 | 315 | 305 | 0 | 78 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 98 | 106 | 68 | 22 | 0 | 58 | 86 | 53 | 50 | 130 | 145 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 115 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 116 |  | 649 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 26 | 16 | 0 | 0 | 50 | 50 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 0 | 0 | 75 | 0 | 184 | 0 | 362 | 0 | 0 | 0 | 15 | 70 | 0 | 0 | 35 |  | 5592 | 2338 | 7930 | 4371 | 649 | 1986 | 562 | 160 | 44 | 60 | 98 | 0 | 0 | 0
22:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 341 | 286 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 0 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 100 | 0 | 0 | 315 | 305 | 0 | 78 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 90 | 108 | 42 | 22 | 0 | 60 | 86 | 53 | 50 | 130 | 143 | 68 | 76 | 0 | 0 | 17 | 39 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 |  | 547 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 23 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 188 | 0 | 0 | 0 | 75 | 0 | 191 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5266 | 2016 | 7282 | 4299 | 547 | 1943 | 199 | 160 | 44 | 0 | 90 | 0 | 0 | 0
23:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 341 | 286 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 203 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 100 | 0 | 0 | 315 | 295 | 0 | 78 | 80 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 86 | 108 | 0 | 22 | 0 | 60 | 86 | 5 | 5 | 100 | 144 | 68 | 50 | 0 | 0 | 0 | 39 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 |  | 305 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 23 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 176 | 0 | 0 | 0 | 48 | 0 | 191 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4937 | 1719 | 6656 | 4216 | 305 | 1712 | 133 | 160 | 44 | 0 | 86 | 0 | 0 | 0
24:00 | 34 | 0 | 103 | 0 | 220 | 0 | 0 | 341 | 295 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 31 | 0 | 0 | 44 | 0 | 100 | 100 | 0 | 176 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 100 | 0 | 0 | 270 | 295 | 0 | 78 | 50 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 107 | 0 | 0 | 0 | 60 | 86 | 5 | 5 | 100 | 144 | 52 | 40 | 0 | 0 | 0 | 6 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 |  | 209 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 21 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4453 | 1547 | 6000 | 3811 | 209 | 1571 | 133 | 160 | 44 | 0 | 72 | 0 | 0 | 0
KWH | 800000 | 0 | 2407000 | 0 | 4187300 | 0 | 0 | 8369660 | 6602000 |  | 0 | 8133250 | 0 | 260160 | 12528 | 21856 | 6613967 | 0 | 0 | 0 | 7680 | 260208 | 57600 | 0 | 0 | 0 | 26304 | 357480 | 63894 | 0 | 371772 | 600000 | 627480 | 637800 | 802400 | 0 | 0 | 983700 | 0 | 2700000 | 2800000 | 0 | 4537652 | 0 | 2477326 | 0 |  | 0 | 28352 | 0 | 0 | 0 | 93120 | 271152 | 351360 | 2348982 | 0 | 0 | 7304000 | 7034500 | 0 | 1187636 | 1738180 | 682920 | 0 | 0 | 717400 | 0 | 0 | 0 | 115920 | 61560 | 467500 | 250290 | 1957440 | 2695280 | 337920 | 300132 | 19800 | 995000 | 2041060 | 444600 | 482040 | 2825738 | 3316000 | 1427616 | 1146240 | 0 | 0 | 260000 | 443640 | 137340 | 7453500 | 275208 | 118992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95985 | 26880 | 0 | 0 | 8014000 | 459600 | 122112 | 43842 | 8550 | 587127 | 0 | 0 | 0 | 1142400 |  | 7823272 | 0 | 6901344 | 0 | 165120 | 0 | 0 | 0 | 0 | 33016 | 0 | 2340869 | 446600 | 91392 | 0 | 0 | 205000 | 218752 | 0 | 0 | 108180 | 0 | 0 | 0 | 0 | 300720 | 118332 | 224892 | 0 | 0 | 4073700 | 0 | 0 | 4453191 | 0 | 0 | 0 | 1387419 | 0 | 4596673 | 0 | 8704872 | 0 | 0 | 0 | 209440 | 388800 | 0 | 21728 | 292128 |  | 114549931 | 43105440 | 157655371 | 96372618 | 7823272 | 40882687 | 5078171 | 4073700 | 983700 | 337720 | 1957440 | 146063 | 0
Fuel Cost | 896000 | 0 | 2575490 | 0 | 3098602 | 0 | 0 | 6026155.2 | 5017520 |  | 0 | 6506600 | 0 | 2653632 | 135678.24 | 224242.56 | 8201319.08 | 0 | 0 | 0 | 85248 | 2643713.28 | 570816 | 0 | 0 | 0 | 246205.44 | 3428233.2 | 609548.76 | 0 | 278829 | 450000 | 0 | 0 | 0 | 0 | 0 | 255762 | 0 | 4131000 | 4284000 | 0 | 4764534.6 | 0 | 3146204.02 | 0 |  | 0 | 300247.68 | 0 | 0 | 0 | 871603.2 | 249459.84 | 976780.8 | 2466431.1 | 0 | 0 | 5404960 | 5908980 | 0 | 1163883.28 | 2311779.4 | 559994.4 | 0 | 0 | 1025882 | 0 | 0 | 0 | 118238.4 | 46170 | 883575 | 187717.5 | 13506336 | 2210129.6 | 3213619.2 | 306134.64 | 324720 | 1353200 | 2775841.6 | 604656 | 602550 | 3503915.12 | 3050720 | 2127147.84 | 2017382.4 | 0 | 0 | 413400 | 519058.8 | 322749 | 5291985 | 206406 | 90433.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107666.9 | 250521.6 | 0 | 0 | 7533160 | 4030692 | 1088017.92 | 414306.9 | 0 | 5413310.94 | 0 | 0 | 0 | 0 |  | 21122834.4 | 0 | 5383048.32 | 0 | 1591756.8 | 0 | 0 | 0 | 0 | 432509.6 | 0 | 1872695.2 | 692230 | 981550.08 | 0 | 0 | 385400 | 2436897.28 | 0 | 0 | 1121826.6 | 0 | 0 | 0 | 0 | 330792 | 195247.8 | 170243.244 | 0 | 0 | 16661433 | 0 | 0 | 3918808.08 | 0 | 0 | 0 | 2205996.21 | 0 | 4045072.24 | 0 | 6354556.56 | 0 | 0 | 0 | 1866110.4 | 3631392 | 0 | 0 | 0 |  | 144983097.36 | 75400399.814 | 220383497.174 | 91831280.224 | 21122834.4 | 37331784.97 | 34501209.12 | 16661433 | 255762 | 3740470.56 | 13506336 | 1432386.9 | 0
Yesterday Day Peak | 34 | 0 | 100 | 0 | 180 | 0 | 0 | 344 | 252 |  | 0 | 340 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 15 | 31 | 0 | 0 | 40 | 0 | 120 | 120 | 0 | 196 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 100 | 0 | 0 | 325 | 300 | 0 | 63 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 84 | 110 | 0 | 22 | 1.9 | 35 | 89 | 17 | 10 | 100 | 156 | 64 | 76 | 0 | 0 | 17 | 12 | 10 | 341 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 333 | 0 | 17 | 0 | 4.1 | 0 | 0 | 0 | 0 | 9 |  | 310 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 11 | 0 | 0 | 160 | 0 | 0 | 169 | 0 | 0 | 0 | 74 | 0 | 187 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 6512.8 | DayPeak
Yesterday Evening Peak | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 343 | 294 | 0 | 0 | 400 | 0 | 100 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 31 | 0 | 0 | 44 | 0 | 120 | 120 | 0 | 204 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 13 | 100 | 0 | 0 | 315 | 305 | 0 | 73 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 111 | 68 | 22 | 0 | 60 | 86 | 53 | 50 | 130 | 144 | 67 | 76 | 0 | 0 | 17 | 39 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 365 | 112 | 17 | 17 | 0 | 174 | 0 | 0 | 0 | 116 |  | 648 | 0 | 310 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 26 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 0 | 0 | 75 | 0 | 187 | 0 | 370 | 0 | 0 | 0 | 32 | 114 | 0 | 0 | 109 |  | 8555 | EvPeak
Forecast for Evening | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 40 | 120 | 150 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 12 | 100 | 0 | 0 | 360 | 360 | 0 | 180 | 90 | 37 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 101 | 160 | 95 | 22 | 0 | 60 | 86 | 51 | 44 | 163 | 160 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 |  |  | 460 | 40 | 410 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 95 | 20 | 110 | 30 | 0 | 60 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 260 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 100 | 0 | 250 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 40 | 120 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 50 | 21 | 5 | 100 | 0 | 0 | 335 | 360 | 0 | 150 | 90 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 87 | 150 | 95 | 22 | 1.6 | 60 | 85 | 51 | 44 | 163 | 160 | 66 | 75 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 150 | 100 | 400 | 100 | 100 | 105 | 5 | 230 | 54 | 50 | 0 |  |  | 180 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 95 | 20 | 70 | 0 | 0 | 60 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 250 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 220 | 0 | 400 | 50 | 100 | 0 | 32 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 34 | 0 | 101 | 0 | 200 | 0 | 0 | 300 | 240 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 10 | 14 | 0 | 0 | 44 | 0 | 100 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 0 | 305 | 300 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 115 | 0 | 0 | 0.1 | 0 | 86 | 2 | 0 | 0 | 142 | 57 | 2 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0.8 | 30 | 0 | 0 | 0 | 117 | 0 | 137 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 157 | 0 | 0 | 0 | 17 | 0 | 130 | 0 | 371 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4984 | 4:00
| Highest Generation |  | 8555 | 19:00
| Day Peak Generation |  | 6512.8 | 12:00
| Evening Peak Generation |  | 8555 | 19:00
| HVDC Max Flow |  | 649 | 18:00
| HVDC EvPeak Flow |  | 648 | 19:00
| Load factor L.F |  | 76.79%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-12-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6512.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4418 | MW
Evening Peak Generation : |  | 8555 | MW Hour : | 19:00 | Available Max Generation : |  | 14261 | MW
E.P. Demand (at gen end) : |  | 8555 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7700 | MW
Maximum Generation : |  | 8555 | MW Hour : | 19:00 | Reserve(Generation end) |  | 6561 | MW
Total Gen. (MKWH) : |  | 157.6554 | System Load Factor : | 76.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -396 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-12-27
Actual : | 96.34 | Ft.(MSL) , | Rule curve : | 103.5 | Ft.( MSL )
Gas Consumed : | Total = | 1072.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129163065.194
: |  | Coal : | 16661433 | Oil : | 38241679.68 | Total : | 184066177.874
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2700.5203 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 909.2825 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 813.0755 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 734.1101 |  |  | 0 | 0%
) | 0 | 0:00 | 663.7202 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 535.5759 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 311.1057 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 138.2044 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 413.007 |  |  | 0 | 0%
Total | 0 |  | 7218.6017 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 11) Sirajganj unit-2
|  |  |  | 2) Summit Meghna 305 MW | 10) Baghabari 100 MW
|  |  |  | 3) Ghorasal Unit-1,3,5 | 12) Sikalbaha 150 MW
4) Chandpur CCPP ST
5) Sylhet 150 MW
6) Bhola-225 MW GT-2 & ST
7) Ashuganj Precision
8) Ashuganj 225 MW CCPP
9) Ashuganj unit-4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kodda 132/33 kV T-2 transformer was under shut down from 08:53 to 16:05 for A/M.
b) Hathazari-GPH 230 kV Ckt was shut down at 08:30 for A/M.
c) Shahmirpur-Sikalbaha 132 kV Ckt-1 was under shut down from 08:05 to 14:32 for A/M.
d) Cumilla(s) 132/33 kV T-1 transformer was under shut down from 08:10 to 16:05 for A/M.
e) Mymensingh 132/33 kV T-3 transformer was under shut down from 09:25 to 16:20 for A/M.
f) Shahjibazar-Srimongal 132 kV Ckt-1 was under shut down from 09:41 to 16:58 for A/M.
g) Sonargaon 132 kV bus-2 was under shut down from 10:04 to 11:11 for A/M.
h) Aminbazar-Meghnaghat 230 kV Ckt-2 was shut down at 10:32 for D/W.
i) Tangail-RPCL 132 kV Ckt-2 was under shut down from 10:12 to 16:56 for A/M.
j) Niamatpur 132/33 kV T-3 transformer was under shut down from 08:41 to 15:19 for A/M.
k) Polashbari-Mohosthangarh 132 kV Ckt-1 was under shut down from 10:33 to 15:06 for A/M.
l) Bogura-Sherpur 132 kV Ckt-1 was under shut down from 11:54 to 12:15 for protection test.
m) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down from 09:29 to 15:53 for A/M.
n) Siddhirganj-Dutch bangla 132 kV Ckt was under shut down from 09:30 to 10:45 for sparking at tower no 2.
o) Dhanmondi-Ullon 132 kV Ckt-1 was under shut down from 10:50 to 12for relay testing by SPMD.
p) Jaldhaka 132/33 kV T-2 transformer was under shut down from 12:15 to 15:28 for oil leakage at Buchholz |  |  |  |  | About 04 MW power interruption occurred under Jaldhaka S/S area
relay. |  |  |  |  | from 12:15 to 15:28.
r) Dhanmondi-Dhaka University 132 kV Cable charged at 12:28 from Dhanmondi end.
s) Tongi(new) 132 kV Bus-1 & T-1 transformer were under shut down from 08:11 to 15:08 for A/M.
t) Aminbazar 230/132 kV T0-2 transformer was under shut down from 08:47 to 16:36.
u) Chowmuhoni HFPL 113 MW Synchronized and started RRT at 15:30.
v) Bhola-Barishal 230 kV Ckt-2 was switched on at 21:36.
w) Hasnabad 132/33 kV all transformer tripped at 01:05(27/12/2019) for 33 kV Lalbagh feeder fault and was |  |  |  |  | About 75 MW power interruption occurred under Hasnabad S/S area
switched on at 01:55. |  |  |  |  | from 01:05(27/12/2019) to 01:55.
x) Sitalakkhya-Hasnabad 132 kV Ckt tripped at 01:01(27/12/2019) showing dist. Z2 at Y,B-phase from Sitalakkhya
end and dist. Z2 at Y,B-phase from Hasnabad end and was switched on at 02:33.
y) Sitalakkhya-Madanganj 132 kV Ckt tripped at 01:01(27/12/2019) showing main protection trip from |  |  |  |  | About 55 MW power interruption occurred under Sitalakkhya S/S area
Madanganj end and was switched on at 02:07. |  |  |  |  | from 01:01(27/12/2019) to 02:07.
z) Bhola 225 MW CCPP tripped at 01:43(27/12/2019) fro GBC fault and was GT-2 synchronized at 04:40.
aa) Sikalbaha 225 MW CCPP tripped at 04:42(27/12/2019) due to low gas pressure.
ab) Sikalbaha 150 MW GT force shut down at 23:49 due to blow valve got stuck up.
ac) Halishahar 132 kV main bus was shut down at 07:39 for A/M & C/M. |  |  |  |  | About 70 MW power interruption occurred under Halishahar S/S area
from 07:39(27/12/2019) to till now.
ab) Mymensing 33 kv bus under T2 transformer shutdown since at 07:11 for PBS maintenance work.
ac) Sirajganj #03 tripped at 07:41 due to DP high.
ad) Faridpur- Bheramara 132 kV Ckt-1 is under shut down since at 07:29 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 34 | 800000 | Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | #REF!
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2407000 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 4187300 | Gas shortage.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 343 | 8369660 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 294 | 6602000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8133250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 260160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 12528 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 21856 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 371772
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 7680 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 6613967 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 260208
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 26304 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 357480
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 57600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 63894 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1227480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 637800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 802400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 122112 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2132 | 41342451
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 95985 | Day peak load
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 93120 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 44 | 983700 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4537652 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 2477326 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 43842 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 28352
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 26880 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 271152
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 351360
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 8550
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 174 | 587127 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 898 | 15005046
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2348982 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7304000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7034500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 682920 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 73 | 1187636 | Transformer O/L
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 717400 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 1738180 | Low demand
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 115920
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 61560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 1957440
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 467500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 250290 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 0 | 116 | 1142400
| Cumilla Area Total |  |  |  | 2920 | 1254 | 25008728
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 111 | 2695280 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 300132
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 68 | 337920 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 19800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 112 | 459600
| Mymensingh Area Total |  |  |  | 637 | 313 | 3812732
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 995000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 86 | 2041060
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2825738
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3316000 | GT2 under shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 444600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 482040
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 118992
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1427616 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1146240 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 260000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 39 | 443640 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 275208
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7453500 | Low demand
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 365 | 8014000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 137340
| Sylhet Area Total |  |  |  | 1949 | 1442 | 29380974
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 648 | 7823272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 165120 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 33016 | Reserve
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 310 | 6901344 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 32 | 209440 | Low demand
| Khulna Area Total |  |  |  | 2314 | 990 | 15132192
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 91392 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 446600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 96 | 2340869 | GT1 & ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 1387419 | Gas shortage.
| Barisal Area Total |  |  |  | 462 | 213 | 4266280
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 205000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 218752
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 108180 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 194 | 4453191 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4596673 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8704872 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 300720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 118332 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224892
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 292128
| Rajshahi Area Total |  |  |  | 2183 | 973 | 19222740
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 4073700
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 114 | 388800
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 21728
| Rangpur Area Total |  |  |  | 605 | 274 | 4484228
| Total |  |  |  | 19047 | 8489 | 157655371
| Eastern Grid Total |  |  |  | 13483 | 6039 | 114549931
| Western Grid Total |  |  |  | 5564 | 2450 | 43105440
| National Grid Total |  |  |  | 19047 | 8489 | 157655371
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-26
(a) ENTIRE EASTERN GRID : |  | 5374 | MW | (b) ENTIRE WESTERN GRID : |  | 2629 | MW
i) Dhaka area |  | 2881 | MW | i) Khulna area |  | 996 | MW
ii) Chittagong area |  | 830 | MW | ii) Rajshahi area |  | 840 | MW
iii) Comilla area |  | 716 | MW | iii) Barisal area |  | 217 | MW
iv) Mymensingh area |  | 627 | MW | iv) Rangpur area |  | 576 | MW
v) Sylhet area |  | 320 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8003 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 17:00 | Shahjibazar | 77 | 18:00 | Bottail | 98 | 18:00
Munsiganj | 70 | 19:00 | Fenchuganj | 25 | 18:00 | G.K Project | 26 | 18:00
Sonargaon | 68 | 18:30 | Kulawara | 31 | 18:00 | Faridpur | 130 | 18:00
Shyampur | 168 | 10:00 | Sylhet | 97 | 18:00 | Madaripur | 57 | 19:30
Bhulta | 149 | 12:00 | Chatak | 17 | 18:30 | Sariatpur | 36 | 18:30
Madanganj | 54 | 18:00 | Sunamganj | 28 | 19:30 | Gopalganj | 65 | 18:00
Shitalakhya | 92 | 12:00 | Biani Bazar | 28 | 18:00 | Bagerhat | 64 | 18:30
Rahim steel | 12 | 18:30 | Comilla (S) | 106 | 18:00 | Mongla | 38 | 9:00
Matuail | 66 | 10:00 | Comilla(N) | 89 | 22:00 | Satkhira | 67 | 18:30
Ghorasal | 68 | 18:30 | Chandpur | 52 | 18:30 | Gallamari | 36 | 13:00
Narsingdi | 102 | 18:30 | Feni | 89 | 19:00 | Magura | 38 | 18:00
Haripur (SBU) | 87 | 10:00 | Chowmuhani | 112 | 19:00 | Norail | 27 | 18:00
Ullon | 53 | 13:00 | Ashuganj | 38 | 18:30 | Chuadanga | 60 | 18:00
Hasnabad | 120 | 18:30 | Daudkandi | 80 | 19:30 | Barisal(N) | 28 | 18:30
Magbazar | 66 | 13:00 | B.Baria | 89 | 19:30 | Barisal (S) | 62 | 18:00
Maniknagar | 74 | 18:00 | Ramganj | 66 | 18:00 | Patuakhali | 74 | 18:30
Bangabhaban | 14 | 13:00 | Chaddagram | 14 | 18:00 | Bhandaria | 40 | 20:00
Narinda | 66 | 11:00 | PHP | 1 | 10:00 | Borhan Uddin | 23 | 19:30
Dhanmondi | 81 | 14:00 | Madunaghat | 41 | 18:30 | Ishurdi | 48 | 18:30
Lalbag | 80 | 13:00 | Hathazari | 69 | 18:30 | Ruppur Paromanobik | 1 | 1:00
Madartek | 30 | 13:00 | Khulshi | 124 | 17:00 | Natore | 85 | 19:00
Mirpur | 62 | 11:00 | Halishahar | 86 | 17:00 | Bogra | 118 | 19:00
Kalyanpur | 69 | 18:00 | Baraulia | 114 | 9:00 | Noagaon | 79 | 19:00
Gulshan | 88 | 18:00 | Sikalbaha | 18 | 18:30 | Rajshahi | 93 | 19:30
Uttara | 37 | 18:00 | Dohazari | 65 | 19:00 | Rajshahi New | 8 | 18:00
Uttara New | 24 | 18:00 | Cox'sbazar | 67 | 18:00 | C.Nawabganj | 53 | 12:00
Kamrangirchar | 59 | 18:00 | Chandraghona | 22 | 18:00 | Amnura | 24 | 18:30
Savar | 94 | 12:00 | Kaptai | 3.5 | 18:00 | Pabna | 71 | 19:00
Bhasantec | 100 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 74 | 18:30
Agargaon | 34 | 13:00 | Bakulia | 69 | 18:30 | Serajganj | 55 | 10:00
Satmosjid | 70 | 13:00 | Julda | 16 | 1:00 | Niyamatpur | 45 | 18:00
Tongi | 101 | 18:00 | TK chemical | 10.3 | 19:00 | Joypurhat | 42 | 18:00
Kabirpur | 121 | 18:30 | Modern Steel | 14 | 10:00 | Sherpur(Bogura) | 34 | 18:00
Basundhara | 63 | 18:00 | Shahmirpur | 23 | 9:00 | Mohastangor | 25 | 18:00
Manikganj | 70 | 18:30 | Khagrachhari | 16 | 18:00 | Rangpur | 109 | 18:30
Joydevpur | 152 | 19:00 | Matarbari | 20.5 | 18:30 | Lalmonirhat | 41 | 18:00
New Tongi | 72 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 86 | 18:30
Korda | 176 | 12:00 | Rangamati | 8 | 18:00 | Purbasadipur | 87 | 19:00
Dhamrai | 36 | 18:00 | Abul Khair 230 | 61 | 14:00 | Thakurgaon | 58 | 18:30
Valuka | 74 | 18:00 | BSRM | 100 | 2:00 | Palashbari | 87 | 18:00
Tangail | 126 | 18:00 | GPH Ispat | 6 | 1:00 | Barapukuria | 42 | 19:30
Mymensing | 154 | 18:30 | Goalpara | 22 | 13:00 | Panchagar | 39 | 18:00
Kishorganj | 74 | 18:30 | Central s/s | 57 | 18:00 | Joldhaka | 20 | 18:00
Netrokona | 60 | 19:00 | Noapara | 47 | 18:00 | Kurigram | 40 | 18:30
Jamalpur | 83 | 18:00 | Jessore | 78 | 18:00
Sherpur | 68 | 19:00 | Benapol | 28 | 18:00
Srimongal | 25 | 18:30 | Jhenida | 78 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-26 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 400 | 0.16667 | 390 | 0.66667 | Kaliakoir | 388 | 0.16667 | 374 | 0.5
Bheramara | 408 | 0.083333 | 396 | 0.45833 | Bhulta | 397 | 0.16667 | 387 | 0.5
Ashuganj(N) | 403 | 0.16667 | 394 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 230 | 0.33333 | Hathazari | 227 | 0.041667 | 222 | 0.54167
Ishurdi | 245 | 0.125 | 232 | 0.75 | Megnaghat | 235 | 0.041667 | 230 | 0.5
Ashuganj | 242 | 0.083333 | 239 | 0.54167 | Fenchuganj | 241 | 0.91667 | 237 | 0.33333
Serajganj | 235 | 0.041667 | 232 | 0.33333 | Siddhirganj | 236 | 0.20833 | 230 | 0.5
Baghabari | 250 | 0.20833 | 241 | 0.8125 | Maniknagar | 235 | 0.083333 | 228 | 0.5
Barapukuria | 233 | 0.66667 | 226 | 0.5 | Old Airport | 235 | 0.125 | 226 | 0.5
Bogra | 234 | 0.16667 | 228 | 0.33333 | Barisal | 241 | 0.375 | 229 | 0.79167
Khulna South | 240 | 0.20833 | 220 | 0.8125 | AKSML | 225 | 0.125 | 220 | 0.16667
Rampura | 232 | 0.20833 | 229 | 0.625 | BSRM | 229 | 0.16667 | 225 | 0.33333
Haripur | 233 | 0.16667 | 230 | 0.41667 | Bibiyana | 240 | 0.125 | 232 | 0.5
Hasnabad | 231 | 0.125 | 228 | 0.5 | Bhulta | 236 | 0.16667 | 229 | 0.5
Aminbazar | 234 | 0.125 | 227 | 0.625 | Ashuganj (S) | 241 | 0.20833 | 236 | 0.41667
Tongi | 228 | 0.95833 | 222 | 0.45833 | Kaliakoir | 234 | 0.16667 | 228 | 0.5
Comilla (N) | 239 | 0.20833 | 235 | 0.5 | GPH | 228 | 0.58333 | 221 | 0.33333
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.083333 | 132 | 0.41667 | Halishahar | 134 | 0.125 | 130 | 0.45833
Munsiganj | 135 | 0.75 | 129 | 0.5 | Baraulia | 132 | 0.041667 | 127 | 0.29167
Sonargaon | 133 | 0.77083 | 130 | 0.5 | Sikalbaha | 132 | 0.041667 | 129 | 0.41667
Shyampur | 134 | 0.041667 | 131 | 0.5 | Dohazari | 132 | 0.20833 | 129 | 0.45833
Bhulta | 129 | 0.75 | 125 | 0.5 | Cox'sbazar | 128 | 0.16667 | 122 | 0.75
Madanganj | 136 | 0.20833 | 128 | 0.625 | Chandraghona | 134 | 0.25 | 131 | 0.41667
Shitalakhya | 136 | 0.041667 | 129 | 0.5 | Kaptai | 134 | 0.041667 | 132 | 0.375
Rahim steal | 135 | 1:00 | 131 | 0.5 | A. Khaer Stl. | 132 | 0.20833 | 125 | 0.5
Matuail | 134 | 0.20833 | 130 | 0.5 | Bakulia | 131 | 0.083333 | 128 | 0.41667
Ghorasal | 142 | 0.041667 | 136 | 0.75 | Julda | 132 | 0.8125 | 128 | 0.41667
Narsinghdi | 133 | 0.29167 | 127 | 0.77083 | TK Chemical | 132 | 0.125 | 129 | 0.66667
Haripur (SBU) | 136 | 0.16667 | 131 | 0.5 | Modern Steel | 131 | 0.041667 | 129 | 0.41667
Ullon | 135 | 0.25 | 131 | 0.54167 | Shahmirpur | 132 | 0.125 | 128 | 0.41667
Hasnabad | 135 | 0.25 | 130 | 0.5 | Khagrachhari | 133 | 0.041667 | 130 | 0.41667
Magbazar | 137 | 0.25 | 132 | 0.70833 | Matarbari | 130 | 0.041667 | 134 | 0.75
Maniknagar | 138 | 0.25 | 134 | 0.5 | Baroiar Hat | 136 | 0.75 | 132 | 0.5
Bangabhaban | 138 | 0.25 | 134 | 0.5 | Rangamati | 133 | 0.041667 | 130 | 0.41667
Narinda | 138 | 0.25 | 134 | 0.5 | Goalpara | 137 | 0.125 | 128 | 13:00
Dhanmondi | 135 | 0.25 | 131 | 0.54167 | Central s/s | 137 | 0.20833 | 128 | 18:30
Lalbag | 136 | 0.25 | 127 | 0.54167 | Noapara | 136 | 0.20833 | 126 | 0.5
Madartek | 136 | 0.25 | 131 | 0.5 | Jessore | 134 | 0.25 | 122 | 0.54167
Mirpur | 137 | 0.16667 | 129 | 0.5 | Benapol | 137 | 0.125 | 124 | 0.54167
Kalyanpur | 140 | 0.20833 | 133 | 0.5 | Jhenida | 136 | 0.083333 | 123 | 0.77083
Gulshan | 135 | 0.25 | 130 | 0.5 | Bottail | 137 | 0.20833 | 129 | 0.77083
Uttara | 136 | 0.25 | 128 | 0.54167 | G.K Project | 140 | 0.125 | 135 | 0.8125
Uttara New | 136 | 0.20833 | 128 | 0.54167 | Faridpur | 135 | 0.20833 | 128 | 0.77083
Kamrangirchar | 136 | 0.20833 | 129 | 0.5 | Madaripur | 136 | 0.375 | 127 | 0.83333
Savar | 136 | 03;00 | 128 | 0.5 | Sariatpur | 137 | 0.20833 | 125 | 0.8125
Bhasantec | 137 | 0.25 | 130 | 0.5 | Gopalganj | 140 | 0.75 | 131 | 0.8125
Agargaon | 136 | 0.25 | 131 | 0.54167 | Bagerhat | 135 | 0.125 | 122 | 0.77083
Satmosjid | 137 | 0.25 | 130 | 0.5 | Mongla | 134 | 0.16667 | 123 | 0.5
Tongi | 137 | 0.95833 | 131 | 0.45833 | Satkhira | 136 | 0.083333 | 125 | 0.83333
Kabirpur | 135 | 0.083333 | 129 | 0.625 | Gallamari | 140 | 0.16667 | 129 | 0.5
Basundhara | 137 | 3:00 | 130 | 0.75 | Magura | 135 | 0.125 | 124 | 0.75
Manikganj | 138 | 24:00 | 134 | 0.77083 | Norail | 136 | 0.16667 | 120 | 0.77083
Joydevpur | 142 | 0.25 | 138 | 0.875 | Chuadanga | 133 | 0.20833 | 120 | 0.77083
New Tongi | 136 | 0.95833 | 129 | 0.5 | Barisal(N) | 140 | 0.375 | 132 | 0.79167
Kodda | 132 | 0.25 | 122 | 0.58333 | Barisal (S) | 137 | 0.33333 | 132 | 21:.00
Dhamrai | 134 | 0.125 | 129 | 0.5 | Patuakhali | 137 | 0.375 | 125 | 0.8125
Valuka | 131 | 0.20833 | 124 | 0.5 | Bhandaria | 136 | 0.083333 | 126 | 0.8125
Tangail | 133 | 0.20833 | 129 | 0.625 | Ishurdi | 140 | 0.125 | 133 | 0.5
Mymensing | 132 | 0.083333 | 125 | 0.54167 | Ruppur Paromanobik | 137 | 0.20833 | 133 | 0.77083
Kishorganj | 133 | 0.20833 | 128 | 0.54167 | Natore | 137 | 0.20833 | 133 | 0.5
Netrokona | 132 | 0.16667 | 124 | 0.95833 | Bogra | 137 | 0.125 | 133 | 0.33333
Jamalpur | 137 | 0.875 | 121 | 0.95833 | Noagaon | 135 | 0.20833 | 130 | 0.33333
Sherpur | 137 | 0.875 | 121 | 0.95833 | Rajshahi | 136 | 0.125 | 126 | 0.5
Srimongal | 138 | 0.375 | 135 | 0.54167 | Rajshahi New | 136 | 0.16667 | 124 | 0.5
Shahjibazar | 136 | 0.375 | 133 | 0.75 | C.Nawabganj | 132 | 0.125 | 121 | 0.5
Fenchuganj | 138 | 0.41667 | 135 | 0.45833 | Amnura | 131 | 0.25 | 123 | 0.5
Khulawara | 137 | 0.041667 | 134 | 17:00 | Pabna | 141 | 0.20833 | 133 | 0.5
Sylhet | 136 | 0.41667 | 132 | 0.5 | Shahjadpur | 143 | 0.125 | 140 | 0.625
Chatak | 136 | 0.91667 | 132 | 0.5 | Serajganj | 139 | 0.125 | 133 | 0.54167
Sunamganj | 135 | 0.083333 | 132 | 0.5 | Niyamatpur | 135 | 0.16667 | 127 | 0.33333
Biani Bazar | 136 | 0.41667 | 132 |  | Joypurhat | 137 | 0.125 | 130 | 0.33333
Comilla(s) | 131 | 0.041667 | 127 | 0.75 | Sherpur(Bogura) | 139 | 0.125 | 133 | 0.54167
Comilla(n) | 141 | 0.29167 | 139 | 0.45833 | Mohastangor | 136 | 0.33333 | 132 | 0.54167
Chandpur | 140 | 18:00 | 137 | 0.58333 | Rangpur | 133 | 0.16667 | 124 | 0.45833
Feni | 138 | 1904-01-02 | 133 | 0.625 | Lalmonirhat | 126 | 0.66667 | 119 | 0.54167
Chowmuhani | 140 | 24:0 | 130 | 0.5 | Saidpur | 130 | 0.20833 | 121 | 0.5
Ashuganj | 138 | 0.20833 | 133 | 0.75 | Purbasadipur | 127 | 0.125 | 115 | 0.5
Daudkandi | 136 | 0.29167 | 134 | 0.41667 | Thakurgaon | 125 | 0.20833 | 112 | 0.5
B.Baria | 133 | 0.375 | 130 | 0.77083 | Palashbari | 133 | 0.125 | 123 | 0.5
Ramganj | 137 | 0.95833 | 130 | 0.83333 | Barapukuria | 133 | 0.66667 | 126 | 0.5
Chaddagram | 140 | 0.95833 | 134 | 0.54167 | Panchagar | 123 | 0.16667 | 109 | 0.5
PHP | 136 | 0.95833 | 130 | 0.625 | Joldhaka | 129 | 0.20833 | 120 | 0.5
Madanhat | 135 | 0.041667 | 132 | 0.41667 | Kurigram | 132 | 0.16667 | 123 | 0.5
Hathazari | 135 | 0.083333 | 132 | 0.41667
Khulshi | 131 | 0.041667 | 128 | 0.41667

## L-Curve
Date | 2019-12-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 208 | 4453 | 1547 | 6000 |  |  |  | QF-LDC-12
0:30 | 261 | 4323 | 1468.5 | 5791.5 | Date: | 2019-12-26
1:00 | 314 | 4193 | 1390 | 5583
1:30 | 304.5 | 4130 | 1346 | 5476
2:00 | 295 | 4067 | 1302 | 5369
2:30 | 304.5 | 4002.5 | 1267.5 | 5270 | [5 empty] | Gen. at Eve. Peak | 8555 | 8555 MW (19:00 )
3:00 | 314 | 3938 | 1233 | 5171 | [6 empty] | 19:00
3:30 | 317 | 3855 | 1222.5 | 5077.5 | [5 empty] | Gen. at Day Peak | 6512.8 | 6512.8 MW (12:00 )
4:00 | 320 | 3772 | 1212 | 4984 | [6 empty] | 12:00
4:30 | 313.5 | 3778.5 | 1211 | 4989.5 | [5 empty] | Highest Generation | 8555
5:00 | 307 | 3785 | 1210 | 4995 | [6 empty] | 19:00
5:30 | 351.5 | 3861.5 | 1211 | 5072.5
6:00 | 396 | 3938 | 1212 | 5150
6:30 | 388.5 | 4070.05 | 1295.05 | 5365.1
7:00 | 381 | 4202.1 | 1378.1 | 5580.2
7:30 | 381.5 | 4352.45 | 1472.45 | 5824.9
8:00 | 382 | 4502.8 | 1566.8 | 6069.6
8:30 | 319.5 | 4588.7 | 1649.5 | 6238.2
9:00 | 257 | 4674.6 | 1732.2 | 6406.8
9:30 | 223.5 | 4733.75 | 1718.3 | 6452.05
10:00 | 190 | 4792.9 | 1704.4 | 6497.3
10:30 | 185 | 4794 | 1698.25 | 6492.25
11:00 | 180 | 4795.1 | 1692.1 | 6487.2
11:30 | 181 | 4784.3 | 1715.7 | 6500
12:00 | 182 | 4773.5 | 1739.3 | 6512.8
12:30 | 183.5 | 4820.95 | 1775.55 | 6596.5
13:00 | 185 | 4868.4 | 1811.8 | 6680.2
13:30 | 167.5 | 4794.4 | 1784.1 | 6578.5
14:00 | 150 | 4720.4 | 1756.4 | 6476.8
14:30 | 84 | 4702.75 | 1758.85 | 6461.6
15:00 | 18 | 4685.1 | 1761.3 | 6446.4
15:30 | 20.5 | 4700 | 1752.55 | 6452.55
16:00 | 23 | 4714.9 | 1743.8 | 6458.7
16:30 | 14.5 | 4785.6 | 1819.45 | 6605.05
17:00 | 6 | 4856.3 | 1895.1 | 6751.4
17:30 | 85.5 | 5248.15 | 2211.55 | 7459.7
18:00 | 165 | 5640 | 2528 | 8168
18:30 | 220.5 | 5839.5 | 2522 | 8361.5
19:00 | 276 | 6039 | 2516 | 8555
19:30 | 285 | 6013 | 2481 | 8494
20:00 | 285 | 5908 | 2420 | 8328 |  |  |  | Executive Engineer
20:30 | 254.5 | 5750 | 2379 | 8129 |  |  |  | Network Operation Division
21:00 | 224 | 5592 | 2338 | 7930
21:30 | 164.5 | 5429 | 2177 | 7606
22:00 | 105 | 5266 | 2016 | 7282 |  |  |  |  | Page 6 of 7
22:30 | 196.5 | 5101.5 | 1867.5 | 6969
23:00 | 288 | 4937 | 1719 | 6656
23:30 | 248 | 4695 | 1633 | 6328
24:00 | 208 | 4453 | 1547 | 6000
8555 MW (19:00 )
6512.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-26 |  | Energy | 157655371
[10 empty] | 2019-12-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3811 | 209 | 1571 | 133 | 160 | 44 | 0 | 0 | 72
0:30 | 3758 | 172.5 | 1505 | 66.5 | 170 | 44 | 3.5 | 0 | 72 | Date: | 2019-12-26
1:00 | 3705 | 136 | 1439 | 0 | 180 | 44 | 7 | 0 | 72
1:30 | 3648 | 136 | 1390 | 0 | 180 | 44 | 7 | 0 | 71 | [7 empty] | Total Energy | 157.6554 | Total Energy Gen 157.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 157.655 MKWHr
2:00 | 3591 | 136 | 1341 | 0 | 180 | 44 | 7 | 0 | 70 | [7 empty] | Energy not Served | 0
2:30 | 3541 | 136 | 1294 | 0 | 180 | 44 | 7 | 0 | 68 | [7 empty] | Energy Requirement | 157.6554
3:00 | 3491 | 136 | 1247 | 0 | 180 | 44 | 7 | 0 | 66
3:30 | 3401 | 136 | 1249 | 0 | 180 | 43 | 3.5 | 0 | 65 | [6 empty] | Shortage
4:00 | 3311 | 136 | 1251 | 0 | 180 | 42 | 0 | 0 | 64
4:30 | 3311.5 | 136 | 1256 | 0 | 180 | 42 | 0 | 0 | 64
5:00 | 3312 | 136 | 1261 | 0 | 180 | 42 | 0 | 0 | 64
5:30 | 3379.5 | 136 | 1271 | 0 | 180 | 42 | 0 | 0 | 64
6:00 | 3447 | 136 | 1281 | 0 | 180 | 42 | 0 | 0 | 64
6:30 | 3547.5 | 136 | 1395 | 0 | 180 | 42 | 0 | 0 | 64 |  |  |  |  | Coal
7:00 | 3648 | 136 | 1509 | 0 | 180 | 42 | 0 | 0 | 64
7:30 | 3809.5 | 136 | 1569.5 | 16 | 180 | 42.5 | 0 | 0 | 67 |  |  |  | Oil |  |  |  | ,
8:00 | 3971 | 136 | 1630 | 32 | 180 | 43 | 0 | 0 | 70
8:30 | 4008.5 | 222.5 | 1691 | 23.5 | 164 | 43 | 0 | 0 | 74
9:00 | 4046 | 309 | 1752 | 15 | 148 | 43 | 0 | 0 | 78
9:30 | 4031 | 309 | 1788.5 | 34.5 | 153 | 43.5 | 0 | 0 | 77
10:00 | 4016 | 309 | 1825 | 54 | 158 | 44 | 0 | 0 | 76
10:30 | 4016.5 | 309 | 1780 | 94 | 159 | 44 | 0 | 0 | 76
11:00 | 4017 | 309 | 1735 | 134 | 160 | 44 | 0 | 0 | 76
11:30 | 4040.5 | 309.5 | 1764.5 | 80 | 160 | 42 | 3.5 | 0 | 80
12:00 | 4064 | 310 | 1794 | 26 | 160 | 40 | 7 | 0 | 84
12:30 | 4086 | 309.5 | 1859 | 30 | 160 | 40 | 7 | 0 | 86
13:00 | 4108 | 309 | 1924 | 34 | 160 | 40 | 7 | 0 | 88
13:30 | 4108 | 309 | 1924 | 34 | 160 | 40 | 7 | 0 | 88
14:00 | 4108 | 309 | 1924 | 34 | 160 | 40 | 7 | 0 | 88
14:30 | 4058.5 | 307.5 | 1863 | 25.5 | 160 | 41 | 7 | 0 | 89
15:00 | 4009 | 306 | 1802 | 17 | 160 | 42 | 7 | 0 | 90
15:30 | 4000 | 306 | 1768 | 73 | 160 | 42 | 7 | 0 | 88
16:00 | 3991 | 306 | 1734 | 129 | 160 | 42 | 7 | 0 | 86
16:30 | 4019.5 | 377.5 | 1745.5 | 162.5 | 160 | 42.5 | 3.5 | 0 | 92
17:00 | 4048 | 449 | 1757 | 196 | 160 | 43 | 0 | 0 | 98
17:30 | 4153.5 | 549 | 1839 | 579.5 | 160 | 43.5 | 33 | 0 | 102
18:00 | 4259 | 649 | 1921 | 963 | 160 | 44 | 66 | 0 | 106
18:30 | 4314.5 | 648.5 | 1955 | 1068.5 | 160 | 44 | 66 | 0 | 105
19:00 | 4370 | 648 | 1989 | 1174 | 160 | 44 | 66 | 0 | 104
19:30 | 4390 | 649 | 2004 | 1079 | 160 | 44 | 66 | 0 | 102
20:00 | 4384 | 649 | 1991 | 932 | 160 | 44 | 66 | 0 | 102
20:30 | 4377.5 | 649 | 1988.5 | 747 | 160 | 44 | 63 | 0 | 100
21:00 | 4371 | 649 | 1986 | 562 | 160 | 44 | 60 | 0 | 98
21:30 | 4335 | 598 | 1964.5 | 380.5 | 160 | 44 | 30 | 0 | 94
22:00 | 4299 | 547 | 1943 | 199 | 160 | 44 | 0 | 0 | 90
22:30 | 4257.5 | 426 | 1827.5 | 166 | 160 | 44 | 0 | 0 | 88
23:00 | 4216 | 305 | 1712 | 133 | 160 | 44 | 0 | 0 | 86
23:30 | 4013.5 | 257 | 1641.5 | 133 | 160 | 44 | 0 | 0 | 79 | Max Temp. in Dhaka |  | 21.8° C
24:00 | 3811 | 209 | 1571 | 133 | 160 | 44 | 0 | 0 | 72
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 157.655 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 157.655 MKWHr
Note on W13: Author:

## Generation
2019-12-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 44 | 44 | 42 | 42 | 42 | 42 | 43 | 43 | 44 | 44 | 40 | 40 | 44 | 42 | 42 | 43 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 983700
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 2700000
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 2800000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.9 | 5.7 | 11.3 | 10.5 | 5.2 | 17.5 | 0 | 14.3 | 10 | 2.3 | 0.3 | [9 empty] | 95985
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 182 | 182 | 182 | 182 | 195 | 190 | 196 | 183 | 183 | 185 | 196 | 182 | 184 | 182 | 182 | 192 | 203 |  | 204 | 203 | 203 | 203 | 203 | 203 | 176 | 4537652
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 75 | 75 | 80 | 80 | 80 | 104 | 107 | 104 | 104 | 104 | 110 | 105 | 104 | 104 | 105 | 103 | 104 |  | 134 | 133 | 134 | 134 | 134 | 108 | 0 | 2477326
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP | 7 | 7 | 7 | 0 | [22 empty] | 28352
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 1 | 17 |  | 17 | [5 empty] | 0 | 43842
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 280 | 300 | 270 | 270 | 250 | 280 | 280 | 280 | 280 | 280 | 280 |  | 310 | 310 | 310 | 310 | 310 | 280 | 250 | 6613967
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 | 61 | 63 | 63 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 1187636
20 | Ghorasal TPP (Unit-1&2) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 800000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 99 | 99 | 102 | 102 | 102 | 101 | 102 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 98 | 100 | 100 | 103 | 2407000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 215 | 215 | 215 | 150 | 150 | 150 | 150 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4187300
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 125 | 125 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2348982
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 37 | 37 | 37 | 37 | 36 | 33 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 682920
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 250 | 260 | 260 | 260 | 305 | 320 | 305 | 305 | 305 | 300 | 275 | 260 | 260 | 270 | 290 | 280 |  | 305 | 305 | 305 | 305 | 305 | 295 | 295 | 7034500
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 290 | 295 | 300 | 290 | 290 | 290 | 325 | 315 | 290 | 290 | 260 | 280 | 310 |  | 315 | 315 | 315 | 315 | 315 | 315 | 270 | 7304000
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 52 | 50 | 50 | 50 | 51 | 49 | 50 | 90 | 81 | 80 | 86 | 90 | 90 | 85 | 80 | 80 | 90 | 90 |  | 81 | 81 | 81 | 80 | 80 | 80 | 50 | 1738180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 341 | 329 | 280 | 280 | 307 | 374 | 371 | 370 | 342 | 342 | 344 | 380 | 343 | 349 | 342 | 347 | 353 |  | 343 | 342 | 341 | 342 | 341 | 341 | 341 | 8369660
40 | Meghnaghat 450 MW CCPP(MPL) | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 370 | 370 | 370 | 340 | 340 | 370 | 370 | 340 | 340 | 340 | 380 |  | 400 | 400 | 400 | 400 | 400 | 370 | 350 | 8133250
41 | Haripur 360MW CCPP(HPL) | 250 | 230 | 200 | 200 | 200 | 200 | 290 | 300 | 307 | 283 | 283 | 252 | 332 | 313 | 313 | 282 | 282 | 302 |  | 294 | 294 | 285 | 285 | 286 | 286 | 295 | 6602000
42 | RPCL 210MW CCPP | 113 | 113 | 135 | 113 | 112 | 112 | 112 | 161 | 131 | 109 | 109 | 110 | 112 | 113 | 110 | 110 | 110 | 110 |  | 111 | 111 | 107 | 106 | 108 | 108 | 107 | 2695280
43
44 | Fenchugonj CCPP Phase-1 | 60 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 33 | 35 | 60 |  | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 995000
45 | Fenchugonj CCPP Phase-2 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 88 | 86 | 86 | 86 | 89 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2041060
46 | Shajibazar 330 MW CCPP | 144 | 145 | 144 | 143 | 143 | 159 | 157 | 160 | 143 | 145 | 145 | 156 | 156 | 145 | 145 | 143 | 151 | 150 |  | 144 | 145 | 146 | 145 | 143 | 144 | 144 | 3316000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 70 | 70 | 68 | 64 | 65 | 66 | 66 | 66 | 66 | 66 |  | 67 | 68 | 68 | 68 | 68 | 68 | 52 | 1427616
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 60 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 50 | 40 | 1146240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 260000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 23 | 25 | 26 | 12 | 13 | 14 | 14 | 14 | 13 | 36 |  | 39 | 39 | 39 | 39 | 39 | 39 | 6 | 443640
53 | Sylhet 10MW PP (Desh) | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 137340
54 | Hobiganj 11MW PP Cofidence-E | [10 empty] | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 0 |  | 0 | 118992
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 45 | 14 | 17 | 14 | 11 | 11 | 14 | 14 | 50 |  | 53 | 53 | 53 | 53 | 53 | 5 | 5 | 444600
56 | Shahjahanulla 25 MW PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 |  |  | 0 | 275208
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 275 | 280 | 290 | 300 | 325 | 325 | 310 | 290 | 280 | 341 | 330 | 305 | 310 | 300 | 310 | 315 |  | 310 | 305 | 300 | 305 | 280 | 280 | 270 | 7453500
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 271152
61 | Narshingdi 22 MW PP (Doreen) | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 371772
62 | Tangail 22 MW PP (Doreen) | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 300132
63 | Impoprt (Tripura) | 72 | 70 | 66 | 64 | 64 | 64 | 64 | 70 | 78 | 76 | 76 | 84 | 88 | 88 | 90 | 86 | 98 | 106 |  | 104 | 102 | 102 | 98 | 90 | 86 | 72 | 1957440
64 | Malancha, Ctg. EPZ (United) | 5 | 5 | 5 | 5 | 7 | 15 | 15 | 5 | 4 | 2 | 2 | 5 | 10 | 6 | 3 | 3 | 3 | 4 |  | 13 | 17 | 18 | 27 | 35 | 36 | 3 | 351360
65 | Feni 22MW PP (Doreen) | [8 empty] | 19 | [8 empty] | 19 |  | 22 | 22 | 22 | 22 | 22 |  | 0 | 115920
66 | Feni 11 MW PP (Doreen) | [8 empty] | 8 | 8 | [7 empty] | 11 |  | 11 | 11 | 11 | 11 |  |  | 0 | 61560
67 | Jangalia 33MW PP (Summit) | [6 empty] | 0 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 21 | 8 | 33 |  | 33 | 33 | 33 | 33 |  |  | 0 | 467500
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 |  |  | 0 | 5 | 10 | 10 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 250290
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 26 | 32 | 28 | 26 | 28 | 24 | 28 | 28 | 28 | 16 |  | 32 | 28 | 25 | 0 | 0 | 32 | 32 | 627480
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 637800
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 802400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [9 empty] | 49 | 117 | 9 |  |  |  | 112 | 116 | 116 |  | 116 | 116 | 116 | 116 | 117 | 116 | 116 | 1142400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 0 | 7 | [7 empty] | 0 | 7680
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [17 empty] | 16 |  | 16 | 16 | 16 | 10 |  |  | 0 | 57600
80 | Jamalpur 95 MW PP(Powerpac) | [16 empty] | 3 | 50 |  | 68 | 68 | 68 | 68 | 42 | 0 |  | 337920
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [9 empty] | 5 | 17 | 17 | 17 |  |  |  | 5 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 122112
| Kaptai 7 MW Solar PP | [6 empty] | 0.2 | 0.8 | 1.4 | 2.3 | 2.6 | 4.1 | 4.8 | 2.7 | 1.1 | 0.3 | 0 | 0 | [8 empty] | 8550
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 4 |  | 0 | 0 | [5 empty] | 12528
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 58 |  | 100 | 100 | 65 |  |  |  | 0 | 260160
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 28 |  | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 482040
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 717400
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 5 | 32 |  | 102 | 102 | 50 | 0 | 0 |  |  | 260208
95 | Patenga 50MW PP (Baraka) | [16 empty] | 0 | 18 |  | 43 | 43 | 35 |  |  |  | 0 | 93120
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 6 | [7 empty] | 0 | 26304
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 0 | 15 |  | 0 | 0 | [5 empty] | 21856
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 35 | [7 empty] | 0 | 63894
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 2825738
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.3 | 0.9 | 0.1 | 1.3 | 1.9 | 1.6 | 1.4 | 1 | 0.3 | 0 | 0 | [8 empty] | 19800
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 35 | 35 | 17 | 17 | 357480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 0
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [26 empty] | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 10 |  | 10 | 0 | 0 |  |  |  |  | 26880
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 362 | 364 | 339 | 305 | 306 | 336 | 328 | 334 | 305 | 307 | 307 | 333 | 307 | 305 | 302 | 305 | 321 | 345 |  | 365 | 365 | 365 | 365 | 364 | 365 | 363 | 8014000
| Jamalpur 115 MW PP (United) | [16 empty] | 1 | 40 |  | 112 | 115 | 115 | 115 | 5 |  | 0 | 459600
| Anwara 300 MW PP (United) | [16 empty] | 16 | 140 |  | 174 | 180 | 184 | 80 |  |  | 0 | 587127
120 | Eastern Zone Total | 4193 | 4067 | 3938 | 3772 | 3785 | 3938 | 4202.1 | 4502.8 | 4674.6 | 4792.9 | 4795.1 | 4773.5 | 4868.4 | 4720.4 | 4685.1 | 4714.9 | 4856.3 | 5640 |  | 6039 | 6013 | 5908 | 5592 | 5266 | 4937 | 4453 | 114549931
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [15 empty] | 0 | 6 | 57 |  | 66 | 49 | 49 | 0 |  |  |  | 165120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 0 | 32 |  | 16 | 16 | 16 | 16 |  |  |  | 91392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 14 | 14 | 14 | 14 | 14 | 14 | 36 | 83 | 92 | 96 | 73 | 74 | 95 | 95 | 74 | 73 | 74 | 74 |  | 75 | 75 | 75 | 75 | 75 | 48 | 0 | 1387419
| Bhola 225 MW CCPP | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 97 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2340869
140 | Bhola 33 MW PP (Venture) | 21 | 18 | 19 | 18 | 16 | 18 | 19 | 18 | 12 | 12 | 17 | 19 | 18 | 20 | 19 | 19 | 12 | 17 |  | 26 | 26 | 25 | 26 | 23 | 23 | 21 | 446600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 7 | 7 | 7 | 7 | 7 | 0 | [9 empty] | 33016
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [7 empty] | 32 | 15 | 0 | [6 empty] | 15 | 67 |  | 32 | 32 | 32 | 15 |  |  |  | 209440
146 | Bheramara HVDC | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 309 | 309 | 309 | 310 | 309 | 309 | 306 | 306 | 449 | 649 |  | 648 | 649 | 649 | 649 | 547 | 305 | 209 | 7823272
147 | Bheramara 360 MW CCPP | 250 | 250 | 220 | 200 | 200 | 200 | 200 | 250 | 270 | 270 | 270 | 270 | 290 | 290 | 290 | 290 | 290 | 320 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 6901344
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 148 | 158 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4073700
153 | Baghabari 71 MW GTPP | [20 empty] | 30 | 30 | 50 | 50 | 50 | 50 | 205000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 0 | 50 |  | 50 | 50 | 50 | 50 | 0 | 0 |  | 218752
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 130 | 130 | 130 | 130 | 130 | 147 | 184 | 183 | 168 | 165 | 169 | 202 | 200 | 199 | 189 | 195 | 202 |  | 194 | 190 | 189 | 190 | 188 | 176 | 165 | 4453191
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 166 | 184 | 190 | 188 | 190 | 187 | 189 | 190 | 193 | 216 | 191 | 191 |  | 187 | 186 | 187 | 184 | 191 | 191 | 170 | 4596673
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 385 | 340 | 300 | 300 | 300 | 300 | 390 | 395 | 378 | 358 | 362 | 396 | 394 | 341 | 370 | 341 | 369 | 386 |  | 370 | 386 | 382 | 362 | 338 | 349 | 355 | 8704872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 300720
163 | Bogura 20 MW PP (Energyprima) | [8 empty] | 7 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 6 | 5 |  | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 118332
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224892
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 12 | 0 | 0 |  | 108180
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 55 |  | 109 | 71 | 35 | 35 | 0 | 0 |  | 292128
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 0 | 109 |  | 114 | 92 | 72 | 70 | 0 | 0 |  | 388800
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.8 | 2.2 | 2.4 | 3.1 | 4.3 | 3.8 | 1.4 | 1.3 | 0.8 | 0.1 | 0 | [8 empty] | 21728
178
178