## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-01-01 | Wednesday
|  | Date (day): | 2020-01-01 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11725.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14460 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-12-31 | 2020-01-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 34 | 34 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 150 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 280 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 347 | 357 | 360 | 360 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 300 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 300 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 40 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 65 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 36 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1827 | 2418 | 3354 | 4003 | 806 | 959
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 115 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 45 | 84 | 84 | 146 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 206 | 203 | 210 | 215 |  |  | FGMO
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 104 | 139 | 135 | 135
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 51 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 18 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.3 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 205 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 504.3 | 895 | 1449 | 1634 | 386 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 125 | 125
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 153 | 0 | 0 | 0 |  | 221 | Test
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 325 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 37 | 35 | 38 |  | 7 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 130 | 150 | 180
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 82 | 90 | 140 |  | 23 | ST under shut down
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 150 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 104 | 90 | 109
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 14 | 14 |  | 11 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
| Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 0 | 0 | 0 | 52 | 113 | 113 |  |  | on test
| Cumilla Area Total |  |  |  |  | 2980 | 2920 | 1174 | 1238 | 1696 | 2312 | 134 | 454
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 127 | 102 | 160 | 160 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 80 | 100 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 145.1 | 299 | 478.6 | 592 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 29 | 30 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 60 | 60 | 85 | 86
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 146 | 160 | 160 |  |  | GT-2 Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 66 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 79 | 75 | 79 |  | 7 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 28 | 31 | 40 | 40 |  | 10 | Engine problem
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 431 | 361 | 400 | 400 |  |  | FGMO
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1239 | 1378 | 1547 | 1552 | 0 | 159
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 295 | 645 | 306 | 504
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 0 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 230 | 400 | 400
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 32 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 600 | 1040 | 938 | 1699 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 25 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 142 | 165 | 175 | 190
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 160 | 222 | 360 | 445 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 40 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 189 | 200 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 215 | 183 | 220 | 220 | 0 |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Under maint.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 382 | 382 | 400 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 14 | 14
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 85 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 886 | 940 | 1522 | 1816 | 100 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 260 | 260
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 77 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 165.4 | 237 | 381 | 407 | 0 | 170
| Total |  |  |  |  | 19570 | 19047 | 6700.8 | 8667 | 11725.6 | 14460 | 1478 | 1863
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6385.3591 | 8259 | 11173.6161 | 13779.2939
A. |  | 2019-12-31 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8667 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5073 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8667 | MW
3 | Day peak Generation : |  |  | 6700.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8259 | MW
4 | Evening peak Generation : |  |  | 8667 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 159.9972 | MKWHr | By Solar | 0.19117 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 138.5635 | MKWHr |  | By Oil: | 6.5029 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.9372 | MKWHr |  | By Hydro: | 1.0868 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1478 | MW | Dhaka | 2961 | 2961 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1863 | MW | Chittagong | 901 | 901 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3341 | MW | Khulna | 1018 | 1018 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1089.18 | MMCFD |  |  | Rajshahi | 874 | 874 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 127471018.96 | ii) Oil : | Taka | 57303571.25 | Comilla | 713 | 713 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 16103148 | Total | Taka | 200877738.21 | Mymensingh | 653 | 653 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.7625 | MKWHr. | Sylhet | 319 | 319 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -353 | MW (E to W) at | 19:00 | hrs | Barisal | 228 | 228 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -412 | MW at | 18:30 | hrs | Rangpur | 592 | 592 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.0° C |  |  | Total | 8259 | 8259 |  | 0
B. |  | 2020-01-01 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14460 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6900 | MW
4 | Reserve(Generation end) |  |  |  | 5660 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 162.4525 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5176 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.7447 | MKWHr. | ii) HVDC Flow at Peak Time |  | 645 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9709 | MKWHr. | iii) Maximum HVDC Flow : |  | 646 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.07 |  | (b) Today: | 95.99 |  | (c) Rule Curve: |  | 103
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-12-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 343 | 313 |  | 0 | 370 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 47 | 0 | 100 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 100 | 0 | 0 | 280 | 295 | 0 | 8 | 50 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 70 | 107 | 0 | 0 | 0 | 30 | 60 | 5 | 5 | 100 | 145 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 21 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4214 | 1541 | 5755 | 3757 | 137 | 1584 | 0 | 160 | 47 | 0 | 70 | 0 | 0 | 96.08
2:00 | 34 | 0 | 101 | 0 | 200 | 0 | 0 | 342 | 283 |  | 0 | 300 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 47 | 0 | 100 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 260 | 295 | 0 | 8 | 50 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 107 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 100 | 145 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 21 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 181 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3973 | 1460 | 5433 | 3629 | 137 | 1392 | 0 | 160 | 47 | 0 | 68 | 0 | 0 | 96.08
3:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 320 | 283 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 46 | 0 | 100 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 260 | 276 | 0 | 8 | 50 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 131 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 100 | 150 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 19 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3913 | 1366 | 5279 | 3484 | 137 | 1384 | 0 | 160 | 46 | 0 | 68 | 0 | 0 | 96.08
4:00 | 34 | 0 | 101 | 0 | 200 | 0 | 0 | 270 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 46 | 0 | 100 | 0 | 0 | 182 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 260 | 260 | 0 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 131 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 100 | 152 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3774 | 1326 | 5100 | 3406 | 136 | 1284 | 0 | 160 | 46 | 0 | 68 | 0 | 0 | 96.07
5:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 270 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 183 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 260 | 270 | 0 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 145 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 130 | 145 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 138 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3822 | 1251 | 5073 | 3350 | 138 | 1312 | 0 | 160 | 45 | 0 | 68 | 0 | 0 | 96.07
6:00 | 34 | 0 | 101 | 0 | 200 | 0 | 0 | 302 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 44 | 0 | 100 | 0 | 0 | 184 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 0 | 275 | 285 | 0 | 8 | 50 | 25 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 144 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 130 | 153 | 45 | 5 | 0 | 0 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3974 | 1368 | 5342 | 3513 | 137 | 1420 | 0 | 160 | 44 | 0 | 68 | 0 | 0 | 96.07
7:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 363 | 268 |  | 0 | 300 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 43 | 0 | 100 | 0 | 0 | 196 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 0 | 306 | 305 | 0 | 8 | 50 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 146 | 0 | 0 | 0 | 15 | 36 | 5 | 5 | 130 | 160 | 48 | 79 | 0 | 0 | 0 | 6 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4283.61 | 1368 | 5651.61 | 3717 | 136 | 1527 | 0 | 160 | 43 | 0 | 68 | 0.61 | 0 | 96.06
8:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 371 | 372 |  | 0 | 340 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 31 | 0 | 0 | 43 | 0 | 100 | 0 | 0 | 212 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 80 | 0 | 0 | 355 | 290 | 0 | 26 | 90 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 10 | 0 | 0 | 14 | 70 | 147 | 0 | 0 | 0.5 | 30 | 60 | 5 | 5 | 163 | 155 | 45 | 76 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 149 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 |  | 4646.6 | 1589.1 | 6235.7 | 4065 | 136 | 1754 | 0 | 160 | 43 | 0 | 70 | 7.7 | 0 | 96.06
9:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 366 | 372 |  | 0 | 340 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 31 | 0 | 0 | 44 | 0 | 100 | 0 | 0 | 232 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 340 | 275 | 0 | 26 | 88 | 40 | 0 | 0 | 11 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 80 | 146 | 7 | 0 | 1.2 | 30 | 60 | 5 | 5 | 163 | 150 | 68 | 76 | 0 | 0 | 0 | 24 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 0 | 0 | 0 | 240 | 0 | 11 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 190 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 |  | 4712.4 | 1886.8 | 6599.2 | 4157 | 301 | 1821 | 18 | 160 | 44 | 0 | 80 | 18.2 | 0 | 96.06
10:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 342 | 372 |  | 0 | 340 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 31 | 0 | 0 | 44 | 0 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 330 | 270 | 126 | 26 | 81 | 37 | 0 | 0 | 39 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 84 | 127 | 16 | 0 | 1.7 | 28 | 60 | 5 | 5 | 163 | 147 | 67 | 76 | 0 | 0 | 0 | 23 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6 | 0 | 0 | 0 | 242 | 0 | 35 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 173 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 4786.8 | 1796.1 | 6582.9 | 4138 | 301 | 1779 | 51 | 160 | 44 | 0 | 84 | 25.9 | 0 | 96.05
11:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 347 | 320 |  | 0 | 340 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 80 | 0 | 0 | 340 | 280 | 136 | 54 | 82 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 84 | 125 | 16 | 0 | 2 | 28 | 60 | 5 | 5 | 130 | 148 | 65 | 20 | 0 | 0 | 0 | 23 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8 | 0 | 0 | 0 | 320 | 0 | 52 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 178 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 |  | 4693.9 | 1781.9 | 6475.8 | 4151 | 301 | 1637 | 68 | 160 | 45 | 0 | 84 | 29.8 | 0 | 96.05
12:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 347 | 320 |  | 0 | 340 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 350 | 290 | 153 | 26 | 90 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 88 | 127 | 16 | 0 | 2.1 | 29 | 60 | 5 | 5 | 130 | 157 | 64 | 20 | 0 | 0 | 0 | 28 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 431 | 0 | 52 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 |  | 295 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 |  | 4889.4 | 1811.4 | 6700.8 | 4353 | 295 | 1661 | 68 | 160 | 45 | 0 | 88 | 30.8 | 0 | 0
13:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 380 | 348 |  | 0 | 400 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 218 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 80 | 0 | 0 | 360 | 305 | 153 | 26 | 91 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 84 | 122 | 16 | 0 | 1.8 | 28 | 60 | 5 | 5 | 130 | 155 | 63 | 20 | 0 | 0 | 0 | 26 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 427 | 0 | 52 | 0 | 4 | 0 | 0 | 0 | 0 | 0 |  | 296 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 |  | 5015.8 | 1826.6 | 6842.4 | 4392 | 296 | 1813 | 68 | 160 | 0 | 0 | 84 | 29.4 | 0 | 0
14:00 | 34 | 0 | 101 | 0 | 200 | 0 | 0 | 354 | 339 |  | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 325 | 275 | 153 | 26 | 82 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 84 | 120 | 16 | 0 | 1.6 | 29 | 60 | 5 | 5 | 130 | 146 | 65 | 20 | 0 | 0 | 0 | 26 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 433 | 0 | 52 | 0 | 3.16 | 0 | 0 | 0 | 0 | 0 |  | 300 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 16 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 204 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 58 | 0 | 0 | 4.3 | 0 |  | 4877.76 | 1729.3 | 6607.06 | 4151 | 300 | 1702 | 142 | 160 | 45 | 0 | 84 | 23.06 | 0 | 96.04
15:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 352 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 205 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 80 | 0 | 0 | 330 | 270 | 149 | 26 | 91 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 86 | 99 | 16 | 0 | 1.2 | 30 | 60 | 5 | 5 | 100 | 151 | 63 | 20 | 0 | 0 | 0 | 25 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 334 | 0 | 52 | 0 | 1.17 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 17 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 159 | 0 | 0 | 214 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 32 | 0 | 0 | 3 | 0 |  | 4646.37 | 1747 | 6393.37 | 3960 | 299 | 1696 | 132 | 159 | 45 | 0 | 86 | 16.37 | 0 | 96.04
16:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 356 | 300 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 46 | 0 | 100 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 80 | 0 | 0 | 340 | 285 | 152 | 26 | 90 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 84 | 99 | 16 | 0 | 0.5 | 30 | 60 | 5 | 5 | 100 | 151 | 63 | 20 | 0 | 0 | 0 | 22 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 334 | 0 | 52 | 0 | 1.27 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 16 | 16 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 436 | 0 | 0 | 0 | 32 | 0 | 0 | 1.6 | 0 |  | 4699.77 | 1725.6 | 6425.37 | 3984 | 299 | 1727 | 116 | 160 | 46 | 0 | 84 | 9.37 | 0 | 96.03
17:00 | 34 | 0 | 100 | 0 | 250 | 0 | 0 | 363 | 300 |  | 0 | 400 | 0 | 1 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 22 | 25 | 25 | 20 | 25 | 0 | 0 | 46 | 0 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 16 | 80 | 0 | 0 | 325 | 270 | 0 | 26 | 89 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 8 | 14 | 86 | 99 | 28 | 0 | 0 | 30 | 60 | 5 | 5 | 130 | 150 | 65 | 79 | 0 | 0 | 0 | 24 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 241 | 5 | 52 | 3 | 0 | 16 | 0 | 0 | 0 | 9 |  | 473 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 15 | 35 | 0 | 0.1 | 6 |  | 4694 | 1958.1 | 6652.1 | 3833 | 473 | 1806 | 243 | 160 | 46 | 5 | 86 | 0.1 | 0 | 96.03
18:00 | 34 | 0 | 150 | 0 | 250 | 0 | 0 | 359 | 300 |  | 0 | 400 | 0 | 53 | 14 | 8 | 280 | 0 | 0 | 0 | 0 | 64 | 50 | 0 | 0 | 0 | 15 | 53 | 55 | 0 | 22 | 25 | 24 | 20 | 33 | 0 | 0 | 46 | 0 | 115 | 0 | 0 | 204 | 0 | 149 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 11 | 80 | 0 | 0 | 330 | 305 | 0 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 14 | 96 | 99 | 95 | 22 | 0 | 30 | 60 | 41 | 28 | 130 | 157 | 65 | 79 | 0 | 0 | 17 | 28 | 8 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 358 | 50 | 52 | 30 | 0 | 201 | 0 | 0 | 0 | 55 |  | 644 | 0 | 230 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 22 | 48 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 196 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 50 | 74 | 0 | 0 | 54 |  | 5889 | 2372 | 8261 | 4250 | 644 | 1885 | 1130 | 160 | 46 | 50 | 96 | 0 | 0 | 96.03
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 357 | 300 |  | 0 | 400 | 0 | 100 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 102 | 65 | 0 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 18 | 80 | 0 | 0 | 325 | 305 | 0 | 130 | 82 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 102 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 146 | 66 | 79 | 0 | 0 | 17 | 31 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 361 | 80 | 36 | 51 | 0 | 205 | 0 | 0 | 0 | 52 |  | 645 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 25 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 50 | 77 | 0 | 0 | 85 |  | 6228 | 2439 | 8667 | 4305 | 645 | 1988 | 1355 | 160 | 45 | 65 | 104 | 0 | 0 | 96.02
19:30 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 344 | 300 |  | 0 | 400 | 0 | 100 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 102 | 65 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 21 | 80 | 0 | 0 | 325 | 305 | 0 | 130 | 87 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 103 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 150 | 67 | 79 | 0 | 0 | 17 | 32 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 362 | 80 | 17 | 51 | 0 | 217 | 0 | 0 | 0 | 0 |  | 645 | 0 | 235 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 26 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 205 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 50 | 77 | 0 | 0 | 108 |  | 6087 | 2492 | 8579 | 4332 | 645 | 2004 | 1226 | 160 | 45 | 65 | 102 | 0 | 0 | 0
20:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 343 | 306 |  | 0 | 400 | 0 | 100 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 102 | 65 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 26 | 80 | 0 | 0 | 325 | 305 | 0 | 130 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 100 | 102 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 147 | 67 | 79 | 0 | 0 | 17 | 32 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 363 | 80 | 17 | 17 | 0 | 216 | 0 | 0 | 0 | 0 |  | 645 | 0 | 235 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 26 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 161 | 0 | 0 | 214 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 50 | 77 | 0 | 0 | 109 |  | 6035 | 2458 | 8493 | 4337 | 645 | 1964 | 1176 | 161 | 45 | 65 | 100 | 0 | 0 | 96.02
21:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 343 | 308 |  | 0 | 400 | 0 | 70 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 50 | 65 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 45 | 0 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 28 | 80 | 0 | 0 | 325 | 355 | 0 | 130 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 98 | 103 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 145 | 55 | 79 | 0 | 0 | 17 | 32 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 8 | 17 | 0 | 0 | 216 | 0 | 0 | 0 | 0 |  | 646 | 0 | 235 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 25 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 50 | 60 | 0 | 0 | 70 |  | 5821 | 2412 | 8233 | 4378 | 646 | 1977 | 864 | 160 | 45 | 65 | 98 | 0 | 0 | 96.02
22:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 342 | 308 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 30 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 20 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 30 | 80 | 0 | 0 | 325 | 290 | 0 | 130 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 90 | 103 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 145 | 56 | 79 | 0 | 0 | 17 | 32 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 |  | 547 | 0 | 235 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 25 | 16 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 |  | 5438 | 2082 | 7520 | 4301 | 547 | 1944 | 402 | 160 | 46 | 30 | 90 | 0 | 0 | 96.01
23:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 341 | 308 |  | 0 | 370 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 80 | 0 | 0 | 325 | 290 | 0 | 130 | 81 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 14 | 82 | 103 | 16 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 146 | 56 | 79 | 0 | 0 | 17 | 32 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 302 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 24 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 193 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 5170 | 1759 | 6929 | 4281 | 302 | 1942 | 99 | 160 | 47 | 16 | 82 | 0 | 0 | 96.01
24:00 | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 342 | 308 |  | 0 | 370 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 33 | 0 | 0 | 47 | 0 | 120 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 80 | 0 | 0 | 325 | 290 | 0 | 130 | 81 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 104 | 0 | 22 | 0 | 30 | 60 | 53 | 3 | 130 | 144 | 45 | 60 | 0 | 0 | 0 | 32 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 205 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 11 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4873 | 1572 | 6445 | 4136 | 205 | 1811 | 0 | 160 | 47 | 10 | 76 | 0 | 0 | 96.01
KWH | 799000 | 0 | 2718000 | 0 | 5325873 | 0 | 0 | 8349700 | 7403000 |  | 0 | 8586250 | 0 | 380160 | 45264 | 22060 | 7137112 | 0 | 0 | 0 | 0 | 358560 | 312000 | 0 | 0 | 0 | 73584 | 337320 | 0 | 0 | 135360 | 600000 | 691020 | 829100 | 815200 | 0 | 0 | 1086824 | 0 | 2400000 | 0 | 0 | 4813412 | 0 | 2698743 | 0 |  | 0 | 0 | 0 | 0 | 0 | 168480 | 296928 | 382560 | 2006858 | 0 | 0 | 7636800 | 7035000 | 981000 | 1170909 | 1759550 | 695736 | 0 | 0 | 733368 | 0 | 0 | 0 | 325944 | 66960 | 295500 | 324520 | 1970880 | 2780440 | 712320 | 139932 | 10900 | 599000 | 1296480 | 423600 | 462384 | 3242937 | 3350400 | 1346400 | 1087680 | 0 | 0 | 122000 | 530500 | 59400 | 7526000 | 175352 | 60960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122175 | 144960 | 0 | 0 | 8079000 | 284400 | 555024 | 140509 | 25200 | 991091 | 0 | 0 | 0 | 82320 |  | 7744727 | 0 | 6555744 | 0 | 459840 | 0 | 0 | 0 | 0 | 0 | 0 | 3349337 | 460600 | 258530 | 0 | 0 | 1240000 | 0 | 0 | 0 | 51870 | 0 | 0 | 0 | 0 | 333600 | 74088 | 224640 | 0 | 0 | 3937200 | 0 | 0 | 4679036 | 0 | 4283991 | 0 | 0 | 0 | 0 | 0 | 9066600 | 0 | 0 | 0 | 406368 | 329280 | 0 | 32892 | 388992 |  | 116119899 | 43877335 | 159997234 | 97020028 | 7744727 | 41543476 | 6190932 | 3937200 | 1086824 | 312000 | 1970880 | 191167 | 0
Fuel Cost | 894880 | 0 | 2908260 | 0 | 3941146.02 | 0 | 0 | 6011784 | 5626280 |  | 0 | 6869000 | 0 | 3877632 | 490209.12 | 226335.6 | 8850018.88 | 0 | 0 | 0 | 0 | 3642969.6 | 3091920 | 0 | 0 | 0 | 688746.24 | 3234898.8 | 0 | 0 | 101520 | 450000 | 0 | 0 | 0 | 0 | 0 | 282574.24 | 0 | 3672000 | 0 | 0 | 5054082.6 | 0 | 3427403.61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1576972.8 | 273173.76 | 1063516.8 | 2107200.9 | 0 | 0 | 5651232 | 5909400 | 902520 | 1147490.82 | 2340201.5 | 570503.52 | 0 | 0 | 1048716.24 | 0 | 0 | 0 | 332462.88 | 50220 | 558495 | 243390 | 13599072 | 2279960.8 | 6774163.2 | 142730.64 | 178760 | 814640 | 1763212.8 | 576096 | 577980 | 4021241.88 | 3082368 | 2006136 | 1914316.8 | 0 | 0 | 193980 | 620685 | 139590 | 5343460 | 131514 | 46329.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1409899.5 | 1351027.2 | 0 | 0 | 7594260 | 2494188 | 4945263.84 | 1327810.05 | 0 | 9137859.02 | 0 | 0 | 0 | 0 |  | 20910762.9 | 0 | 5113480.32 | 0 | 4432857.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2679469.6 | 713930 | 2776612.2 | 0 | 0 | 2331200 | 0 | 0 | 0 | 537891.9 | 0 | 0 | 0 | 0 | 366960 | 122245.2 | 170052.48 | 0 | 0 | 16103148 | 0 | 0 | 4117551.68 | 0 | 3984111.63 | 0 | 0 | 0 | 0 | 0 | 6618618 | 0 | 0 | 0 | 3620738.88 | 3075475.2 | 0 | 0 | 0 |  | 159583701.26 | 77675105.59 | 237258806.85 | 90700892.22 | 20910762.9 | 36770126.74 | 54211651.25 | 16103148 | 282574.24 | 3091920 | 13599072 | 1588659.5 | 0
Yesterday Day Peak | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 347 | 320 |  | 0 | 340 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 350 | 290 | 153 | 26 | 90 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 14 | 88 | 127 | 16 | 0 | 2.1 | 29 | 60 | 5 | 5 | 130 | 157 | 64 | 20 | 0 | 0 | 0 | 28 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 431 | 0 | 52 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 |  | 295 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 0 | 0 | 160 | 0 | 0 | 189 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 |  | 6700.8 | DayPeak
Yesterday Evening Peak | 34 | 0 | 150 | 0 | 280 | 0 | 0 | 357 | 300 | 0 | 0 | 400 | 0 | 100 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 102 | 65 | 0 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 31 | 20 | 33 | 0 | 0 | 45 | 0 | 115 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 18 | 80 | 0 | 0 | 325 | 305 | 0 | 130 | 82 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 102 | 95 | 22 | 0 | 30 | 60 | 53 | 50 | 130 | 146 | 66 | 79 | 0 | 0 | 17 | 31 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 361 | 80 | 36 | 51 | 0 | 205 | 0 | 0 | 0 | 52 |  | 645 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 25 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 160 | 0 | 0 | 200 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 50 | 77 | 0 | 0 | 85 |  | 8667 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 360 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 40 | 120 | 0 | 25 | 215 | 0 | 135 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 15 | 125 | 0 | 0 | 360 | 360 | 0 | 180 | 140 | 38 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 109 | 160 | 95 | 22 | 0 | 60 | 86 | 51 | 44 | 163 | 160 | 66 | 79 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 504 | 40 | 400 | 0 | 115 | 200 | 0 | 0 | 25 | 70 | 40 | 190 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 22 | 14 | 11 | 0 | 0 | 260 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 200 | 0 | 360 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 44 | 40 | 120 | 0 | 25 | 210 | 0 | 135 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 50 | 21 | 10 | 125 | 0 | 0 | 360 | 360 | 0 | 150 | 90 | 35 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 90 | 160 | 95 | 22 | 1.6 | 60 | 85 | 51 | 44 | 163 | 160 | 66 | 75 | 0 | 0 | 17 | 40 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 150 | 100 | 400 | 100 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 306 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 175 | 20 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 260 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 0 | 0 | 400 | 50 | 100 | 0 | 32 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 359 | 372 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 15 | 33 | 0 | 0 | 46 | 0 | 120 | 0 | 0 | 205 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 125 | 0 | 0 | 315 | 330 | 0 | 104 | 30 | 33 | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 0 | 33 | 0 | 72 | 104 | 0 | 22 | 0.4 | 28 | 58 | 53 | 29 | 163 | 155 | 68 | 50 | 0 | 0 | 0 | 24 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 1.57 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 11 | 0 | 0 | 160 | 0 | 0 | 182 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0
199
| Minimum Generation |  | 5073 | 5:00
| Highest Generation |  | 8667 | 19:00
| Day Peak Generation |  | 6700.8 | 12:00
| Evening Peak Generation |  | 8667 | 19:00
| HVDC Max Flow |  | 646 | 21:00
| HVDC EvPeak Flow |  | 645 | 19:00
| Load factor L.F |  | 76.92%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-01-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-12-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6700.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5176 | MW
Evening Peak Generation : |  | 8667 | MW Hour : | 19:00 | Available Max Generation : |  | 14460 | MW
E.P. Demand (at gen end) : |  | 8667 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 8667 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5660 | MW
Total Gen. (MKWH) : |  | 159.9972 | System Load Factor : | 76.92% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -412 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-01-01
Actual : | 95.99 | Ft.(MSL) , | Rule curve : | 103 | Ft.( MSL )
Gas Consumed : | Total = | 1089.18 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 127471018.96
: |  | Coal : | 16103148 | Oil : | 57303571.25 | Total : | 200877738.21
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3133.3944 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1059.622 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 948.3339 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 856.5261 |  |  | 0 | 0%
) | 0 | 0:00 | 774.2362 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 624.7663 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 356.9381 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.0617 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 481.8145 |  |  | 0 | 0%
Total | 0 |  | 8396.693 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2. | 9) Sirajganj unit-3
|  |  |  | 2) Summit Meghna 305 MW | 10) Baghabari 100 MW
3) Ghorasal Unit-1,3,5
4) Chandpur CCPP ST
5) Sylhet 150 MW
6) Siddhirganj 335 MW
7) Ashuganj Precision
8) Ashuganj unit-4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ashuganj-Sirajganj 230 kV Ckt-2 was under shut down from 09:02 to 14:49 for A/M.
b) Tongi-Ghorashal 132 kV Ckt-2 was under shut down from 07:14 to 16:08 for A/M.
c) Joydevpur 132/33 kV GT-3 transformer was under shut down from 10:05 to 12:10 for A/M.
d) Aminbazar-Savar 132 kV Ckt-1 was under shut down from 08:38 to 15:19 for A/M.
e) Dohazari-Cox's Bazar 132 kV Ckt-2 was under shut down from 08:08 to 15:19 for A/M.
f) Shahmirpur-Sikalbaha 132 kV Ckt-2 was under shut down from 08:02 to 14:59 for A/M.
g) Ullon 132/33 kV T-1 transformer was under shut down from 08:22 to 21:18 for A/M.
h) Chandpur 132 kV bus bar-B was under shut down from 09:15 to 17:45 for A/M.
i) Sylhet 132/33 kV T-1 transformer was under shut down from 09:59 to 12:43 for A/M.
j) Srimongal Fenchuganj 132 kV Ckt-1 was under shut down from 11:29 to 14:20 for A/M.
k) Fenchuganj-Kulaura 132 kV Ckt-1 was under shut down from 09:03 to 17:17 for A/M.
l) Halishahar 132/33 kV T-3 transformer was shut down at 10:49 for B-phase bushing of LT side maintenance.
m) Natore 132/33 kV T-2 transformer was under shut down from 08:28 to 14:01 for A/M.
n) Faridpur-Bheramara 132 kV Ckt-2 was under shut down from 07:16 to 14:41 for A/M.
o) Goalpara-Bagerhat 132 kV Ckt-1 was under shut down from 07:13 to 15:44 for A/M.
p) Shahjadpur-Pabna 132 kV Ckt was under shut down from 10:35 to 12:22 for CB gas refill at pabna end.
q) Goalpara-Orion PP-Bagerhat 132 kV both Ckts tripped at 13:37 showing O/C relay and was switched on
at 14:06.
r) Gopalganj-Payra 400 kV Ckt-2 was switched on at 16:51 from Gopalganj end and Shut down at 17:38 for
inspection unbalance voltage at Payra power plant end.
s) Ashuganj 225 MW GT was shut down at 16:35 on test basis.
t) Agargaon-Satmosjid 132 kV Ckt-2 tripped at 14:06 from Satmosjid end showing general trip & Diff. relay and |  |  |  |  | About 60 MW power interruption occurred under Satmosjid S/S area
was switched on at 14:23. |  |  |  |  | from 14:06 to 14:23.
u) Faridpur 132/33 kV T-1 & T-2 transformers tripped at 13:37 for 33 kV operating SPS and was switched on |  |  |  |  | About 75 MW power interruption occurred under Faridpur S/S area
at 14:02. |  |  |  |  | from 13:37 to 14:02.
v) Pabna 132/33 kV T-3 transformer was under shut down from 16:59 to 20:22 for SCADA integration.
w) Bhola CCPP ST was synchronized at 17:22.
x) Gopalganj-payra 400 kV Ckt-2 was switched on at 20:06 & shut down at 21:45 due to high voltage.
y) Siddhirganj EGCB 335 MW shut down at 07:28(01/01/2020) for GT air intake filter change.
z) Mymensingh-Netrokona 132 kV Ckt-2 was shut down at 07:44(01/01/2020) for A/M.
aa) Khulshi-Madunaghat 132 kV Ckt-1 was shut down at 08:00(01/01/2020) for A/M.
ab) Mymensing 33 kv bus under T2 transformer shutdown since at 07:11 for PBS maintenance work.
ac) Sirajganj #03 tripped at 07:41 due to DP high.
ad) Faridpur- Bheramara 132 kV Ckt-1 is under shut down since at 07:29 for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-12-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 34 | 799000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 2718000 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 5325873 | Transformer O/L
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 357 | 8349700 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 300 | 7403000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8586250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 380160
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 45264 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 22060 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 135360
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7137112 | Low demand
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 358560
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 40 | 73584 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 337320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 65 | 312000 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 0
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1291020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 829100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 36 | 555024 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2418 | 45473587
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122175
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 168480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1086824 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4813412 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2698743
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 140509 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 144960 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 296928
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 382560
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25200
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 205 | 991091 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 895 | 13270882
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2006858 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 981000 | Under shut down.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7636800 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7035000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 695736 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
| Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 130 | 1170909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 733368 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 82 | 1759550
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 325944
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 66960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 1970880
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 295500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 324520 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 0 | 52 | 82320 | on test
| Cumilla Area Total |  |  |  | 2920 | 1238 | 25085345
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 2780440 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 139932
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 712320
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10900
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 80 | 284400 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 299 | 3927992
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 599000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1296480
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3242937 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 146 | 3350400 | GT2 under shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 423600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 462384
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 60960
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1346400 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1087680 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 122000 | Engine problem
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 31 | 530500 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 175352
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7526000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 361 | 8079000 | FGMO
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 59400
| Sylhet Area Total |  |  |  | 1949 | 1378 | 28362093
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 645 | 7744727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 459840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 6555744 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 406368 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1040 | 15166679
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 258530 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 460600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 165 | 3349337 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Line under development work.
| Barisal Area Total |  |  |  | 462 | 222 | 4068467
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 40 | 1240000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 51870 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 200 | 4679036 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4283991 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 382 | 9066600 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 333600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 74088 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224640
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 85 | 388992 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 940 | 20342817
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3937200
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 77 | 329280 | Low voltage
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32892
| Rangpur Area Total |  |  |  | 605 | 237 | 4299372
| Total |  |  |  | 19047 | 8667 | 159997234
| Eastern Grid Total |  |  |  | 13483 | 6228 | 116119899
| Western Grid Total |  |  |  | 5564 | 2439 | 43877335
| National Grid Total |  |  |  | 19047 | 8667 | 159997234
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-12-31
(a) ENTIRE EASTERN GRID : |  | 5547 | MW | (b) ENTIRE WESTERN GRID : |  | 2712 | MW
i) Dhaka area |  | 2961 | MW | i) Khulna area |  | 1018 | MW
ii) Chittagong area |  | 901 | MW | ii) Rajshahi area |  | 874 | MW
iii) Comilla area |  | 713 | MW | iii) Barisal area |  | 228 | MW
iv) Mymensingh area |  | 653 | MW | iv) Rangpur area |  | 592 | MW
v) Sylhet area |  | 319 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8259 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 12:00 | Shahjibazar | 78 | 18:30 | Bottail | 88 | 18:30
Munsiganj | 82 | 19:00 | Fenchuganj | 26 | 18:00 | G.K Project | 34 | 18:30
Sonargaon | 70 | 19:00 | Kulawara | 29 | 18:00 | Faridpur | 128 | 18:30
Shyampur | 180 | 9:00 | Sylhet | 97 | 19:30 | Madaripur | 57 | 19:30
Bhulta | 156 | 18:30 | Chatak | 17 | 20:00 | Sariatpur | 40 | 21:00
Madanganj | 47 | 18:00 | Sunamganj | 27 | 18:00 | Gopalganj | 60 | 18:30
Shitalakhya | 96 | 12:00 | Biani Bazar | 28 | 19:00 | Bagerhat | 67 | 18:30
Rahim steel | 20 | 1:00 | Comilla (S) | 104 | 19:00 | Mongla | 36 | 10:00
Matuail | 76 | 10:00 | Comilla(N) | 71 | 18:30 | Satkhira | 67 | 18:30
Ghorasal | 69 | 21:00 | Chandpur | 53 | 20:00 | Gallamari | 37 | 13:00
Narsingdi | 130 | 2:00 | Feni | 88 | 18:00 | Magura | 38 | 18:00
Haripur (SBU) | 135 | 5:00 | Chowmuhani | 110 | 19:30 | Norail | 26 | 19:00
Ullon | 40 | 18:30 | Ashuganj | 38 | 20:00 | Chuadanga | 59 | 18:30
Hasnabad | 144 | 18:30 | Daudkandi | 86 | 19:30 | Barisal(N) | 29 | 20:00
Magbazar | 69 | 14:00 | B.Baria | 92 | 20:00 | Barisal (S) | 70 | 21:00
Maniknagar | 72 | 18:00 | Ramganj | 66 | 19:00 | Patuakhali | 77 | 21:00
Bangabhaban | 14 | 13:00 | Chaddagram | 14 | 8:00 | Bhandaria | 40 | 19:30
Narinda | 68 | 17:00 | PHP | 2 | 11:00 | Borhan Uddin | 27 | 22:00
Dhanmondi | 72 | 13:00 | Madunaghat | 41 | 10:00 | Ishurdi | 43 | 19:00
Lalbag | 64 | 18:00 | Hathazari | 67 | 18:00 | Ruppur Paromanobik | 1 | 3:00
Madartek | 42 | 20:00 | Khulshi | 138 | 12:00 | Natore | 84 | 18:30
Mirpur | 68 | 18:30 | Halishahar | 103 | 12:00 | Bogra | 121 | 18:30
Kalyanpur | 63 | 18:00 | Baraulia | 139 | 24:00 | Noagaon | 75 | 19:30
Gulshan | 88 | 13:00 | Sikalbaha | 15 | 12:00 | Rajshahi | 90 | 18:00
Uttara | 56 | 18:00 | Dohazari | 64 | 18:00 | Rajshahi New | 8 | 18:30
Uttara New | 25 | 18:00 | Cox'sbazar | 67 | 19:00 | C.Nawabganj | 55 | 20:00
Kamrangirchar | 62 | 18:00 | Chandraghona | 24 | 18:00 | Amnura | 24 | 18:30
Savar | 94 | 18:30 | Kaptai | 3.5 | 18:00 | Pabna | 72 | 18:30
Bhasantec | 99 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 80 | 18:30
Agargaon | 36 | 18:30 | Bakulia | 68 | 18:30 | Serajganj | 66 | 19:00
Satmosjid | 65 | 18:00 | Julda | 17 | 24:00 | Niyamatpur | 46 | 19:00
Tongi | 89 | 19:30 | TK chemical | 11 | 18:30 | Joypurhat | 47 | 19:00
Kabirpur | 141 | 15:00 | Modern Steel | 15 | 11:00 | Sherpur(Bogura) | 32 | 18:00
Basundhara | 62 | 18:00 | Shahmirpur | 21.5 | 18:00 | Mohastangor | 25 | 18:00
Manikganj | 62 | 20:00 | Khagrachhari | 16 | 18:00 | Rangpur | 107 | 18:30
Joydevpur | 145 | 18:00 | Matarbari | 22 | 18:00 | Lalmonirhat | 42 | 19:00
New Tongi | 76 | 11:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 88 | 18:00
Korda | 174 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 86 | 19:30
Dhamrai | 42 | 18:30 | Abul Khair 230 | 10 | 12:00 | Thakurgaon | 57 | 19:30
Valuka | 64 | 19:00 | BSRM | 154 | 18:30 | Palashbari | 85 | 18:30
Tangail | 126 | 19:00 | GPH Ispat | 10 | 19:30 | Barapukuria | 44 | 19:30
Mymensing | 151 | 18:30 | Goalpara | 13 | 3:00 | Panchagar | 36 | 18:00
Kishorganj | 84 | 19:00 | Central s/s | 72 | 18:30 | Joldhaka | 20 | 18:30
Netrokona | 81 | 20:00 | Noapara | 41 | 18:30 | Kurigram | 41 | 18:30
Jamalpur | 82 | 19:30 | Jessore | 84 | 18:30
Sherpur | 74 | 19:00 | Benapol | 30 | 19:00
Srimongal | 26 | 18:00 | Jhenida | 80 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-12-31 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 399 | 0.20833 | 391 | 0.41667 | Kaliakoir | 387 | 0.125 | 373 | 0.5
Bheramara | 409 | 0.20833 | 396 | 0.41667 | Bhulta | 397 | 0.16667 | 387 | 0.41667
Ashuganj(N) | 402 | 0.16667 | 392 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 230 | 0.75 | Hathazari | 226 | 0.91667 | 222 | 0.54167
Ishurdi | 243 | 0.083333 | 227 | 0.75 | Megnaghat | 233 | 0.20833 | 230 | 0.41667
Ashuganj | 241 | 0.083333 | 236 | 0.45833 | Fenchuganj | 241 | 0.95833 | 235 | 0.5
Serajganj | 235 | 0.125 | 228 | 0.77083 | Siddhirganj | 236 | 0.20833 | 230 | 0.41667
Baghabari | 244 | 0.16667 | 237 | 0.83333 | Maniknagar | 235 | 0.125 | 227 | 0.5
Barapukuria | 234 | 0.125 | 226 | 0.77083 | Old Airport | 235 | 0.16667 | 225 | 0.5
Bogra | 233 | 0.20833 | 223 | 0.75 | Barisal | 239 | 0.125 | 227 | 0.54167
Khulna South | 237 | 0.125 | 216 | 0.75 | AKSML | 224 | 0.16667 | 218 | 0.54167
Rampura | 231 | 0.041667 | 228 | 0.5 | BSRM | 227 | 0.16667 | 222 | 0.5
Haripur | 232 | 0.16667 | 229 | 0.5 | Bibiyana | 238 | 0.125 | 232 | 0.45833
Hasnabad | 234 | 0.16667 | 226 | 0.45833 | Bhulta | 236 | 0.16667 | 229 | 0.5
Aminbazar | 234 | 0.125 | 226 | 0.5 | Ashuganj (S) | 239 | 0.125 | 232 | 0.5
Tongi | 230 | 0.29167 | 220 | 0.45833 | Kaliakoir | 237 | 0.125 | 228 | 0.5
Comilla (N) | 240 | 0.375 | 234 | 0.54167 | GPH | 223 | 0.25 | 218 | 0.54167
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.125 | 130 | 0.5 | Halishahar | 133 | 0.75 | 128 | 0.5
Munsiganj | 135 | 0.75 | 127 | 0.5 | Baraulia | 132 | 0.041667 | 128 | 0.5
Sonargaon | 132 | 0.041667 | 129 | 0.5 | Sikalbaha | 132 | 0.125 | 129 | 0.41667
Shyampur | 134 | 0.041667 | 130 | 0.58333 | Dohazari | 131 | 0.20833 | 128 | 0.5
Bhulta | 129 | 0.75 | 125 | 0.5 | Cox'sbazar | 127 | 0.16667 | 119 | 0.5
Madanganj | 134 | 0.83333 | 126 | 0.5 | Chandraghona | 133 | 0.083333 | 128 | 0.54167
Shitalakhya | 135 | 0.20833 | 127 | 0.5 | Kaptai | 132 | 0.041667 | 130 | 0.58333
Rahim steal | 135 | 4:00 | 131 | 0.45833 | A. Khaer Stl. | 131 | 0.041667 | 129 | 0.45833
Matuail | 134 | 0.125 | 129 | 0.5 | Bakulia | 131 | 0.20833 | 127 | 0.45833
Ghorasal | 142 | 0.041667 | 138 | 0.58333 | Julda | 132 | 0.77083 | 127 | 0.45833
Narsinghdi | 130 | 0.083333 | 126 | 0.79167 | TK Chemical | 133 | 0.79167 | 128 | 0.5
Haripur (SBU) | 135 | 0.20833 | 131 | 0.45833 | Modern Steel | 132 | 0.875 | 128 | 0.5
Ullon | 131 | 0.25 | 125 | 0.54167 | Shahmirpur | 132 | 0.8125 | 127 | 0.45833
Hasnabad | 135 | 0.25 | 129 | 0.25 | Khagrachhari | 133 | 0.125 | 127 | 0.54167
Magbazar | 131 | 0.25 | 125 | 0.5 | Matarbari | 130 | 0.041667 | 122 | 0.5
Maniknagar | 138 | 0.25 | 134 | 0.5 | Baroiar Hat | 134 | 0.79167 | 130 | 0.5
Bangabhaban | 138 | 0.25 | 134 | 0.5 | Rangamati | 133 | 0.125 | 127 | 0.54167
Narinda | 138 | 0.25 | 134 | 0.5 | Goalpara | 138 | 0.20833 | 125 | 13:00
Dhanmondi | 131 | 0.25 | 125 | 0.54167 | Central s/s | 137 | 0.083333 | 126 | 12:00
Lalbag | 136 | 0.20833 | 127 | 0.5 | Noapara | 136 | 0.16667 | 124 | 0.75
Madartek | 131 | 0.25 | 125 | 0.5 | Jessore | 133 | 0.20833 | 120 | 0.75
Mirpur | 137 | 0.25 | 133 | 0.5 | Benapol | 134 | 0.125 | 121 | 0.75
Kalyanpur | 138 | 0.16667 | 132 | 0.5 | Jhenida | 134 | 0.125 | 120 | 0.75
Gulshan | 130 | 0.25 | 125 | 0.5 | Bottail | 137 | 0.16667 | 128 | 0.75
Uttara | 136 | 0.16667 | 128 | 0.5 | G.K Project | 141 | 0.125 | 135 | 0.75
Uttara New | 135 | 0.25 | 128 | 0.5 | Faridpur | 137 | 0.70833 | 122 | 0.54167
Kamrangirchar | 134 | 0.16667 | 127 | 0.5 | Madaripur | 137 | 0.70833 | 124 | 0.33333
Savar | 135 | 0.25 | 127 | 0.5 | Sariatpur | 132 | 0.041667 | 124 | 0.83333
Bhasantec | 135 | 0.20833 | 129 | 0.5 | Gopalganj | 142 | 0.70833 | 126 | 0.33333
Agargaon | 137 | 0.20833 | 131 | 0.5 | Bagerhat | 136 | 0.125 | 119 | 0.58333
Satmosjid | 136 |  | 129 | 0.5 | Mongla | 132 | 0.041667 | 119 | 0.5
Tongi | 137 | 0.33333 | 133 | 0.625 | Satkhira | 138 | 0.20833 | 125 | 0.54167
Kabirpur | 133 | 0.20833 | 127 | 0.5 | Gallamari | 138 | 0.125 | 127 | 0.5
Basundhara | 131 | 2:00 | 126 | 0.54167 | Magura | 136 | 0.20833 | 118 | 0.75
Manikganj | 140 | 4:00 | 132 | 0.5 | Norail | 133 | 0.16667 | 119 | 0.75
Joydevpur | 142 | 0.79167 | 136 | 0.5 | Chuadanga | 132 | 0.125 | 117 | 0.75
New Tongi | 138 | 0.125 | 131 | 0.5 | Barisal(N) | 138 | 0.70833 | 126 | 0.33333
Kodda | 134 | 0.70833 | 127 | 0.375 | Barisal (S) | 136 | 0.125 | 127 | 0.5
Dhamrai | 134 | 0.20833 | 127 | 0.66667 | Patuakhali | 133 | 0.16667 | 121 | 0.66667
Valuka | 130 | 0.20833 | 124 | 0.54167 | Bhandaria | 134 | 0.25 | 121 | 0.54167
Tangail | 134 | 0.16667 | 126 | 0.75 | Ishurdi | 139 | 0.125 | 131 | 0.77083
Mymensing | 130 | 0.16667 | 123 | 0.75 | Ruppur Paromanobik | 137 | 0.25 | 131 | 0.75
Kishorganj | 134 | 0.16667 | 126 | 0.75 | Natore | 136 | 0.125 | 127 | 0.77083
Netrokona | 130 | 0.20833 | 122 | 0.75 | Bogra | 137 | 0.083333 | 130 | 0.54167
Jamalpur | 133 | 0.79167 | 124 | 0.625 | Noagaon | 135 | 0.083333 | 126 | 0.77083
Sherpur | 133 | 0.83333 | 119 | 0.33333 | Rajshahi | 133 | 0.083333 | 123 | 0.54167
Srimongal | 138 | 0.041667 | 135 | 0.54167 | Rajshahi New | 134 | 0.125 | 121 | 0.5
Shahjibazar | 136 | 0.20833 | 132 | 0.75 | C.Nawabganj | 131 | 0.083333 | 121 | 0.54167
Fenchuganj | 137 | 0.83333 | 134 | 0.45833 | Amnura | 132 | 0.20833 | 121 | 0.5
Khulawara | 137 | 0.041667 | 133 | 12:00 | Pabna | 140 | 0.125 | 132 | 0.54167
Sylhet | 135 | 0.041667 | 132 | 0.45833 | Shahjadpur | 142 | 0.125 | 137 | 0.75
Chatak | 135 | 0.041667 | 131 | 0.5 | Serajganj | 138 | 0.125 | 131 | 0.77083
Sunamganj | 135 | 0.041667 | 130 | 0.70833 | Niyamatpur | 135 | 0.16667 | 124 | 0.75
Biani Bazar | 136 | 0.16667 | 132 | 0.375 | Joypurhat | 136 | 0.083333 | 125 | 0.75
Comilla(s) | 132 | 0.20833 | 129 | 0.375 | Sherpur(Bogura) | 139 | 0.125 | 131 | 0.75
Comilla(n) | 140 | 0.875 | 137 | 0.91667 | Mohastangor | 135 | 0.125 | 128 | 0.77083
Chandpur | 136 | 20:00 | 135 | 0.45833 | Rangpur | 133 | 0.125 | 124 | 0.75
Feni | 135 | 0.29167 | 132 | 0.625 | Lalmonirhat | 127 | 0.16667 | 120 | 0.75
Chowmuhani | 132 | 0.79167 | 129 | 0.625 | Saidpur | 133 | 0.25 | 120 | 0.75
Ashuganj | 136 | 0.29167 | 133 | 0.75 | Purbasadipur | 132 | 0.25 | 113 | 0.79167
Daudkandi | 134 | 0.75 | 131 | 0.5 | Thakurgaon | 128 | 0.16667 | 110 | 0.77083
B.Baria | 133 | 0.29167 | 129 | 0.79167 | Palashbari | 131 | 0.25 | 123 | 0.75
Ramganj | 136 | 0.33333 | 130 | 0.625 | Barapukuria | 134 | 0.125 | 126 | 0.77083
Chaddagram | 137 | 0.083333 | 133 | 0.66667 | Panchagar | 127 | 0.16667 | 105 | 0.75
PHP | 133 | 0.77083 | 129 | 0.70833 | Joldhaka | 131 | 0.125 | 117 | 0.77083
Madanhat | 134 | 0.16667 | 131 | 0.5 | Kurigram | 132 | 0.20833 | 121 | 0.77083
Hathazari | 135 | 0.91667 | 131 | 0.45833
Khulshi | 130 | 0.041667 | 126 | 0.66667

## L-Curve
Date | 2019-12-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 371 | 4873 | 1572 | 6445 |  |  |  | QF-LDC-12
0:30 | 317.5 | 4543.5 | 1556.5 | 6100 | Date: | 2019-12-31
1:00 | 264 | 4214 | 1541 | 5755
1:30 | 243 | 4093.5 | 1500.5 | 5594
2:00 | 222 | 3973 | 1460 | 5433
2:30 | 216 | 3943 | 1413 | 5356 | [5 empty] | Gen. at Eve. Peak | 8667 | 8667 MW (19:00 )
3:00 | 210 | 3913 | 1366 | 5279 | [6 empty] | 19:00
3:30 | 217.5 | 3843.5 | 1346 | 5189.5 | [5 empty] | Gen. at Day Peak | 6700.8 | 6700.8 MW (12:00 )
4:00 | 225 | 3774 | 1326 | 5100 | [6 empty] | 12:00
4:30 | 252.5 | 3798 | 1288.5 | 5086.5 | [5 empty] | Highest Generation | 8667
5:00 | 280 | 3822 | 1251 | 5073 | [6 empty] | 19:00
5:30 | 285 | 3898 | 1309.5 | 5207.5
6:00 | 290 | 3974 | 1368 | 5342
6:30 | 332.5 | 4128.805 | 1368 | 5496.805
7:00 | 375 | 4283.61 | 1368 | 5651.61
7:30 | 385 | 4465.105 | 1478.55 | 5943.655
8:00 | 395 | 4646.6 | 1589.1 | 6235.7
8:30 | 269 | 4679.5 | 1737.95 | 6417.45
9:00 | 143 | 4712.4 | 1886.8 | 6599.2
9:30 | 115 | 4749.6 | 1841.45 | 6591.05
10:00 | 87 | 4786.8 | 1796.1 | 6582.9
10:30 | 61 | 4740.35 | 1789 | 6529.35
11:00 | 35 | 4693.9 | 1781.9 | 6475.8
11:30 | 50 | 4791.65 | 1796.65 | 6588.3
12:00 | 65 | 4889.4 | 1811.4 | 6700.8
12:30 | 82 | 4952.6 | 1819 | 6771.6
13:00 | 99 | 5015.8 | 1826.6 | 6842.4
13:30 | 73.5 | 4946.78 | 1777.95 | 6724.73
14:00 | 48 | 4877.76 | 1729.3 | 6607.06
14:30 | 40 | 4762.065 | 1738.15 | 6500.215
15:00 | 32 | 4646.37 | 1747 | 6393.37
15:30 | 16.5 | 4673.07 | 1736.3 | 6409.37
16:00 | 1 | 4699.77 | 1725.6 | 6425.37
16:30 | 69.5 | 4696.885 | 1841.85 | 6538.735
17:00 | 138 | 4694 | 1958.1 | 6652.1
17:30 | 236.5 | 5291.5 | 2165.05 | 7456.55
18:00 | 335 | 5889 | 2372 | 8261
18:30 | 344 | 6058.5 | 2405.5 | 8464
19:00 | 353 | 6228 | 2439 | 8667
19:30 | 313 | 6087 | 2492 | 8579
20:00 | 320 | 6035 | 2458 | 8493 |  |  |  | Executive Engineer
20:30 | 313 | 5928 | 2435 | 8363 |  |  |  | Network Operation Division
21:00 | 306 | 5821 | 2412 | 8233
21:30 | 306 | 5629.5 | 2247 | 7876.5
22:00 | 306 | 5438 | 2082 | 7520 |  |  |  |  | Page 6 of 7
22:30 | 338.5 | 5304 | 1920.5 | 7224.5
23:00 | 371 | 5170 | 1759 | 6929
23:30 | 371 | 5021.5 | 1665.5 | 6687
24:00 | 371 | 4873 | 1572 | 6445
8667 MW (19:00 )
6700.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-12-31 |  | Energy | 159997234
[10 empty] | 2019-12-31 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4136 | 205 | 1811 | 99 | 160 | 47 | 10 | 0 | 76
0:30 | 3946.5 | 171 | 1697.5 | 49.5 | 160 | 47 | 5 | 0 | 73 | Date: | 2019-12-31
1:00 | 3757 | 137 | 1584 | 0 | 160 | 47 | 0 | 0 | 70
1:30 | 3693 | 137 | 1488 | 0 | 160 | 47 | 0 | 0 | 69 | [7 empty] | Total Energy | 159.9972 | Total Energy Gen 159.997 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.997 MKWHr
2:00 | 3629 | 137 | 1392 | 0 | 160 | 47 | 0 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 3556.5 | 137 | 1388 | 0 | 160 | 46.5 | 0 | 0 | 68 | [7 empty] | Energy Requirement | 159.9972
3:00 | 3484 | 137 | 1384 | 0 | 160 | 46 | 0 | 0 | 68
3:30 | 3445 | 136.5 | 1334 | 0 | 160 | 46 | 0 | 0 | 68 | [6 empty] | Shortage
4:00 | 3406 | 136 | 1284 | 0 | 160 | 46 | 0 | 0 | 68
4:30 | 3378 | 137 | 1298 | 0 | 160 | 45.5 | 0 | 0 | 68
5:00 | 3350 | 138 | 1312 | 0 | 160 | 45 | 0 | 0 | 68
5:30 | 3431.5 | 137.5 | 1366 | 0 | 160 | 44.5 | 0 | 0 | 68
6:00 | 3513 | 137 | 1420 | 0 | 160 | 44 | 0 | 0 | 68
6:30 | 3615 | 136.5 | 1473.5 | 0 | 160 | 43.5 | 0 | 0 | 68 |  |  |  |  | Coal
7:00 | 3717 | 136 | 1527 | 0 | 160 | 43 | 0 | 0 | 68
7:30 | 3891 | 136 | 1640.5 | 0 | 160 | 43 | 0 | 0 | 69 |  |  |  | Oil |  |  |  | ,
8:00 | 4065 | 136 | 1754 | 0 | 160 | 43 | 0 | 0 | 70
8:30 | 4111 | 218.5 | 1787.5 | 9 | 160 | 43.5 | 0 | 0 | 75
9:00 | 4157 | 301 | 1821 | 18 | 160 | 44 | 0 | 0 | 80
9:30 | 4147.5 | 301 | 1800 | 34.5 | 160 | 44 | 0 | 0 | 82
10:00 | 4138 | 301 | 1779 | 51 | 160 | 44 | 0 | 0 | 84
10:30 | 4144.5 | 301 | 1708 | 59.5 | 160 | 44.5 | 0 | 0 | 84
11:00 | 4151 | 301 | 1637 | 68 | 160 | 45 | 0 | 0 | 84
11:30 | 4252 | 298 | 1649 | 68 | 160 | 45 | 0 | 0 | 86
12:00 | 4353 | 295 | 1661 | 68 | 160 | 45 | 0 | 0 | 88
12:30 | 4372.5 | 295.5 | 1737 | 68 | 160 | 22.5 | 0 | 0 | 86
13:00 | 4392 | 296 | 1813 | 68 | 160 | 0 | 0 | 0 | 84
13:30 | 4392 | 296 | 1813 | 68 | 160 | 0 | 0 | 0 | 84
14:00 | 4392 | 296 | 1813 | 68 | 160 | 0 | 0 | 0 | 84
14:30 | 4176 | 297.5 | 1754.5 | 100 | 159.5 | 22.5 | 0 | 0 | 85
15:00 | 3960 | 299 | 1696 | 132 | 159 | 45 | 0 | 0 | 86
15:30 | 3972 | 299 | 1711.5 | 124 | 159.5 | 45.5 | 0 | 0 | 85
16:00 | 3984 | 299 | 1727 | 116 | 160 | 46 | 0 | 0 | 84
16:30 | 3908.5 | 386 | 1766.5 | 179.5 | 160 | 46 | 2.5 | 0 | 85
17:00 | 3833 | 473 | 1806 | 243 | 160 | 46 | 5 | 0 | 86
17:30 | 4041.5 | 558.5 | 1845.5 | 686.5 | 160 | 46 | 27.5 | 0 | 91
18:00 | 4250 | 644 | 1885 | 1130 | 160 | 46 | 50 | 0 | 96
18:30 | 4277.5 | 644.5 | 1936.5 | 1242.5 | 160 | 45.5 | 57.5 | 0 | 100
19:00 | 4305 | 645 | 1988 | 1355 | 160 | 45 | 65 | 0 | 104
19:30 | 4332 | 645 | 2004 | 1226 | 160 | 45 | 65 | 0 | 102
20:00 | 4337 | 645 | 1964 | 1176 | 161 | 45 | 65 | 0 | 100
20:30 | 4357.5 | 645.5 | 1970.5 | 1020 | 160.5 | 45 | 65 | 0 | 99
21:00 | 4378 | 646 | 1977 | 864 | 160 | 45 | 65 | 0 | 98
21:30 | 4339.5 | 596.5 | 1960.5 | 633 | 160 | 45.5 | 47.5 | 0 | 94
22:00 | 4301 | 547 | 1944 | 402 | 160 | 46 | 30 | 0 | 90
22:30 | 4291 | 424.5 | 1943 | 250.5 | 160 | 46.5 | 23 | 0 | 86
23:00 | 4281 | 302 | 1942 | 99 | 160 | 47 | 16 | 0 | 82
23:30 | 4208.5 | 253.5 | 1876.5 | 99 | 160 | 47 | 13 | 0 | 79 | Max Temp. in Dhaka |  | 28.0° C
24:00 | 4136 | 205 | 1811 | 99 | 160 | 47 | 10 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 159.997 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 159.997 MKWHr
Note on W13: Author:

## Generation
2019-12-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 47 | 47 | 46 | 46 | 45 | 44 | 43 | 43 | 44 | 44 | 45 | 45 | 0 | 45 | 45 | 46 | 46 | 46 |  | 45 | 45 | 45 | 45 | 46 | 47 | 47 | 1086824
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 115 |  | 115 | 115 | 120 | 120 | 120 | 120 | 120 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.51 | 5.1 | 12.6 | 16.6 | 18.8 | 19 | 18 | 14 | 11 | 6 | 0 | [9 empty] | 122175
6 | Sikalbaha 225MW CCPP (Gas) | 182 | 182 | 182 | 182 | 183 | 184 | 196 | 212 | 232 | 203 | 203 | 206 | 218 | 203 | 205 | 205 | 204 | 204 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4813412
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 104 | 80 | 80 | 80 | 80 | 139 | 140 | 140 | 104 | 104 | 106 | 104 | 105 | 104 | 104 | 149 |  | 139 | 139 | 139 | 140 | 140 | 140 | 140 | 2698743
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 3 | 30 |  | 51 | 51 | 17 | 0 |  |  | 0 | 140509
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 230 | 230 | 230 | 230 | 260 | 350 | 350 | 350 | 325 | 325 | 336 | 335 | 280 | 280 | 280 | 280 |  | 300 | 300 | 300 | 300 | 300 | 301 | 301 | 7137112
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 54 | 26 | 26 | 26 | 26 | 26 | 26 | 83 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1170909
20 | Ghorasal TPP (Unit-1&2) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 799000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 101 | 100 | 101 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2718000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 250 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 5325873
26
28 | Ashuganj TPP Unit- 3 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2006858
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 10 | 10 | 25 | 40 | 40 | 40 | 37 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 |  | 37 | 37 | 40 | 40 | 40 | 40 | 37 | 695736
33 | Ashuganj 225 MW CCPP | [9 empty] | 126 | 136 | 153 | 153 | 153 | 149 | 152 | 0 | 0 | [8 empty] | 981000
34 | Ashuganj 450 MW CCPP(South) | 295 | 295 | 276 | 260 | 270 | 285 | 305 | 290 | 275 | 270 | 280 | 290 | 305 | 275 | 270 | 285 | 270 | 305 |  | 305 | 305 | 305 | 355 | 290 | 290 | 290 | 7035000
| Ashuganj 450 MW CCPP(North) | 280 | 260 | 260 | 260 | 260 | 275 | 306 | 355 | 340 | 330 | 340 | 350 | 360 | 325 | 330 | 340 | 325 | 330 |  | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 7636800
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 88 | 81 | 82 | 90 | 91 | 82 | 91 | 90 | 89 | 90 |  | 82 | 87 | 80 | 80 | 80 | 81 | 81 | 1759550
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 343 | 342 | 320 | 270 | 270 | 302 | 363 | 371 | 366 | 342 | 347 | 347 | 380 | 354 | 352 | 356 | 363 | 359 |  | 357 | 344 | 343 | 343 | 342 | 341 | 342 | 8349700
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 300 | 300 | 300 | 300 | 300 | 300 | 340 | 340 | 340 | 340 | 340 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 8586250
41 | Haripur 360MW CCPP(HPL) | 313 | 283 | 283 | 260 | 260 | 260 | 268 | 372 | 372 | 372 | 320 | 320 | 348 | 339 | 300 | 300 | 300 | 300 |  | 300 | 300 | 306 | 308 | 308 | 308 | 308 | 7403000
42 | RPCL 210MW CCPP | 107 | 107 | 131 | 131 | 145 | 144 | 146 | 147 | 146 | 127 | 125 | 127 | 122 | 120 | 99 | 99 | 99 | 99 |  | 102 | 103 | 102 | 103 | 103 | 103 | 104 | 2780440
43
44 | Fenchugonj CCPP Phase-1 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 28 | 28 | 29 | 28 | 29 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 599000
45 | Fenchugonj CCPP Phase-2 | 60 | 36 | 36 | 36 | 36 | 36 | 36 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1296480
46 | Shajibazar 330 MW CCPP | 145 | 145 | 150 | 152 | 145 | 153 | 160 | 155 | 150 | 147 | 148 | 157 | 155 | 146 | 151 | 151 | 150 | 157 |  | 146 | 150 | 147 | 145 | 145 | 146 | 144 | 3350400
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 48 | 45 | 68 | 67 | 65 | 64 | 63 | 65 | 63 | 63 | 65 | 65 |  | 66 | 67 | 67 | 55 | 56 | 56 | 45 | 1346400
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 79 | 76 | 76 | 76 | 20 | 20 | 20 | 20 | 20 | 20 | 79 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 60 | 1087680
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 122000
52 | Sylhet 50MW PP (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 17 | 24 | 23 | 23 | 28 | 26 | 26 | 25 | 22 | 24 | 28 |  | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 530500
53 | Sylhet 10MW PP (Desh) | [17 empty] | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 59400
54 | Hobiganj 11MW PP Cofidence-E | [16 empty] | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 60960
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 41 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 423600
56 | Shahjahanulla 25 MW PP | [16 empty] | 0 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 175352
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 310 | 300 | 290 | 290 | 300 | 325 | 330 | 320 | 300 | 270 | 310 | 325 | 280 | 290 | 320 | 310 | 300 |  | 310 | 320 | 300 | 300 | 285 | 275 | 280 | 7526000
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 296928
61 | Narshingdi 22 MW PP (Doreen) | [16 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 135360
62 | Tangail 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 139932
63 | Impoprt (Tripura) | 70 | 68 | 68 | 68 | 68 | 68 | 68 | 70 | 80 | 84 | 84 | 88 | 84 | 84 | 86 | 84 | 86 | 96 |  | 104 | 102 | 100 | 98 | 90 | 82 | 76 | 1970880
64 | Malancha, Ctg. EPZ (United) | 6 | 6 | 5 | 6 | 6 | 8 | 8 | 10 | 3 | 3 | 3 | 7 | 12 | 7 | 5 | 8 | 16 | 11 |  | 18 | 21 | 26 | 28 | 30 | 35 | 35 | 382560
65 | Feni 22MW PP (Doreen) | [7 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 0 | 325944
66 | Feni 11 MW PP (Doreen) | [16 empty] | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 66960
67 | Jangalia 33MW PP (Summit) | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 295500
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 324520
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 24 |  | 31 | 31 | 28 | 28 | 28 | 32 | 32 | 691020
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 829100
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [16 empty] | 9 | 55 |  | 52 | 0 |  |  | 0 |  | 0 | 82320
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [16 empty] | 5 | 50 |  | 65 | 65 | 65 | 65 | 30 | 16 | 10 | 312000
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 0 | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 28 | 95 |  | 95 | 95 | 95 | 95 | 95 | 16 | 0 | 712320
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [8 empty] | 11 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 36 | 17 | 17 | 17 |  |  | 0 | 555024
| Kaptai 7 MW Solar PP | [6 empty] | 0.1 | 1 | 1.6 | 3.5 | 4.1 | 4.3 | 4 | 3.16 | 1.17 | 1.27 | 0 | [9 empty] | 25200
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 0 | 14 |  | 15 | 0 | 0 |  |  |  |  | 45264
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 53 |  | 100 | 100 | 100 | 70 |  |  | 0 | 380160
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 |  | 50 | 50 | 50 | 50 | 50 | 50 | 3 | 462384
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 39 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 733368
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 5 | 64 |  | 102 | 102 | 102 | 50 | 7 | 0 |  | 358560
95 | Patenga 50MW PP (Baraka) | [16 empty] | 1 | 24 |  | 50 | 50 | 50 | 32 |  |  | 0 | 168480
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 15 |  | 40 | [5 empty] | 0 | 73584
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 22060
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 55 | 17 | 17
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 100 | 100 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3242937
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.5 | 1.2 | 1.7 | 2 | 2.1 | 1.8 | 1.6 | 1.2 | 0.5 | [10 empty] | 10900
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 12 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 0 | 337320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 0
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 7 | 50 |  | 50 | 50 | 50 | 0 |  |  |  | 144960
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 351 | 291 | 306 | 316 | 318 | 373 | 396 | 252 | 240 | 242 | 320 | 431 | 427 | 433 | 334 | 334 | 241 | 358 |  | 361 | 362 | 363 | 365 | 364 | 363 | 365 | 8079000
| Jamalpur 115 MW PP (United) | [16 empty] | 5 | 50 |  | 80 | 80 | 80 | 8 |  |  | 0 | 284400
| Anwara 300 MW PP (United) | [16 empty] | 16 | 201 |  | 205 | 217 | 216 | 216 | 124 | 15 | 0 | 991091
120 | Eastern Zone Total | 4214 | 3973 | 3913 | 3774 | 3822 | 3974 | 4283.61 | 4646.6 | 4712.4 | 4786.8 | 4693.9 | 4889.4 | 5015.8 | 4877.76 | 4646.37 | 4699.77 | 4694 | 5889 |  | 6228 | 6087 | 6035 | 5821 | 5438 | 5170 | 4873 | 116119899
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 16 | 73 |  | 115 | 115 | 99 | 99 | 75 | 0 |  | 459840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [13 empty] | 16 | 32 | 16 | 32 | 48 |  | 32 | 32 | 32 | 32 | 16 | 0 |  | 258530
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 148 | 148 | 110 | 110 | 110 | 110 | 110 | 150 | 150 | 144 | 144 | 142 | 140 | 75 | 75 | 85 | 86 | 167 |  | 165 | 170 | 172 | 173 | 162 | 175 | 164 | 3349337
140 | Bhola 33 MW PP (Venture) | 21 | 21 | 19 | 17 | 16 | 18 | 18 | 17 | 17 | 17 | 15 | 18 | 18 | 17 | 17 | 16 | 17 | 22 |  | 25 | 26 | 26 | 25 | 25 | 24 | 22 | 460600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [13 empty] | 58 | 32 | 32 | 15 | 50 |  | 50 | 50 | 50 | 50 | 32 | 15 | 0 | 406368
146 | Bheramara HVDC | 137 | 137 | 137 | 136 | 138 | 137 | 136 | 136 | 301 | 301 | 301 | 295 | 296 | 300 | 299 | 299 | 473 | 644 |  | 645 | 645 | 645 | 646 | 547 | 302 | 205 | 7744727
147 | Bheramara 410 MW CCPP | 255 | 265 | 275 | 305 | 230 | 230 | 230 | 365 | 360 | 340 | 325 | 305 | 280 | 260 | 235 | 225 | 230 | 230 |  | 230 | 235 | 235 | 235 | 235 | 235 | 235 | 6555744
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 159 | 160 | 160 | 160 |  | 160 | 160 | 161 | 160 | 160 | 160 | 160 | 3937200
153 | Baghabari 71 MW GTPP | 45 | 45 | 45 | 50 | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 50 | 45 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 45 | 50 | 1240000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 181 | 130 | 130 | 130 | 130 | 130 | 149 | 190 | 173 | 178 | 189 | 214 | 204 | 214 | 214 | 214 | 196 |  | 200 | 205 | 214 | 214 | 214 | 193 | 185 | 4679036
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 157 | 139 | 133 | 133 | 135 | 136 | 142 | 166 | 166 | 167 | 215 | 200 | 178 | 173 | 167 | 175 | 179 |  | 183 | 196 | 196 | 196 | 196 | 196 | 195 | 4283991
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 430 | 338 | 343 | 277 | 276 | 370 | 370 | 372 | 432 | 383 | 382 | 382 | 428 | 378 | 434 | 436 | 424 | 385 |  | 382 | 383 | 352 | 362 | 342 | 376 | 341 | 9066600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [7 empty] | 16 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 333600
163 | Bogura 20 MW PP (Energyprima) | [8 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 74088
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 224640
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 12 | 12 | 12 | 0 |  |  | 51870
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 6 | 54 |  | 85 | 108 | 109 | 70 | 0 |  |  | 388992
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 74 |  | 77 | 77 | 77 | 60 | 0 |  |  | 329280
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1.1 | 2.8 | 4.1 | 4.9 | 5.4 | 5.6 | 4.3 | 3 | 1.6 | 0.1 | [9 empty] | 32892
178
178