## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-01-10 | Friday
|  | Date (day): | 2020-01-10 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11413.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14264 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-01-09 | 2020-01-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 34 | 34 | 35 | 35 |  | 50 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 250 | 200 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 320 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 335 | 360 | 360 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 284 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 18 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 343 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 42 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 15 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2080 | 2477 | 3669 | 4318 | 806 | 624
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.35 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 47 | 45 | 45 | 46 | 184 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 214 | 203 | 210 | 215 |  |  | FGMO
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 139 | 130 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 70 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 26 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.36 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 151 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 554.71 | 829 | 1405 | 1616 | 244 | 278
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 125 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 234 | 155 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 365 | 290 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 40 | 40 |  | 5 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 83 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 104 | 92 | 107
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 8 | 14 | 14 | 14 |  | 11 | Engine problem
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 7 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1417 | 1312 | 1658 | 2337 | 309 | 281
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 107 | 89 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.3 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 40 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 179.3 | 246 | 483.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 50 | 66 | 66 | 66
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 147 | 150 | 160 |  | 170 | GT-1 Under maint
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 67 | 69 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 1 | 79 | 73 | 73 |  | 13 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 16 | 16 | 16 |  |  | Engine problem
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 229 | 230 | 230 | 230 |  |  | PG test
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1011 | 1263 | 1305 | 1315 | 0 | 325
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 314 | 653 | 178 | 463
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 100 | 60 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 37
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 36 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 314 | 803 | 474 | 1270 | 0 | 410
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 5 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 103 | 161 | 175 | 190
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 68 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 176 | 277 | 360 | 445 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 32 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 214 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 19 | 220 | 220 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 209 | 212 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 368 | 400 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 909 | 1023 | 1738 | 2034 | 100 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 54 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 204.3 | 254 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19630 | 19107 | 6845.31 | 8484 | 11413.6 | 14264 | 1511 | 2111
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6495.9442 | 8051 | 10831.0813 | 13536.0047
A. |  | 2020-01-09 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8484 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5190 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8484 | MW
3 | Day peak Generation : |  |  | 6845.31 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8051 | MW
4 | Evening peak Generation : |  |  | 8484 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 161.2456 | MKWHr | By Solar | 0.18447 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 140.6185 | MKWHr |  | By Oil: | 4.525 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.8496 | MKWHr |  | By Hydro: | 1.0622 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1511 | MW | Dhaka | 2926 | 2926 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2111 | MW | Chittagong | 839 | 839 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3622 | MW | Khulna | 1000 | 1000 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1097.45 | MMCFD |  |  | Rajshahi | 843 | 843 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 130679017.558 | ii) Oil : | Taka | 41410957.15 | Comilla | 657 | 657 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19834864 | Total | Taka | 191924838.708 | Mymensingh | 652 | 652 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5.141 | MKWHr. | Sylhet | 323 | 323 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -434 | MW (E to W) at | 19:00 | hrs | Barisal | 236 | 236 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -517 | MW at | 18:30 | hrs | Rangpur | 575 | 575 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 23.0° C |  |  | Total | 8051 | 8051 |  | 0
B. |  | 2020-01-10 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 24.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14264 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6400 | MW
4 | Reserve(Generation end) |  |  |  | 6664 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 144.4445 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5055 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.0196 | MKWHr. | ii) HVDC Flow at Peak Time |  | 653 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9862 | MKWHr. | iii) Maximum HVDC Flow : |  | 653 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.72 |  | (b) Today: | 95.64 |  | (c) Rule Curve: |  | 101.29
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-01-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 34 | 0 | 101 | 0 | 319 | 0 | 0 | 335 | 312 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 196 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 0 | 340 | 265 | 161 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 74 | 108 | 16 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 148 | 42 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 15 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 187 | 0 | 178 | 0 | 12 | 0 | 189 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4423 | 1561 | 5984 | 3932 | 137 | 1580 | 16 | 200 | 45 | 0 | 74 | 0 | 0 | 95.73
2:00 | 34 | 0 | 102 | 0 | 318 | 0 | 0 | 336 | 318 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 182 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 0 | 260 | 265 | 144 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 109 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 154 | 42 | 1 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 151 | 0 | 12 | 0 | 180 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4194 | 1409 | 5603 | 3704 | 137 | 1447 | 0 | 200 | 45 | 0 | 70 | 0 | 0 | 95.73
3:00 | 34 | 0 | 102 | 0 | 308 | 0 | 0 | 337 | 283 |  | 0 | 320 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 190 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 0 | 275 | 280 | 143 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 66 | 108 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 150 | 42 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 14 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 198 | 0 | 0 | 130 | 0 | 137 | 0 | 13 | 0 | 130 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4109 | 1350 | 5459 | 3594 | 139 | 1417 | 0 | 198 | 45 | 0 | 66 | 0 | 0 | 95.73
4:00 | 34 | 0 | 100 | 0 | 199 | 0 | 0 | 339 | 262 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 182 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 0 | 260 | 260 | 143 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 66 | 109 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 163 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 136 | 0 | 13 | 0 | 130 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3879 | 1323 | 5202 | 3451 | 139 | 1301 | 0 | 200 | 45 | 0 | 66 | 0 | 0 | 95.72
5:00 | 34 | 0 | 100 | 0 | 220 | 0 | 0 | 290 | 363 |  | 0 | 400 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 182 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 0 | 240 | 240 | 143 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 68 | 108 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 130 | 148 | 42 | 1 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4055 | 1135 | 5190 | 3240 | 138 | 1499 | 0 | 200 | 45 | 0 | 68 | 0 | 0 | 95.72
6:00 | 34 | 0 | 105 | 0 | 200 | 0 | 0 | 300 | 352 |  | 0 | 380 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 194 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 100 | 0 | 0 | 235 | 270 | 143 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 68 | 108 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 130 | 158 | 54 | 1 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4137 | 1187 | 5324 | 3327 | 139 | 1545 | 0 | 200 | 45 | 0 | 68 | 0 | 0 | 95.72
7:00 | 34 | 0 | 100 | 0 | 200 | 0 | 0 | 365 | 374 |  | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 216 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 100 | 0 | 0 | 360 | 305 | 170 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 66 | 106 | 0 | 0 | 0 | 60 | 50 | 0 | 0 | 130 | 160 | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 0 | 130 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4558.75 | 1260 | 5818.75 | 3697 | 139 | 1671 | 0 | 200 | 45 | 0 | 66 | 0.75 | 0 | 95.71
8:00 | 34 | 0 | 200 | 0 | 300 | 0 | 0 | 375 | 372 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 31 | 0 | 0 | 46 | 0 | 110 | 0 | 0 | 206 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 100 | 0 | 0 | 345 | 290 | 199 | 8 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 108 | 0 | 0 | 0.1 | 60 | 50 | 0 | 0 | 130 | 151 | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 100 | 0 | 0 | 141 | 0 | 0 | 0 | 13 | 0 | 156 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 |  | 4817.6 | 1386.2 | 6203.8 | 3931 | 313 | 1733 | 0 | 100 | 46 | 0 | 72 | 8.8 | 0 | 95.71
9:00 | 34 | 0 | 200 | 0 | 300 | 0 | 0 | 352 | 372 |  | 0 | 450 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 31 | 0 | 0 | 46 | 0 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 100 | 0 | 0 | 340 | 315 | 234 | 8 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 108 | 44 | 20 | 0.2 | 58 | 50 | 0 | 0 | 163 | 148 | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.91 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0.94 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 204 | 0 | 0 | 0 | 12 | 0 | 197 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 |  | 5051.05 | 1572.9 | 6623.95 | 4185 | 313 | 1742 | 44 | 200 | 46 | 0 | 78 | 15.95 | 0 | 95.71
10:00 | 34 | 0 | 201 | 0 | 300 | 0 | 0 | 349 | 361 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 31 | 0 | 0 | 46 | 0 | 110 | 0 | 0 | 215 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 100 | 0 | 0 | 375 | 350 | 204 | 8 | 90 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 107 | 94 | 20 | 0.2 | 60 | 50 | 0 | 0 | 130 | 157 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.56 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 2.013 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 12 | 0 | 209 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 |  | 5078.773 | 1559.2 | 6637.973 | 4246 | 313 | 1637 | 94 | 200 | 46 | 0 | 80 | 21.973 | 0 | 95.7
11:00 | 34 | 0 | 252 | 0 | 300 | 0 | 0 | 348 | 334 |  | 0 | 370 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 31 | 0 | 0 | 47 | 0 | 110 | 0 | 0 | 203 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 100 | 0 | 0 | 350 | 330 | 235 | 36 | 87 | 40 | 0 | 0 | 12 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 84 | 107 | 95 | 17 | 0.3 | 60 | 50 | 0 | 10 | 100 | 151 | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.54 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 4.17 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 5 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 209 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 |  | 5076.01 | 1598.6 | 6674.61 | 4277 | 313 | 1631 | 95 | 200 | 47 | 0 | 84 | 27.61 | 0 | 95.7
12:00 | 34 | 0 | 250 | 0 | 300 | 0 | 0 | 351 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 33 | 0 | 0 | 47 | 0 | 110 | 0 | 0 | 214 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 100 | 0 | 0 | 365 | 350 | 234 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 82 | 107 | 50 | 22 | 0.3 | 58 | 50 | 0 | 10 | 130 | 156 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.35 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 4.36 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 5 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 68 | 0 | 209 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 5242.01 | 1603.3 | 6845.31 | 4326 | 314 | 1798 | 50 | 200 | 47 | 0 | 82 | 28.31 | 0 | 95.7
13:00 | 34 | 0 | 250 | 0 | 300 | 0 | 0 | 359 | 275 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 33 | 0 | 0 | 48 | 0 | 110 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 13 | 100 | 0 | 0 | 340 | 320 | 233 | 83 | 81 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 86 | 52 | 50 | 22 | 1.2 | 58 | 50 | 0 | 10 | 130 | 149 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 0 | 0 | 0 | 228 | 0 | 17 | 0 | 4.23 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 6 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 45 | 0 | 211 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 5097.83 | 1667.1 | 6764.93 | 4283 | 313 | 1740 | 67 | 200 | 48 | 0 | 86 | 27.93 | 0 | 95.69
14:00 | 32 | 0 | 250 | 0 | 300 | 0 | 0 | 336 | 284 |  | 0 | 360 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 15 | 33 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 100 | 0 | 0 | 340 | 290 | 233 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 86 | 53 | 50 | 22 | 2 | 60 | 66 | 0 | 10 | 130 | 155 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 229 | 0 | 17 | 0 | 3.48 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 207 | 0 | 0 | 0 | 41 | 0 | 212 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 |  | 5009.18 | 1661.1 | 6670.28 | 4245 | 314 | 1688 | 67 | 200 | 45 | 0 | 86 | 25.28 | 0 | 95.69
15:00 | 34 | 0 | 224 | 0 | 320 | 0 | 0 | 340 | 285 |  | 0 | 360 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 25 | 30 | 15 | 33 | 0 | 0 | 43 | 0 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 100 | 0 | 0 | 340 | 290 | 234 | 83 | 85 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 88 | 103 | 32 | 22 | 0.4 | 58 | 66 | 0 | 10 | 130 | 149 | 45 | 1 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.3 | 0 | 0 | 0 | 230 | 0 | 17 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 12 | 0 | 210 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 |  | 4946.1 | 1543.9 | 6490 | 4218 | 313 | 1556 | 54 | 200 | 43 | 0 | 88 | 18 | 0 | 95.69
16:00 | 34 | 0 | 200 | 0 | 334 | 0 | 0 | 347 | 284 |  | 0 | 330 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 15 | 33 | 0 | 0 | 43 | 0 | 110 | 0 | 0 | 215 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 100 | 0 | 0 | 285 | 310 | 173 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 80 | 104 | 16 | 22 | 0.5 | 60 | 66 | 0 | 10 | 130 | 156 | 45 | 1 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 229 | 0 | 17 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 12 | 0 | 180 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 |  | 4851 | 1554.4 | 6405.4 | 4122 | 313 | 1589 | 50 | 200 | 43 | 0 | 80 | 8.4 | 0 | 95.68
17:00 | 34 | 0 | 200 | 0 | 330 | 0 | 0 | 379 | 285 |  | 0 | 330 | 0 | 4 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 25 | 31 | 15 | 33 | 0 | 0 | 43 | 0 | 110 | 0 | 0 | 207 | 0 | 102 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 100 | 0 | 0 | 270 | 295 | 79 | 83 | 91 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 12 | 86 | 104 | 16 | 22 | 0 | 60 | 66 | 11 | 10 | 130 | 152 | 57 | 10 | 0 | 0 | 16 | 0 | 10 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 10 | 0 | 0 | 230 | 8 | 17 | 0 | 0.13 | 15 | 0 | 0 | 0 | 1 |  | 511 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 173 | 6 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 10 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 15 |  | 4946.03 | 1798.2 | 6744.23 | 4087 | 511 | 1668 | 147 | 200 | 43 | 1 | 86 | 1.23 | 0 | 95.68
18:00 | 34 | 0 | 200 | 0 | 319 | 0 | 0 | 339 | 284 |  | 0 | 420 | 0 | 66 | 7 | 18 | 344 | 0 | 0 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 9 | 53 | 55 | 0 | 22 | 25 | 14 | 15 | 31 | 0 | 0 | 44 | 0 | 110 | 0 | 0 | 202 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 18 | 100 | 0 | 0 | 290 | 305 | 154 | 83 | 83 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 108 | 107 | 78 | 22 | 0 | 60 | 66 | 53 | 40 | 130 | 148 | 68 | 79 | 0 | 0 | 16 | 0 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 10 | 230 | 16 | 17 | 12 | 0 | 97 | 0 | 0 | 0 | 9 |  | 653 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 6 | 0 | 169 | 10 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 5 | 0 | 94 | 0 | 185 | 0 | 398 | 0 | 0 | 0 | 15 | 54 | 0 | 0 | 60 |  | 5837 | 2282 | 8119 | 4261 | 653 | 1964 | 883 | 200 | 44 | 6 | 108 | 0 | 0 | 95.68
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 34 | 0 | 200 | 0 | 320 | 0 | 0 | 335 | 284 |  | 0 | 450 | 0 | 100 | 18 | 0 | 343 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 42 | 53 | 55 | 0 | 22 | 25 | 31 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 26 | 125 | 0 | 0 | 290 | 305 | 155 | 83 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 89 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 147 | 69 | 79 | 0 | 0 | 16 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 230 | 40 | 17 | 17 | 0 | 151 | 0 | 0 | 0 | 7 |  | 653 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 19 | 0 | 96 | 0 | 212 | 0 | 368 | 0 | 0 | 0 | 50 | 54 | 0 | 0 | 70 |  | 6127 | 2357 | 8484 | 4322 | 653 | 2037 | 1123 | 200 | 45 | 0 | 104 | 0 | 0 | 95.67
19:30 | 34 | 0 | 201 | 0 | 320 | 0 | 0 | 350 | 274 |  | 0 | 450 | 0 | 100 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 29 | 125 | 0 | 0 | 290 | 305 | 155 | 83 | 82 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 93 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 147 | 69 | 79 | 0 | 0 | 16 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 227 | 20 | 0 | 17 | 0 | 158 | 0 | 0 | 0 | 0 |  | 653 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 46 | 0 | 96 | 0 | 208 | 0 | 377 | 0 | 0 | 0 | 32 | 55 | 0 | 0 | 70 |  | 6013 | 2372 | 8385 | 4369 | 653 | 2065 | 949 | 200 | 45 | 0 | 104 | 0 | 0 | 95.67
20:00 | 34 | 0 | 200 | 0 | 319 | 0 | 0 | 335 | 274 |  | 0 | 450 | 0 | 76 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 48 | 18 | 32 | 125 | 0 | 0 | 290 | 305 | 154 | 83 | 85 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 91 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 147 | 68 | 79 | 0 | 0 | 16 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 20 | 0 | 17 | 0 | 158 | 0 | 0 | 0 | 0 |  | 653 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 62 | 0 | 96 | 0 | 210 | 0 | 381 | 0 | 0 | 0 | 32 | 55 | 0 | 0 | 0 |  | 5923 | 2341 | 8264 | 4374 | 653 | 2057 | 831 | 200 | 45 | 0 | 104 | 0 | 0 | 95.67
21:00 | 34 | 0 | 201 | 0 | 320 | 0 | 0 | 337 | 265 |  | 0 | 450 | 0 | 26 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 34 | 125 | 0 | 0 | 290 | 305 | 155 | 83 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 98 | 93 | 65 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 148 | 69 | 79 | 0 | 0 | 16 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 |  | 653 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 155 | 0 | 72 | 0 | 205 | 0 | 347 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 0 |  | 5687 | 2284 | 7971 | 4465 | 653 | 1982 | 528 | 200 | 45 | 0 | 98 | 0 | 0 | 95.67
22:00 | 34 | 0 | 200 | 0 | 319 | 0 | 0 | 335 | 265 |  | 0 | 450 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 125 | 0 | 0 | 290 | 305 | 157 | 83 | 82 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 92 | 92 | 40 | 22 | 0 | 58 | 63 | 50 | 50 | 163 | 147 | 70 | 79 | 0 | 0 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 556 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 211 | 0 | 73 | 0 | 208 | 0 | 345 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 |  | 5299 | 2147 | 7446 | 4474 | 556 | 1971 | 108 | 200 | 45 | 0 | 92 | 0 | 0 | 95.66
23:00 | 34 | 0 | 200 | 0 | 328 | 0 | 0 | 337 | 267 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 33 | 31 | 0 | 0 | 46 | 0 | 110 | 0 | 0 | 205 | 0 | 109 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 125 | 0 | 0 | 305 | 320 | 26 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 86 | 91 | 40 | 22 | 0 | 30 | 66 | 50 | 50 | 163 | 150 | 68 | 79 | 0 | 0 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 180 | 0 | 165 | 0 | 72 | 0 | 198 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5130 | 1826 | 6956 | 4274 | 314 | 1979 | 57 | 200 | 46 | 0 | 86 | 0 | 0 | 95.66
24:00 | 34 | 0 | 150 | 0 | 326 | 0 | 0 | 340 | 278 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 31 | 0 | 0 | 46 | 0 | 100 | 0 | 0 | 202 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 125 | 0 | 0 | 290 | 305 | 49 | 83 | 50 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 78 | 93 | 0 | 22 | 0 | 30 | 66 | 2 | 50 | 163 | 150 | 57 | 79 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 165 | 0 | 0 | 180 | 0 | 165 | 0 | 11 | 0 | 193 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4758 | 1556 | 6314 | 4028 | 216 | 1764 | 17 | 165 | 46 | 0 | 78 | 0 | 0 | 95.66
KWH | 834000 | 0 | 4279000 | 0 | 6976882 | 0 | 0 | 8313170 | 7333000 |  | 0 | 9241250 | 0 | 304320 | 32400 | 43221 | 7469149 | 0 | 0 | 0 | 10560 | 356256 | 0 | 0 | 0 | 0 | 79920 | 323280 | 192093 | 0 | 135288 | 600000 | 690300 | 756900 | 811700 | 0 | 0 | 1062196 | 0 | 2600000 | 0 | 0 | 4774368 | 0 | 2641510 | 0 |  | 0 | 0 | 0 | 0 | 0 | 134400 | 261648 | 394560 | 2659334 | 0 | 0 | 7706500 | 7232000 | 4068000 | 1170909 | 1688660 | 609336 | 0 | 0 | 601460 | 0 | 0 | 0 | 292608 | 72000 | 201600 | 293790 | 1986240 | 2314600 | 995200 | 322992 | 4950 | 1372000 | 1374960 | 322200 | 435672 | 3426979 | 3546000 | 1435968 | 559680 | 0 | 0 | 132000 | 0 | 66960 | 7470000 | 135552 | 68904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127170 | 155520 | 0 | 23418 | 5509000 | 94800 | 104712 | 51017 | 23400 | 544473 | 0 | 0 | 0 | 19320 |  | 8019636 | 0 | 0 | 0 | 371520 | 0 | 0 | 0 | 0 | 5760 | 0 | 3828510 | 296100 | 17280 | 0 | 0 | 1535000 | 0 | 0 | 0 | 108410 | 0 | 0 | 0 | 0 | 141840 | 63252 | 236124 | 0 | 0 | 4849600 | 0 | 0 | 4846673 | 0 | 1502818 | 0 | 928724 | 0 | 4778536 | 0 | 9258547 | 0 | 0 | 0 | 117792 | 259200 | 0 | 28953 | 180096 |  | 119871255 | 41374371 | 161245626 | 98907380 | 8019636 | 41711133 | 4519208 | 4849600 | 1062196 | 5760 | 1986240 | 184473 | 0
Fuel Cost | 934080 | 0 | 4578530 | 0 | 5162892.68 | 0 | 0 | 5985482.4 | 5573080 |  | 0 | 7393000 | 0 | 3104064 | 350892 | 443447.46 | 9261744.76 | 0 | 0 | 0 | 117216 | 3619560.96 | 0 | 0 | 0 | 0 | 748051.2 | 3100255.2 | 1832567.22 | 0 | 101466 | 450000 | 0 | 0 | 0 | 0 | 0 | 276170.96 | 0 | 3978000 | 0 | 0 | 5013086.4 | 0 | 3354717.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1257984 | 240716.16 | 1096876.8 | 2792300.7 | 0 | 0 | 5702810 | 6074880 | 3742560 | 1147490.82 | 2245917.8 | 499655.52 | 0 | 0 | 860087.8 | 0 | 0 | 0 | 298460.16 | 54000 | 381024 | 220342.5 | 13705056 | 1897972 | 9464352 | 329451.84 | 81180 | 1865920 | 1869945.6 | 438192 | 544590 | 4249453.96 | 3262320 | 2139592.32 | 985036.8 | 0 | 0 | 209880 | 0 | 157356 | 5303700 | 101664 | 52367.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1467541.8 | 1449446.4 | 0 | 219426.66 | 5178460 | 831396 | 932983.92 | 482110.65 | 0 | 5020041.06 | 0 | 0 | 0 | 0 |  | 21653017.2 | 0 | 0 | 0 | 3581452.8 | 0 | 0 | 0 | 0 | 75456 | 0 | 3062808 | 458955 | 185587.2 | 0 | 0 | 2885800 | 0 | 0 | 0 | 1124211.7 | 0 | 0 | 0 | 0 | 156024 | 104365.8 | 178745.868 | 0 | 0 | 19834864 | 0 | 0 | 4265072.24 | 0 | 1397620.74 | 0 | 1476671.16 | 0 | 4205111.68 | 0 | 6758739.31 | 0 | 0 | 0 | 1049526.72 | 2420928 | 0 | 0 | 0 |  | 154232847.25 | 74874957.418 | 229107804.668 | 93975398.108 | 21653017.2 | 36703619.45 | 41335501.15 | 19834864 | 276170.96 | 75456 | 13705056 | 1548721.8 | 0
Yesterday Day Peak | 34 | 0 | 250 | 0 | 300 | 0 | 0 | 351 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 15 | 33 | 0 | 0 | 47 | 0 | 110 | 0 | 0 | 214 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 100 | 0 | 0 | 365 | 350 | 234 | 83 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 82 | 107 | 50 | 22 | 0.3 | 58 | 50 | 0 | 10 | 130 | 156 | 67 | 1 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.35 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 4.36 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 5 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 205 | 0 | 0 | 0 | 68 | 0 | 209 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 |  | 6845.31 | DayPeak
Yesterday Evening Peak | 34 | 0 | 200 | 0 | 320 | 0 | 0 | 335 | 284 | 0 | 0 | 450 | 0 | 100 | 18 | 0 | 343 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 42 | 53 | 55 | 0 | 22 | 25 | 31 | 15 | 31 | 0 | 0 | 45 | 0 | 110 | 0 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 26 | 125 | 0 | 0 | 290 | 305 | 155 | 83 | 80 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 89 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 147 | 69 | 79 | 0 | 0 | 16 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 230 | 40 | 17 | 17 | 0 | 151 | 0 | 0 | 0 | 7 |  | 653 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 200 | 0 | 0 | 214 | 0 | 19 | 0 | 96 | 0 | 212 | 0 | 368 | 0 | 0 | 0 | 50 | 54 | 0 | 0 | 70 |  | 8484 | EvPeak
Forecast for Evening | 35 | 0 | 180 | 0 | 360 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 46 | 0 | 120 | 0 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 100 | 0 | 0 | 360 | 360 | 225 | 55 | 90 | 40 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 107 | 150 | 95 | 22 | 0 | 60 | 66 | 51 | 44 | 163 | 160 | 66 | 73 | 0 | 0 | 16 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 463 | 40 | 0 | 0 | 115 | 200 | 0 | 0 | 37 | 70 | 40 | 190 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 0 | 0 | 200 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 35 | 0 | 180 | 0 | 360 | 0 | 0 | 360 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 45 | 0 | 120 | 0 | 25 | 210 | 0 | 130 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 50 | 21 | 10 | 100 | 0 | 0 | 360 | 360 | 225 | 55 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 92 | 150 | 95 | 22 | 1.6 | 60 | 66 | 51 | 44 | 163 | 150 | 66 | 73 | 0 | 0 | 16 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 0 | 100 | 230 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 178 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 30 | 40 | 175 | 20 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 220 | 0 | 400 | 50 | 100 | 0 | 36 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 34 | 0 | 100 | 0 | 250 | 0 | 0 | 353 | 280 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 25 | 31 | 0 | 0 | 45 | 0 | 100 | 0 | 0 | 196 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 80 | 0 | 0 | 385 | 250 | 184 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 106 | 0 | 0 | 0.3 | 20 | 66 | 2 | 2 | 100 | 161 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 1.03 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 136 | 0 | 13 | 0 | 130 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0
199
| Minimum Generation |  | 5190 | 5:00
| Highest Generation |  | 8484 | 19:00
| Day Peak Generation |  | 6845.31 | 12:00
| Evening Peak Generation |  | 8484 | 19:00
| HVDC Max Flow |  | 653 | 18:00
| HVDC EvPeak Flow |  | 653 | 19:00
| Load factor L.F |  | 79.19%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-01-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-01-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6845.31 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5055 | MW
Evening Peak Generation : |  | 8484 | MW Hour : | 19:00 | Available Max Generation : |  | 14264 | MW
E.P. Demand (at gen end) : |  | 8484 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7600 | MW
Maximum Generation : |  | 8484 | MW Hour : | 19:00 | Reserve(Generation end) |  | 6664 | MW
Total Gen. (MKWH) : |  | 161.2456 | System Load Factor : | 79.19% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -517 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-01-10
Actual : | 95.64 | Ft.(MSL) , | Rule curve : | 101.29 | Ft.( MSL )
Gas Consumed : | Total = | 1097.45 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 130679017.558
: |  | Coal : | 19834864 | Oil : | 41410957.15 | Total : | 191924838.708
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2702.5695 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 909.9942 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 813.7158 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 734.6896 |  |  | 0 | 0%
) | 0 | 0:00 | 664.2434 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 535.9981 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 311.3227 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 138.3126 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 413.3328 |  |  | 0 | 0%
Total | 0 |  | 7224.1787 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2.
2) Summit Meghna 305 MW
3) Ghorasal Unit-1,3,5
4) Baghabari 100 MW
5) Sylhet 150 MW
6) Shajibazar 330 MW GT-1
7) Ashuganj Precision
8) Ashuganj unit-4,5
9) Bheramara 410 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Kaliakoir 400/132 kV T2 transformer was under shut down from 09:07 to 11:06 for C/M.
b)Kallyanpur 132/33 kV T2 transformer was under shut down from 08:42 to 21:16 for A/M.
c) Cantonment 132/33 kV T2 transformer was under shut down from 08:02 to 18:50 for A/M.
d) After maintenance Hasnabad-Shyampur 230 kV Ckt was switched on at 10:52.
e) Bhulta-Rampura 230 kV Ckt-1 was under shut down from 09:44 to 17:55 for A/M.
f) Rajshahi 132/33 kV T3 transformer was under shut down from 08:25 to 16:20 for A/M.
g) Fenchuganj-Sreemongal 132 kV Ckt-2 was under shut down from 09:50 to 16:29 for A/M.
h) Khulna©-KPCL-2 P/P 132 kV Ckt was under shut down from 09:26 to 15:30 for A/M.
i) Faridpur-Gopalganj 132 kV Ckt-2 was switched on at 13:44.
j) Bagherhat 132/33 kV T1 transformer was under shut down from 09:09 to 16:18 for A/M.
k) Mymenshing RPCL 210 MW GT-2 tripped at 12:40 due to voltage fluctuation.
l) Bagerhat 132 kV Bus was under shut down from 14:29 to 16:10 for C/M. |  |  |  |  | About 68 MW power interruption occurred under Bagerhat, Mongla S/S
m) Bheramara-Kustia 132 kV Ckt-2 was under shut down from 08:08 to 14:49 for A/M. |  |  |  |  | area from14:29 to 16:10.
n) Jamalpur 33 kV Bus section-4 was under shut down from 16:06 to 16:40 due to PDB work. |  |  |  |  | About 06 MW power interruption occurred under Jamalpur S/S
area from 16:06 to 16:40.
o) Sirajganj 225 MW unit-2 GT was synchronized at 17:45.
p) Sirajganj 225 MW unit-2 STG was synchronized at 19:35.
q) Shajadpur 132/33 kV new transformer was switched on at 18:13.
r) Ashuganj 225 MW CCPP ST was synchronized at 01:29(10/01/2020).
s) Mymenshing 132/33 kV T1 transformer & T-1 Bus were shut down at 07:10 (10/01/2020) for A/M.
t) Nator-Rajshahi 132 kV Ckt-1 was shut down at 06:26(10/01/2020) for D/W.
u) Bheramara-Faridpur 132 kV Ckt-1 was shut down at 07:22(10/01/2020) for A/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-01-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 34 | 834000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4279000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 6976882 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8313170 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 284 | 7333000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9241250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 304320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 18 | 32400 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 43221 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 135288
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 10560 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 343 | 7469149
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 356256
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 42 | 79920 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 323280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 192093
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1290300 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 756900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 811700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 104712 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2477 | 48887401
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under shut down.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127170
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 134400
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 45 | 1062196 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4774368 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2641510
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 51017 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 155520 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 261648
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 394560
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23400
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 151 | 544473 | Transformer over load
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 829 | 12770262
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 125 | 2659334 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 155 | 4068000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7706500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7232000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 609336 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 83 | 1170909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 601460 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 23418 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1688660 | Machine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 292608
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 72000
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 1986240
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 201600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 293790 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 7 | 19320 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1312 | 28625175
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 89 | 2314600 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 322992
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 995200
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4950
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 40 | 94800 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 246 | 3732542
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1372000 | Gas shortage.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1374960 | Gas shortage.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3426979
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 147 | 3546000 | GT-1 under shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 322200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 435672
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 68904
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 69 | 1435968 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 559680 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 132000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 135552
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7470000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 230 | 5509000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 66960
| Sylhet Area Total |  |  |  | 1949 | 1263 | 25855875
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 653 | 8019636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 100 | 371520 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 5760 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 117792 | Low demand
| Khulna Area Total |  |  |  | 2314 | 803 | 8514708
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 17280 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 296100 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 161 | 3828510 | Grid problem
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 928724
| Barisal Area Total |  |  |  | 462 | 277 | 5070614
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1535000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 32 | 108410 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4846673 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 19 | 1502818 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 212 | 4778536 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 368 | 9258547 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 141840
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 63252 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236124
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 180096 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1023 | 22651296
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4849600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 54 | 259200 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28953
| Rangpur Area Total |  |  |  | 605 | 254 | 5137753
| Total |  |  |  | 19107 | 8484 | 161245626
| Eastern Grid Total |  |  |  | 13543 | 6127 | 119871255
| Western Grid Total |  |  |  | 5564 | 2357 | 41374371
| National Grid Total |  |  |  | 19107 | 8484 | 161245626
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-01-09
(a) ENTIRE EASTERN GRID : |  | 5397 | MW | (b) ENTIRE WESTERN GRID : |  | 2654 | MW
i) Dhaka area |  | 2926 | MW | i) Khulna area |  | 1000 | MW
ii) Chittagong area |  | 839 | MW | ii) Rajshahi area |  | 843 | MW
iii) Comilla area |  | 657 | MW | iii) Barisal area |  | 236 | MW
iv) Mymensingh area |  | 652 | MW | iv) Rangpur area |  | 575 | MW
v) Sylhet area |  | 323 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8051 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 12:00 | Shahjibazar | 76 | 18:00 | Bottail | 90 | 18:30
Munsiganj | 86 | 19:30 | Fenchuganj | 24 | 18:00 | G.K Project | 36 | 18:30
Sonargaon | 62 | 18:00 | Kulawara | 30 | 18:30 | Faridpur | 130 | 18:30
Shyampur | 170 | 9:00 | Sylhet | 94 | 18:30 | Madaripur | 57 | 20:00
Bhulta | 165 | 12:00 | Chatak | 17 | 18:00 | Sariatpur | 40 | 20:00
Madanganj | 48 | 18:30 | Sunamganj | 27 | 19:00 | Gopalganj | 66 | 18:30
Shitalakhya | 98 | 11:00 | Biani Bazar | 35 |  | Bagerhat | 66 | 18:00
Rahim steel | 24 | 18:00 | Comilla (S) | 108 | 18:00 | Mongla | 30 | 12:00
Matuail | 80 | 10:00 | Comilla(N) | 79 | 18:30 | Satkhira | 65 | 19:00
Ghorasal | 65 | 19:00 | Chandpur | 62 | 19:30 | Gallamari | 37 | 13:00
Narsingdi | 102 | 19:00 | Feni | 88 | 18:00 | Magura | 36 | 18:30
Haripur (SBU) | 84 | 19:30 | Chowmuhani | 110 | 19:00 | Norail | 26 | 18:30
Ullon | 48 | 18:00 | Ashuganj | 39 | 19:30 | Chuadanga | 60 | 18:30
Hasnabad | 120 | 18:00 | Daudkandi | 75 | 18:00 | Barisal(N) | 31 | 19:30
Magbazar | 70 | 18:00 | B.Baria | 84 | 18:00 | Barisal (S) | 66 | 18:00
Maniknagar | 74 | 12:00 | Ramganj | 60 | 18:00 | Patuakhali | 84 | 18:30
Bangabhaban | 15 | 12:00 | Chaddagram | 14 | 19:00 | Bhandaria | 38 | 18:30
Narinda | 70 | 12:00 | PHP | 2 | 13:00 | Borhan Uddin | 24 | 20:00
Dhanmondi | 85 | 12:00 | Madunaghat | 41 | 18:00 | Ishurdi | 48 | 18:30
Lalbag | 80 | 13:00 | Hathazari | 70 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 42 | 20:00 | Khulshi | 139 | 13:00 | Natore | 85 | 18:30
Mirpur | 66 | 18:00 | Halishahar | 88 | 19:00 | Bogra | 111 | 19:00
Kalyanpur | 68 | 18:00 | Baraulia | 130 | 0:00 | Noagaon | 81 | 19:00
Gulshan | 90 | 18:00 | Sikalbaha | 21 | 18:30 | Rajshahi | 88 | 19:00
Uttara | 53 | 18:00 | Dohazari | 64 | 18:00 | Rajshahi New | 8 | 18:00
Uttara New | 32 | 18:00 | Cox'sbazar | 68 | 18:30 | C.Nawabganj | 51 | 19:00
Kamrangirchar | 65 | 18:00 | Chandraghona | 22 | 18:00 | Amnura | 23 | 18:30
Savar | 102 | 12:00 | Kaptai | 3.5 | 18:00 | Pabna | 71 | 19:00
Bhasantec | 89 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 75 | 19:00
Agargaon | 37 | 18:00 | Bakulia | 72 | 18:00 | Serajganj | 55 | 18:30
Satmosjid | 62 | 13:00 | Julda | 16 | 10:00 | Niyamatpur | 50 | 18:00
Tongi | 65 | 18:00 | TK chemical | 10.6 | 18:00 | Joypurhat | 45 | 18:30
Kabirpur | 160 | 11:00 | Modern Steel | 15 | 23:00 | Sherpur(Bogura) | 33 | 18:30
Basundhara | 76 | 18:00 | Shahmirpur | 22 | 18:00 | Mohastangor | 30 | 18:30
Manikganj | 63 | 18:30 | Khagrachhari | 100 | 15:00 | Rangpur | 108 | 18:30
Joydevpur | 142 | 18:00 | Matarbari | 22 | 18:00 | Lalmonirhat | 41 | 18:30
New Tongi | 75 | 12:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 86 | 18:30
Korda | 177 | 12:00 | Rangamati | 8 | 13:00 | Purbasadipur | 84 | 19:00
Dhamrai | 42 | 18:00 | Abul Khair 230 | 125 | 1:00 | Thakurgaon | 56 | 18:30
Valuka | 86 | 19:00 | BSRM | 137 | 5:00 | Palashbari | 88 | 18:30
Tangail | 124 | 19:00 | GPH Ispat | 14 | 16:00 | Barapukuria | 36 | 18:30
Mymensing | 135 | 18:30 | Goalpara | 19 | 18:30 | Panchagar | 35 | 19:00
Kishorganj | 80 | 19:00 | Central s/s | 66 | 19:00 | Joldhaka | 20 | 19:00
Netrokona | 77 | 19:00 | Noapara | 47 | 18:30 | Kurigram | 38 | 19:00
Jamalpur | 86 | 18:00 | Jessore | 80 | 18:30
Sherpur | 74 | 18:00 | Benapol | 30 | 18:30
Srimongal | 23 | 18:30 | Jhenida | 76 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-01-09 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.083333 | 397 | 0.41667 | Kaliakoir | 389 | 0.16667 | 379 | 0.41667
Bheramara | 408 | 0.125 | 396 | 0.41667 | Bhulta | 395 | 0.041667 | 386 | 0.41667
Ashuganj(N) | 400 | 0.16667 | 391 | 0.41667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 230 | 0.33333 | Hathazari | 224 | 0.91667 | 218 | 0.5
Ishurdi | 241 | 0.20833 | 225 | 0.33333 | Megnaghat | 238 | 0.16667 | 230 | 0.5
Ashuganj | 240 | 0.041667 | 236 | 0.41667 | Fenchuganj | 244 | 0.91667 | 239 | 0.41667
Serajganj | 236 | 0.25 | 228 | 0.77083 | Siddhirganj | 237 | 0.16667 | 229 | 0.5
Baghabari | 241 | 0.125 | 235 | 0.375 | Maniknagar | 234 | 0.083333 | 227 | 0.5
Barapukuria | 235 | 0.16667 | 225 | 0.77083 | Old Airport | 235 | 0.16667 | 223 | 0.5
Bogra | 233 | 0.16667 | 223 | 0.75 | Barisal | 242 | 0.125 | 235 | 0.70833
Khulna South | 246 | 0.20833 | 222 | 0.33333 | AKSML | 222 | 0.79167 | 216 | 0.5
Rampura | 232 | 0.125 | 228 | 0.41667 | BSRM | 226 | 0.16667 | 220 | 0.45833
Haripur | 233 | 24:00 | 229 | 0.5 | Bibiyana | 242 | 0.91667 | 236 | 0.66667
Hasnabad | 234 | 0.125 | 226 | 0.5 | Bhulta | 236 | 0.20833 | 229 | 0.45833
Aminbazar | 234 | 0.041667 | 224 | 0.5 | Ashuganj (S) | 239 | 0.16667 | 233 | 0.41667
Tongi | 231 | 0.20833 | 225 | 0.45833 | Kaliakoir | 236 | 0.20833 | 224 | 0.58333
Comilla (N) | 238 | 0.875 | 234 | 0.45833 | GPH | 223 | 0.8125 | 215 | 0.45833
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.041667 | 130 | 0.41667 | Halishahar | 134 | 0.8125 | 129 | 0.41667
Munsiganj | 137 | 0.77083 | 128 | 0.5 | Baraulia | 133 | 0.8125 | 127 | 0.45833
Sonargaon | 133 | 0.125 | 129 | 0.66667 | Sikalbaha | 133 | 0.79167 | 128 | 0.5
Shyampur | 135 | 0.75 | 131 | 0.5 | Dohazari | 130 | 0.041667 | 127 | 0.5
Bhulta | 130 | 0.75 | 123 | 0.5 | Cox'sbazar | 127 | 0.083333 | 123 | 0.45833
Madanganj | 134 | 0.125 | 127 | 0.41667 | Chandraghona | 134 | 0.8125 | 129 | 0.5
Shitalakhya | 138 | 0.75 | 128 | 0.5 | Kaptai | 133 | 0.77083 | 128 | 0.5
Rahim steal | 135 | 18:00 | 130 | 0.5 | A. Khaer Stl. | 131 | 0.79167 | 128 | 0.29167
Matuail | 134 | 0.125 | 128 | 0.5 | Bakulia | 131 | 0.77083 | 126 | 0.66667
Ghorasal | 140 | 0.041667 | 138 | 0.5 | Julda | 132 | 0.8125 | 127 | 0.41667
Narsinghdi | 134 | 0.125 | 131 | 0.29167 | TK Chemical | 133 | 0 | 129 | 0.33333
Haripur (SBU) | 135 | 0.125 | 131 | 0.66667 | Modern Steel | 132 | 0.79167 | 127 | 0.5
Ullon | 130 | 0.25 | 125 | 0.5 | Shahmirpur | 133 | 0.79167 | 127 | 0.5
Hasnabad | 136 | 0.25 | 130 | 0.5 | Khagrachhari | 132 | 0.20833 | 128 | 0.41667
Magbazar | 133 | 0.25 | 125 | 0.5 | Matarbari | 130 | 0.041667 | 124 | 0.5
Maniknagar | 137 | 0.25 | 133 | 0.5 | Baroiar Hat | 133 | 0.041667 | 130 | 0.41667
Bangabhaban | 137 | 0.25 | 133 | 0.5 | Rangamati | 133 | 0.8125 | 128 | 0.5
Narinda | 137 | 0.25 | 133 | 0.5 | Goalpara | 137 | 0.625 | 124 | 8:00
Dhanmondi | 130 | 0.25 | 125 | 0.5 | Central s/s | 138 | 0.16667 | 125 | 8:00
Lalbag | 135 | 0.20833 | 126 | 0.5 | Noapara | 136 | 0.625 | 124 | 0.41667
Madartek | 131 | 0.20833 | 125 | 0.5 | Jessore | 133 | 0.625 | 120 | 0.29167
Mirpur | 135 | 0.125 | 128 | 0.5 | Benapol | 134 | 0.125 | 122 | 0.29167
Kalyanpur | 138 | 0.125 | 129 | 0.5 | Jhenida | 132 | 0.16667 | 119 | 0.33333
Gulshan | 130 | 0.16667 | 124 | 0.5 | Bottail | 135 | 0.083333 | 124 | 0.33333
Uttara | 135 | 0.16667 | 125 | 0.5 | G.K Project | 136 | 0.20833 | 128 | 0.75
Uttara New | 135 | 0.16667 | 125 | 0.5 | Faridpur | 137 | 0.625 | 130 | 0.33333
Kamrangirchar | 136 | 0.16667 | 125 | 0.5 | Madaripur | 138 | 0.45833 | 131 | 0.29167
Savar | 134 | 0.16667 | 124 | 0.5 | Sariatpur | 140 | 0.91667 | 132 | 0.375
Bhasantec | 136 | 0.20833 | 128 | 0.5 | Gopalganj | 142 | 0.20833 | 136 | 0.33333
Agargaon | 137 | 0.16667 | 131 | 0.58333 | Bagerhat | 136 | 0.16667 | 121 | 0.75
Satmosjid | 137 | 0.16667 | 128 | 0.5 | Mongla | 131 | 0.25 | 123 | 0.77083
Tongi | 138 | 0.95833 | 133 | 0.45833 | Satkhira | 137 | 0.125 | 124 | 0.41667
Kabirpur | 134 | 1904-01-02 | 127 | 0.41667 | Gallamari | 138 | 0.16667 | 126 | 0.33333
Basundhara | 131 | 8:00 | 125 | 0.5 | Magura | 135 | 0.083333 | 118 | 0.75
Manikganj | 139 | 4:00 | 130 | 0.375 | Norail | 133 | 0.125 | 118 | 0.75
Joydevpur | 142 | 0.25 | 138 | 0.70833 | Chuadanga | 131 | 0.16667 | 115 | 0.75
New Tongi | 138 | 0.16667 | 131 | 0.5 | Barisal(N) | 139 | 0.125 | 134 | 0.70833
Kodda | 135 | 0.20833 | 124 | 0.5 | Barisal (S) | 138 | 0.625 | 133 | 0.33333
Dhamrai | 135 | 0.16667 | 127 | 0.41667 | Patuakhali | 135 | 0.16667 | 125 | 0.75
Valuka | 128 | 0.20833 | 119 | 0.875 | Bhandaria | 135 | 0.041667 | 127 | 0.75
Tangail | 132 | 0.16667 | 128 | 0.875 | Ishurdi | 137 | 0.20833 | 127 | 0.375
Mymensing | 129 | 0.375 | 121 | 0.33333 | Ruppur Paromanobik | 134 | 0.16667 | 128 | 0.75
Kishorganj | 133 | 0.16667 | 126 | 0.875 | Natore | 134 | 0.125 | 125 | 0.54167
Netrokona | 128 | 0.20833 | 120 | 0.875 | Bogra | 137 | 0.16667 | 130 | 0.77083
Jamalpur | 132 | 0.45833 | 117 | 0.33333 | Noagaon | 134 | 0.125 | 126 | 0.83333
Sherpur | 131 | 0.45833 | 117 | 0.33333 | Rajshahi | 131 | 0.20833 | 122 | 0.54167
Srimongal | 140 | 0.95833 | 135 | 0.66667 | Rajshahi New | 132 | 0.16667 | 120 | 0.5
Shahjibazar | 137 | 0.125 | 134 | 0.66667 | C.Nawabganj | 132 | 0.041667 | 119 | 0.54167
Fenchuganj | 135 | 0.375 | 134 | 0.66667 | Amnura | 130 | 0.29167 | 119 | 0.54167
Khulawara | 138 | 0.95833 | 134 | 12:00 | Pabna | 138 | 0.16667 | 129 | 0.5
Sylhet | 136 | 0.91667 | 131 | 0.54167 | Shahjadpur | 142 | 0.125 | 130 | 0.41667
Chatak | 136 | 0.95833 | 131 | 0.54167 | Serajganj | 138 | 0.125 | 130 | 0.41667
Sunamganj | 136 | 0.95833 | 130 | 0.54167 | Niyamatpur | 132 | 0.083333 | 124 | 0.375
Biani Bazar | 136 | 0.125 | 132 | 0.45833 | Joypurhat | 135 | 0.125 | 126 | 0.77083
Comilla(s) | 133 | 0.083333 | 128 | 0.375 | Sherpur(Bogura) | 137 | 0.083333 | 130 | 0.5
Comilla(n) | 139 | 0.375 | 137 | 0.66667 | Mohastangor | 136 | 0.16667 | 128 | 0.33333
Chandpur | 135 | 1:00 | 133 | 0.75 | Rangpur | 133 | 0.125 | 123 | 0.75
Feni | 133 | 0.29167 | 130 | 0.41667 | Lalmonirhat | 130 | 0.20833 | 118 | 0.77083
Chowmuhani | 132 | 0.70833 | 129 | 0.375 | Saidpur | 132 | 0.16667 | 120 | 0.77083
Ashuganj | 140 | 0.25 | 136 | 0.33333 | Purbasadipur | 129 | 0.16667 | 108 | 0.77083
Daudkandi | 135 | 0.29167 | 132 | 0.41667 | Thakurgaon | 129 | 0.16667 | 110 | 0.77083
B.Baria | 134 | 0.29167 | 132 | 0.875 | Palashbari | 131 | 0.20833 | 122 | 0.75
Ramganj | 130 | 0.875 | 127 | 0.91667 | Barapukuria | 135 | 0.16667 | 125 | 0.77083
Chaddagram | 135 | 0.83333 | 133 | 0.29167 | Panchagar | 127 | 0.20833 | 101 | 0.77083
PHP | 132 | 0.29167 | 128 | 0.41667 | Joldhaka | 131 | 0.16667 | 116 | 0.75
Madanhat | 134 | 0.8125 | 130 | 0.5 | Kurigram | 132 | 0.125 | 119 | 0.77083
Hathazari | 134 | 0.77083 | 131 | 0.45833
Khulshi | 131 | 0.041667 | 126 | 0.45833

## L-Curve
Date | 2020-01-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 386 | 4758 | 1556 | 6314 |  |  |  | QF-LDC-12
0:30 | 340.5 | 4590.5 | 1558.5 | 6149 | Date: | 2020-01-09
1:00 | 295 | 4423 | 1561 | 5984
1:30 | 299 | 4308.5 | 1485 | 5793.5
2:00 | 303 | 4194 | 1409 | 5603
2:30 | 296.5 | 4151.5 | 1379.5 | 5531 | [5 empty] | Gen. at Eve. Peak | 8484 | 8484 MW (19:00 )
3:00 | 290 | 4109 | 1350 | 5459 | [6 empty] | 19:00
3:30 | 290 | 3994 | 1336.5 | 5330.5 | [5 empty] | Gen. at Day Peak | 6845.31 | 6845.31 MW (12:00 )
4:00 | 290 | 3879 | 1323 | 5202 | [6 empty] | 12:00
4:30 | 327 | 3967 | 1229 | 5196 | [5 empty] | Highest Generation | 8484
5:00 | 364 | 4055 | 1135 | 5190 | [6 empty] | 19:00
5:30 | 348 | 4096 | 1161 | 5257
6:00 | 332 | 4137 | 1187 | 5324
6:30 | 379.5 | 4347.875 | 1223.5 | 5571.375
7:00 | 427 | 4558.75 | 1260 | 5818.75
7:30 | 426 | 4688.175 | 1323.1 | 6011.275
8:00 | 425 | 4817.6 | 1386.2 | 6203.8
8:30 | 357 | 4934.325 | 1479.55 | 6413.875
9:00 | 289 | 5051.05 | 1572.9 | 6623.95
9:30 | 274.5 | 5064.9115 | 1566.05 | 6630.9615
10:00 | 260 | 5078.773 | 1559.2 | 6637.973
10:30 | 253 | 5077.3915 | 1578.9 | 6656.2915
11:00 | 246 | 5076.01 | 1598.6 | 6674.61
11:30 | 258 | 5159.01 | 1600.95 | 6759.96
12:00 | 270 | 5242.01 | 1603.3 | 6845.31
12:30 | 264.5 | 5169.92 | 1635.2 | 6805.12
13:00 | 259 | 5097.83 | 1667.1 | 6764.93
13:30 | 227 | 5053.505 | 1664.1 | 6717.605
14:00 | 195 | 5009.18 | 1661.1 | 6670.28
14:30 | 169 | 4977.64 | 1602.5 | 6580.14
15:00 | 143 | 4946.1 | 1543.9 | 6490
15:30 | 131.5 | 4898.55 | 1549.15 | 6447.7
16:00 | 120 | 4851 | 1554.4 | 6405.4
16:30 | 75.5 | 4898.515 | 1676.3 | 6574.815
17:00 | 31 | 4946.03 | 1798.2 | 6744.23
17:30 | 199.5 | 5391.515 | 2040.1 | 7431.615
18:00 | 368 | 5837 | 2282 | 8119
18:30 | 401 | 5982 | 2319.5 | 8301.5
19:00 | 434 | 6127 | 2357 | 8484
19:30 | 431 | 6013 | 2372 | 8385
20:00 | 379 | 5923 | 2341 | 8264 |  |  |  | Executive Engineer
20:30 | 348.5 | 5805 | 2312.5 | 8117.5 |  |  |  | Network Operation Division
21:00 | 318 | 5687 | 2284 | 7971
21:30 | 292 | 5493 | 2215.5 | 7708.5
22:00 | 266 | 5299 | 2147 | 7446 |  |  |  |  | Page 6 of 7
22:30 | 273.5 | 5214.5 | 1986.5 | 7201
23:00 | 281 | 5130 | 1826 | 6956
23:30 | 333.5 | 4944 | 1691 | 6635
24:00 | 386 | 4758 | 1556 | 6314
8484 MW (19:00 )
6845.31 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-01-09 |  | Energy | 161245626
[10 empty] | 2020-01-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4028 | 216 | 1764 | 57 | 165 | 46 | 0 | 0 | 78
0:30 | 3980 | 176.5 | 1672 | 36.5 | 182.5 | 45.5 | 0 | 0 | 76 | Date: | 2020-01-09
1:00 | 3932 | 137 | 1580 | 16 | 200 | 45 | 0 | 0 | 74
1:30 | 3818 | 137 | 1513.5 | 8 | 200 | 45 | 0 | 0 | 72 | [7 empty] | Total Energy | 161.2456 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3704 | 137 | 1447 | 0 | 200 | 45 | 0 | 0 | 70 | [7 empty] | Energy not Served | 0
2:30 | 3649 | 138 | 1432 | 0 | 199 | 45 | 0 | 0 | 68 | [7 empty] | Energy Requirement | 161.2456
3:00 | 3594 | 139 | 1417 | 0 | 198 | 45 | 0 | 0 | 66
3:30 | 3522.5 | 139 | 1359 | 0 | 199 | 45 | 0 | 0 | 66 | [6 empty] | Shortage
4:00 | 3451 | 139 | 1301 | 0 | 200 | 45 | 0 | 0 | 66
4:30 | 3345.5 | 138.5 | 1400 | 0 | 200 | 45 | 0 | 0 | 67
5:00 | 3240 | 138 | 1499 | 0 | 200 | 45 | 0 | 0 | 68
5:30 | 3283.5 | 138.5 | 1522 | 0 | 200 | 45 | 0 | 0 | 68
6:00 | 3327 | 139 | 1545 | 0 | 200 | 45 | 0 | 0 | 68
6:30 | 3512 | 139 | 1608 | 0 | 200 | 45 | 0 | 0 | 67 |  |  |  |  | Coal
7:00 | 3697 | 139 | 1671 | 0 | 200 | 45 | 0 | 0 | 66
7:30 | 3814 | 226 | 1702 | 0 | 150 | 45.5 | 0 | 0 | 69 |  |  |  | Oil |  |  |  | ,
8:00 | 3931 | 313 | 1733 | 0 | 100 | 46 | 0 | 0 | 72
8:30 | 4058 | 313 | 1737.5 | 22 | 150 | 46 | 0 | 0 | 75
9:00 | 4185 | 313 | 1742 | 44 | 200 | 46 | 0 | 0 | 78
9:30 | 4215.5 | 313 | 1689.5 | 69 | 200 | 46 | 0 | 0 | 79
10:00 | 4246 | 313 | 1637 | 94 | 200 | 46 | 0 | 0 | 80
10:30 | 4261.5 | 313 | 1634 | 94.5 | 200 | 46.5 | 0 | 0 | 82
11:00 | 4277 | 313 | 1631 | 95 | 200 | 47 | 0 | 0 | 84
11:30 | 4301.5 | 313.5 | 1714.5 | 72.5 | 200 | 47 | 0 | 0 | 83
12:00 | 4326 | 314 | 1798 | 50 | 200 | 47 | 0 | 0 | 82
12:30 | 4304.5 | 313.5 | 1769 | 58.5 | 200 | 47.5 | 0 | 0 | 84
13:00 | 4283 | 313 | 1740 | 67 | 200 | 48 | 0 | 0 | 86
13:30 | 4283 | 313 | 1740 | 67 | 200 | 48 | 0 | 0 | 86
14:00 | 4283 | 313 | 1740 | 67 | 200 | 48 | 0 | 0 | 86
14:30 | 4250.5 | 313 | 1648 | 60.5 | 200 | 45.5 | 0 | 0 | 87
15:00 | 4218 | 313 | 1556 | 54 | 200 | 43 | 0 | 0 | 88
15:30 | 4170 | 313 | 1572.5 | 52 | 200 | 43 | 0 | 0 | 84
16:00 | 4122 | 313 | 1589 | 50 | 200 | 43 | 0 | 0 | 80
16:30 | 4104.5 | 412 | 1628.5 | 98.5 | 200 | 43 | 0.5 | 0 | 83
17:00 | 4087 | 511 | 1668 | 147 | 200 | 43 | 1 | 0 | 86
17:30 | 4174 | 582 | 1816 | 515 | 200 | 43.5 | 3.5 | 0 | 97
18:00 | 4261 | 653 | 1964 | 883 | 200 | 44 | 6 | 0 | 108
18:30 | 4291.5 | 653 | 2000.5 | 1003 | 200 | 44.5 | 3 | 0 | 106
19:00 | 4322 | 653 | 2037 | 1123 | 200 | 45 | 0 | 0 | 104
19:30 | 4369 | 653 | 2065 | 949 | 200 | 45 | 0 | 0 | 104
20:00 | 4374 | 653 | 2057 | 831 | 200 | 45 | 0 | 0 | 104
20:30 | 4419.5 | 653 | 2019.5 | 679.5 | 200 | 45 | 0 | 0 | 101
21:00 | 4465 | 653 | 1982 | 528 | 200 | 45 | 0 | 0 | 98
21:30 | 4469.5 | 604.5 | 1976.5 | 318 | 200 | 45 | 0 | 0 | 95
22:00 | 4474 | 556 | 1971 | 108 | 200 | 45 | 0 | 0 | 92
22:30 | 4374 | 435 | 1975 | 82.5 | 200 | 45.5 | 0 | 0 | 89
23:00 | 4274 | 314 | 1979 | 57 | 200 | 46 | 0 | 0 | 86
23:30 | 4151 | 265 | 1871.5 | 57 | 182.5 | 46 | 0 | 0 | 82 | Max Temp. in Dhaka |  | 23.0° C
24:00 | 4028 | 216 | 1764 | 57 | 165 | 46 | 0 | 0 | 78
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2020-01-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 46 | 46 | 47 | 47 | 48 | 45 | 43 | 43 | 43 | 44 |  | 45 | 45 | 45 | 45 | 45 | 46 | 46 | 1062196
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.6 | 6.97 | 12.91 | 16.56 | 18.54 | 19.35 | 18.4 | 15.7 | 12.3 | 6 | 0.9 | [8 empty] | 0 | 127170
6 | Sikalbaha 225MW CCPP (Gas) | 196 | 182 | 190 | 182 | 182 | 194 | 216 | 206 | 203 | 215 | 203 | 214 | 204 | 203 | 204 | 215 | 207 | 202 |  | 203 | 203 | 203 | 202 | 203 | 205 | 202 | 4774368
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 139 | 145 | 141 | 140 | 140 | 138 | 104 | 104 | 102 | 141 |  | 139 | 139 | 139 | 139 | 104 | 109 | 106 | 2641510
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 12 |  | 17 | 17 | 17 | 0 |  |  | 0 | 51017
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 250 | 230 | 230 | 250 | 250 | 335 | 335 | 345 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 344 |  | 343 | 344 | 344 | 344 | 340 | 300 | 300 | 7469149
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1170909
20 | Ghorasal TPP (Unit-1&2) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 834000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 101 | 102 | 102 | 100 | 100 | 105 | 100 | 200 | 200 | 201 | 252 | 250 | 250 | 250 | 224 | 200 | 200 | 200 |  | 200 | 201 | 200 | 201 | 200 | 200 | 150 | 4279000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 319 | 318 | 308 | 199 | 220 | 200 | 200 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 334 | 330 | 319 |  | 320 | 320 | 319 | 320 | 319 | 328 | 326 | 6976882
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2659334
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 33 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 609336
33 | Ashuganj 225 MW CCPP | 161 | 144 | 143 | 143 | 143 | 143 | 170 | 199 | 234 | 204 | 235 | 234 | 233 | 233 | 234 | 173 | 79 | 154 |  | 155 | 155 | 154 | 155 | 157 | 26 | 49 | 4068000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 280 | 260 | 240 | 270 | 305 | 290 | 315 | 350 | 330 | 350 | 320 | 290 | 290 | 310 | 295 | 305 |  | 305 | 305 | 305 | 305 | 305 | 320 | 305 | 7232000
| Ashuganj 450 MW CCPP(North) | 340 | 260 | 275 | 260 | 240 | 235 | 360 | 345 | 340 | 375 | 350 | 365 | 340 | 340 | 340 | 285 | 270 | 290 |  | 290 | 290 | 290 | 290 | 290 | 305 | 290 | 7706500
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 87 | 90 | 81 | 90 | 85 | 90 | 91 | 83 |  | 80 | 82 | 85 | 80 | 82 | 90 | 50 | 1688660
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 336 | 337 | 339 | 290 | 300 | 365 | 375 | 352 | 349 | 348 | 351 | 359 | 336 | 340 | 347 | 379 | 339 |  | 335 | 350 | 335 | 337 | 335 | 337 | 340 | 8313170
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 350 | 320 | 300 | 400 | 380 | 400 | 450 | 450 | 400 | 370 | 400 | 400 | 360 | 360 | 330 | 330 | 420 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 9241250
41 | Haripur 360MW CCPP(HPL) | 312 | 318 | 283 | 262 | 363 | 352 | 374 | 372 | 372 | 361 | 334 | 330 | 275 | 284 | 285 | 284 | 285 | 284 |  | 284 | 274 | 274 | 265 | 265 | 267 | 278 | 7333000
42 | RPCL 210MW CCPP | 108 | 109 | 108 | 109 | 108 | 108 | 106 | 108 | 108 | 107 | 107 | 107 | 52 | 53 | 103 | 104 | 104 | 107 |  | 89 | 93 | 91 | 93 | 92 | 91 | 93 | 2314600
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 58 | 58 | 60 | 58 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 58 | 30 | 30 | 1372000
45 | Fenchugonj CCPP Phase-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 63 | 66 | 66 | 1374960
46 | Shajibazar 330 MW CCPP | 148 | 154 | 150 | 163 | 148 | 158 | 160 | 151 | 148 | 157 | 151 | 156 | 149 | 155 | 149 | 156 | 152 | 148 |  | 147 | 147 | 147 | 148 | 147 | 150 | 150 | 3546000
47 | Shahjibazar GTPP Unit- 8 & 9 | 42 | 42 | 42 | 42 | 42 | 54 | 68 | 68 | 68 | 67 | 68 | 67 | 67 | 67 | 45 | 45 | 57 | 68 |  | 69 | 69 | 68 | 69 | 70 | 68 | 57 | 1435968
48 | Shahjibazar 86MW PP (Shahjibazar) | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 79 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 559680
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [16 empty] | 16 | 16 |  | 16 | 16 | 16 | 16 | 17 | 17 | 0 | 132000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [16 empty] | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 66960
54 | Hobiganj 11MW PP Cofidence-E | [16 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 68904
55 | Fenchugonj 51 MW PP (Barakatullah) | [16 empty] | 11 | 53 |  | 53 | 53 | 53 | 53 | 50 | 50 | 2 | 322200
56 | Shahjahanulla 25 MW PP | [16 empty] | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 135552
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 300 | 255 | 270 | 310 | 320 | 325 | 310 | 300 | 290 | 310 | 320 | 300 | 270 | 300 | 320 | 275 |  | 285 | 310 | 295 | 285 | 280 | 280 | 280 | 7470000
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 261648
61 | Narshingdi 22 MW PP (Doreen) | [17 empty] | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 135288
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 20 | 20 | 17 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 322992
63 | Impoprt (Tripura) | 74 | 70 | 66 | 66 | 68 | 68 | 66 | 72 | 78 | 80 | 84 | 82 | 86 | 86 | 88 | 80 | 86 | 108 |  | 104 | 104 | 104 | 98 | 92 | 86 | 78 | 1986240
64 | Malancha, Ctg. EPZ (United) | 2 | 2 | 2 | 2 | 2 | 13 | 14 | 13 | 6 | 4 | 4 | 4 | 13 | 8 | 5 | 5 | 10 | 18 |  | 26 | 29 | 32 | 34 | 34 | 40 | 38 | 394560
65 | Feni 22MW PP (Doreen) | [9 empty] | 0 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 292608
66 | Feni 11 MW PP (Doreen) | [16 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 72000
67 | Jangalia 33MW PP (Summit) | [16 empty] | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 201600
68 | Cumilla 25 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 293790
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 18 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 28 | 30 | 30 | 31 | 14 |  | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 690300
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 33 | 33 | 756900
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 811700
73 | Ghorashal 108MW PP (Regent)
Feni Lanka Power
| Chowmuhani 113 MW | [16 empty] | 1 | 9 |  | 7 | [5 empty] | 0 | 19320
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 7 | [7 empty] | 0 | 10560
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 16 | 0 | [5 empty] | 0 | 44 | 94 | 95 | 50 | 50 | 50 | 32 | 16 | 16 | 78 |  | 95 | 95 | 95 | 65 | 40 | 40 | 0 | 995200
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [11 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | [5 empty] | 0 | 104712
| Kaptai 7 MW Solar PP | [6 empty] | 0.15 | 0.53 | 0.94 | 2.013 | 4.17 | 4.36 | 4.23 | 3.48 | 2.4 | 0.5 | 0.13 | [9 empty] | 23400
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 7 |  | 18 | 0 | 0 |  |  |  |  | 32400
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 4 | 66 |  | 100 | 100 | 76 | 26 |  |  | 0 | 304320
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | [9 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 435672
93 | Ashuganj 51 MW PP (Midland) | 0 | [9 empty] | 12 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 5 | 601460
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 16 | 102 |  | 102 | 102 | 102 | 33 | 0 | 0 |  | 356256
95 | Patenga 50MW PP (Baraka) | [17 empty] | 17 |  | 50 | 50 | 48 | 18 |  |  | 0 | 134400
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 9 |  | 42 | [5 empty] | 0 | 79920
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 18 |  | 0 | 0 | [5 empty] | 43221
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 |  | 35 | 35 |  |  | 0 | 192093
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 163 | 130 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3426979
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.1 | 0.2 | 0.2 | 0.3 | 0.3 | 1.2 | 2 | 0.4 | 0.5 | 0 | [9 empty] | 4950
103 | Kamalaghat 54 MW PP(Banco Energy) | [14 empty] | 5 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 323280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 0
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 70 |  | 70 | 70 | 0 | 0 |  |  |  | 155520
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 10 | [7 empty] | 0 | 23418
118 | Bibiyana-III 400 MW CCPP | 229 | 227 | 228 | 227 | 228 | 226 | 228 | 229 | 229 | 228 | 229 | 229 | 228 | 229 | 230 | 229 | 230 | 230 |  | 230 | 227 | 227 | 227 | 227 | 227 | 229 | 5509000
| Jamalpur 115 MW PP (United) | [16 empty] | 8 | 16 |  | 40 | 20 | 20 |  |  |  | 0 | 94800
| Anwara 300 MW PP (United) | [16 empty] | 15 | 97 |  | 151 | 158 | 158 | 158 |  |  | 0 | 544473
120 | Eastern Zone Total | 4423 | 4194 | 4109 | 3879 | 4055 | 4137 | 4558.75 | 4817.6 | 5051.05 | 5078.773 | 5076.01 | 5242.01 | 5097.83 | 5009.18 | 4946.1 | 4851 | 4946.03 | 5837 |  | 6127 | 6013 | 5923 | 5687 | 5299 | 5130 | 4758 | 119871255
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 11 | 63 |  | 100 | 102 | 115 | 78 | 16 | 0 |  | 371520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 0 | 16 |  | 0 | [6 empty] | 17280
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 13 | 13 | 12 | 12 | 12 | 13 | 12 | 12 | 52 | 68 | 45 | 41 | 12 | 12 | 12 | 94 |  | 96 | 96 | 96 | 72 | 73 | 72 | 11 | 928724
| Bhola 225 MW CCPP | 160 | 160 | 160 | 161 | 159 | 159 | 159 | 160 | 144 | 106 | 106 | 103 | 179 | 179 | 173 | 173 | 173 | 169 |  | 161 | 165 | 169 | 169 | 162 | 174 | 170 | 3828510
140 | Bhola 33 MW PP (Venture) | 15 | 14 | 14 | 13 | 13 | 14 | 13 | 13 | 13 | 12 | 5 | 5 | 6 | 20 | 7 | 6 | 6 | 10 |  | 20 | 21 | 21 | 21 | 19 | 18 | 16 | 296100
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 1 | 6 |  | 0 | [6 empty] | 5760
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 50 | 32 | 32 | 15 | 0 |  |  | 117792
146 | Bheramara HVDC | 137 | 137 | 139 | 139 | 138 | 139 | 139 | 313 | 313 | 313 | 313 | 314 | 313 | 314 | 313 | 313 | 511 | 653 |  | 653 | 653 | 653 | 653 | 556 | 314 | 216 | 8019636
147 | Bheramara 410 MW CCPP
148
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 198 | 200 | 200 | 200 | 200 | 100 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 165 | 4849600
153 | Baghabari 71 MW GTPP | 45 | 45 | 45 | 45 | 45 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 60 | 60 | 60 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1535000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 187 | 150 | 130 | 130 | 130 | 130 | 130 | 141 | 204 | 214 | 214 | 205 | 214 | 207 | 205 | 214 | 214 | 214 |  | 214 | 214 | 214 | 214 | 214 | 180 | 180 | 4846673
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 178 | 151 | 137 | 136 | 0 | [12 empty] | 5 |  | 19 | 46 | 62 | 155 | 211 | 165 | 165 | 1502818
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 180 | 130 | 130 | 130 | 130 | 130 | 156 | 197 | 209 | 209 | 209 | 211 | 212 | 210 | 180 | 177 | 185 |  | 212 | 208 | 210 | 205 | 208 | 198 | 193 | 4778536
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 430 | 352 | 376 | 348 | 300 | 325 | 399 | 408 | 407 | 409 | 412 | 409 | 409 | 403 | 345 | 380 | 381 | 398 |  | 368 | 377 | 381 | 347 | 345 | 397 | 359 | 9258547
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [16 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 141840
163 | Bogura 20 MW PP (Energyprima) | [9 empty] | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 63252
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 10 | 10 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236124
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 0 | 32 |  | 32 | 25 | 25 | 12 | 0 | 0 |  | 108410
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 15 | 60 |  | 70 | 70 | 0 |  |  |  |  | 180096
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 0 | 54 |  | 54 | 55 | 55 | 35 | 35 | 0 | 0 | 259200
177 | Sympa Solar Power 8MW | [7 empty] | 1.2 | 1.9 | 3.2 | 4.6 | 4.3 | 4.1 | 4.1 | 2.9 | 1.4 | 0.2 | [9 empty] | 28953
178
178