## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-01-14 | Tuesday
|  | Date (day): | 2020-01-14 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11363.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14466 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-01-13 | 2020-01-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 34 | 64 | 64 | 64 | 21 |  | Gas shortage
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 340 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 298 | 318 | 360 |  |  | ST Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 371 | 267 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 225 | 225 |  | 225 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 20 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 97 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 360 | 330 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 5 | 74 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 46 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 47 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 34 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1647 | 2433 | 3248 | 3941 | 827 | 800
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 60 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 5.87 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 201 | 202 | 215 | 215 |  |  | FGMO
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 134 | 130 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 26 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.13 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 141 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 532 | 862 | 1495 | 1700 | 340 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 125 | 125
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 120 | 135 | 100 | 100 | 34 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 189 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 345 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 235 | 0 | 250 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 43 | 40 | 40 |  | 5 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 158 | 194 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 45 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 90 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 104 | 84 | 104
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 8 | 14 | 14 | 14 |  | 11 | Engine problem
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 18 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 18 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1325 | 1311 | 1665 | 2459 | 174 | 281
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 163 | 109 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 32 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 191.9 | 258 | 483.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 66 | 66 | 66 | 66
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 291 | 305 | 300 | 330 |  |  | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 44 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 69 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 76 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17 |  |  | Engine problem
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 229 | 229 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1363 | 1425 | 1439 | 1469 | 0 | 322
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 316 | 658 | 318 | 663
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 32 | 60 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 6 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 36 | 100
| Payra 660 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 316 | 786 | 614 | 1469 | 0 | 410
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 176 | 208 | 175 | 210
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 37 | 0 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 226 | 260 | 360 | 465 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 200 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 207 | 200 | 220 | 220 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 219 | 205 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 434 | 400 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1141 | 1267 | 1738 | 2034 | 100 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 75 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 151.4 | 225 | 321 | 347 | 0 | 170
| Total |  |  |  |  | 19630 | 19107 | 6893.3 | 8827 | 11363.6 | 14466 | 1493 | 2104
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6486.4336 | 8306 | 10692.8811 | 13612.1668
A. |  | 2020-01-13 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8827 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5029 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8827 | MW
3 | Day peak Generation : |  |  | 6893.3 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8306 | MW
4 | Evening peak Generation : |  |  | 8827 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 162.3827 | MKWHr | By Solar | 0.13296 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 139.6124 | MKWHr |  | By Oil: | 6.8587 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 4.7658 | MKWHr |  | By Hydro: | 0.90684 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1493 | MW | Dhaka | 2970 | 2970 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2104 | MW | Chittagong | 913 | 913 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3597 | MW | Khulna | 1025 | 1025 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1124.04 | MMCFD |  |  | Rajshahi | 882 | 882 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 132027254.724 | ii) Oil : | Taka | 62479559.03 | Comilla | 708 | 708 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14975535 | Total | Taka | 209482348.754 | Mymensingh | 662 | 662 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4.0795 | MKWHr. | Sylhet | 316 | 316 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -442 | MW (E to W) at | 19:00 | hrs | Barisal | 228 | 228 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -446 | MW at | 18:30 | hrs | Rangpur | 602 | 602 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 23.6° C |  |  | Total | 8306 | 8306 |  | 0
B. |  | 2020-01-14 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 25.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14466 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 5566 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 163.7256 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5219 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.0727 | MKWHr. | ii) HVDC Flow at Peak Time |  | 658 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0333 | MKWHr. | iii) Maximum HVDC Flow : |  | 658 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.4 |  | (b) Today: | 95.32 |  | (c) Rule Curve: |  | 100.53
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-01-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 660 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 34 | 0 | 0 | 0 | 300 | 0 | 0 | 112 | 344 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 201 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 100 | 340 | 325 | 164 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 148 | 16 | 0 | 0 | 40 | 66 | 0 | 0 | 100 | 305 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 15 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 205 | 0 | 157 | 0 | 0 | 0 | 184 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4303 | 1509 | 5812 | 3844 | 136 | 1552 | 16 | 150 | 40 | 0 | 74 | 0 | 0 | 95.41
2:00 | 34 | 0 | 0 | 0 | 260 | 0 | 0 | 145 | 285 |  | 0 | 330 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 180 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 100 | 280 | 290 | 176 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 148 | 16 | 0 | 0 | 40 | 66 | 0 | 0 | 100 | 300 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 14 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 160 | 0 | 0 | 0 | 184 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4113 | 1422 | 5535 | 3702 | 140 | 1413 | 16 | 150 | 40 | 0 | 74 | 0 | 0 | 95.41
3:00 | 34 | 0 | 0 | 0 | 260 | 0 | 0 | 145 | 286 |  | 0 | 300 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 181 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 100 | 260 | 270 | 162 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 148 | 0 | 0 | 0 | 40 | 66 | 0 | 0 | 100 | 295 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 14 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 161 | 0 | 0 | 0 | 184 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3973 | 1374 | 5347 | 3615 | 141 | 1329 | 0 | 150 | 40 | 0 | 72 | 0 | 0 | 95.41
4:00 | 34 | 0 | 0 | 0 | 220 | 0 | 0 | 145 | 264 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 38 | 0 | 110 | 0 | 0 | 181 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 100 | 265 | 270 | 170 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 108 | 0 | 0 | 0 | 40 | 66 | 0 | 0 | 100 | 294 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 143 | 0 | 0 | 0 | 185 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3827 | 1367 | 5194 | 3464 | 177 | 1295 | 0 | 150 | 38 | 0 | 70 | 0 | 0 | 95.4
5:00 | 34 | 0 | 0 | 0 | 220 | 0 | 0 | 145 | 245 |  | 0 | 300 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 25 | 31 | 0 | 0 | 38 | 0 | 110 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 100 | 260 | 250 | 166 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 68 | 107 | 0 | 0 | 0 | 40 | 66 | 0 | 0 | 100 | 293 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 13 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 139 | 0 | 0 | 0 | 184 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3755 | 1274 | 5029 | 3388 | 139 | 1246 | 0 | 150 | 38 | 0 | 68 | 0 | 0 | 95.4
6:00 | 34 | 0 | 0 | 0 | 240 | 0 | 0 | 151 | 275 |  | 0 | 350 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 39 | 0 | 110 | 0 | 0 | 194 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 100 | 295 | 270 | 182 | 8 | 50 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 107 | 0 | 0 | 0 | 40 | 66 | 0 | 0 | 130 | 301 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 139 | 0 | 0 | 0 | 185 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4089 | 1392 | 5481 | 3620 | 139 | 1461 | 0 | 150 | 39 | 0 | 72 | 0 | 0 | 95.4
7:00 | 34 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 276 |  | 0 | 350 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 0 | 0 | 100 | 330 | 235 | 173 | 83 | 50 | 33 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 0 | 8 | 8 | 70 | 162 | 0 | 20 | 0 | 40 | 66 | 0 | 10 | 130 | 294 | 45 | 5 | 0 | 0 | 0 | 0 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0.088 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 146 | 0 | 13 | 0 | 184 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4302.288 | 1473.1 | 5775.388 | 3740 | 139 | 1636 | 0 | 150 | 40 | 0 | 70 | 0.388 | 0 | 95.39
8:00 | 34 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 375 |  | 0 | 380 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 200 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 100 | 385 | 235 | 185 | 130 | 51 | 30 | 0 | 0 | 38 | 0 | 0 | 0 | 22 | 0 | 8 | 8 | 72 | 161 | 0 | 20 | 0.3 | 40 | 66 | 5 | 44 | 163 | 318 | 45 | 5 | 0 | 0 | 0 | 0 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0.588 | 0 | 0 | 0 | 0 | 0 |  | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 194 | 0 | 167 | 0 | 43 | 0 | 205 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 |  | 4804.468 | 1801.5 | 6605.968 | 4018 | 311 | 1995 | 17 | 150 | 40 | 0 | 72 | 2.968 | 0 | 95.39
9:00 | 34 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 371 |  | 0 | 380 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 201 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 120 | 325 | 235 | 181 | 158 | 80 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 82 | 163 | 8 | 20 | 0.9 | 40 | 66 | 44 | 50 | 163 | 291 | 69 | 60 | 0 | 0 | 16 | 0 | 9 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.87 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 1.13 | 16 | 0 | 0 | 0 | 0 |  | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 205 | 0 | 207 | 0 | 37 | 0 | 219 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 |  | 5058.9 | 1834.4 | 6893.3 | 4144 | 316 | 2071 | 81 | 150 | 40 | 0 | 82 | 9.3 | 0 | 95.39
10:00 | 34 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 307 |  | 0 | 360 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 22 | 25 | 32 | 25 | 31 | 0 | 0 | 41 | 0 | 110 | 0 | 0 | 208 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 120 | 315 | 225 | 198 | 158 | 88 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 82 | 148 | 16 | 20 | 1.6 | 40 | 66 | 42 | 50 | 130 | 306 | 68 | 76 | 0 | 0 | 16 | 0 | 9 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.79 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 1.774 | 16 | 0 | 0 | 0 | 0 |  | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 182 | 0 | 12 | 0 | 201 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 | 0 |  | 4940.164 | 1704.1 | 6644.264 | 4034 | 316 | 1876 | 123 | 150 | 41 | 0 | 82 | 22.264 | 0 | 95.38
11:00 | 34 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 312 |  | 0 | 360 | 0 | 0 | 0 | 0 | 300 | 0 | 60 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 23 | 25 | 31 | 0 | 0 | 41 | 0 | 110 | 0 | 0 | 201 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 130 | 280 | 235 | 194 | 158 | 81 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 84 | 148 | 16 | 20 | 1.9 | 40 | 66 | 47 | 50 | 163 | 311 | 67 | 76 | 0 | 0 | 16 | 0 | 9 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.41 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 4.158 | 16 | 0 | 0 | 0 | 0 |  | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 169 | 0 | 12 | 0 | 177 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 0 |  | 4993.468 | 1675.3 | 6668.768 | 4002 | 316 | 1944 | 103 | 150 | 41 | 0 | 84 | 28.768 | 0 | 95.38
12:00 | 34 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 371 |  | 0 | 390 | 0 | 1 | 0 | 0 | 350 | 0 | 60 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 23 | 25 | 31 | 0 | 0 | 41 | 0 | 110 | 0 | 0 | 202 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 130 | 310 | 0 | 182 | 185 | 86 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 88 | 127 | 16 | 20 | 1.9 | 40 | 66 | 43 | 50 | 163 | 307 | 67 | 76 | 0 | 0 | 17 | 0 | 10 | 305 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 3 | 0 | 4.513 | 100 | 0 | 0 | 0 | 0 |  | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 192 | 0 | 1 | 0 | 193 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 118 |  | 5044.413 | 1819.3 | 6863.713 | 3840 | 316 | 2049 | 250 | 268 | 41 | 0 | 88 | 11.713 | 0 | 95.38
13:00 | 34 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 371 |  | 0 | 390 | 0 | 16 | 0 | 0 | 346 | 0 | 60 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 25 | 22 | 25 | 31 | 0 | 0 | 41 | 0 | 110 | 0 | 0 | 202 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 0 | 135 | 310 | 0 | 188 | 185 | 88 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 84 | 125 | 16 | 22 | 1.8 | 40 | 66 | 53 | 50 | 163 | 308 | 68 | 76 | 0 | 0 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 17 | 0 | 4.207 | 100 | 0 | 0 | 0 | 0 |  | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 187 | 0 | 0 | 0 | 204 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 121 |  | 5066.007 | 1836.2 | 6902.207 | 3832 | 318 | 2056 | 289 | 271 | 41 | 0 | 84 | 11.207 | 0 | 95.37
14:00 | 34 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 313 |  | 0 | 390 | 0 | 16 | 0 | 0 | 300 | 0 | 37 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 42 | 0 | 110 | 0 | 0 | 202 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 135 | 280 | 0 | 185 | 185 | 85 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 0 | 8 | 90 | 118 | 16 | 22 | 1.5 | 40 | 66 | 53 | 50 | 130 | 299 | 67 | 73 | 0 | 0 | 17 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 17 | 0 | 3.49 | 100 | 0 | 0 | 0 | 0 |  | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 185 | 0 | 0 | 0 | 204 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 121 |  | 4844.99 | 1791.2 | 6636.19 | 3703 | 318 | 1914 | 289 | 271 | 42 | 0 | 90 | 9.19 | 0 | 0
15:00 | 34 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 312 |  | 0 | 390 | 0 | 16 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 42 | 0 | 110 | 5 | 0 | 202 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 135 | 280 | 0 | 181 | 185 | 87 | 40 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 8 | 90 | 118 | 16 | 20 | 1 | 40 | 66 | 53 | 50 | 130 | 301 | 67 | 76 | 0 | 0 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | 0 | 0 | 0 | 230 | 0 | 17 | 0 | 2.43 | 108 | 0 | 0 | 0 | 0 |  | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 186 | 0 | 0 | 0 | 200 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 122 |  | 4830.63 | 1772 | 6602.63 | 3729 | 319 | 1904 | 228 | 272 | 42 | 0 | 90 | 18.63 | 0 | 0
16:00 | 35 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 313 |  | 0 | 390 | 0 | 7 | 0 | 0 | 300 | 0 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 22 | 18 | 31 | 0 | 0 | 42 | 0 | 110 | 0 | 0 | 217 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 135 | 325 | 0 | 203 | 185 | 90 | 40 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 88 | 117 | 16 | 22 | 0.4 | 40 | 66 | 11 | 10 | 130 | 314 | 66 | 30 | 0 | 0 | 17 | 0 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0 | 0 | 0 | 228 | 0 | 17 | 0 | 1.16 | 52 | 0 | 0 | 0 | 0 |  | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 170 | 0 | 0 | 0 | 203 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 25 |  | 4728.76 | 1718.6 | 6447.36 | 3812 | 318 | 1857 | 145 | 175 | 42 | 0 | 88 | 10.36 | 0 | 0
17:00 | 34 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 314 |  | 0 | 390 | 0 | 7 | 0 | 0 | 300 | 0 | 38 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 22 | 18 | 31 | 0 | 0 | 40 | 0 | 110 | 35 | 0 | 203 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 5 | 0 | 0 | 135 | 280 | 0 | 187 | 185 | 83 | 43 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 90 | 116 | 16 | 22 | 0.1 | 40 | 66 | 11 | 10 | 130 | 303 | 67 | 30 | 0 | 0 | 17 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 3 | 228 | 9 | 17 | 0 | 0.14 | 52 | 0 | 0 | 0 | 3 |  | 319 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 199 | 0 | 0 | 0 | 210 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 |  | 4704.24 | 1799.2 | 6503.44 | 3814 | 319 | 1889 | 200 | 150 | 40 | 0 | 90 | 1.44 | 0 | 0
18:00 | 34 | 0 | 0 | 0 | 305 | 0 | 0 | 70 | 313 |  | 0 | 390 | 0 | 37 | 16 | 22 | 300 | 0 | 37 | 0 | 30 | 50 | 0 | 0 | 0 | 0 | 21 | 53 | 55 | 0 | 22 | 25 | 6 | 18 | 31 | 0 | 0 | 40 | 0 | 110 | 45 | 0 | 215 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 14 | 23 | 19 | 16 | 0 | 0 | 135 | 310 | 0 | 202 | 192 | 90 | 40 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 106 | 117 | 58 | 22 | 0 | 40 | 66 | 53 | 29 | 130 | 314 | 67 | 76 | 0 | 0 | 17 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 23 | 229 | 32 | 22 | 0 | 0 | 140 | 0 | 0 | 10 | 18 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 5 | 164 | 19 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 196 | 0 | 12 | 0 | 202 | 0 | 431 | 0 | 0 | 0 | 15 | 76 | 0 | 0 | 45 | 0 |  | 5517 | 2379 | 7896 | 3976 | 658 | 2053 | 913 | 150 | 40 | 0 | 106 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 64 | 0 | 0 | 0 | 340 | 0 | 0 | 298 | 267 |  | 0 | 450 | 0 | 100 | 20 | 30 | 330 | 0 | 97 | 0 | 50 | 74 | 0 | 0 | 0 | 0 | 46 | 53 | 55 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 60 | 0 | 202 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 26 | 0 | 0 | 135 | 345 | 0 | 189 | 194 | 90 | 43 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 109 | 95 | 22 | 0 | 40 | 66 | 53 | 44 | 163 | 305 | 67 | 76 | 0 | 0 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 229 | 32 | 34 | 0 | 0 | 141 | 0 | 0 | 18 | 18 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 6 | 40 | 208 | 20 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 205 | 0 | 434 | 0 | 0 | 0 | 50 | 75 | 0 | 0 | 70 | 0 |  | 6289 | 2538 | 8827 | 4445 | 658 | 2129 | 1295 | 150 | 40 | 6 | 104 | 0 | 0 | 0
19:30 | 64 | 0 | 0 | 0 | 340 | 0 | 0 | 305 | 252 |  | 0 | 450 | 0 | 100 | 30 | 30 | 330 | 0 | 90 | 0 | 50 | 74 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 60 | 0 | 201 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 28 | 0 | 0 | 135 | 340 | 0 | 183 | 194 | 80 | 43 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 106 | 111 | 95 | 22 | 0 | 40 | 66 | 53 | 47 | 163 | 296 | 68 | 76 | 0 | 0 | 17 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 229 | 32 | 34 | 0 | 0 | 143 | 0 | 0 | 18 | 18 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 2 | 40 | 204 | 21 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 199 | 0 | 186 | 0 | 15 | 0 | 203 | 0 | 398 | 0 | 0 | 0 | 67 | 75 | 0 | 0 | 70 | 0 |  | 6243 | 2510 | 8753 | 4388 | 658 | 2084 | 1325 | 150 | 40 | 2 | 106 | 0 | 0 | 0
20:00 | 68 | 0 | 0 | 0 | 340 | 0 | 0 | 304 | 245 |  | 0 | 450 | 0 | 100 | 0 | 0 | 330 | 0 | 65 | 0 | 50 | 74 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 100 | 0 | 201 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 30 | 0 | 0 | 135 | 340 | 80 | 182 | 195 | 80 | 23 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 106 | 110 | 95 | 22 | 0 | 40 | 66 | 53 | 50 | 163 | 300 | 68 | 76 | 0 | 0 | 17 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 15 | 229 | 32 | 17 | 0 | 0 | 144 | 0 | 0 | 0 | 18 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 204 | 21 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 199 | 0 | 184 | 0 | 84 | 0 | 198 | 0 | 423 | 0 | 0 | 0 | 67 | 72 | 0 | 0 | 70 | 0 |  | 6154 | 2592 | 8746 | 4462 | 658 | 2167 | 1163 | 150 | 40 | 0 | 106 | 0 | 0 | 0
21:00 | 68 | 0 | 0 | 0 | 340 | 0 | 0 | 304 | 227 |  | 0 | 450 | 0 | 68 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 100 | 0 | 202 | 0 | 133 | 0 |  | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 25 | 0 | 0 | 135 | 350 | 255 | 189 | 197 | 85 | 23 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 106 | 95 | 22 | 0 | 40 | 66 | 50 | 50 | 163 | 309 | 68 | 76 | 0 | 0 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 229 | 32 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 21 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 187 | 0 | 0 | 0 | 192 | 0 | 432 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 35 | 125 |  | 5935 | 2435 | 8370 | 4603 | 658 | 2063 | 629 | 275 | 40 | 0 | 102 | 0 | 0 | 0
22:00 | 64 | 0 | 0 | 0 | 340 | 0 | 0 | 306 | 226 |  | 0 | 450 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 22 | 25 | 25 | 0 | 0 | 42 | 0 | 110 | 100 | 0 | 202 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 0 | 135 | 340 | 235 | 163 | 110 | 80 | 23 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 96 | 106 | 95 | 22 | 0 | 40 | 66 | 50 | 50 | 163 | 301 | 69 | 76 | 0 | 0 | 17 | 0 | 10 | 300 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 8 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 |  | 563 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 197 | 0 | 184 | 0 | 0 | 0 | 199 | 0 | 385 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 125 |  | 5611 | 2224 | 7835 | 4527 | 563 | 1942 | 390 | 275 | 42 | 0 | 96 | 0 | 0 | 0
23:00 | 64 | 0 | 0 | 0 | 360 | 0 | 0 | 306 | 226 |  | 0 | 420 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 22 | 25 | 31 | 0 | 0 | 42 | 0 | 110 | 100 | 0 | 217 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 135 | 380 | 0 | 204 | 80 | 90 | 26 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 88 | 106 | 40 | 22 | 0 | 40 | 66 | 2 | 2 | 130 | 295 | 45 | 76 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 |  | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 18 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 194 | 0 | 194 | 0 | 0 | 0 | 202 | 0 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 |  | 4995 | 1951 | 6946 | 4293 | 362 | 1780 | 109 | 272 | 42 | 0 | 88 | 0 | 0 | 0
24:00 | 64 | 0 | 0 | 0 | 314 | 0 | 0 | 307 | 243 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 22 | 25 | 31 | 0 | 0 | 42 | 0 | 110 | 100 | 0 | 201 | 0 | 136 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 0 | 135 | 310 | 30 | 183 | 78 | 90 | 23 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 78 | 106 | 24 | 22 | 0 | 40 | 66 | 2 | 2 | 130 | 262 | 69 | 76 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 193 | 0 | 189 | 0 | 0 | 0 | 209 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 |  | 4757 | 1745 | 6502 | 4166 | 225 | 1676 | 41 | 274 | 42 | 0 | 78 | 0 | 0 | 0
KWH | 995000 | 0 | 0 | 0 | 7128982 | 0 | 0 | 2916360 | 7100000 |  | 0 | 8681000 | 0 | 418560 | 70800 | 80444 | 7330521 | 0 | 650000 | 0 | 180480 | 439776 | 0 | 0 | 0 | 0 | 156912 | 566280 | 471754 | 0 | 266868 | 600000 | 583020 | 696500 | 790200 | 0 | 0 | 906840 | 0 | 2600000 | 700000 | 0 | 4774657 | 0 | 2957952 | 0 |  | 0 | 0 | 0 | 0 | 70080 | 180960 | 331104 | 349920 | 88947 | 0 | 2905220 | 7878600 | 3657500 | 4437000 | 2877090 | 1728980 | 570384 | 0 | 0 | 823196 | 0 | 0 | 0 | 370728 | 130140 | 454300 | 280680 | 2033280 | 2957160 | 725760 | 354816 | 11150 | 964000 | 1598700 | 576000 | 671472 | 3417194 | 6982000 | 1407744 | 1100160 | 0 | 0 | 263000 | 0 | 158820 | 7558300 | 232728 | 125216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66555 | 189120 | 0 | 128800 | 5232000 | 170400 | 180372 | 0 | 25680 | 1309745 | 0 | 0 | 35340 | 69720 |  | 8072727 | 0 | 0 | 0 | 175680 | 0 | 0 | 0 | 0 | 8448 | 95625 | 4268804 | 352800 | 114240 | 0 | 0 | 1485000 | 0 | 0 | 0 | 313360 | 0 | 0 | 0 | 0 | 332400 | 75312 | 239562 | 0 | 0 | 3661500 | 0 | 0 | 4793964 | 0 | 4430627 | 0 | 205979 | 0 | 4915273 | 0 | 9258545 | 0 | 0 | 0 | 146448 | 300480 | 0 | 29575 | 259104 | 1104300 |  | 117742967 | 44639753 | 162382720 | 96074237 | 8072727 | 43538188 | 6850240 | 4765800 | 906840 | 8448 | 2033280 | 132960 | 0
Fuel Cost | 1114400 | 0 | 0 | 0 | 5275446.68 | 0 | 0 | 2099779.2 | 5396000 |  | 0 | 6944800 | 0 | 4269312 | 766764 | 825355.44 | 9089846.04 | 0 | 812500 | 0 | 2003328 | 4468124.16 | 0 | 0 | 0 | 0 | 1468696.32 | 5430625.2 | 4500533.16 | 0 | 200151 | 450000 | 0 | 0 | 0 | 0 | 0 | 235778.4 | 0 | 3978000 | 1071000 | 0 | 5013389.85 | 0 | 3756599.04 | 0 |  | 0 | 0 | 0 | 0 | 666460.8 | 1693785.6 | 304615.68 | 972777.6 | 93394.35 | 0 | 3050481 | 5830164 | 3072300 | 4082040 | 2819548.2 | 2299543.4 | 467714.88 | 0 | 0 | 1177170.28 | 0 | 0 | 0 | 378142.56 | 97605 | 858627 | 210510 | 14029632 | 2424871.2 | 6901977.6 | 361912.32 | 182860 | 1311040 | 2174232 | 783360 | 839340 | 4237320.56 | 6423440 | 2097538.56 | 1936281.6 | 0 | 0 | 418170 | 0 | 373227 | 5366393 | 174546 | 95164.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768044.7 | 1762598.4 | 0 | 1206856 | 4918080 | 1494408 | 1607114.52 | 0 | 0 | 12075848.9 | 0 | 0 | 0 | 0 |  | 21796362.9 | 0 | 0 | 0 | 1693555.2 | 0 | 0 | 0 | 0 | 110668.8 | 945731.25 | 3415043.2 | 546840 | 1226937.6 | 0 | 0 | 2791800 | 0 | 0 | 0 | 3249543.2 | 0 | 0 | 0 | 0 | 365640 | 124264.8 | 181348.434 | 0 | 0 | 14975535 | 0 | 0 | 4218688.32 | 0 | 4120483.11 | 0 | 327506.61 | 0 | 4325440.24 | 0 | 6758737.85 | 0 | 0 | 0 | 1304851.68 | 2806483.2 | 0 | 0 | 0 | 0 |  | 171209565.36 | 75285461.394 | 246495026.754 | 93058047.224 | 21796362.9 | 38969207.5 | 62368890.23 | 14975535 | 235778.4 | 110668.8 | 14029632 | 950904.7 | 0
Yesterday Day Peak | 34 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 371 |  | 0 | 380 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 32 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 0 | 0 | 201 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 120 | 325 | 235 | 181 | 158 | 80 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 82 | 163 | 8 | 20 | 0.9 | 40 | 66 | 44 | 50 | 163 | 291 | 69 | 60 | 0 | 0 | 16 | 0 | 9 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.87 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 1.13 | 16 | 0 | 0 | 0 | 0 |  | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 205 | 0 | 207 | 0 | 37 | 0 | 219 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 |  | 6893.3 | DayPeak
Yesterday Evening Peak | 64 | 0 | 0 | 0 | 340 | 0 | 0 | 298 | 267 | 0 | 0 | 450 | 0 | 100 | 20 | 30 | 330 | 0 | 97 | 0 | 50 | 74 | 0 | 0 | 0 | 0 | 46 | 53 | 55 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 40 | 0 | 110 | 60 | 0 | 202 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 26 | 0 | 0 | 135 | 345 | 0 | 189 | 194 | 90 | 43 | 0 | 0 | 45 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 109 | 95 | 22 | 0 | 40 | 66 | 53 | 44 | 163 | 305 | 67 | 76 | 0 | 0 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 229 | 32 | 34 | 0 | 0 | 141 | 0 | 0 | 18 | 18 |  | 658 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 6 | 40 | 208 | 20 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 205 | 0 | 434 | 0 | 0 | 0 | 50 | 75 | 0 | 0 | 70 | 0 |  | 8827 | EvPeak
Forecast for Evening | 64 | 0 | 0 | 0 | 360 | 0 | 0 | 360 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 0 | 110 | 100 | 25 | 215 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 125 | 0 | 100 | 360 | 360 | 225 | 55 | 90 | 40 | 0 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 104 | 150 | 95 | 22 | 0 | 40 | 66 | 51 | 44 | 163 | 330 | 66 | 76 | 0 | 0 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 663 | 40 | 0 | 0 | 115 | 200 | 0 | 0 | 36 | 70 | 40 | 210 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 0 | 0 | 200 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 64 | 0 | 0 | 0 | 360 | 0 | 0 | 318 | 360 | 0 | 0 | 225 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 0 | 110 | 100 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 80 | 100 | 50 | 50 | 21 | 10 | 125 | 0 | 100 | 360 | 250 | 225 | 55 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 84 | 150 | 95 | 22 | 1.6 | 40 | 66 | 51 | 44 | 163 | 300 | 66 | 76 | 0 | 0 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 0 | 100 | 230 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 318 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 30 | 40 | 175 | 20 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 220 | 0 | 400 | 50 | 100 | 0 | 36 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 64 | 0 | 0 | 0 | 329 | 0 | 0 | 311 | 361 | 0 | 0 | 420 | 0 | 4 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 18 | 22 | 31 | 0 | 0 | 39 | 0 | 110 | 100 | 0 | 215 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 135 | 330 | 0 | 194 | 182 | 81 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 78 | 130 | 9 | 20 | 0.1 | 40 | 66 | 50 | 22 | 163 | 300 | 63 | 73 | 0 | 0 | 16 | 0 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.32 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0.496 | 50 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 176 | 0 | 216 | 0 | 43 | 0 | 211 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0
199
| Minimum Generation |  | 5029 | 5:00
| Highest Generation |  | 8827 | 19:00
| Day Peak Generation |  | 6893.3 | 9:00
| Evening Peak Generation |  | 8827 | 19:00
| HVDC Max Flow |  | 658 | 18:00
| HVDC EvPeak Flow |  | 658 | 19:00
| Load factor L.F |  | 76.65%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-01-14
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-01-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6893.3 | MW Hour : | 9:00 | Min. Gen. at | 5:00 | 5219 | MW
Evening Peak Generation : |  | 8827 | MW Hour : | 19:00 | Available Max Generation : |  | 14466 | MW
E.P. Demand (at gen end) : |  | 8827 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8900 | MW
Maximum Generation : |  | 8827 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5566 | MW
Total Gen. (MKWH) : |  | 162.3827 | System Load Factor : | 76.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -446 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-01-14
Actual : | 95.32 | Ft.(MSL) , | Rule curve : | 100.53 | Ft.( MSL )
Gas Consumed : | Total = | 1124.04 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 132027254.724
: |  | Coal : | 14975535 | Oil : | 62479559.03 | Total : | 209482348.754
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3130.4329 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1058.5935 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 947.4085 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 855.6886 |  |  | 0 | 0%
) | 0 | 0:00 | 773.4801 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 624.1561 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 356.6245 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 160.9053 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 481.3437 |  |  | 0 | 0%
Total | 0 |  | 8388.6332 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2.
2) Summit Meghna 305 MW
3) Ghorasal Unit-1,3,5
4) Baghabari 100 MW
5) Sylhet 150 MW
6) Bheramara 410 MW
7) Ashuganj Precision
8) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hathazari 230/132 kV MT4 transformer was under shut down from 09:18 to 16:28 for A/M.
b) Savar 132/33 kV T1 transformer was under shut down from 08:31 to 15:18 for A/M.
c) Kulshi-Abul Khair-Baraulia 132 kV Ckt was under shut down from 07:55 to 16:23 for A/M.
d) Rampura-Bhulta 230 kV Ckt-3 was under shut down from 10:08 to 13:25 for A/M.
e) Cumilla(S) 132/33 kV T4 transformer was under shut down from 08:45 to 15:08 for A/M.
f) Madanganj-Munshiganj 132 kV Ckt-1 was under shut down from 10:05 to 16:09 for A/M.
g) Jamalpur 132/33 kV T4 transformer was under shut down from 08:10 to 10:02 for A/M.
h) Fenchuganj 132 kV Bus-1 was under shut down from 09:54 to 17:20 for A/M.
i) Shahjibazar-Srimongal 132 kV Ckt-2 was under shut down from 08:08 to 14:41 for A/M.
j) Kamrangichar 132/33 kV T1 transformer was under shut down from 08:16 to 20:22 for A/M.
k) Kustia-Jhenaidah 132 kV Ckt-1 was under shut down from 09:05 to 16:07 for A/M.
l) Baghabari 230/132 kV T02 transformer was under shut down from 08:53 to 16:49 for A/M.
m) Rajshahi New 132 kV Bus-2 was under shut down from 08:45 to 13:27 for A/M.
n) Joydebpur 132 kV Bus was under shut down from 10:28 to 14:10 for A/M.
o) Ashuganj South GT tripped at 11:12 due to outlet temperature sensor problem and was synchronized at 19:44.
p) Payra STG unit-1 was synchronized at 11:05 for the first time and tripped at 11:26 for condenser vacuum
pressure high. Again synchronized at 11:48 and shut down at 16:12 and synchronized at 20:27.
q) Amnura-Rajshahi New 132 kV Ckt was under shut down from 11:08 to 14:28 for A/M.
r) Barishal(N) 230/132/33 kV T-1 transformer was under shut down from 10:29 to 12:40 for C/M.
s) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 09:10 to 13:50 for A/M.
t) Fenchuganj-Sylhet 132 kV Ckt tripped from both ends at 22:19 showing Gen. Dist. Protection |  |  |  |  | About 25 MW power interruption occurred under Biyanibazar S/S area
3-phase, Z1 at Fenchuganj end & Z3, B-phase at Sylhet end and was switched on at 22:41. |  |  |  |  | from 22:19 to 22:41.
u) Ashuganj South GT tripped at 22:47 due to outlet temperature sensor problem and was synchronized at 23:23.
v) Bhola GT-2 tripped at 05:16(14/01/2020) and was synchronized at 07:28(14/01/2020).
w) HVDC Pole 1&2 tripped at 05:46(14/01/2020) and switched on at 06:18(14/01/2020).
x) Payra unit-1 tripped at 05:45(14/01/2020) and synchronized at 10:02. the machine again
tripped at 10:22 due to boiler burner system problem.
y) Siddhirganj 335 MW EGCB tripped at 05:47(14/01/2020) due to DP high and GT synchronized
at 07:25(14/01/2020).
z) Ishwardi-HVDC 230 kV Ckt-1&2 tripped at 05:47(14/01/2020) from both ends showing main
protection trip and were switched on at 08:09(14/01/2020).
aa) Ishwardi 230/132 kV T01 & T02 transformers tripped at 04:47(14/01/2020) and were
switched on at 07:24(14/01/2020).
ab) Bheramara-Ishwardi 230 kV Ckt-1&2 tripped at 05:47(14/01/2020) showing 21F, 21N at
Bheramara end & Dist. 21F at Ishwardi end.
ac) Ishwardi 132/33 kV T1 transformer tripped at 05:47(14/01/2020) showing 51M, CB61 and was
switched on at 07:30(14/01/2020).
ad) Labanchara 100 MW PS-Bagerhat 132 kV Ckt was shut down at 07:39(14/01/2020) for A/M.
ae) Barishal-Patuakhali 132 kV single Ckt was shut down at 06:54(14/01/2020) for C/M. |  |  |  |  | About 35 MW power interruption has been occurring under Patuakhali S/S
area since 06:54(14/01/2020).
af) Bheramara(GK) 132/33 kV T2 transformer was shut down at 07:40(14/01/2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-01-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 64 | 995000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 7128982 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 298 | 2916360 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 267 | 7100000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8681000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 418560
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 20 | 70800 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 80444 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 266868
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 650000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 180480 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7330521
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 74 | 439776 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 156912 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 566280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 471754
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1183020 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 696500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 790200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 180372 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2433 | 40303829
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 60 | 700000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 66555
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 180960
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 906840 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4774657 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 134 | 2957952 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 189120 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 331104
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 349920
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 70080 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25680
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 141 | 1309745 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 862 | 14462613
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 88947 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 2905220
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4437000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7878600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 3657500 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 570384
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 194 | 2877090
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 45 | 823196 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 128800 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1728980
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 370728
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 130140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2033280
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 454300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 280680 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 18 | 35340 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 69720 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1311 | 28469905
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 109 | 2957160 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 354816
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 725760
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 32 | 170400 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 258 | 4219286
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 964000 | Gas shortage.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1598700
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3417194
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 305 | 6982000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 576000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 671472
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 125216
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1407744 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1100160 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Under shut down.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 263000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 232728
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7558300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 229 | 5232000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 158820
| Sylhet Area Total |  |  |  | 1949 | 1425 | 30287334
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 658 | 8072727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 32 | 175680 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 6 | 8448 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 95625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 146448 | Low demand
| Payra 660 MW |  | NWPGCL | 0 | 0 | 0 | 1104300
| Khulna Area Total |  |  |  | 2314 | 786 | 9603228
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 114240 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 352800 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 208 | 4268804
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 205979 | Machine tripped at 18:38.
| Barisal Area Total |  |  |  | 462 | 260 | 4941823
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1485000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 313360
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 200 | 4793964 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4430627 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 205 | 4915273 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 434 | 9258545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 332400
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 75312 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239562
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 259104 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1267 | 26103147
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3661500
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 75 | 300480 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29575
| Rangpur Area Total |  |  |  | 605 | 225 | 3991555
| Total |  |  |  | 19107 | 8827 | 162382720
| Eastern Grid Total |  |  |  | 13543 | 6289 | 117742967
| Western Grid Total |  |  |  | 5564 | 2538 | 44639753
| National Grid Total |  |  |  | 19107 | 8827 | 162382720
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-01-13
(a) ENTIRE EASTERN GRID : |  | 5569 | MW | (b) ENTIRE WESTERN GRID : |  | 2737 | MW
i) Dhaka area |  | 2970 | MW | i) Khulna area |  | 1025 | MW
ii) Chittagong area |  | 913 | MW | ii) Rajshahi area |  | 882 | MW
iii) Comilla area |  | 708 | MW | iii) Barisal area |  | 228 | MW
iv) Mymensingh area |  | 662 | MW | iv) Rangpur area |  | 602 | MW
v) Sylhet area |  | 316 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8306 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 18:00 | Shahjibazar | 79 | 18:00 | Bottail | 100 | 19:00
Munsiganj | 84 | 20:00 | Fenchuganj | 28 | 18:00 | G.K Project | 27 | 18:30
Sonargaon | 60 | 19:00 | Kulawara | 28 | 20:00 | Faridpur | 134 | 19:30
Shyampur | 156 | 12:00 | Sylhet | 98 | 18:30 | Madaripur | 59 | 19:30
Bhulta | 157 | 16:00 | Chatak | 19 | 18:00 | Sariatpur | 44 | 20:00
Madanganj | 49 | 15:00 | Sunamganj | 28 | 19:00 | Gopalganj | 69 | 18:30
Shitalakhya | 102 | 12:00 | Biani Bazar | 34 | 19:00 | Bagerhat | 65 | 18:30
Rahim steel | 15 | 19:30 | Comilla (S) | 108 | 18:30 | Mongla | 30 | 10:00
Matuail | 72 | 10:00 | Comilla(N) | 77 | 16:00 | Satkhira | 69 | 20:00
Ghorasal | 67 | 19:00 | Chandpur | 50 | 20:00 | Gallamari | 36 | 13:00
Narsingdi | 106 | 19:00 | Feni | 88 | 18:30 | Magura | 38 | 18:30
Haripur (SBU) | 85 | 23:00 | Chowmuhani | 122 | 21:00 | Norail | 26 | 19:00
Ullon | 48 | 18:00 | Ashuganj | 41 | 19:00 | Chuadanga | 60 | 19:00
Hasnabad | 120 | 18:00 | Daudkandi | 92 | 18:30 | Barisal(N) | 32 | 20:00
Magbazar | 68 | 18:00 | B.Baria | 92 | 19:30 | Barisal (S) | 68 | 19:30
Maniknagar | 72 | 12:00 | Ramganj | 60 | 18:30 | Patuakhali | 87 | 19:30
Bangabhaban | 14 | 17:00 | Chaddagram | 14 | 18:00 | Bhandaria | 42 | 20:00
Narinda | 70 | 14:00 | PHP | 2.8 | 18:00 | Borhan Uddin | 25 | 19:30
Dhanmondi | 82 | 18:00 | Madunaghat | 33 | 18:00 | Ishurdi | 46 | 19:30
Lalbag | 78 | 18:00 | Hathazari | 66 | 19:00 | Ruppur Paromanobik | 1 | 20:00
Madartek | 41 | 19:00 | Khulshi | 136 | 12:00 | Natore | 90 | 18:30
Mirpur | 67 | 18:00 | Halishahar | 86 | 18:30 | Bogra | 123 | 18:30
Kalyanpur | 69 | 18:00 | Baraulia | 126 | 7:00 | Noagaon | 84 | 19:30
Gulshan | 92 | 18:00 | Sikalbaha | 16 | 9:00 | Rajshahi | 88 | 20:00
Uttara | 57 | 18:00 | Dohazari | 64 | 19:00 | Rajshahi New | 10 | 20:00
Uttara New | 36 | 18:30 | Cox'sbazar | 69 | 19:00 | C.Nawabganj | 55 | 19:30
Kamrangirchar | 52 | 19:00 | Chandraghona | 22 | 18:00 | Amnura | 25 | 20:00
Savar | 92 | 18:00 | Kaptai | 3.6 | 18:00 | Pabna | 70 | 20:00
Bhasantec | 98 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 81 | 19:00
Agargaon | 37 | 18:00 | Bakulia | 65 | 18:00 | Serajganj | 66 | 19:00
Satmosjid | 68 | 19:00 | Julda | 18 | 12:00 | Niyamatpur | 57 | 19:00
Tongi | 84 | 19:00 | TK chemical | 9.8 | 20:00 | Joypurhat | 47 | 20:00
Kabirpur | 157 | 16:00 | Modern Steel | 15 | 10:00 | Sherpur(Bogura) | 32 | 18:00
Basundhara | 74 | 18:00 | Shahmirpur | 22 | 18:00 | Mohastangor | 30 | 18:30
Manikganj | 58 | 19:30 | Khagrachhari | 16 | 18:00 | Rangpur | 110 | 18:30
Joydevpur | 139 | 18:00 | Matarbari | 21.5 | 18:00 | Lalmonirhat | 41 | 19:00
New Tongi | 74 | 12:00 | Baroiar Hat | 16 | 18:30 | Saidpur | 92 | 18:00
Korda | 185 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 92 | 18:30
Dhamrai | 46 | 19:00 | Abul Khair 230 | 120 | 10:00 | Thakurgaon | 61 | 19:30
Valuka | 68 | 18:30 | BSRM | 152 | 21:00 | Palashbari | 87 | 19:00
Tangail | 116 | 18:00 | GPH Ispat | 14 | 11:00 | Barapukuria | 39 | 20:00
Mymensing | 156 | 18:00 | Goalpara | 21 | 18:30 | Panchagar | 38 | 19:00
Kishorganj | 78 | 21:00 | Central s/s | 60 | 18:30 | Joldhaka | 18 | 20:00
Netrokona | 90 | 19:00 | Noapara | 46 | 20:00 | Kurigram | 39 | 19:00
Jamalpur | 90 | 18:30 | Jessore | 88 | 18:00
Sherpur | 74 | 18:30 | Benapol | 30 | 18:30
Srimongal | 24 | 19:30 | Jhenida | 80 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-01-13 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 405 | 0.125 | 396 | 0.66667 | Kaliakoir | 391 | 0.125 | 377 | 0.5
Bheramara | 407 | 0.041667 | 395 | 0.375 | Bhulta | 397 | 24:00 | 385 | 0.66667
Ashuganj(N) | 400 | 0.125 | 391 | 0.66667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 238 | 0.041667 | Hathazari | 225 | 0.77083 | 220 | 0.45833
Ishurdi | 238 | 0.125 | 225 | 0.33333 | Megnaghat | 238 | 0.16667 | 230 | 0.5
Ashuganj | 242 | 0.29167 | 238 | 0.66667 | Fenchuganj | 242 | 0.375 | 239 | 0.45833
Serajganj | 234 | 0.16667 | 229 | 0.77083 | Siddhirganj | 237 | 0.083333 | 228 | 0.66667
Baghabari | 243 | 0.083333 | 238 | 0.33333 | Maniknagar | 235 | 0.20833 | 226 | 0.66667
Barapukuria | 234 | 0.125 | 225 | 0.77083 | Old Airport | 235 | 0.125 | 224 | 0.66667
Bogra | 230 | 0.125 | 222 | 0.33333 | Barisal | 244 | 0.20833 | 231 | 0.77083
Khulna South | 238 | 0.125 | 213 | 0.75 | AKSML | 223 | 0.625 | 215 | 0.66667
Rampura | 232 | 0.16667 | 228 | 0.5 | BSRM | 227 | 0.125 | 220 | 0.66667
Haripur | 232 | 0.125 | 228 | 0.45833 | Bibiyana | 240 | 0.20833 | 235 | 0.58333
Hasnabad | 232 | 0.16667 | 226 | 0.625 | Bhulta | 236 | 0.20833 | 227 | 0.66667
Aminbazar | 235 | 0.125 | 226 | 0.5 | Ashuganj (S) | 239 | 0.83333 | 234 | 0.66667
Tongi | 233 | 0.16667 | 225 | 0.625 | Kaliakoir | 238 | 0.125 | 228 | 0.66667
Comilla (N) | 240 | 0.125 | 234 | 0.41667 | GPH | 224 | 0.125 | 217 | 0.66667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.125 | 128 | 0.66667 | Halishahar | 135 | 0.8125 | 129 | 0.45833
Munsiganj | 137 | 0.8125 | 127 | 0.66667 | Baraulia | 133 | 0.77083 | 130 | 0.041667
Sonargaon | 134 | 0.8125 | 127 | 0.45833 | Sikalbaha | 133 | 0.8125 | 129 | 0.41667
Shyampur | 135 | 0.125 | 130 | 0.66667 | Dohazari | 130 | 0.041667 | 129 | 0.16667
Bhulta | 128 | 0.125 | 122 | 0.625 | Cox'sbazar | 127 | 0.041667 | 122 | 0.75
Madanganj | 135 | 0.25 | 128 | 0.45833 | Chandraghona | 133 | 0.125 | 130 | 0.41667
Shitalakhya | 137 | 0.083333 | 129 | 0.66667 | Kaptai | 132 | 0.29167 | 130 | 0.041667
Rahim steal | 135 | 3:00 | 130 | 0.375 | A. Khaer Stl. | 132 | 0.8125 | 0 | 0.375
Matuail | 134 | 0.041667 | 128 | 0.41667 | Bakulia | 132 | 0.8125 | 127 | 0.41667
Ghorasal | 142 | 0.041667 | 142 | 0.041667 | Julda | 1360 | 0.16667 | 128 | 0.41667
Narsinghdi | 136 | 0.16667 | 133 | 0.77083 | TK Chemical | 133 | 0.77083 | 129 | 0.25
Haripur (SBU) | 136 | 0.16667 | 132 | 0.375 | Modern Steel | 132 | 0.16667 | 128 | 0.41667
Ullon | 131 | 0.25 | 124 | 0.70833 | Shahmirpur | 132 | 0.77083 | 128 | 0.41667
Hasnabad | 136 | 0.25 | 132 | 0.70833 | Khagrachhari | 133 | 0.125 | 129 | 0.45833
Magbazar | 133 | 0.20833 | 124 | 0.66667 | Matarbari | 130 | 0.041667 | 125 | 0.75
Maniknagar | 138 | 0.25 | 134 | 0.70833 | Baroiar Hat | 133 | 0.041667 | 130 | 0.66667
Bangabhaban | 138 | 0.25 | 134 | 0.70833 | Rangamati | 133 | 0.16667 | 129 | 0.41667
Narinda | 138 | 0.25 | 134 | 0.70833 | Goalpara | 138 | 0.16667 | 120 | 18:00
Dhanmondi | 131 | 0.25 | 124 | 0.70833 | Central s/s | 135 | 0.083333 | 120 | 18:00
Lalbag | 135 | 0.25 | 128 | 0.70833 | Noapara | 131 | 0.041667 | 122 | 0.75
Madartek | 131 | 0.25 | 123 | 0.66667 | Jessore | 135 | 0.16667 | 116 | 0.75
Mirpur | 137 | 0.25 | 130 | 0.5 | Benapol | 135 | 0.125 | 119 | 0.75
Kalyanpur | 138 | 0.25 | 132 | 0.5 | Jhenida | 131 | 0.041667 | 114 | 0.75
Gulshan | 130 | 0.25 | 124 | 0.5 | Bottail | 135 | 0.16667 | 122 | 0.75
Uttara | 136 | 0.25 | 130 | 0.5 | G.K Project | 137 | 0.083333 | 127 | 0.75
Uttara New | 135 | 0.25 | 127 | 0.5 | Faridpur | 137 | 0.16667 | 124 | 0.75
Kamrangirchar | 136 | 0.20833 | 130 | 0.5 | Madaripur | 140 | 0.625 | 125 | 0.75
Savar | 134 | 0.20833 | 127 | 0.5 | Sariatpur | 141 | 0.16667 | 128 | 0.77083
Bhasantec | 136 | 0.20833 | 130 | 0.5 | Gopalganj | 144 | 0.83333 | 127 | 0.75
Agargaon | 137 | 0.20833 | 131 | 0.5 | Bagerhat | 132 | 0.125 | 120 | 0.33333
Satmosjid | 137 | 0.20833 | 130 | 0.5 | Mongla | 132 | 0.125 | 120 | 0.75
Tongi | 140 | 0.16667 | 133 | 0.625 | Satkhira | 133 | 0.16667 | 119 | 0.75
Kabirpur | 135 | 0.083333 | 128 | 0.66667 | Gallamari | 135 | 0.125 | 119 | 0.75
Basundhara | 131 | 3:00 | 123 | 0.66667 | Magura | 133 | 0.083333 | 115 | 0.75
Manikganj | 140 | 2:00 | 134 | 0.75 | Norail | 132 | 0.083333 | 115 | 0.77083
Joydevpur | 143 | 0.75 | 139 | 0.54167 | Chuadanga | 131 | 0.083333 | 110 | 0.75
New Tongi | 139 | 0.20833 | 131 | 0.66667 | Barisal(N) | 140 | 0.20833 | 129 | 0.77083
Kodda | 135 | 0.75 | 126 | 0.33333 | Barisal (S) | 137 | 0.083333 | 128 | 0.75
Dhamrai | 135 | 0.125 | 128 | 0.66667 | Patuakhali | 135 | 0.083333 | 122 | 0.77083
Valuka | 131 | 0.25 | 124 | 0.77083 | Bhandaria | 135 | 0.375 | 124 | 0.75
Tangail | 134 | 0.29167 | 128 | 0.77083 | Ishurdi | 136 | 0.20833 | 127 | 0.77083
Mymensing | 132 | 0.25 | 125 | 0.77083 | Ruppur Paromanobik | 134 | 0.83333 | 126 | 0.77083
Kishorganj | 134 | 0.375 | 128 | 0.79167 | Natore | 132 | 0.625 | 124 | 0.77083
Netrokona | 131 | 0.25 | 123 | 0.77083 | Bogra | 136 | 0.25 | 128 | 0.77083
Jamalpur | 130 | 0.375 | 120 | 0.29167 | Noagaon | 132 | 0.20833 | 124 | 0.77083
Sherpur | 129 | 0.875 | 118 | 0.33333 | Rajshahi | 132 | 0.16667 | 122 | 0.33333
Srimongal | 140 | 0.125 | 137 | 0.33333 | Rajshahi New | 131 | 0.20833 | 123 | 0.75
Shahjibazar | 138 | 0.20833 | 136 | 0.041667 | C.Nawabganj | 129 | 0.83333 | 119 | 0.33333
Fenchuganj | 139 | 0.375 | 136 | 0.041667 | Amnura | 129 | 0.83333 | 122 | 0.5
Khulawara | 138 | 0.375 | 136 | 16:00 | Pabna | 137 | 0.25 | 128 | 0.75
Sylhet | 135 | 0.041667 | 133 | 0.66667 | Shahjadpur | 140 | 0.25 | 131 | 0.54167
Chatak | 135 | 0.041667 | 129 | 0.77083 | Serajganj | 137 | 0.16667 | 128 | 0.54167
Sunamganj | 136 | 0.625 | 129 | 0.77083 | Niyamatpur | 131 | 0.16667 | 121 | 0.33333
Biani Bazar | 136 | 0.125 | 133 | 0.79167 | Joypurhat | 133 | 0.25 | 125 | 0.77083
Comilla(s) | 131 | 0.29167 | 128 | 0.70833 | Sherpur(Bogura) | 136 | 0.16667 | 128 | 0.77083
Comilla(n) | 139 | 0.77083 | 136 | 0.41667 | Mohastangor | 135 | 0.20833 | 127 | 0.77083
Chandpur | 136 | 14:00 | 133 | 0.041667 | Rangpur | 130 | 0.625 | 122 | 0.77083
Feni | 135 | 0.83333 | 132 | 0.45833 | Lalmonirhat | 128 | 0.20833 | 118 | 0.77083
Chowmuhani | 132 | 0.625 | 128 | 0.875 | Saidpur | 132 | 0.25 | 120 | 0.79167
Ashuganj | 140 | 0.041667 | 138 | 0.70833 | Purbasadipur | 130 | 0.25 | 113 | 0.77083
Daudkandi | 135 | 0.29167 | 131 | 0.66667 | Thakurgaon | 127 | 0.25 | 113 | 0.75
B.Baria | 137 | 0.625 | 134 | 0.79167 | Palashbari | 130 | 0.20833 | 122 | 0.33333
Ramganj | 132 | 0.33333 | 128 | 0.75 | Barapukuria | 134 | 0.20833 | 125 | 0.77083
Chaddagram | 136 | 0.79167 | 133 | 0.625 | Panchagar | 125 | 0.25 | 105 | 0.77083
PHP | 133 | 0.625 | 129 | 0.66667 | Joldhaka | 129 | 0.25 | 116 | 0.77083
Madanhat | 134 | 0.20833 | 131 | 0.41667 | Kurigram | 132 | 0.125 | 118 | 0.77083
Hathazari | 135 | 0.8125 | 131 | 0.16667
Khulshi | 131 | 0.70833 | 127 | 0.375

## L-Curve
Date | 2020-01-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 288 | 4757 | 1745 | 6502 |  |  |  | QF-LDC-12
0:30 | 302 | 4530 | 1627 | 6157 | Date: | 2020-01-13
1:00 | 316 | 4303 | 1509 | 5812
1:30 | 311 | 4208 | 1465.5 | 5673.5
2:00 | 306 | 4113 | 1422 | 5535
2:30 | 291 | 4043 | 1398 | 5441 | [5 empty] | Gen. at Eve. Peak | 8827 | 8827 MW (19:00 )
3:00 | 276 | 3973 | 1374 | 5347 | [6 empty] | 19:00
3:30 | 263 | 3900 | 1370.5 | 5270.5 | [5 empty] | Gen. at Day Peak | 6893.3 | 6893.3 MW (09:00 )
4:00 | 250 | 3827 | 1367 | 5194 | [6 empty] | 9:00
4:30 | 268 | 3791 | 1320.5 | 5111.5 | [5 empty] | Highest Generation | 8827
5:00 | 286 | 3755 | 1274 | 5029 | [6 empty] | 19:00
5:30 | 287 | 3922 | 1333 | 5255
6:00 | 288 | 4089 | 1392 | 5481
6:30 | 313 | 4195.644 | 1432.55 | 5628.194
7:00 | 338 | 4302.288 | 1473.1 | 5775.388
7:30 | 366.5 | 4553.378 | 1637.3 | 6190.678
8:00 | 395 | 4804.468 | 1801.5 | 6605.968
8:30 | 310.5 | 4931.684 | 1817.95 | 6749.634
9:00 | 226 | 5058.9 | 1834.4 | 6893.3
9:30 | 188 | 4999.532 | 1769.25 | 6768.782
10:00 | 150 | 4940.164 | 1704.1 | 6644.264
10:30 | 152 | 4966.816 | 1689.7 | 6656.516
11:00 | 154 | 4993.468 | 1675.3 | 6668.768
11:30 | 108.5 | 5018.9405 | 1747.3 | 6766.2405
12:00 | 63 | 5044.413 | 1819.3 | 6863.713
12:30 | 94 | 5055.21 | 1827.75 | 6882.96
13:00 | 125 | 5066.007 | 1836.2 | 6902.207
13:30 | 69.5 | 4955.4985 | 1813.7 | 6769.1985
14:00 | 14 | 4844.99 | 1791.2 | 6636.19
14:30 | 17 | 4837.81 | 1781.6 | 6619.41
15:00 | 20 | 4830.63 | 1772 | 6602.63
15:30 | 72.5 | 4779.695 | 1745.3 | 6524.995
16:00 | 125 | 4728.76 | 1718.6 | 6447.36
16:30 | 63.5 | 4716.5 | 1758.9 | 6475.4
17:00 | 2 | 4704.24 | 1799.2 | 6503.44
17:30 | 71.5 | 5110.62 | 2089.1 | 7199.72
18:00 | 141 | 5517 | 2379 | 7896
18:30 | 291.5 | 5903 | 2458.5 | 8361.5
19:00 | 442 | 6289 | 2538 | 8827
19:30 | 432 | 6243 | 2510 | 8753
20:00 | 405 | 6154 | 2592 | 8746 |  |  |  | Executive Engineer
20:30 | 351.5 | 6044.5 | 2513.5 | 8558 |  |  |  | Network Operation Division
21:00 | 298 | 5935 | 2435 | 8370
21:30 | 281 | 5773 | 2329.5 | 8102.5
22:00 | 264 | 5611 | 2224 | 7835 |  |  |  |  | Page 6 of 7
22:30 | 234.5 | 5303 | 2087.5 | 7390.5
23:00 | 205 | 4995 | 1951 | 6946
23:30 | 246.5 | 4876 | 1848 | 6724
24:00 | 288 | 4757 | 1745 | 6502
8827 MW (19:00 )
6893.3 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-01-13 |  | Energy | 162382720
[10 empty] | 2020-01-13 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4166 | 225 | 1676 | 109 | 274 | 42 | 0 | 0 | 78
0:30 | 4005 | 180.5 | 1614 | 62.5 | 212 | 41 | 0 | 0 | 76 | Date: | 2020-01-13
1:00 | 3844 | 136 | 1552 | 16 | 150 | 40 | 0 | 0 | 74
1:30 | 3773 | 138 | 1482.5 | 16 | 150 | 40 | 0 | 0 | 74 | [7 empty] | Total Energy | 162.3827 | Total Energy Gen 162.383 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.383 MKWHr
2:00 | 3702 | 140 | 1413 | 16 | 150 | 40 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3658.5 | 140.5 | 1371 | 8 | 150 | 40 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 162.3827
3:00 | 3615 | 141 | 1329 | 0 | 150 | 40 | 0 | 0 | 72
3:30 | 3539.5 | 159 | 1312 | 0 | 150 | 39 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3464 | 177 | 1295 | 0 | 150 | 38 | 0 | 0 | 70
4:30 | 3426 | 158 | 1270.5 | 0 | 150 | 38 | 0 | 0 | 69
5:00 | 3388 | 139 | 1246 | 0 | 150 | 38 | 0 | 0 | 68
5:30 | 3504 | 139 | 1353.5 | 0 | 150 | 38.5 | 0 | 0 | 70
6:00 | 3620 | 139 | 1461 | 0 | 150 | 39 | 0 | 0 | 72
6:30 | 3680 | 139 | 1548.5 | 0 | 150 | 39.5 | 0 | 0 | 71 |  |  |  |  | Coal
7:00 | 3740 | 139 | 1636 | 0 | 150 | 40 | 0 | 0 | 70
7:30 | 3879 | 225 | 1815.5 | 8.5 | 150 | 40 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 4018 | 311 | 1995 | 17 | 150 | 40 | 0 | 0 | 72
8:30 | 4081 | 313.5 | 2033 | 49 | 150 | 40 | 0 | 0 | 77
9:00 | 4144 | 316 | 2071 | 81 | 150 | 40 | 0 | 0 | 82
9:30 | 4089 | 316 | 1973.5 | 102 | 150 | 40.5 | 0 | 0 | 82
10:00 | 4034 | 316 | 1876 | 123 | 150 | 41 | 0 | 0 | 82
10:30 | 4018 | 316 | 1910 | 113 | 150 | 41 | 0 | 0 | 83
11:00 | 4002 | 316 | 1944 | 103 | 150 | 41 | 0 | 0 | 84
11:30 | 3921 | 316 | 1996.5 | 176.5 | 209 | 41 | 0 | 0 | 86
12:00 | 3840 | 316 | 2049 | 250 | 268 | 41 | 0 | 0 | 88
12:30 | 3836 | 317 | 2052.5 | 269.5 | 269.5 | 41 | 0 | 0 | 86
13:00 | 3832 | 318 | 2056 | 289 | 271 | 41 | 0 | 0 | 84
13:30 | 3832 | 318 | 2056 | 289 | 271 | 41 | 0 | 0 | 84
14:00 | 3832 | 318 | 2056 | 289 | 271 | 41 | 0 | 0 | 84
14:30 | 3780.5 | 318.5 | 1980 | 258.5 | 271.5 | 41.5 | 0 | 0 | 87
15:00 | 3729 | 319 | 1904 | 228 | 272 | 42 | 0 | 0 | 90
15:30 | 3770.5 | 318.5 | 1880.5 | 186.5 | 223.5 | 42 | 0 | 0 | 89
16:00 | 3812 | 318 | 1857 | 145 | 175 | 42 | 0 | 0 | 88
16:30 | 3813 | 318.5 | 1873 | 172.5 | 162.5 | 41 | 0 | 0 | 89
17:00 | 3814 | 319 | 1889 | 200 | 150 | 40 | 0 | 0 | 90
17:30 | 3895 | 488.5 | 1971 | 556.5 | 150 | 40 | 0 | 0 | 98
18:00 | 3976 | 658 | 2053 | 913 | 150 | 40 | 0 | 0 | 106
18:30 | 4210.5 | 658 | 2091 | 1104 | 150 | 40 | 3 | 0 | 105
19:00 | 4445 | 658 | 2129 | 1295 | 150 | 40 | 6 | 0 | 104
19:30 | 4388 | 658 | 2084 | 1325 | 150 | 40 | 2 | 0 | 106
20:00 | 4462 | 658 | 2167 | 1163 | 150 | 40 | 0 | 0 | 106
20:30 | 4532.5 | 658 | 2115 | 896 | 212.5 | 40 | 0 | 0 | 104
21:00 | 4603 | 658 | 2063 | 629 | 275 | 40 | 0 | 0 | 102
21:30 | 4565 | 610.5 | 2002.5 | 509.5 | 275 | 41 | 0 | 0 | 99
22:00 | 4527 | 563 | 1942 | 390 | 275 | 42 | 0 | 0 | 96
22:30 | 4410 | 462.5 | 1861 | 249.5 | 273.5 | 42 | 0 | 0 | 92
23:00 | 4293 | 362 | 1780 | 109 | 272 | 42 | 0 | 0 | 88
23:30 | 4229.5 | 293.5 | 1728 | 109 | 273 | 42 | 0 | 0 | 83 | Max Temp. in Dhaka |  | 23.6° C
24:00 | 4166 | 225 | 1676 | 109 | 274 | 42 | 0 | 0 | 78
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 162.383 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 162.383 MKWHr
Note on W13: Author:

## Generation
2020-01-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 38 | 38 | 39 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 40 | 40 |  | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 906840
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2 | [13 empty] | 0 | 5 | 0 | 35 | 45 |  | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 700000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.2 | 1.58 | 5.87 | 15.79 | 17.41 |  |  | 0 | 12.2 | 7.2 | 1 | [9 empty] | 66555
6 | Sikalbaha 225MW CCPP (Gas) | 201 | 180 | 181 | 181 | 182 | 194 | 182 | 200 | 201 | 208 | 201 | 202 | 202 | 202 | 202 | 217 | 203 | 215 |  | 202 | 201 | 201 | 202 | 202 | 217 | 201 | 4774657
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 104 | 106 | 104 | 104 | 104 | 116 | 135 | 134 | 134 | 134 | 135 | 135 | 130 | 110 | 134 | 140 |  | 134 | 134 | 135 | 133 | 134 | 146 | 136 | 2957952
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [10 empty] | 60 | 60 | 60 | 37 | 35 | 37 | 38 | 37 |  | 97 | 90 | 65 | 0 |  |  |  | 650000
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 240 | 200 | 200 | 250 | 300 | 342 | 360 | 300 | 300 | 350 | 346 | 300 | 300 | 300 | 300 | 300 |  | 330 | 330 | 330 | 330 | 330 | 345 | 335 | 7330521
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 83 | 130 | 158 | 158 | 158 | 185 | 185 | 185 | 185 | 185 | 185 | 192 |  | 194 | 194 | 195 | 197 | 110 | 80 | 78 | 2877090
20 | Ghorasal TPP (Unit-1&2) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 34 | 34 |  | 64 | 64 | 68 | 68 | 64 | 64 | 64 | 995000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 260 | 260 | 220 | 220 | 240 | 316 | 360 | 310 | 330 | 310 | 280 | 275 | 275 | 275 | 307 | 284 | 305 |  | 340 | 340 | 340 | 340 | 340 | 360 | 314 | 7128982
26
28 | Ashuganj TPP Unit- 3 | [26 empty] | 88947
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 130 | 130 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2905220
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 33 | 30 | 30 | 30 | 33 | 37 | 37 | 40 | 40 | 40 | 43 | 40 |  | 43 | 43 | 23 | 23 | 23 | 26 | 23 | 570384
33 | Ashuganj 225 MW CCPP | 164 | 176 | 162 | 170 | 166 | 182 | 173 | 185 | 181 | 198 | 194 | 182 | 188 | 185 | 181 | 203 | 187 | 202 |  | 189 | 183 | 182 | 189 | 163 | 204 | 183 | 4437000
34 | Ashuganj 450 MW CCPP(South) | 325 | 290 | 270 | 270 | 250 | 270 | 235 | 235 | 235 | 225 | 235 | [10 empty] | 80 | 255 | 235 | 0 | 30 | 3657500
| Ashuganj 450 MW CCPP(North) | 340 | 280 | 260 | 265 | 260 | 295 | 330 | 385 | 325 | 315 | 280 | 310 | 310 | 280 | 280 | 325 | 280 | 310 |  | 345 | 340 | 340 | 350 | 340 | 380 | 310 | 7878600
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 80 | 88 | 81 | 86 | 88 | 85 | 87 | 90 | 83 | 90 |  | 90 | 80 | 80 | 85 | 80 | 90 | 90 | 1728980
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 112 | 145 | 145 | 145 | 145 | 151 | 0 | 0 | [9 empty] | 70 |  | 298 | 305 | 304 | 304 | 306 | 306 | 307 | 2916360
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 330 | 300 | 300 | 300 | 350 | 350 | 380 | 380 | 360 | 360 | 390 | 390 | 390 | 390 | 390 | 390 | 390 |  | 450 | 450 | 450 | 450 | 450 | 420 | 420 | 8681000
41 | Haripur 360MW CCPP(HPL) | 344 | 285 | 286 | 264 | 245 | 275 | 276 | 375 | 371 | 307 | 312 | 371 | 371 | 313 | 312 | 313 | 314 | 313 |  | 267 | 252 | 245 | 227 | 226 | 226 | 243 | 7100000
42 | RPCL 210MW CCPP | 148 | 148 | 148 | 108 | 107 | 107 | 162 | 161 | 163 | 148 | 148 | 127 | 125 | 118 | 118 | 117 | 116 | 117 |  | 109 | 111 | 110 | 106 | 106 | 106 | 106 | 2957160
43
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
45 | Fenchugonj CCPP Phase-2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1598700
46 | Shajibazar 330 MW CCPP | 305 | 300 | 295 | 294 | 293 | 301 | 294 | 318 | 291 | 306 | 311 | 307 | 308 | 299 | 301 | 314 | 303 | 314 |  | 305 | 296 | 300 | 309 | 301 | 295 | 262 | 6982000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 69 | 68 | 67 | 67 | 68 | 67 | 67 | 66 | 67 | 67 |  | 67 | 68 | 68 | 68 | 69 | 45 | 69 | 1407744
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 60 | 76 | 76 | 76 | 76 | 73 | 76 | 30 | 30 | 76 |  | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 1100160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | [8 empty] | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 263000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [6 empty] | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 158820
54 | Hobiganj 11MW PP Cofidence-E | [11 empty] | 10 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 125216
55 | Fenchugonj 51 MW PP (Barakatullah) | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 44 | 42 | 47 | 43 | 53 | 53 | 53 | 11 | 11 | 53 |  | 53 | 53 | 53 | 50 | 50 | 2 | 2 | 576000
56 | Shahjahanulla 25 MW PP | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 16 | 16 | 24 | 22 |  |  | 232728
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 295 | 290 | 280 | 270 | 310 | 320 | 320 | 310 | 280 | 300 | 305 | 295 | 290 | 295 | 315 | 310 | 310 |  | 320 | 305 | 295 | 290 | 300 | 300 | 295 | 7558300
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [6 empty] | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 331104
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 266868
62 | Tangail 22 MW PP (Doreen) | [6 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 354816
63 | Impoprt (Tripura) | 74 | 74 | 72 | 70 | 68 | 72 | 70 | 72 | 82 | 82 | 84 | 88 | 84 | 90 | 90 | 88 | 90 | 106 |  | 104 | 106 | 106 | 102 | 96 | 88 | 78 | 2033280
64 | Malancha, Ctg. EPZ (United) | 4 | 4 | 4 | 4 | 4 | 7 | 10 | 8 | 4 | 5 | 4 | 4 | 6 | 5 | 3 | 4 | 5 | 16 |  | 26 | 28 | 30 | 25 | 31 | 32 | 16 | 349920
65 | Feni 22MW PP (Doreen) | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 370728
66 | Feni 11 MW PP (Doreen) | [8 empty] | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 130140
67 | Jangalia 33MW PP (Summit) | [6 empty] | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 454300
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 280680
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 19 | 28 | 28 | 32 | 32 | 32 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 6 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 583020
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 18 | 18 | 18 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 696500
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 25 | 31 | 31 | 790200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 10 |  | 18 | 18 | [5 empty] | 35340
| Chowmuhani 113 MW | [16 empty] | 3 | 18 |  | 18 | 18 | 18 |  |  |  |  | 69720
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 30 |  | 50 | 50 | 50 |  |  |  |  | 180480
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 16 | 16 | 0 | [5 empty] | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 58 |  | 95 | 95 | 95 | 95 | 95 | 40 | 24 | 725760
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [11 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 22 |  | 34 | 34 | 17 |  |  |  |  | 180372
| Kaptai 7 MW Solar PP | [6 empty] | 0.088 | 0.588 | 1.13 | 1.774 | 4.158 | 4.513 | 4.207 | 3.49 | 2.43 | 1.16 | 0.14 | 0 | [8 empty] | 25680
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 16 |  | 20 | 30 | [5 empty] | 70800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 1 | 16 | 16 | 16 | 7 | 7 | 37 |  | 100 | 100 | 100 | 68 |  |  |  | 418560
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | [6 empty] | 10 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 29 |  | 44 | 47 | 50 | 50 | 50 | 2 | 2 | 671472
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 38 | 43 | 43 | 43 | 43 | 43 | 43 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 823196
94 | Gagnagar 102 MW PP (Digital Power) |  | 0 | 0 | [5 empty] | 5 | 7 | 7 | 30 | 40 | 40 | 7 | 7 | 16 | 50 |  | 74 | 74 | 74 | 16 | 0 |  |  | 439776
95 | Patenga 50MW PP (Baraka) | [16 empty] | 4 | 23 |  | 50 | 50 | 50 | 43 |  |  |  | 180960
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 14 |  | 30 | 30 | [5 empty] | 70080
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 21 |  | 46 | 47 | 47 |  |  |  |  | 156912
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 22 |  | 30 | 30 | 0 |  |  |  |  | 80444
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 35 | 55 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 55 |  | 55 | 55 | 55 |  |  |  |  | 471754
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 130 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3417194
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.3 | 0.9 | 1.6 | 1.9 | 1.9 | 1.8 | 1.5 | 1 | 0.4 | 0.1 | 0 | [8 empty] | 11150
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 17 | 17 | 17 | 53 | 53 | 53 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 566280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United)
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 50 |  | 50 | 50 | 50 | 20 | 0 |  |  | 189120
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 3 | 23 |  | 50 | 50 | 15 |  |  |  |  | 128800
118 | Bibiyana-III 400 MW CCPP | 229 | 229 | 229 | 229 | 229 | 229 | 229 | 227 | 229 | 230 | 230 | 230 | 230 | 230 | 230 | 228 | 228 | 229 |  | 229 | 229 | 229 | 229 | 229 | 228 | 228 | 5232000
| Jamalpur 115 MW PP (United) | [16 empty] | 9 | 32 |  | 32 | 32 | 32 | 32 | 8 |  |  | 170400
| Anwara 300 MW PP (United) | [8 empty] | 16 | 16 | 16 | 100 | 100 | 100 | 108 | 52 | 52 | 140 |  | 141 | 143 | 144 | 143 | 143 | 52 | 0 | 1309745
120 | Eastern Zone Total | 4303 | 4113 | 3973 | 3827 | 3755 | 4089 | 4302.288 | 4804.468 | 5058.9 | 4940.164 | 4993.468 | 5044.413 | 5066.007 | 4844.99 | 4830.63 | 4728.76 | 4704.24 | 5517 |  | 6289 | 6243 | 6154 | 5935 | 5611 | 4995 | 4757 | 117742967
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 15 | 32 |  | 32 | 32 | 32 | 32 | 32 | 0 |  | 175680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 32 | 32 | 32 | 32 | 0 |  |  | 114240
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 0 |  |  |  |  | 0 | 13 | 43 | 37 | 12 | 12 | 1 | [5 empty] | 12 |  | 0 | 15 | 84 | 0 |  |  |  | 205979
| Bhola 225 MW CCPP | 188 | 164 | 164 | 170 | 170 | 170 | 176 | 176 | 176 | 163 | 163 | 163 | 164 | 164 | 164 | 164 | 164 | 164 |  | 208 | 204 | 204 | 206 | 203 | 204 | 205 | 4268804
140 | Bhola 33 MW PP (Venture) | 15 | 14 | 14 | 13 | 13 | 14 | 14 | 14 | 13 | 13 | 12 | 12 | 13 | 13 | 12 | 12 | 12 | 19 |  | 20 | 21 | 21 | 21 | 19 | 18 | 16 | 352800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 5 |  | 40 | 40 | 40 | 0 |  |  |  | 95625
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 6 | 2 | 0 |  |  |  |  | 8448
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 50 | 67 | 67 | 0 |  |  |  | 146448
146 | Bheramara HVDC | 136 | 140 | 141 | 177 | 139 | 139 | 139 | 311 | 316 | 316 | 316 | 316 | 318 | 318 | 319 | 318 | 319 | 658 |  | 658 | 658 | 658 | 658 | 563 | 362 | 225 | 8072727
147 | Bheramara 410 MW CCPP
148 | Payra 660 MW | [11 empty] | 118 | 121 | 121 | 122 | 25 | [5 empty] | 0 | 125 | 125 | 122 | 124 | 1104300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3661500
153 | Baghabari 71 MW GTPP | 35 | 35 | 35 | 35 | 35 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 45 | 70 | 1485000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 205 | 200 | 200 | 170 | 140 | 170 | 170 | 194 | 205 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 200 | 200 |  | 200 | 199 | 199 | 197 | 197 | 194 | 193 | 4793964
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 160 | 161 | 143 | 139 | 139 | 146 | 167 | 207 | 182 | 169 | 192 | 187 | 185 | 186 | 170 | 199 | 196 |  | 200 | 186 | 184 | 187 | 184 | 194 | 189 | 4430627
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 184 | 184 | 185 | 184 | 185 | 184 | 205 | 219 | 201 | 177 | 193 | 204 | 204 | 200 | 203 | 210 | 202 |  | 205 | 203 | 198 | 192 | 199 | 202 | 209 | 4915273
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 431 | 367 | 317 | 316 | 296 | 357 | 385 | 437 | 402 | 364 | 371 | 369 | 374 | 332 | 316 | 375 | 410 | 431 |  | 434 | 398 | 423 | 432 | 385 | 449 | 353 | 9258545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [6 empty] | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 |  | 332400
163 | Bogura 20 MW PP (Energyprima) | [7 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 0 |  | 75312
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239562
165 | Amnura 50 MW PP(Sinha) | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 50 |  | 50 | 50 | 50 | 24 | 24 | 0 |  | 313360
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 45 |  | 70 | 70 | 70 | 35 | 0 |  |  | 259104
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 76 |  | 75 | 75 | 72 | 36 | 35 | 0 |  | 300480
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.5 | 1.4 | 3.1 | 5.3 | 5.3 | 5.2 | 4.2 | 3 | 1.6 | 0.2 | 0 | [8 empty] | 29575
178
178