## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-01-20 | Monday
|  | Date (day): | 2020-01-20 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11559.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14500 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-01-19 | 2020-01-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 71 | 71 | 71 | 71 | 14 |  | Gas shortage
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 99 | 150 | 150 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 345 | 250 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 256 | 256 | 260 | 260 | 152 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 332 | 344 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 25 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 22 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 28 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 230 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 44 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2040 | 2229 | 3572 | 4223 | 972 | 575
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.08 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 48 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 43 | 43 | 43 | 43 | 187 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 221 | 202 | 210 | 210 |  |  | FGMO
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 108 | 139 | 115 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 14 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.62 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 160 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 552.7 | 852 | 1438 | 1598 | 427 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  | 135 | Under maint.
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 85 | 100 | 100 | 34 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 229 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 300 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 295 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 10 | 40 | 43
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under Maint.
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 45 |  | 6 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 90 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 108 | 88 | 104
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 8 | 14 | 14 | 14 |  | 11 | Engine problem
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 61 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1326 | 1309 | 1654 | 2339 | 174 | 409
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 128 | 163 | 163 | 39 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.3 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 50 | 0 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 209.3 | 295 | 381.6 | 595 | 39 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 66 | 66 | 66 | 66
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 149 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 72 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 18 | 98 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17 |  |  | Engine problem
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 230 | 231 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1273 | 1365 | 1469 | 1469 | 0 | 350
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 314 | 654 | 308 | 652
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 32 | 36 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 314 | 818 | 659 | 1458 | 0 | 410
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 110 | 140 | 140 | 140 |  |  | ST shut down
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 95 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 322 | 372 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 444 | 627 | 325 | 395 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 180 | 210 | 210 |  |  | FGNO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 188 | 220 | 220 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 148 | 105 | 127 | 127 |  |  | ST Under maint
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 392 | 410 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 3 | 3 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 747 | 1084 | 1655 | 1941 | 100 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 95 | 85 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 250 | 200 | 250
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 54 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 242.7 | 399 | 406 | 482 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7148.7 | 8978 | 11559.6 | 14500 | 1712 | 1950
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6675.7297 | 8384 | 10794.7969 | 13540.6549
A. |  | 2020-01-19 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 8978 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5472 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8978 | MW
3 | Day peak Generation : |  |  | 7148.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8384 | MW
4 | Evening peak Generation : |  |  | 8978 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 169.7782 | MKWHr | By Solar | 0.15136 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 138.0133 | MKWHr |  | By Oil: | 7.0439 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.6064 | MKWHr |  | By Hydro: | 0.9435 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1712 | MW | Dhaka | 3037 | 3037 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1950 | MW | Chittagong | 843 | 843 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3662 | MW | Khulna | 1056 | 1056 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1106.6 | MMCFD |  |  | Rajshahi | 902 | 902 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129507932.996 | ii) Oil : | Taka | 62616952.98 | Comilla | 719 | 719 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 30907858.97 | Total | Taka | 223032744.946 | Mymensingh | 692 | 692 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.665 | MKWHr. | Sylhet | 315 | 315 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -75 | MW (E to W) at | 19:00 | hrs | Barisal | 244 | 244 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -506 | MW at | 7:00 | hrs | Rangpur | 576 | 576 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.0° C |  |  | Total | 8384 | 8384 |  | 0
B. |  | 2020-01-20 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 25.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14500 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 5500 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 170.1943 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5518 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.9404 | MKWHr. | ii) HVDC Flow at Peak Time |  | 654 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0794 | MKWHr. | iii) Maximum HVDC Flow : |  | 654 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95 |  | (b) Today: | 94.95 |  | (c) Rule Curve: |  | 99.39
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-01-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 71 | 0 | 103 | 0 | 285 | 0 | 0 | 254 | 320 |  | 0 | 300 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 189 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 0 | 80 | 305 | 290 | 175 | 45 | 86 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 76 | 161 | 0 | 22 | 0 | 60 | 66 | 5 | 5 | 100 | 136 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 12 | 0 | 178 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 |  | 4591 | 1599 | 6190 | 3891 | 136 | 1561 | 27 | 457 | 42 | 0 | 76 | 0 | 0 | 95
2:00 | 71 | 0 | 99 | 0 | 285 | 0 | 0 | 254 | 320 |  | 0 | 320 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 184 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 280 | 265 | 162 | 8 | 86 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 72 | 163 | 0 | 0 | 0 | 30 | 66 | 5 | 5 | 130 | 132 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 |  | 4336 | 1547 | 5883 | 3623 | 136 | 1542 | 10 | 458 | 42 | 0 | 72 | 0 | 0 | 95
3:00 | 71 | 0 | 100 | 0 | 285 | 0 | 0 | 254 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 182 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 270 | 265 | 166 | 8 | 86 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 111 | 0 | 0 | 0 | 30 | 66 | 5 | 5 | 130 | 134 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 |  | 4200 | 1529 | 5729 | 3529 | 136 | 1481 | 10 | 461 | 42 | 0 | 70 | 0 | 0 | 95
4:00 | 71 | 0 | 99 | 0 | 285 | 0 | 0 | 254 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 184 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 270 | 265 | 164 | 8 | 87 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 111 | 0 | 0 | 0 | 30 | 66 | 5 | 5 | 130 | 135 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 |  | 4169 | 1423 | 5592 | 3477 | 136 | 1393 | 10 | 463 | 43 | 0 | 70 | 0 | 0 | 95
5:00 | 71 | 0 | 100 | 0 | 285 | 0 | 0 | 254 | 230 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 197 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 305 | 300 | 162 | 8 | 87 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 111 | 0 | 0 | 0 | 30 | 66 | 5 | 5 | 100 | 134 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 |  | 4175 | 1297 | 5472 | 3476 | 136 | 1275 | 10 | 462 | 43 | 0 | 70 | 0 | 0 | 95
6:00 | 71 | 0 | 102 | 0 | 285 | 0 | 0 | 254 | 300 |  | 0 | 330 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 305 | 300 | 182 | 8 | 86 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 111 | 0 | 0 | 0 | 30 | 66 | 5 | 5 | 100 | 163 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 81 | 0 | 160 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 |  | 4368 | 1411 | 5779 | 3600 | 136 | 1460 | 10 | 460 | 43 | 0 | 70 | 0 | 0 | 95
7:00 | 71 | 0 | 100 | 0 | 285 | 0 | 0 | 254 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 197 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 80 | 310 | 305 | 181 | 8 | 86 | 18 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 159 | 0 | 0 | 0 | 60 | 66 | 5 | 5 | 163 | 163 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 229 | 0 | 0 | 0 | 0.282 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 81 | 0 | 160 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 |  | 4734.282 | 1472 | 6206.282 | 3840 | 136 | 1632 | 10 | 470 | 43 | 0 | 74 | 1.282 | 0 | 94.99
8:00 | 71 | 0 | 149 | 0 | 285 | 0 | 0 | 254 | 330 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 25 | 26 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 80 | 310 | 315 | 164 | 8 | 86 | 40 | 0 | 0 | 15 | 0 | 0 | 0 | 22 | 0 | 27 | 8 | 78 | 163 | 8 | 22 | 0.3 | 60 | 66 | 50 | 36 | 163 | 152 | 68 | 75 | 0 | 100 | 17 | 0 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 0 | 2 | 230 | 0 | 0 | 0 | 1.338 | 0 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 81 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 284 |  | 5115.038 | 1775.21 | 6890.248 | 4033 | 314 | 1855 | 33 | 525 | 43 | 0 | 78 | 9.248 | 0 | 94.99
9:00 | 71 | 0 | 150 | 0 | 313 | 0 | 0 | 254 | 364 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 80 | 310 | 315 | 183 | 8 | 88 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 33 | 8 | 82 | 160 | 32 | 22 | 0.5 | 60 | 66 | 50 | 50 | 163 | 148 | 67 | 73 | 0 | 18 | 17 | 0 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 2.713 | 16 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 81 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 298 |  | 5226.213 | 1801.7 | 7027.913 | 4023 | 314 | 1928 | 95 | 539 | 43 | 0 | 82 | 3.913 | 0 | 94.99
10:00 | 71 | 0 | 150 | 0 | 313 | 0 | 0 | 255 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 80 | 370 | 315 | 184 | 8 | 89 | 43 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 8 | 84 | 159 | 32 | 22 | 0 | 60 | 66 | 50 | 50 | 130 | 148 | 66 | 75 | 0 | 18 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 3.53 | 16 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 81 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 298 |  | 5250.53 | 1697.1 | 6947.63 | 4052 | 314 | 1810 | 100 | 539 | 43 | 0 | 84 | 5.63 | 0 | 94.99
11:00 | 71 | 0 | 150 | 0 | 314 | 0 | 0 | 255 | 333 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 80 | 310 | 315 | 183 | 8 | 89 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 8 | 86 | 159 | 32 | 22 | 0.3 | 60 | 66 | 50 | 50 | 100 | 151 | 64 | 75 | 0 | 17 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.83 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 4.52 | 16 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 11 | 79 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 303 |  | 5181.65 | 1723.2 | 6904.85 | 3997 | 314 | 1798 | 100 | 542 | 43 | 0 | 86 | 24.85 | 0 | 94.99
12:00 | 71 | 0 | 150 | 0 | 345 | 0 | 0 | 256 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 221 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 340 | 355 | 204 | 8 | 86 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 8 | 90 | 155 | 32 | 22 | 0.3 | 60 | 66 | 50 | 50 | 130 | 162 | 62 | 73 | 0 | 18 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.08 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 4.62 | 16 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 81 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 322 |  | 5401 | 1747.7 | 7148.7 | 4193 | 314 | 1820 | 100 | 563 | 43 | 0 | 90 | 25.7 | 0 | 94.99
13:00 | 71 | 0 | 150 | 0 | 314 | 0 | 0 | 256 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 204 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | 100 | 310 | 310 | 185 | 8 | 87 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 2 | 33 | 14 | 88 | 158 | 32 | 22 | 0.3 | 60 | 66 | 50 | 50 | 130 | 148 | 63 | 73 | 0 | 18 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.65 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 4.55 | 50 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 81 | 0 | 160 | 0 | 0 | 214 | 0 | 10 | 0 | 0 | 0 | 150 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 337 |  | 5367.5 | 1845.5 | 7213 | 4128 | 313 | 1840 | 199 | 578 | 43 | 0 | 88 | 24 | 0 | 94.99
14:00 | 71 | 0 | 150 | 0 | 313 | 0 | 0 | 257 | 259 |  | 0 | 370 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 100 | 290 | 280 | 183 | 8 | 87 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 8 | 33 | 14 | 94 | 144 | 32 | 22 | 0.2 | 60 | 66 | 53 | 50 | 130 | 152 | 62 | 75 | 0 | 19 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 3.9 | 52 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 8 | 81 | 0 | 160 | 0 | 0 | 190 | 0 | 27 | 0 | 0 | 0 | 143 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 333 |  | 5176.3 | 1781.1 | 6957.4 | 4028 | 313 | 1682 | 203 | 574 | 43 | 0 | 94 | 20.4 | 0 | 94.99
15:00 | 71 | 0 | 152 | 0 | 315 | 0 | 0 | 257 | 292 |  | 0 | 340 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 24 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 205 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 290 | 285 | 196 | 8 | 86 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 8 | 8 | 14 | 86 | 144 | 8 | 22 | 0.6 | 60 | 66 | 11 | 10 | 100 | 148 | 62 | 50 | 0 | 18 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 2.9 | 30 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 8 | 82 | 0 | 160 | 0 | 0 | 150 | 0 | 29 | 0 | 0 | 0 | 80 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 340 |  | 4940.9 | 1722.8 | 6663.7 | 3920 | 313 | 1590 | 113 | 582 | 42 | 0 | 86 | 17.7 | 0 | 94.98
16:00 | 71 | 0 | 100 | 0 | 338 | 0 | 0 | 257 | 292 |  | 0 | 390 | 0 | 1 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 229 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 340 | 335 | 142 | 8 | 87 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 8 | 8 | 11 | 90 | 141 | 8 | 20 | 0.2 | 60 | 66 | 11 | 10 | 163 | 165 | 62 | 50 | 0 | 18 | 17 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 10 | 0 | 0 | 231 | 0 | 0 | 0 | 1.5 | 30 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 8 | 81 | 0 | 160 | 0 | 0 | 150 | 0 | 56 | 0 | 0 | 0 | 87 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 342 |  | 5047 | 1784.1 | 6831.1 | 3941 | 313 | 1764 | 89 | 583 | 42 | 0 | 90 | 9.1 | 0 | 94.99
17:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 256 | 312 |  | 0 | 390 | 0 | 34 | 0 | 0 | 230 | 0 | 0 | 0 | 4 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 19 | 3 | 0 | 0 | 80 | 260 | 260 | 172 | 8 | 87 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 11 | 92 | 127 | 30 | 22 | 0 | 60 | 66 | 53 | 38 | 130 | 145 | 63 | 50 | 0 | 48 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 10 | 0 | 0 | 230 | 6 | 0 | 14 | 0.1 | 68 | 0 | 0 | 0 | 0 |  | 313 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 2 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 8 | 81 | 0 | 160 | 0 | 0 | 175 | 0 | 103 | 0 | 11 | 0 | 150 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 20 | 340 |  | 4975 | 1913.1 | 6888.1 | 3787 | 313 | 1756 | 312 | 581 | 43 | 2 | 92 | 2.1 | 0 | 94.98
18:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 256 | 312 |  | 0 | 400 | 0 | 64 | 3 | 11 | 230 | 0 | 0 | 0 | 15 | 64 | 0 | 0 | 0 | 0 | 12 | 53 | 35 | 0 | 19 | 25 | 18 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 7 | 0 | 0 | 80 | 260 | 260 | 224 | 8 | 89 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 110 | 128 | 60 | 20 | 0 | 60 | 66 | 53 | 50 | 163 | 147 | 66 | 75 | 0 | 89 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 65 | 0 | 3 | 231 | 22 | 17 | 17 | 0 | 153 | 0 | 0 | 0 | 107 |  | 653 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 7 | 24 | 136 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 85 | 0 | 186 | 0 | 0 | 180 | 0 | 147 | 0 | 81 | 0 | 115 | 0 | 332 | 0 | 0 | 0 | 32 | 54 | 0 | 0 | 50 | 362 |  | 5652 | 2675 | 8327 | 3959 | 653 | 1866 | 1006 | 633 | 43 | 57 | 110 | 0 | 0 | 94.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 71 | 0 | 99 | 0 | 250 | 0 | 0 | 256 | 344 |  | 0 | 420 | 0 | 100 | 25 | 22 | 230 | 0 | 0 | 0 | 28 | 102 | 0 | 0 | 0 | 0 | 44 | 53 | 35 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 48 | 19 | 14 | 0 | 0 | 85 | 300 | 295 | 229 | 8 | 90 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 108 | 128 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 149 | 64 | 72 | 0 | 98 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 231 | 50 | 17 | 17 | 0 | 160 | 0 | 0 | 0 | 61 |  | 654 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 140 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 95 | 0 | 250 | 0 | 0 | 180 | 0 | 188 | 0 | 95 | 0 | 105 | 0 | 392 | 0 | 0 | 0 | 32 | 54 | 0 | 0 | 108 | 372 |  | 6050 | 2928 | 8978 | 4099 | 654 | 2009 | 1298 | 717 | 43 | 50 | 108 | 0 | 0 | 94.98
19:30 | 71 | 0 | 99 | 0 | 250 | 0 | 0 | 256 | 345 |  | 0 | 420 | 0 | 100 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 12 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 20 | 0 | 0 | 100 | 300 | 300 | 229 | 8 | 90 | 10 | 2 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 128 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 149 | 65 | 72 | 0 | 100 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 231 | 50 | 10 | 9 | 0 | 160 | 0 | 0 | 0 | 0 |  | 653 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 140 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 96 | 0 | 260 | 0 | 0 | 180 | 0 | 184 | 0 | 97 | 0 | 105 | 0 | 402 | 0 | 0 | 0 | 21 | 54 | 0 | 0 | 70 | 381 |  | 5840 | 2930 | 8770 | 4121 | 653 | 2031 | 1033 | 737 | 43 | 50 | 102 | 0 | 0 | 94.99
20:00 | 71 | 0 | 99 | 0 | 250 | 0 | 0 | 256 | 362 |  | 0 | 420 | 0 | 75 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 42 | 19 | 21 | 0 | 0 | 100 | 312 | 315 | 227 | 8 | 90 | 10 | 4 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 128 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 153 | 65 | 72 | 0 | 100 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 231 | 50 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 |  | 654 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 140 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 100 | 0 | 260 | 0 | 0 | 180 | 0 | 189 | 0 | 94 | 0 | 105 | 0 | 396 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 70 | 381 |  | 5736 | 2904 | 8640 | 4159 | 654 | 2040 | 851 | 741 | 43 | 50 | 102 | 0 | 0 | 94.97
21:00 | 71 | 0 | 101 | 0 | 250 | 0 | 0 | 256 | 364 |  | 0 | 420 | 0 | 55 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 26 | 0 | 0 | 120 | 300 | 305 | 228 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 102 | 128 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 148 | 64 | 72 | 0 | 100 | 17 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 231 | 50 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 |  | 654 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 140 | 21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 102 | 0 | 260 | 0 | 0 | 195 | 0 | 200 | 0 | 62 | 0 | 119 | 0 | 396 | 0 | 0 | 0 | 32 | 35 | 0 | 0 | 35 | 383 |  | 5620 | 2900 | 8520 | 3992 | 654 | 2043 | 891 | 745 | 43 | 50 | 102 | 0 | 0 | 94.99
22:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 256 | 324 |  | 0 | 420 | 0 | 50 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 38 | 0 | 0 | 120 | 300 | 305 | 183 | 8 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 98 | 128 | 73 | 22 | 0 | 60 | 66 | 53 | 50 | 130 | 146 | 66 | 72 | 0 | 100 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 0 |  | 552 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 105 | 0 | 250 | 0 | 0 | 200 | 0 | 185 | 0 | 63 | 0 | 112 | 0 | 350 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 370 |  | 5417 | 2498 | 7915 | 3961 | 552 | 1911 | 626 | 725 | 42 | 0 | 98 | 0 | 0 | 94.97
23:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 256 | 325 |  | 0 | 380 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 84 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 0 | 120 | 335 | 345 | 201 | 8 | 88 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 14 | 92 | 128 | 24 | 22 | 0 | 60 | 66 | 53 | 50 | 130 | 155 | 65 | 72 | 0 | 97 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 112 | 0 | 200 | 0 | 0 | 200 | 0 | 188 | 0 | 61 | 0 | 115 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 5130 | 2078 | 7208 | 4060 | 310 | 1890 | 202 | 613 | 41 | 0 | 92 | 0 | 0 | 94.97
24:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 255 | 374 |  | 0 | 380 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 25 | 33 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 80 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 80 | 316 | 305 | 196 | 8 | 88 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 84 | 149 | 24 | 22 | 0 | 60 | 66 | 5 | 50 | 163 | 152 | 45 | 40 | 0 | 97 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 116 | 0 | 171 | 0 | 0 | 170 | 0 | 187 | 0 | 34 | 0 | 113 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 |  | 4848 | 1823 | 6671 | 3885 | 213 | 1854 | 57 | 537 | 41 | 0 | 84 | 0 | 0 | 94.97
KWH | 1710000 | 0 | 2810000 | 0 | 6861009 | 0 | 0 | 6295072 | 7539000 |  | 0 | 8824750 | 0 | 410880 | 33744 | 39054 | 6484330 | 0 | 0 | 0 | 48000 | 467280 | 0 | 0 | 0 | 0 | 85824 | 607320 | 387861 | 0 | 266400 | 600000 | 704520 | 611300 | 814500 | 0 | 0 | 943500 | 0 | 0 | 3000000 | 0 | 4144437 | 0 | 2792336 | 0 |  | 0 | 0 | 0 | 0 | 0 | 160800 | 336144 | 380640 | 0 | 0 | 2153870 | 8018500 | 7292500 | 4467000 | 250909 | 2078100 | 593928 | 25920 | 0 | 782556 | 0 | 0 | 0 | 326556 | 109080 | 530900 | 293420 | 2079360 | 3303480 | 799680 | 380844 | 3050 | 1294000 | 1512600 | 849000 | 853560 | 3406090 | 3349000 | 1384896 | 1246080 | 0 | 1673700 | 290000 | 0 | 158040 | 7512000 | 358104 | 138048 | 0 | 0 | 0 | 0 | 4800 | 0 | 0 | 109080 | 199680 | 0 | 110400 | 5526000 | 231600 | 23652 | 61054 | 29640 | 1480364 | 0 | 0 | 0 | 157080 |  | 7940364 | 0 | 0 | 0 | 600960 | 0 | 0 | 0 | 0 | 7296 | 124500 | 2852000 | 351400 | 0 | 0 | 0 | 0 | 190512 | 0 | 0 | 144830 | 0 | 0 | 0 | 0 | 347760 | 50544 | 209268 | 2037381 | 0 | 4383800 | 0 | 0 | 4745673 | 0 | 1588000 | 0 | 501141 | 0 | 3593973 | 0 | 9440454 | 0 | 0 | 0 | 133776 | 170880 | 0 | 9586 | 362112 | 7185200 |  | 122806822 | 46971410 | 169778232 | 95493488 | 7940364 | 42519844 | 6846131 | 13606381 | 943500 | 197808 | 2079360 | 151356 | 0
Fuel Cost | 1915200 | 0 | 3006700 | 0 | 5077146.66 | 0 | 0 | 4532451.84 | 5729640 |  | 0 | 7059800 | 0 | 4190976 | 365447.52 | 400694.04 | 8040569.2 | 0 | 0 | 0 | 532800 | 4747564.8 | 0 | 0 | 0 | 0 | 803312.64 | 5824198.8 | 3700193.94 | 0 | 199800 | 450000 | 0 | 0 | 0 | 0 | 0 | 245310 | 0 | 0 | 4590000 | 0 | 4351658.85 | 0 | 3546266.72 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1505088 | 309252.48 | 1058179.2 | 0 | 0 | 2261563.5 | 5933690 | 6125700 | 4109640 | 245890.82 | 2763873 | 487020.96 | 26697.6 | 0 | 1119055.08 | 0 | 0 | 0 | 333087.12 | 81810 | 1003401 | 220065 | 14347584 | 2708853.6 | 7604956.8 | 388460.88 | 50020 | 1759840 | 2057136 | 1154640 | 1066950 | 4223551.6 | 3081080 | 2063495.04 | 2193100.8 | 0 | 2544024 | 461100 | 0 | 371394 | 5333520 | 268578 | 104916.48 | 0 | 0 | 0 | 0 | 46176 | 0 | 0 | 1258783.2 | 1861017.6 | 0 | 1034448 | 5194440 | 2031132 | 210739.32 | 576960.3 | 0 | 13648956.08 | 0 | 0 | 0 | 0 |  | 21438982.8 | 0 | 0 | 0 | 5793254.4 | 0 | 0 | 0 | 0 | 95577.6 | 1231305 | 2281600 | 544670 | 0 | 0 | 0 | 0 | 2122303.68 | 0 | 0 | 1501887.1 | 0 | 0 | 0 | 0 | 382536 | 83397.6 | 158415.876 | 12978116.97 | 0 | 17929742 | 0 | 0 | 4176192.24 | 0 | 1476840 | 0 | 796814.19 | 0 | 3162696.24 | 0 | 6891531.42 | 0 | 0 | 0 | 1191944.16 | 1596019.2 | 0 | 0 | 0 | 0 |  | 174539598.47 | 85833826.476 | 260373424.946 | 91226564.686 | 21438982.8 | 38281368.31 | 60399071.7 | 30907858.97 | 245310 | 2217881.28 | 14347584 | 1308803.2 | 0
Yesterday Day Peak | 71 | 0 | 150 | 0 | 345 | 0 | 0 | 256 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 221 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 340 | 355 | 204 | 8 | 86 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 8 | 90 | 155 | 32 | 22 | 0.3 | 60 | 66 | 50 | 50 | 130 | 162 | 62 | 73 | 0 | 18 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.08 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 4.62 | 16 | 0 | 0 | 0 | 0 |  | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 81 | 0 | 160 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 322 |  | 7148.7 | DayPeak
Yesterday Evening Peak | 71 | 0 | 99 | 0 | 250 | 0 | 0 | 256 | 344 | 0 | 0 | 420 | 0 | 100 | 25 | 22 | 230 | 0 | 0 | 0 | 28 | 102 | 0 | 0 | 0 | 0 | 44 | 53 | 35 | 0 | 19 | 25 | 31 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 202 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 19 | 14 | 0 | 0 | 85 | 300 | 295 | 229 | 8 | 90 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 108 | 128 | 95 | 22 | 0 | 60 | 66 | 53 | 50 | 163 | 149 | 64 | 72 | 0 | 98 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 231 | 50 | 17 | 17 | 0 | 160 | 0 | 0 | 0 | 61 |  | 654 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 140 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 95 | 0 | 250 | 0 | 0 | 180 | 0 | 188 | 0 | 95 | 0 | 105 | 0 | 392 | 0 | 0 | 0 | 32 | 54 | 0 | 0 | 108 | 372 |  | 8978 | EvPeak
Forecast for Evening | 71 | 0 | 150 | 0 | 360 | 0 | 0 | 260 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 0 | 0 | 120 | 25 | 210 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 0 | 0 | 100 | 360 | 360 | 225 | 55 | 90 | 43 | 0 | 0 | 45 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 104 | 163 | 95 | 22 | 0 | 60 | 66 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 150 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 652 | 40 | 0 | 0 | 115 | 200 | 0 | 0 | 36 | 70 | 40 | 140 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 85 | 0 | 250 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 127 | 0 | 430 | 105 | 200 | 113 | 100 | 113 | 0 |  | 113
Forecast for Day | 71 | 0 | 150 | 0 | 360 | 0 | 0 | 260 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 43 | 0 | 0 | 120 | 25 | 210 | 0 | 115 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 360 | 360 | 225 | 55 | 90 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 88 | 163 | 95 | 22 | 1.6 | 60 | 66 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 150 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 0 | 100 | 230 | 0 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 308 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 140 | 20 | 70 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 85 | 0 | 200 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 127 | 0 | 410 | 50 | 100 | 0 | 36 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 71 | 0 | 101 | 0 | 325 | 0 | 0 | 254 | 374 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 25 | 10 | 25 | 33 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 151 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 0 | 0 | 80 | 350 | 360 | 203 | 8 | 89 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 76 | 161 | 0 | 20 | 0.3 | 30 | 66 | 5 | 3 | 130 | 163 | 45 | 5 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 115 | 0 | 160 | 0 | 0 | 170 | 0 | 198 | 0 | 0 | 0 | 127 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 300 | 0
199
| Minimum Generation |  | 5472 | 5:00
| Highest Generation |  | 8978 | 19:00
| Day Peak Generation |  | 7148.7 | 12:00
| Evening Peak Generation |  | 8978 | 19:00
| HVDC Max Flow |  | 654 | 19:00
| HVDC EvPeak Flow |  | 654 | 19:00
| Load factor L.F |  | 78.79%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-01-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-01-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7148.7 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5518 | MW
Evening Peak Generation : |  | 8978 | MW Hour : | 19:00 | Available Max Generation : |  | 14500 | MW
E.P. Demand (at gen end) : |  | 8978 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8978 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5500 | MW
Total Gen. (MKWH) : |  | 169.7782 | System Load Factor : | 78.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -506 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-01-20
Actual : | 94.95 | Ft.(MSL) , | Rule curve : | 99.39 | Ft.( MSL )
Gas Consumed : | Total = | 1106.6 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129507932.996
: |  | Coal : | 30907858.97 | Oil : | 62616952.98 | Total : | 223032744.946
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3142.0566 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1062.6304 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 951.0405 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 858.9757 |  |  | 0 | 0%
) | 0 | 0:00 | 776.4478 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 626.5511 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 357.8552 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.519 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 483.1914 |  |  | 0 | 0%
Total | 0 |  | 8420.2678 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Shajibazar 330 MW GT-1
|  |  |  | 2) Summit Meghna 305 MW | 11) Sirajganj unit-3 ST
3) Ghorasal Unit-3,5
4) Baghabari 100 MW
5) Ashuganj unit-3
6) Bheramara 410 MW
7) Ashuganj Precision
8) Ashuganj unit-4
9) Bhola 225 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sirajganj unit-3 STG was shut down at 09:42 due to leakage at boiler side.
b) Chandpur-Cumilla(N) 132 kV Ckt-1 was under shut down from 10:46 to 11:21 for removing nest at Chandpur S/S.
c) Kaliakoir 400/230 kV T02 transformer was under shut down from 10:26 to 12:14 to attend R/H at 400 kV R-phase
Isolator nut.
d) Saver 132/33 kV T2 transformer was under shut down from 08:12 to 15:11 for A/M.
e) Mirpur 132 kV reserve bus was under shut down from 08:45 to 16:54 for A/M.
f) Cox's Bazar 132/33 kV T3 transformer was under shut down from 08:44 to 16:46 for A/M. |  |  |  |  | About 25 MW power interruption occurred under Cox's Bazar S/S area
from 08:44 to 16:46.
g) Khulshi-Baraulia 132 kV express Ckt was under shut down from 08:47 to 17:07 for A/M.
h) Gulshan 132/33 kV T1 transformer was under shut down from 09:58 to 12:29 for A/M.
i) Rampura-Gulshan 132 kV Ckt-2 was under shut down from 10:54 to 15:23 for A/M.
j) Bibiyana-Kaliakoir 400 kV Ckt-1 was under shut down from 08:31 to 17:12 for A/M.
k) Kallyanpur-Lalbag 132 kV Ckt-1 was under shut down from 08:56 to 20:07 for A/M.
l) Ashuganj-Comilla(N) 230 kV Ckt-2 was under shut down from 09:22 to 15:52 for A/M.
m) Munshiganj 132/33 kV T1 transformer was under shut down from 09:16 to 13:45 for A/M.
n) Mymensingh 132/33 kV T1 transformer was under shut down from 09:35 to 13:16 for A/M.
o) B.Baria-Narshingdi 132 kV Ckt-2 was under shut down from 08:52 to 15:44 for A/M.
p) Bakulia 132/33 kV T1 transformer was under shut down from 08:20 to 15:23 for A/M.
q) Ishwardi-Ghorashal 230 kV Ckt-2 was under shut down from 08:45 to 15:58 for A/M.
r) Saver 33 kV bus was under shut down from 10:24 to 11:46 for D/W.
s) Ishurdi 132/33 kV T2 transformer was under shut down from 09:10 to 16:22 for A/M.
t) Mymensingh 132/33 kV T3 transformer was under shut down from 13:22 to 15:25 for A/M.
u) Sirajganj unit-2 GT & ST was synchronized at 12:41 & 14:48 respectively.
v) Rajshahi(N)-Rajshahi(O) 132 kV Ckt-1 tripped from both end at 10:59 showing Dist. R-phase, Z1 at Rajshahi(N)
end & Dist. R-phase at Rajshahi(O) end and was switched on at 21:54.
w) Barapukuria 132/33 T3(New) transformer was switched on at 16:45.
x) Ashuganj Network-Ashuganj Precision 132 kV Ckt was switched on at 16:20.
y) Sikalbaha 225 MW CCPP tripped at 20:21 due to GBC problem and GT synchronized at 22:30.
z) Barishal(S)-Patuakhali 132 kV single Ckt was shut down at 06:49(20/01/2020) for A/M. |  |  |  |  | About 40 MW power interruption has been occurring under Patuakhali S/S
area since 06:49(20/01/2020).
aa) Joydevpur-Kodda 132 kV Ckt-1 tripped from both end at 06:53(20/01/2020) showing Dist. R-phase at Joydevpur
end & Dist. Z2 at Kodda end.
ab) Sylhet 132/33 kV T1 transformer was shut down at 07:32(20/01/2020) for C/M.
ac) Bogura(O)-Bogura(N) 132 kV Ckt-2 was shut down at 07:51(20/01/2020) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-01-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 71 | 1710000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 99 | 2810000 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6861009 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 256 | 6295072 | Gas shortage.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 344 | 7539000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8824750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 410880
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 25 | 33744 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 22 | 39054 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 266400
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 28 | 48000 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 230 | 6484330 | Gas shortage.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 467280
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 44 | 85824 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 607320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 387861 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1304520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 611300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 814500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 23652 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2229 | 45624496
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 109080
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 160800
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 43 | 943500 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4144437 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2792336 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 61054 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 199680 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 336144
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 380640
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29640
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 160 | 1480364 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 852 | 13637675
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 85 | 2153870 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 229 | 4467000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 8018500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7292500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 593928 | Machine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 0 | 25920 | Under maint.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 250909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 782556 | Machine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 110400 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2078100 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 326556
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 109080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2079360
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 530900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 293420 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 61 | 157080 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1309 | 29270079
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 128 | 3303480 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 380844
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 799680
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3050
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 4800 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 50 | 231600 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 295 | 4723454
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1294000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1512600
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3406090
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 149 | 3349000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 849000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 853560
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 138048 | Engine problem
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1384896 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1246080 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 98 | 1673700 | Machine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 290000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 358104
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7512000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 231 | 5526000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 158040
| Sylhet Area Total |  |  |  | 1949 | 1365 | 29551118
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 654 | 7940364
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 600960 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 7296 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 124500 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 32 | 133776 | Low demand
| Khulna Area Total |  |  |  | 2314 | 818 | 8806896
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 351400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 140 | 2852000 | ST Under S/D.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 501141
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 372 | 7185200 | On test
| Barisal Area Total |  |  |  | 462 | 627 | 10889741
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 190512
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 25 | 144830 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4745673 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 1588000 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 105 | 3593973 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 9440454 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 347760
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 3 | 50544 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 209268
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 108 | 362112
| Rajshahi Area Total |  |  |  | 2183 | 1084 | 20673126
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 95 | 2037381
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 4383800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 54 | 170880 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 9586
| Rangpur Area Total |  |  |  | 605 | 399 | 6601647
| Total |  |  |  | 19107 | 8978 | 169778232
| Eastern Grid Total |  |  |  | 13543 | 6050 | 122806822
| Western Grid Total |  |  |  | 5564 | 2928 | 46971410
| National Grid Total |  |  |  | 19107 | 8978 | 169778232
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-01-19
(a) ENTIRE EASTERN GRID : |  | 5606 | MW | (b) ENTIRE WESTERN GRID : |  | 2778 | MW
i) Dhaka area |  | 3037 | MW | i) Khulna area |  | 1056 | MW
ii) Chittagong area |  | 843 | MW | ii) Rajshahi area |  | 902 | MW
iii) Comilla area |  | 719 | MW | iii) Barisal area |  | 244 | MW
iv) Mymensingh area |  | 692 | MW | iv) Rangpur area |  | 576 | MW
v) Sylhet area |  | 315 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8384 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 12:00 | Shahjibazar | 77 | 19:00 | Bottail | 100 | 18:30
Munsiganj | 78 | 19:30 | Fenchuganj | 25 | 18:30 | G.K Project | 27 | 19:00
Sonargaon | 68 | 18:00 | Kulawara | 28 | 20:00 | Faridpur | 130 | 20:00
Shyampur | 170 | 0:00 | Sylhet | 100 | 18:30 | Madaripur | 57 | 19:30
Bhulta | 164 | 16:00 | Chatak | 20 | 18:00 | Sariatpur | 40 | 19:30
Madanganj | 54 | 18:30 | Sunamganj | 26 | 18:30 | Gopalganj | 66 | 19:00
Shitalakhya | 93 | 12:00 | Biani Bazar | 28 | 18:30 | Bagerhat | 63 | 18:30
Rahim steel | 11 | 0:00 | Comilla (S) | 110 | 18:00 | Mongla | 40 | 9:00
Matuail | 80 | 9:00 | Comilla(N) | 75 | 18:30 | Satkhira | 71 | 19:30
Ghorasal | 64 | 19:00 | Chandpur | 58 | 20:00 | Gallamari | 32 | 9:00
Narsingdi | 108 | 18:30 | Feni | 91 | 18:30 | Magura | 38 | 18:30
Haripur (SBU) | 91 | 22:00 | Chowmuhani | 110 | 21:00 | Norail | 26 | 18:30
Ullon | 48 | 18:30 | Ashuganj | 39 | 18:00 | Chuadanga | 61 | 18:30
Hasnabad | 126 | 19:00 | Daudkandi | 88 | 21:00 | Barisal(N) | 31 | 18:30
Magbazar | 73 | 13:00 | B.Baria | 90 | 19:30 | Barisal (S) | 68 | 19:00
Maniknagar | 78 | 12:00 | Ramganj | 68 | 18:30 | Patuakhali | 86 | 18:30
Bangabhaban | 16 | 12:00 | Chaddagram | 14 | 18:00 | Bhandaria | 40 | 19:30
Narinda | 58 | 14:00 | PHP | 2.6 | 16:00 | Borhan Uddin | 24 | 20:00
Dhanmondi | 92 | 12:00 | Madunaghat | 41 | 18:30 | Ishurdi | 43 | 18:00
Lalbag | 79 | 18:00 | Hathazari | 70 | 18:30 | Ruppur Paromanobik | 1 | 1:00
Madartek | 44 | 18:30 | Khulshi | 134 | 18:30 | Natore | 85 | 19:00
Mirpur | 71 | 18:00 | Halishahar | 89 | 18:30 | Bogra | 120 | 18:00
Kalyanpur | 75 | 18:00 | Baraulia | 140 | 10:00 | Noagaon | 91 | 19:30
Gulshan | 94 | 18:00 | Sikalbaha | 19 | 18:00 | Rajshahi | 90 | 19:30
Uttara | 51 | 13:00 | Dohazari | 64 | 19:00 | Rajshahi New | 10 | 19:00
Uttara New | 30 | 13:00 | Cox'sbazar | 75 | 19:30 | C.Nawabganj | 57 | 19:00
Kamrangirchar | 60 | 12:00 | Chandraghona | 32 | 18:00 | Amnura | 26 | 19:00
Savar | 91 | 18:00 | Kaptai | 3.5 | 18:00 | Pabna | 72 | 19:30
Bhasantec | 102 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 82 | 19:30
Agargaon | 37 | 13:00 | Bakulia | 74 | 18:30 | Serajganj | 66 | 19:30
Satmosjid | 65 | 18:00 | Julda | 21 | 18:00 | Niyamatpur | 65 | 19:30
Tongi | 83 | 18:00 | TK chemical | 10 | 18:30 | Joypurhat | 44 | 18:30
Kabirpur | 183 | 11:00 | Modern Steel | 16 | 10:00 | Sherpur(Bogura) | 36 | 18:00
Basundhara | 85 | 19:00 | Shahmirpur | 22 | 18:30 | Mohastangor | 30 | 18:00
Manikganj | 59 | 19:00 | Khagrachhari | 16 | 19:00 | Rangpur | 104 | 18:30
Joydevpur | 160 | 18:30 | Matarbari | 22 | 18:00 | Lalmonirhat | 41 | 19:00
New Tongi | 65 | 18:00 | Baroiar Hat | 18 | 18:00 | Saidpur | 91 | 18:30
Korda | 174 | 18:00 | Rangamati | 6 | 7:00 | Purbasadipur | 91 | 20:00
Dhamrai | 46 | 18:30 | Abul Khair 230 | 128 | 23:00 | Thakurgaon | 59 | 19:00
Valuka | 74 | 18:00 | BSRM | 108 | 16:00 | Palashbari | 88 | 18:30
Tangail | 126 | 19:30 | GPH Ispat | 54 | 12:00 | Barapukuria | 39 | 18:30
Mymensing | 156 | 18:30 | Goalpara | 6 | 20:00 | Panchagar | 37 | 18:30
Kishorganj | 90 | 19:30 | Central s/s | 78 | 18:30 | Joldhaka | 13 | 19:30
Netrokona | 102 | 19:00 | Noapara | 41 | 8:00 | Kurigram | 40 | 19:00
Jamalpur | 88 | 18:00 | Jessore | 98 | 18:30
Sherpur | 76 | 18:00 | Benapol | 32 | 8:00
Srimongal | 23 | 18:00 | Jhenida | 81 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-01-19 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 401 | 0.16667 | 395 | 0.41667 | Kaliakoir | 387 | 0.20833 | 364 | 0.66667
Bheramara | 409 | 0.125 | 397 | 0.375 | Bhulta | 394 | 0.16667 | 382 | 0.5
Ashuganj(N) | 398 | 0.16667 | 388 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 236 | 0.041667 | 230 | 0.66667 | Hathazari | 224 | 0.125 | 217 | 0.5
Ishurdi | 238 | 0.083333 | 224 | 0.77083 | Megnaghat | 237 | 0.16667 | 226 | 0.625
Ashuganj | 240 | 0.041667 | 234 | 0.29167 | Fenchuganj | 242 | 0.375 | 237 | 0.66667
Serajganj | 235 | 0.16667 | 228 | 0.33333 | Siddhirganj | 235 | 0.16667 | 227 | 0.5
Baghabari | 241 | 0.20833 | 236 | 0.29167 | Maniknagar | 233 | 0.083333 | 225 | 0.5
Barapukuria | 234 | 0.125 | 228 | 0.33333 | Old Airport | 233 | 0.16667 | 221 | 0.66667
Bogra | 230 | 0.58333 | 222 | 0.33333 | Barisal | 239 | 0.125 | 235 | 0.875
Khulna South | 239 | 0.083333 | 213 | 0.33333 | AKSML | 222 | 0.91667 | 214 | 0.5
Rampura | 230 | 0.041667 | 226 | 0.5 | BSRM | 225 | 0.79167 | 218 | 0.66667
Haripur | 231 | 24:00 | 224 | 0.66667 | Bibiyana | 240 | 0.16667 | 236 | 0.625
Hasnabad | 231 | 0.041667 | 220 | 0.5 | Bhulta | 236 | 0.16667 | 226 | 0.5
Aminbazar | 233 | 0.125 | 222 | 0.5 | Ashuganj (S) | 239 | 0.16667 | 233 | 0.66667
Tongi | 231 | 0.16667 | 221 | 0.5 | Kaliakoir | 235 | 0.20833 | 223 | 0.5
Comilla (N) | 237 | 0.20833 | 231 | 0.54167 | GPH | 222 | 0.79167 | 214 | 0.66667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.041667 | 128 | 0.66667 | Halishahar | 135 | 0.91667 | 127 | 0.5
Munsiganj | 136 | 0.77083 | 127 | 0.5 | Baraulia | 132 | 0.75 | 127 | 0.625
Sonargaon | 133 | 0.77083 | 127 | 0.5 | Sikalbaha | 134 | 0.91667 | 128 | 0.5
Shyampur | 134 | 0.041667 | 129 | 0.5 | Dohazari | 131 | 0.95833 | 127 | 0.58333
Bhulta | 129 | 0.20833 | 123 | 0.45833 | Cox'sbazar | 127 | 0.16667 | 121 | 0.8125
Madanganj | 134 | 0.16667 | 125 | 0.5 | Chandraghona | 134 | 0.91667 | 128 | 0.5
Shitalakhya | 1231 | 0.95833 | 125 | 0.5 | Kaptai | 133 | 0.5 | 130 | 0.33333
Rahim steal | 134 | 1:00 | 129 | 0.5 | A. Khaer Stl. | 130 | 0.041667 | 128 | 0.45833
Matuail | 133 | 0.041667 | 127 | 0.5 | Bakulia | 132 | 0.91667 | 126 | 0.5
Ghorasal | 140 | 0.041667 | 138 | 0.58333 | Julda | 131 | 0.75 | 127 | 0.29167
Narsinghdi | 132 | 0.041667 | 124 | 0.33333 | TK Chemical | 134 | 0.91667 | 127 | 0.5
Haripur (SBU) | 134 | 0.041667 | 129 | 0.5 | Modern Steel | 131 | 0.77083 | 103 | 0.75
Ullon | 129 | 0.25 | 124 | 0.5 | Shahmirpur | 132 | 0.77083 | 127 | 0.5
Hasnabad | 135 | 0.25 | 127 | 0.5 | Khagrachhari | 133 | 0.91667 | 127 | 0.5
Magbazar | 131 | 0.25 | 124 | 0.5 | Matarbari | 130 | 0.083333 | 124 | 0.625
Maniknagar | 137 | 0.25 | 132 | 0.5 | Baroiar Hat | 132 | 0.041667 | 130 | 0.54167
Bangabhaban | 137 | 0.25 | 132 | 0.5 | Rangamati | 133 | 0.91667 | 128 | 0.5
Narinda | 137 | 0.25 | 132 | 0.5 | Goalpara | 137 | 0.125 | 122 | 8:00
Dhanmondi | 129 | 0.25 | 124 | 0.5 | Central s/s | 135 | 0.041667 | 122 | 8:00
Lalbag | 134 | 0.20833 | 123 | 0.5 | Noapara | 136 | 0.083333 | 121 | 0.33333
Madartek | 130 | 0.25 | 123 | 0.5 | Jessore | 134 | 0.083333 | 116 | 0.33333
Mirpur | 134 | 1;00 | 125 | 0.66667 | Benapol | 134 | 0.041667 | 119 | 0.33333
Kalyanpur | 136 | 1;00 | 130 | 0.66667 | Jhenida | 132 | 0.041667 | 116 | 0.33333
Gulshan | 129 | 06;00 | 123 | 0.66667 | Bottail | 133 | 0.041667 | 122 | 0.77083
Uttara | 134 | 06;00 | 127 | 0.66667 | G.K Project | 139 | 0.20833 | 130 | 0.33333
Uttara New | 134 | 06;00 | 127 | 0.66667 | Faridpur | 138 | 0.16667 | 131 | 0.77083
Kamrangirchar | 135 | 06;00 | 124 | 0.5 | Madaripur | 139 | 0.41667 | 135 | 0.16667
Savar | 133 | 06;00 | 127 | 0.70833 | Sariatpur | 139 | 0.16667 | 134 | 0.83333
Bhasantec | 135 | 06;00 | 126 | 16;00 | Gopalganj | 142 | 0.16667 | 136 | 0.8125
Agargaon | 135 | 06;00 | 128 | 0.70833 | Bagerhat | 132 | 0.16667 | 115 | 0.33333
Satmosjid | 135 | 06;00 | 128 | 12;00 | Mongla | 129 | 0.083333 | 115 | 0.33333
Tongi | 138 | 0.16667 | 130 | 0.375 | Satkhira | 135 | 0.083333 | 118 | 0.33333
Kabirpur | 132 | 0.041667 | 125 | 0.625 | Gallamari | 136 | 0.083333 | 122 | 0.33333
Basundhara | 130 | 2:00 | 123 | 0.54167 | Magura | 133 | 0.083333 | 116 | 0.77083
Manikganj | 138 | 5:00 | 130 | 0.66667 | Norail | 131 | 0.16667 | 114 | 0.77083
Joydevpur | 142 | 0.125 | 136 | 0.5 | Chuadanga | 129 | 0.16667 | 111 | 0.77083
New Tongi | 137 | 0.16667 | 130 | 0.5 | Barisal(N) | 140 | 0.41667 | 136 | 0.77083
Kodda | 134 | 0.041667 | 125 | 0.625 | Barisal (S) | 138 | 0.125 | 135 | 0.75
Dhamrai | 133 | 0.083333 | 124 | 0.66667 | Patuakhali | 135 | 0.16667 | 129 | 0.77083
Valuka | 126 | 0.58333 | 114 | 0.375 | Bhandaria | 138 | 0.16667 | 133
Tangail | 132 | 0.041667 | 123 | 0.66667 | Ishurdi | 135 | 0.083333 | 127 | 0.77083
Mymensing | 126 | 0.083333 | 118 | 0.33333 | Ruppur Paromanobik | 135 | 0.041667 | 129 | 0.77083
Kishorganj | 131 | 0.20833 | 125 | 0.66667 | Natore | 133 | 0.125 | 123 | 0.33333
Netrokona | 125 | 0.20833 | 115 | 0.375 | Bogra | 136 | 0.125 | 128 | 0.33333
Jamalpur | 131 | 0.875 | 114 | 0.29167 | Noagaon | 132 | 0.125 | 123 | 0.33333
Sherpur | 128 | 0.83333 | 114 | 0.33333 | Rajshahi | 130 | 0.083333 | 121 | 0.33333
Srimongal | 139 | 0.041667 | 137 | 0.70833 | Rajshahi New | 128 | 0.041667 | 117 | 0.33333
Shahjibazar | 136 | 0.041667 | 134 | 0.79167 | C.Nawabganj | 128 | 0.041667 | 116 | 0.33333
Fenchuganj | 140 | 0.41667 | 137 | 0.66667 | Amnura | 126 | 0.041667 | 117 | 0.29167
Khulawara | 139 | 0.20833 | 138 | 1:00 | Pabna | 135 | 0.16667 | 127 | 0.33333
Sylhet | 137 | 0.041667 | 135 | 0.625 | Shahjadpur | 140 | 0.041667 | 135 | 0.33333
Chatak | 136 | 0.041667 | 134 | 0.66667 | Serajganj | 137 | 0.16667 | 129 | 0.33333
Sunamganj | 137 | 0.041667 | 135 | 0.45833 | Niyamatpur | 130 | 0.16667 | 122 | 0.77083
Biani Bazar | 137 | 0.041667 | 136 | 0.5 | Joypurhat | 133 | 0.041667 | 124 | 0.33333
Comilla(s) | 131 | 0.083333 | 127 | 0.375 | Sherpur(Bogura) | 135 | 0.041667 | 128 | 0.33333
Comilla(n) | 139 | 0.77083 | 135 | 0.5 | Mohastangor | 135 | 0.16667 | 127 | 0.33333
Chandpur | 137 | 8:00 | 135 | 0.58333 | Rangpur | 131 | 0.16667 | 125 | 0.33333
Feni | 136 | 0.79167 | 130 | 0.625 | Lalmonirhat | 128 | 0.125 | 121 | 0.33333
Chowmuhani | 134 | 0.75 | 130 | 0.8125 | Saidpur | 130 | 0.041667 | 122 | 0.33333
Ashuganj | 137 | 0.16667 | 135 | 0.33333 | Purbasadipur | 129 | 0.625 | 120 | 0.375
Daudkandi | 134 | 0.75 | 130 | 0.5 | Thakurgaon | 128 | 0.16667 | 120 | 0.33333
B.Baria | 134 | 0.91667 | 132 | 0.625 | Palashbari | 130 | 0.125 | 121 | 0.33333
Ramganj | 131 | 0.91667 | 129 | 0.75 | Barapukuria | 134 | 0.125 | 128 | 0.33333
Chaddagram | 136 | 0.75 | 132 | 0.5 | Panchagar | 125 | 0.16667 | 112 | 0.77083
PHP | 134 | 0.79167 | 128 | 0.5 | Joldhaka | 131 | 0.16667 | 122 | 0.77083
Madanhat | 134 | 0.083333 | 130 | 0.625 | Kurigram | 132 | 0.16667 | 123 | 0.33333
Hathazari | 135 | 0.91667 | 130 | 0.5
Khulshi | 130 | 0.16667 | 125 | 0.5

## L-Curve
Date | 2020-01-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 222 | 4848 | 1823 | 6671 |  |  |  | QF-LDC-12
0:30 | 276 | 4719.5 | 1711 | 6430.5 | Date: | 2020-01-19
1:00 | 330 | 4591 | 1599 | 6190
1:30 | 308.5 | 4463.5 | 1573 | 6036.5
2:00 | 287 | 4336 | 1547 | 5883
2:30 | 281 | 4268 | 1538 | 5806 | [5 empty] | Gen. at Eve. Peak | 8978 | 8978 MW (19:00 )
3:00 | 275 | 4200 | 1529 | 5729 | [6 empty] | 19:00
3:30 | 282.5 | 4184.5 | 1476 | 5660.5 | [5 empty] | Gen. at Day Peak | 7148.7 | 7148.7 MW (12:00 )
4:00 | 290 | 4169 | 1423 | 5592 | [6 empty] | 12:00
4:30 | 336 | 4172 | 1360 | 5532 | [5 empty] | Highest Generation | 8978
5:00 | 382 | 4175 | 1297 | 5472 | [6 empty] | 19:00
5:30 | 367 | 4271.5 | 1354 | 5625.5
6:00 | 352 | 4368 | 1411 | 5779
6:30 | 429 | 4551.141 | 1441.5 | 5992.641
7:00 | 506 | 4734.282 | 1472 | 6206.282
7:30 | 496 | 4924.66 | 1623.605 | 6548.265
8:00 | 486 | 5115.038 | 1775.21 | 6890.248
8:30 | 395 | 5170.6255 | 1788.455 | 6959.0805
9:00 | 304 | 5226.213 | 1801.7 | 7027.913
9:30 | 295.5 | 5238.3715 | 1749.4 | 6987.7715
10:00 | 287 | 5250.53 | 1697.1 | 6947.63
10:30 | 245.5 | 5216.09 | 1710.15 | 6926.24
11:00 | 204 | 5181.65 | 1723.2 | 6904.85
11:30 | 207.5 | 5291.325 | 1735.45 | 7026.775
12:00 | 211 | 5401 | 1747.7 | 7148.7
12:30 | 211.5 | 5384.25 | 1796.6 | 7180.85
13:00 | 212 | 5367.5 | 1845.5 | 7213
13:30 | 194.5 | 5271.9 | 1813.3 | 7085.2
14:00 | 177 | 5176.3 | 1781.1 | 6957.4
14:30 | 109 | 5058.6 | 1751.95 | 6810.55
15:00 | 41 | 4940.9 | 1722.8 | 6663.7
15:30 | 24.5 | 4993.95 | 1753.45 | 6747.4
16:00 | 8 | 5047 | 1784.1 | 6831.1
16:30 | 18 | 5011 | 1848.6 | 6859.6
17:00 | 28 | 4975 | 1913.1 | 6888.1
17:30 | 30.5 | 5313.5 | 2294.05 | 7607.55
18:00 | 33 | 5652 | 2675 | 8327
18:30 | 54 | 5851 | 2801.5 | 8652.5
19:00 | 75 | 6050 | 2928 | 8978
19:30 | 74 | 5840 | 2930 | 8770
20:00 | 9 | 5736 | 2904 | 8640 |  |  |  | Executive Engineer
20:30 | 31 | 5678 | 2902 | 8580 |  |  |  | Network Operation Division
21:00 | 53 | 5620 | 2900 | 8520
21:30 | 52.5 | 5518.5 | 2699 | 8217.5
22:00 | 52 | 5417 | 2498 | 7915 |  |  |  |  | Page 6 of 7
22:30 | 107.5 | 5273.5 | 2288 | 7561.5
23:00 | 163 | 5130 | 2078 | 7208
23:30 | 192.5 | 4989 | 1950.5 | 6939.5
24:00 | 222 | 4848 | 1823 | 6671
8978 MW (19:00 )
7148.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-01-19 |  | Energy | 169778232
[10 empty] | 2020-01-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3885 | 213 | 1854 | 202 | 537 | 41 | 0 | 0 | 84
0:30 | 3888 | 174.5 | 1707.5 | 114.5 | 497 | 41.5 | 0 | 0 | 80 | Date: | 2020-01-19
1:00 | 3891 | 136 | 1561 | 27 | 457 | 42 | 0 | 0 | 76
1:30 | 3757 | 136 | 1551.5 | 18.5 | 457.5 | 42 | 0 | 0 | 74 | [7 empty] | Total Energy | 169.7782 | Total Energy Gen 169.778 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.778 MKWHr
2:00 | 3623 | 136 | 1542 | 10 | 458 | 42 | 0 | 0 | 72 | [7 empty] | Energy not Served | 0
2:30 | 3576 | 136 | 1511.5 | 10 | 459.5 | 42 | 0 | 0 | 71 | [7 empty] | Energy Requirement | 169.7782
3:00 | 3529 | 136 | 1481 | 10 | 461 | 42 | 0 | 0 | 70
3:30 | 3503 | 136 | 1437 | 10 | 462 | 42.5 | 0 | 0 | 70 | [6 empty] | Shortage
4:00 | 3477 | 136 | 1393 | 10 | 463 | 43 | 0 | 0 | 70
4:30 | 3476.5 | 136 | 1334 | 10 | 462.5 | 43 | 0 | 0 | 70
5:00 | 3476 | 136 | 1275 | 10 | 462 | 43 | 0 | 0 | 70
5:30 | 3538 | 136 | 1367.5 | 10 | 461 | 43 | 0 | 0 | 70
6:00 | 3600 | 136 | 1460 | 10 | 460 | 43 | 0 | 0 | 70
6:30 | 3720 | 136 | 1546 | 10 | 465 | 43 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3840 | 136 | 1632 | 10 | 470 | 43 | 0 | 0 | 74
7:30 | 3936.5 | 225 | 1743.5 | 21.5 | 497.5 | 43 | 0 | 0 | 76 |  |  |  | Oil |  |  |  | ,
8:00 | 4033 | 314 | 1855 | 33 | 525 | 43 | 0 | 0 | 78
8:30 | 4028 | 314 | 1891.5 | 64 | 532 | 43 | 0 | 0 | 80
9:00 | 4023 | 314 | 1928 | 95 | 539 | 43 | 0 | 0 | 82
9:30 | 4037.5 | 314 | 1869 | 97.5 | 539 | 43 | 0 | 0 | 83
10:00 | 4052 | 314 | 1810 | 100 | 539 | 43 | 0 | 0 | 84
10:30 | 4024.5 | 314 | 1804 | 100 | 540.5 | 43 | 0 | 0 | 85
11:00 | 3997 | 314 | 1798 | 100 | 542 | 43 | 0 | 0 | 86
11:30 | 4095 | 314 | 1809 | 100 | 552.5 | 43 | 0 | 0 | 88
12:00 | 4193 | 314 | 1820 | 100 | 563 | 43 | 0 | 0 | 90
12:30 | 4160.5 | 313.5 | 1830 | 149.5 | 570.5 | 43 | 0 | 0 | 89
13:00 | 4128 | 313 | 1840 | 199 | 578 | 43 | 0 | 0 | 88
13:30 | 4128 | 313 | 1840 | 199 | 578 | 43 | 0 | 0 | 88
14:00 | 4128 | 313 | 1840 | 199 | 578 | 43 | 0 | 0 | 88
14:30 | 4024 | 313 | 1715 | 156 | 580 | 42.5 | 0 | 0 | 87
15:00 | 3920 | 313 | 1590 | 113 | 582 | 42 | 0 | 0 | 86
15:30 | 3930.5 | 313 | 1677 | 101 | 582.5 | 42 | 0 | 0 | 88
16:00 | 3941 | 313 | 1764 | 89 | 583 | 42 | 0 | 0 | 90
16:30 | 3864 | 313 | 1760 | 200.5 | 582 | 42.5 | 1 | 0 | 91
17:00 | 3787 | 313 | 1756 | 312 | 581 | 43 | 2 | 0 | 92
17:30 | 3873 | 483 | 1811 | 659 | 607 | 43 | 29.5 | 0 | 101
18:00 | 3959 | 653 | 1866 | 1006 | 633 | 43 | 57 | 0 | 110
18:30 | 4029 | 653.5 | 1937.5 | 1152 | 675 | 43 | 53.5 | 0 | 109
19:00 | 4099 | 654 | 2009 | 1298 | 717 | 43 | 50 | 0 | 108
19:30 | 4121 | 653 | 2031 | 1033 | 737 | 43 | 50 | 0 | 102
20:00 | 4159 | 654 | 2040 | 851 | 741 | 43 | 50 | 0 | 102
20:30 | 4075.5 | 654 | 2041.5 | 871 | 743 | 43 | 50 | 0 | 102
21:00 | 3992 | 654 | 2043 | 891 | 745 | 43 | 50 | 0 | 102
21:30 | 3976.5 | 603 | 1977 | 758.5 | 735 | 42.5 | 25 | 0 | 100
22:00 | 3961 | 552 | 1911 | 626 | 725 | 42 | 0 | 0 | 98
22:30 | 4010.5 | 431 | 1900.5 | 414 | 669 | 41.5 | 0 | 0 | 95
23:00 | 4060 | 310 | 1890 | 202 | 613 | 41 | 0 | 0 | 92
23:30 | 3972.5 | 261.5 | 1872 | 202 | 575 | 41 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 28.0° C
24:00 | 3885 | 213 | 1854 | 202 | 537 | 41 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 169.778 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 169.778 MKWHr
Note on W13: Author:

## Generation
2020-01-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 | 43 |  | 43 | 43 | 43 | 43 | 42 | 41 | 41 | 943500
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7.4 |  |  | 18.83 | 19.08 | 18.65 | 15.2 | 13.4 | 6.3 | 1.9 | [9 empty] | 109080
6 | Sikalbaha 225MW CCPP (Gas) | 189 | 184 | 182 | 184 | 197 | 202 | 197 | 182 | 204 | 203 | 203 | 221 | 204 | 203 | 205 | 229 | 202 | 203 |  | 202 | 202 | 203 | 0 |  | 84 | 80 | 4144437
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 103 | 70 | 70 | 70 | 70 | 70 | 116 | 104 | 104 | 104 | 104 | 108 | 142 | 140 | 145 | 147 | 104 | 139 |  | 139 | 139 | 139 | 139 | 140 | 140 | 140 | 2792336
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 14 | 17 |  | 17 | 9 | 0 |  |  |  | 0 | 61054
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 255 | 254 | 253 | 250 | 230 | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 260 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 6484330
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 250909
20 | Ghorasal TPP (Unit-1&2) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1710000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 103 | 99 | 100 | 99 | 100 | 102 | 100 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 152 | 100 | 100 | 100 |  | 99 | 99 | 99 | 101 | 100 | 100 | 100 | 2810000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 313 | 313 | 314 | 345 | 314 | 313 | 315 | 338 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6861009
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 80 | 80 |  | 85 | 100 | 100 | 120 | 120 | 120 | 80 | 2153870
32 | Ashuganj 50 MW PP | 43 | 5 | 5 | 5 | 5 | 5 | 18 | 40 | 40 | 43 | 40 | 40 | 43 | 43 | 43 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 43 | 40 | 40 | 593928
33 | Ashuganj 225 MW CCPP | 175 | 162 | 166 | 164 | 162 | 182 | 181 | 164 | 183 | 184 | 183 | 204 | 185 | 183 | 196 | 142 | 172 | 224 |  | 229 | 229 | 227 | 228 | 183 | 201 | 196 | 4467000
34 | Ashuganj 450 MW CCPP(South) | 290 | 265 | 265 | 265 | 300 | 300 | 305 | 315 | 315 | 315 | 315 | 355 | 310 | 280 | 285 | 335 | 260 | 260 |  | 295 | 300 | 315 | 305 | 305 | 345 | 305 | 7292500
| Ashuganj 450 MW CCPP(North) | 305 | 280 | 270 | 270 | 305 | 305 | 310 | 310 | 310 | 370 | 310 | 340 | 310 | 290 | 290 | 340 | 260 | 260 |  | 300 | 300 | 312 | 300 | 300 | 335 | 316 | 8018500
35 | Ashuganj 55 MW PP (Precision) | [20 empty] | 2 | 4 | 5 | 5 | 5 | 5 | 25920
36 | Chandpur 150 MW CCPP | 86 | 86 | 86 | 87 | 87 | 86 | 86 | 86 | 88 | 89 | 89 | 86 | 87 | 87 | 86 | 87 | 87 | 89 |  | 90 | 90 | 90 | 90 | 89 | 88 | 88 | 2078100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 255 | 255 | 256 | 256 | 257 | 257 | 257 | 256 | 256 |  | 256 | 256 | 256 | 256 | 256 | 256 | 255 | 6295072
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 320 | 300 | 300 | 300 | 330 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 370 | 340 | 390 | 390 | 400 |  | 420 | 420 | 420 | 420 | 420 | 380 | 380 | 8824750
41 | Haripur 360MW CCPP(HPL) | 320 | 320 | 260 | 260 | 230 | 300 | 330 | 330 | 364 | 332 | 333 | 332 | 332 | 259 | 292 | 292 | 312 | 312 |  | 344 | 345 | 362 | 364 | 324 | 325 | 374 | 7539000
42 | RPCL 210MW CCPP | 161 | 163 | 111 | 111 | 111 | 111 | 159 | 163 | 160 | 159 | 159 | 155 | 158 | 144 | 144 | 141 | 127 | 128 |  | 128 | 128 | 128 | 128 | 128 | 128 | 149 | 3303480
43
44 | Fenchugonj CCPP Phase-1 | 60 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1294000
45 | Fenchugonj CCPP Phase-2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1512600
46 | Shajibazar 330 MW CCPP | 136 | 132 | 134 | 135 | 134 | 163 | 163 | 152 | 148 | 148 | 151 | 162 | 148 | 152 | 148 | 165 | 145 | 147 |  | 149 | 149 | 153 | 148 | 146 | 155 | 152 | 3349000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 68 | 67 | 66 | 64 | 62 | 63 | 62 | 62 | 62 | 63 | 66 |  | 64 | 65 | 65 | 64 | 66 | 65 | 45 | 1384896
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 75 | 73 | 75 | 75 | 73 | 73 | 75 | 50 | 50 | 50 | 75 |  | 72 | 72 | 72 | 72 | 72 | 72 | 40 | 1246080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 18 | 18 | 17 | 18 | 18 | 19 | 18 | 18 | 48 | 89 |  | 98 | 100 | 100 | 100 | 100 | 97 | 97 | 1673700
51 | Sylhet 20 MW GTPP | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 290000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 0 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 158040
54 | Hobiganj 11MW PP Cofidence-E | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 8 | 11 | 11 | 11 | 11 |  | 0 | 138048
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 11 | 11 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 5 | 849000
56 | Shahjahanulla 25 MW PP | [7 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 |  | 0 | 358104
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 300 | 310 | 280 | 290 | 310 | 310 | 310 | 310 | 285 | 290 | 310 | 300 | 290 | 290 | 325 | 300 | 290 |  | 300 | 300 | 300 | 325 | 300 | 290 | 300 | 7512000
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 336144
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 |  | 0 | 266400
62 | Tangail 22 MW PP (Doreen) | 22 | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 380844
63 | Impoprt (Tripura) | 76 | 72 | 70 | 70 | 70 | 70 | 74 | 78 | 82 | 84 | 86 | 90 | 88 | 94 | 86 | 90 | 92 | 110 |  | 108 | 102 | 102 | 102 | 98 | 92 | 84 | 2079360
64 | Malancha, Ctg. EPZ (United) | 6 | 6 | 6 | 6 | 6 | 6 | 15 | 10 | 2 | 2 | 2 | 2 | 9 | 3 | 2 | 2 | 3 | 7 |  | 14 | 20 | 21 | 26 | 38 | 34 | 37 | 380640
65 | Feni 22MW PP (Doreen) | 22 | [5 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 326556
66 | Feni 11 MW PP (Doreen) | [9 empty] | 8 | 5 | 5 | 2 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 109080
67 | Jangalia 33MW PP (Summit) | [7 empty] | 27 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 530900
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 14 | 14 | 11 | 11 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 293420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 28 | 26 | 26 | 26 | 31 | 32 | 32 | 32 | 32 | 30 | 24 | 31 | 31 | 18 |  | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 704520
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 611300
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [16 empty] | 0 | 107 |  | 61 | 0 |  |  |  |  | 0 | 157080
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 4 | 15 |  | 28 | [5 empty] | 0 | 48000
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [7 empty] | 8 | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 30 | 60 |  | 95 | 95 | 95 | 95 | 73 | 24 | 24 | 799680
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 17 |  | 17 | 10 |  |  |  |  | 0 | 23652
| Kaptai 7 MW Solar PP | [6 empty] | 0.282 | 1.338 | 2.713 | 3.53 | 4.52 | 4.62 | 4.55 | 3.9 | 2.9 | 1.5 | 0.1 | 0 | [8 empty] | 29640
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 3 |  | 25 | 0 | [5 empty] | 33744
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [15 empty] | 1 | 34 | 64 |  | 100 | 100 | 75 | 55 | 50 |  | 0 | 410880
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 38 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 853560
93 | Ashuganj 51 MW PP (Midland) | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 35 | 35 | 35 | 35 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 782556
94 | Gagnagar 102 MW PP (Digital Power) | [12 empty] | 5 | 7 | 7 | 7 | 32 | 64 |  | 102 | 102 | 64 | 64 | 40 | 0 |  | 467280
95 | Patenga 50MW PP (Baraka) | [16 empty] | 9 | 15 |  | 48 | 50 | 42 | 19 | 18 |  | 0 | 160800
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 12 |  | 44 | 12 |  |  |  |  | 0 | 85824
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 11 |  | 22 | 0 | [5 empty] | 39054
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 |  | 35 | 17 |  |  |  |  | 0 | 387861
101 | Kushiara 163 MW CCPP (KP) | 100 | 130 | 130 | 130 | 100 | 100 | 163 | 163 | 163 | 130 | 100 | 130 | 130 | 130 | 100 | 163 | 130 | 163 |  | 163 | 163 | 163 | 163 | 130 | 130 | 163 | 3406090
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.3 | 0.5 |  | 0.3 | 0.3 | 0.3 | 0.2 | 0.6 | 0.2 | 0 | 0 | [8 empty] | 3050
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [7 empty] | 12 | 17 | 17 | 17 | 53 | 53 | 17 | 17 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 607320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 2 | [7 empty] | 0 | 4800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [15 empty] | 10 | 10 | 65 |  | 90 | 50 | 10 | 10 | 10 | 0 |  | 199680
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 2 | [9 empty] | 3 |  | 0 | [5 empty] | 0 | 110400
118 | Bibiyana-III 400 MW CCPP | 230 | 230 | 230 | 230 | 229 | 229 | 229 | 230 | 230 | 231 | 230 | 230 | 230 | 230 | 231 | 231 | 230 | 231 |  | 231 | 231 | 231 | 231 | 230 | 229 | 229 | 5526000
| Jamalpur 115 MW PP (United) | [16 empty] | 6 | 22 |  | 50 | 50 | 50 | 50 |  |  | 0 | 231600
| Anwara 300 MW PP (United) | [8 empty] | 16 | 16 | 16 | 16 | 50 | 52 | 30 | 30 | 68 | 153 |  | 160 | 160 | 162 | 263 | 267 | 161 | 16 | 1480364
120 | Eastern Zone Total | 4591 | 4336 | 4200 | 4169 | 4175 | 4368 | 4734.282 | 5115.038 | 5226.213 | 5250.53 | 5181.65 | 5401 | 5367.5 | 5176.3 | 4940.9 | 5047 | 4975 | 5652 |  | 6050 | 5840 | 5736 | 5620 | 5417 | 5130 | 4848 | 122806822
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [12 empty] | 16 | 16 | 16 | 16 | 32 | 103 |  | 99 | 115 | 115 | 115 | 51 | 0 |  | 600960
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 0 | [14 empty] | 11 | 81 |  | 95 | 97 | 94 | 62 | 63 | 61 | 34 | 501141
| Bhola 225 MW CCPP | 144 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 136 |  | 140 | 140 | 140 | 140 | 140 | 141 | 143 | 2852000
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 15 | 14 | 14 | 15 | 14 | 13 | 13 | 12 | 12 | 12 | 13 | 12 | 11 | 12 | 12 | 17 |  | 20 | 21 | 19 | 21 | 20 | 18 | 17 | 351400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 8 | 8 | 0 |  |  | 24 |  | 33 | 33 | 33 | 33 | 0 |  |  | 124500
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 7 |  | 0 | [6 empty] | 7296
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 32 |  | 32 | 21 | 15 | 32 | 32 | 0 |  | 133776
146 | Bheramara HVDC | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 314 | 314 | 314 | 314 | 314 | 313 | 313 | 313 | 313 | 313 | 653 |  | 654 | 653 | 654 | 654 | 552 | 310 | 213 | 7940364
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 217 | 218 | 221 | 222 | 221 | 219 | 229 | 284 | 298 | 298 | 303 | 322 | 337 | 333 | 340 | 342 | 340 | 362 |  | 372 | 381 | 381 | 383 | 370 | 301 | 250 | 7185200
149
150 | Barapukuria TPP Unit-1 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 79 | 81 | 81 | 81 | 82 | 81 | 81 | 85 |  | 95 | 96 | 100 | 102 | 105 | 112 | 116 | 2037381
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 186 |  | 250 | 260 | 260 | 260 | 250 | 200 | 171 | 4383800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 50 | 0 | 0 |  | 190512
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 180 | 130 | 130 | 150 | 175 | 180 | 180 | 180 | 180 | 180 | 214 | 190 | 150 | 150 | 175 | 180 |  | 180 | 180 | 180 | 195 | 200 | 200 | 170 | 4745673
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | [12 empty] | 10 | 27 | 29 | 56 | 103 | 147 |  | 188 | 184 | 189 | 200 | 185 | 188 | 187 | 1588000
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 183 | 187 | 187 | 130 | 161 | 184 | 187 | 184 | 108 | 120 | 148 | 150 | 143 | 80 | 87 | 150 | 115 |  | 105 | 105 | 105 | 119 | 112 | 115 | 113 | 3593973
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 434 | 423 | 432 | 375 | 307 | 371 | 372 | 412 | 423 | 394 | 407 | 405 | 397 | 354 | 398 | 423 | 371 | 332 |  | 392 | 402 | 396 | 396 | 350 | 396 | 395 | 9440454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [7 empty] | 18 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 347760
163 | Bogura 20 MW PP (Energyprima) | [7 empty] | 5 | 5 | 5 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 50544
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 209268
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 25 |  | 25 | 32 | 32 | 32 | 32 | 0 | 0 | 144830
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 20 | 50 |  | 108 | 70 | 70 | 35 | 0 | 0 |  | 362112
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 54 |  | 54 | 54 | 35 | 35 | 0 | 0 |  | 170880
177 | Sympa Solar Power 8MW | [7 empty] | 0.21 | 0.7 | 2.1 | 1.2 | 1.7 | 0.5 | 1.1 | 0.8 | 1.1 | 0.1 | [9 empty] | 9586
178
178