## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-01-22 | Wednesday
|  | Date (day): | 2020-01-22 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11614.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14600 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-01-21 | 2020-01-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 71 | 71 | 71 | 71
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 150 | 150 | 30 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 343 | 360 | 360
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 330 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 290 | 317 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 45 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 310 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 100 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 36 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 |  |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1835 | 2477 | 3724 | 4375 | 836 | 575
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.22 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 40 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 151 | 150 | 150 |  | 75 | ST under shut down
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 141 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 28 | 12 | 22
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 2 | 25 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3.98 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 85 | 194 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 584.2 | 875 | 1407 | 1542 | 430 | 173
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  | 135 | Under maint.
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 135 | 100 | 100 | 34 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 172 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 345 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 340 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 37 | 43 | 40 | 43
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 42 | 42 | 42 |  | 13 | Engine problem
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 40 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 89 | 89 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 80 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 92 | 86 | 104
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 5 | 14 | 14 | 14 |  | 11 | Engine problem
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1203 | 1506 | 1647 | 2332 | 221 | 369
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 147 | 128 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 70 | 0 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 214 | 315 | 368.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 66 | 66 | 66 | 66
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 144 | 150 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 2 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 74 | 74 | 74 |  | 12 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 18 | 122 | 100 | 122
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 229 | 231 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1118 | 1345 | 1387 | 1409 | 0 | 352
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 305 | 647 | 312 | 658
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 83 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 230
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 16 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 105 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 305 | 851 | 677 | 1499 | 0 | 410
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 19 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 96 | 98 | 100 | 100 |  |  | GT-2 under shut down
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 44 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 401 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 510 | 193 | 285 | 355 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 32 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 180 | 210 | 210 |  |  | FGNO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 176 | 182 | 220 | 220 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 432 | 385 | 410 | 430 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 3 | 3 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 108 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 844 | 923 | 1678 | 1964 | 171 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 123 | 122 | 120 | 120
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 300 | 200 | 275
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 102 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 386.2 | 524 | 441 | 542 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 6999.4 | 9009 | 11614.6 | 14600 | 1710 | 1987
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6577.5247 | 8466 | 10914.5525 | 13720.0133
A. |  | 2020-01-21 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9009 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5479 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9009 | MW
3 | Day peak Generation : |  |  | 6999.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8466 | MW
4 | Evening peak Generation : |  |  | 9009 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 167.456 | MKWHr | By Solar | 0.16543 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 134.3301 | MKWHr |  | By Oil: | 8.1002 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.3293 | MKWHr |  | By Hydro: | 0.89364 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1710 | MW | Dhaka | 2978 | 2978 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1987 | MW | Chittagong | 926 | 926 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3697 | MW | Khulna | 1075 | 1075 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1073.84 | MMCFD |  |  | Rajshahi | 937 | 937 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 125389549.384 | ii) Oil : | Taka | 73808958 | Comilla | 703 | 703 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 41783766.97 | Total | Taka | 240982274.354 | Mymensingh | 697 | 697 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4.8865 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -575 | MW (E to W) at | 19:00 | hrs | Barisal | 237 | 237 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -575 | MW at | 19:00 | hrs | Rangpur | 591 | 591 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 23.7° C |  |  | Total | 8466 | 8466 |  | 0
B. |  | 2020-01-22 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14600 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7100 | MW
4 | Reserve(Generation end) |  |  |  | 5500 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 169.1475 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5382 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.7375 | MKWHr. | ii) HVDC Flow at Peak Time |  | 647 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8998 | MKWHr. | iii) Maximum HVDC Flow : |  | 648 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.89 |  | (b) Today: | 94.83 |  | (c) Rule Curve: |  | 99
.

## YesterdayGen
2020-01-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 71 | 0 | 130 | 0 | 288 | 0 | 0 | 362 | 314 |  | 0 | 310 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 151 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 100 | 300 | 310 | 194 | 8 | 89 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 78 | 149 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 130 | 155 | 45 | 5 | 0 | 48 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 122 | 0 | 160 | 0 | 0 | 150 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4575 | 1505 | 6080 | 3834 | 137 | 1448 | 0 | 542 | 41 | 0 | 78 | 0 | 0 | 94.9
2:00 | 71 | 0 | 100 | 0 | 290 | 0 | 0 | 362 | 314 |  | 0 | 310 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 150 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 100 | 260 | 270 | 166 | 8 | 89 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 151 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 130 | 152 | 45 | 5 | 0 | 48 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 123 | 0 | 160 | 0 | 0 | 150 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 |  | 4427 | 1530 | 5957 | 3687 | 136 | 1473 | 0 | 546 | 41 | 0 | 74 | 0 | 0 | 94.9
3:00 | 71 | 0 | 100 | 0 | 290 | 0 | 0 | 305 | 252 |  | 0 | 310 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 100 | 260 | 270 | 159 | 8 | 88 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 151 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 130 | 146 | 45 | 5 | 0 | 48 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 122 | 0 | 160 | 0 | 0 | 150 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4240 | 1482 | 5722 | 3540 | 136 | 1390 | 0 | 542 | 42 | 0 | 72 | 0 | 0 | 94.9
4:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 275 | 254 |  | 0 | 300 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 100 | 260 | 270 | 141 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 151 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 100 | 146 | 45 | 5 | 0 | 48 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 123 | 0 | 160 | 0 | 0 | 140 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 |  | 4107 | 1417 | 5524 | 3435 | 135 | 1298 | 0 | 542 | 42 | 0 | 72 | 0 | 0 | 94.89
5:00 | 71 | 0 | 100 | 0 | 200 | 0 | 0 | 260 | 254 |  | 0 | 300 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 151 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 100 | 265 | 275 | 131 | 8 | 89 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 152 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 100 | 150 | 45 | 5 | 0 | 48 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 122 | 0 | 160 | 0 | 0 | 130 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4070 | 1409 | 5479 | 3367 | 139 | 1316 | 0 | 542 | 43 | 0 | 72 | 0 | 0 | 94.89
6:00 | 71 | 0 | 100 | 0 | 230 | 0 | 0 | 270 | 316 |  | 0 | 360 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 151 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 100 | 265 | 270 | 160 | 8 | 89 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 165 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 100 | 146 | 45 | 5 | 0 | 49 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 122 | 0 | 160 | 0 | 0 | 130 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 |  | 4282 | 1487 | 5769 | 3442 | 140 | 1529 | 0 | 543 | 43 | 0 | 72 | 0 | 0 | 94.89
7:00 | 71 | 0 | 100 | 0 | 290 | 0 | 0 | 335 | 374 |  | 0 | 420 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 151 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 100 | 290 | 270 | 191 | 8 | 89 | 12 | 5 | 0 | 5 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 72 | 165 | 0 | 0 | 0 | 30 | 66 | 2 | 3 | 130 | 150 | 45 | 5 | 0 | 49 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0.24 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 120 | 0 | 165 | 0 | 0 | 130 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4671.84 | 1561 | 6232.84 | 3691 | 139 | 1742 | 0 | 545 | 43 | 0 | 72 | 0.84 | 0 | 94.88
8:00 | 71 | 0 | 100 | 0 | 290 | 0 | 0 | 370 | 372 |  | 0 | 420 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 43 | 0 | 0 | 120 | 0 | 151 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 100 | 290 | 295 | 237 | 8 | 89 | 40 | 5 | 0 | 22 | 0 | 0 | 0 | 22 | 8 | 8 | 8 | 78 | 165 | 22 | 17 | 0.2 | 30 | 66 | 2 | 3 | 163 | 149 | 69 | 5 | 0 | 38 | 0 | 0 | 10 | 295 | 22 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0.59 | 5 | 0 | 0 | 0 | 0 |  | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 121 | 0 | 190 | 0 | 0 | 145 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 288 |  | 4963.7 | 1792.2 | 6755.9 | 3955 | 308 | 1724 | 44 | 599 | 43 | 0 | 78 | 4.9 | 0 | 94.88
9:00 | 71 | 0 | 106 | 0 | 290 | 0 | 0 | 370 | 370 |  | 0 | 420 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 100 | 290 | 295 | 185 | 8 | 89 | 40 | 5 | 0 | 35 | 0 | 0 | 0 | 22 | 8 | 8 | 8 | 78 | 164 | 48 | 14 | 0.5 | 30 | 66 | 2 | 26 | 163 | 151 | 67 | 50 | 0 | 20 | 17 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.22 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 1.22 | 16 | 0 | 0 | 0 | 0 |  | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 11 | 121 | 0 | 233 | 0 | 0 | 170 | 0 | 189 | 0 | 25 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 306 |  | 5090.94 | 1884.8 | 6975.74 | 3927 | 308 | 1833 | 116 | 660 | 42 | 0 | 78 | 11.74 | 0 | 94.88
10:00 | 71 | 0 | 100 | 0 | 270 | 0 | 0 | 370 | 289 |  | 0 | 350 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 153 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 100 | 310 | 295 | 175 | 8 | 89 | 37 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 8 | 8 | 82 | 162 | 48 | 14 | 1.5 | 30 | 66 | 2 | 50 | 100 | 145 | 66 | 50 | 0 | 20 | 17 | 0 | 10 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.27 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 2.1 | 16 | 0 | 0 | 0 | 0 |  | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 260 | 0 | 0 | 170 | 0 | 159 | 0 | 24 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 382 |  | 4885.87 | 1943.3 | 6829.17 | 3878 | 308 | 1620 | 116 | 764 | 42 | 0 | 82 | 19.17 | 0 | 94.88
11:00 | 71 | 0 | 100 | 0 | 270 | 0 | 0 | 370 | 290 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 295 | 310 | 178 | 8 | 89 | 37 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 8 | 5 | 86 | 146 | 48 | 17 | 1.7 | 30 | 66 | 2 | 50 | 100 | 147 | 64 | 50 | 0 | 18 | 17 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.48 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 3.747 | 50 | 0 | 0 | 0 | 0 |  | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 121 | 0 | 260 | 0 | 0 | 170 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 401 |  | 4916.927 | 1946.9 | 6863.827 | 3877 | 305 | 1598 | 150 | 782 | 42 | 0 | 86 | 23.827 | 0 | 94.88
12:00 | 71 | 0 | 100 | 0 | 270 | 0 | 0 | 356 | 290 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 19 | 3 | 0 | 0 | 100 | 305 | 305 | 180 | 8 | 89 | 37 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 5 | 80 | 147 | 48 | 17 | 2 | 30 | 66 | 2 | 50 | 100 | 144 | 64 | 50 | 0 | 18 | 17 | 0 | 9 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.22 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 3.98 | 85 | 0 | 0 | 0 | 0 |  | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 123 | 0 | 260 | 0 | 0 | 200 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 401 |  | 4954.2 | 2045.2 | 6999.4 | 3904 | 305 | 1670 | 187 | 784 | 42 | 0 | 80 | 27.4 | 0 | 94.88
13:00 | 71 | 0 | 100 | 0 | 270 | 0 | 0 | 369 | 290 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 150 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 100 | 270 | 360 | 162 | 8 | 89 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 5 | 80 | 126 | 48 | 20 | 2 | 30 | 66 | 2 | 50 | 100 | 142 | 64 | 50 | 0 | 18 | 17 | 0 | 9 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.36 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 3.8 | 85 | 0 | 0 | 0 | 0 |  | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 124 | 0 | 260 | 0 | 0 | 200 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 462 |  | 4963.16 | 2074.7 | 7037.86 | 3907 | 305 | 1650 | 185 | 846 | 38 | 0 | 80 | 26.86 | 0 | 94.88
14:00 | 71 | 0 | 101 | 0 | 250 | 0 | 0 | 305 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 100 | 265 | 325 | 167 | 8 | 89 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 10 | 82 | 127 | 48 | 20 | 1.3 | 30 | 66 | 2 | 46 | 100 | 142 | 64 | 50 | 0 | 18 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 3.2 | 89 | 0 | 0 | 0 | 0 |  | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 124 | 0 | 260 | 0 | 0 | 195 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 493 |  | 4763.5 | 2055.9 | 6819.4 | 3775 | 305 | 1529 | 189 | 877 | 40 | 0 | 82 | 22.4 | 0 | 94.87
15:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 300 | 260 |  | 0 | 300 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 100 | 260 | 320 | 161 | 8 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 10 | 78 | 127 | 48 | 20 | 1.5 | 30 | 66 | 2 | 46 | 100 | 142 | 65 | 50 | 0 | 18 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 2.3 | 89 | 0 | 0 | 0 | 0 |  | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 123 | 0 | 261 | 0 | 0 | 170 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 523 |  | 4741.8 | 2044.4 | 6786.2 | 3723 | 304 | 1531 | 189 | 907 | 38 | 0 | 78 | 16.2 | 0 | 94.87
16:00 | 71 | 0 | 100 | 0 | 250 | 0 | 0 | 300 | 260 |  | 0 | 260 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 0 | 100 | 260 | 320 | 162 | 8 | 88 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 10 | 76 | 127 | 32 | 20 | 0.6 | 30 | 66 | 2 | 46 | 100 | 143 | 45 | 20 | 0 | 18 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 1.2 | 51 | 0 | 0 | 0 | 0 |  | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 260 | 0 | 0 | 170 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 500 |  | 4552.7 | 2001.2 | 6553.9 | 3708 | 304 | 1419 | 117 | 882 | 38 | 0 | 76 | 9.9 | 0 | 94.86
17:00 | 71 | 0 | 100 | 0 | 290 | 0 | 0 | 300 | 305 |  | 0 | 400 | 0 | 2 | 0 | 0 | 230 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 151 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 3 | 0 | 19 | 4 | 0 | 0 | 100 | 260 | 320 | 160 | 8 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 0 | 10 | 76 | 127 | 32 | 20 | 0.2 | 30 | 66 | 2 | 50 | 100 | 143 | 45 | 20 | 0 | 77 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 2 | 230 | 5 | 0 | 0 | 0.2 | 51 | 0 | 0 | 5 | 0 |  | 304 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 120 | 0 | 260 | 0 | 0 | 175 | 0 | 171 | 0 | 10 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 |  | 4875.4 | 1582.2 | 6457.6 | 3808 | 304 | 1680 | 170 | 380 | 38 | 0 | 76 | 1.6 | 0 | 94.88
18:00 | 71 | 0 | 101 | 0 | 270 | 0 | 0 | 300 | 290 |  | 0 | 370 | 0 | 60 | 30 | 33 | 230 | 0 | 0 | 0 | 24 | 85 | 0 | 21 | 0 | 0 | 4 | 53 | 35 | 0 | 22 | 25 | 17 | 25 | 16 | 0 | 0 | 38 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 46 | 32 | 19 | 17 | 0 | 0 | 135 | 285 | 345 | 198 | 8 | 88 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 10 | 94 | 127 | 65 | 20 | 0 | 40 | 66 | 28 | 50 | 130 | 150 | 45 | 74 | 0 | 118 | 17 | 0 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 32 | 20 | 230 | 38 | 0 | 17 | 0 | 188 | 0 | 0 | 18 | 0 |  | 547 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 121 | 0 | 272 | 0 | 0 | 180 | 0 | 167 | 0 | 43 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 40 | 0 |  | 5829 | 2107 | 7936 | 3976 | 547 | 1756 | 1132 | 393 | 38 | 0 | 94 | 0 | 0 | 94.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 71 | 0 | 100 | 0 | 343 | 0 | 0 | 330 | 317 |  | 0 | 450 | 0 | 100 | 15 | 15 | 310 | 0 | 0 | 0 | 45 | 100 | 0 | 0 | 0 | 0 | 36 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 25 | 50 | 19 | 28 | 0 | 0 | 135 | 345 | 340 | 172 | 8 | 89 | 43 | 42 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 92 | 128 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 130 | 150 | 67 | 74 | 0 | 122 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 80 | 40 | 231 | 70 | 0 | 17 | 0 | 194 | 0 | 0 | 0 | 0 |  | 647 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 16 | 98 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 300 | 0 | 0 | 180 | 0 | 182 | 0 | 44 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 105 | 102 | 0 | 0 | 108 | 0 |  | 6518 | 2491 | 9009 | 4262 | 647 | 1988 | 1558 | 422 | 40 | 0 | 92 | 0 | 0 | 94.88
19:30 | 71 | 0 | 152 | 0 | 330 | 0 | 0 | 342 | 333 |  | 0 | 450 | 0 | 100 | 15 | 15 | 326 | 0 | 0 | 0 | 7 | 93 | 0 | 0 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 32 | 0 | 0 | 100 | 330 | 330 | 194 | 8 | 89 | 43 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 92 | 127 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 148 | 67 | 74 | 0 | 127 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 229 | 16 | 0 | 17 | 0 | 194 | 0 | 0 | 0 | 0 |  | 648 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 16 | 97 | 20 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 300 | 0 | 0 | 180 | 0 | 177 | 0 | 44 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 105 | 113 | 0 | 0 | 108 | 0 |  | 6353 | 2508 | 8861 | 4283 | 648 | 2032 | 1344 | 422 | 40 | 0 | 92 | 0 | 0 | 94.88
20:00 | 71 | 0 | 150 | 0 | 335 | 0 | 0 | 355 | 344 |  | 0 | 450 | 0 | 100 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 48 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 100 | 345 | 345 | 200 | 8 | 89 | 43 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 86 | 126 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 150 | 68 | 74 | 0 | 122 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 229 | 16 | 0 | 17 | 0 | 199 | 0 | 0 | 0 | 0 |  | 648 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 16 | 97 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 300 | 0 | 0 | 180 | 0 | 174 | 0 | 43 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 105 | 113 | 0 | 0 | 108 | 0 |  | 6385 | 2511 | 8896 | 4337 | 648 | 2042 | 1321 | 422 | 40 | 0 | 86 | 0 | 0 | 94.88
21:00 | 71 | 0 | 150 | 0 | 325 | 0 | 0 | 352 | 332 |  | 0 | 450 | 0 | 100 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 28 | 25 | 16 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 36 | 0 | 0 | 100 | 320 | 330 | 174 | 8 | 88 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 104 | 126 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 150 | 69 | 74 | 0 | 117 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 228 | 16 | 0 | 17 | 0 | 197 | 0 | 0 | 0 | 0 |  | 648 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 16 | 97 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 123 | 0 | 300 | 0 | 0 | 180 | 0 | 172 | 0 | 43 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 105 | 113 | 0 | 0 | 0 | 0 |  | 6177 | 2402 | 8579 | 4213 | 648 | 2008 | 1143 | 423 | 40 | 0 | 104 | 0 | 0 | 94.88
22:00 | 71 | 0 | 151 | 0 | 320 | 0 | 0 | 340 | 322 |  | 0 | 450 | 0 | 96 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 100 | 310 | 320 | 180 | 8 | 88 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 90 | 106 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 148 | 69 | 74 | 0 | 117 | 17 | 0 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 0 |  | 549 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 123 | 0 | 295 | 0 | 0 | 180 | 0 | 172 | 0 | 44 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 50 | 74 | 0 | 0 | 0 | 0 |  | 5857 | 2154 | 8011 | 4123 | 549 | 1982 | 809 | 418 | 40 | 0 | 90 | 0 | 0 | 94.88
23:00 | 71 | 0 | 150 | 0 | 320 | 0 | 0 | 335 | 332 |  | 0 | 350 | 0 | 55 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 100 | 310 | 325 | 181 | 8 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 76 | 109 | 50 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 144 | 69 | 74 | 0 | 119 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 306 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 122 | 0 | 295 | 0 | 0 | 180 | 0 | 171 | 0 | 43 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 32 | 15 | 0 | 0 | 0 | 0 |  | 5505 | 1677 | 7182 | 4121 | 306 | 1830 | 392 | 417 | 40 | 0 | 76 | 0 | 0 | 94.88
24:00 | 71 | 0 | 150 | 0 | 335 | 0 | 0 | 352 | 313 |  | 0 | 350 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 18 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 0 | 100 | 285 | 310 | 199 | 8 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 70 | 128 | 24 | 22 | 0 | 30 | 66 | 53 | 50 | 163 | 140 | 69 | 30 | 0 | 77 | 16 | 0 | 10 | 270 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 295 | 0 | 0 | 180 | 0 | 159 | 0 | 44 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 |  | 5092 | 1513 | 6605 | 4029 | 210 | 1767 | 72 | 417 | 40 | 0 | 70 | 0 | 0 | 94.84
KWH | 1689000 | 0 | 2679000 | 0 | 6738727 | 0 | 0 | 8124410 | 7242000 |  | 0 | 8549250 | 0 | 557760 | 113040 | 90865 | 5971430 | 0 | 0 | 0 | 79680 | 51088 | 0 | 56928 | 0 | 0 | 110448 | 535320 | 503553 | 0 | 332064 | 600000 | 692460 | 614600 | 799100 | 0 | 0 | 893640 | 0 | 0 | 3000000 | 0 | 3648988 | 0 | 3144769 | 0 |  | 0 | 0 | 0 | 35760 | 88320 | 218880 | 443232 | 540960 | 0 | 0 | 2454410 | 7296300 | 7510000 | 4245000 | 200727 | 2119310 | 743832 | 207360 | 0 | 795404 | 0 | 0 | 0 | 370512 | 145260 | 350000 | 302480 | 1899840 | 3266880 | 1019520 | 320040 | 11500 | 716000 | 1563120 | 369000 | 825120 | 3264954 | 3308000 | 1377120 | 967680 | 0 | 1451880 | 311000 | 0 | 161280 | 7418200 | 397248 | 140104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110970 | 331200 | 116640 | 75272 | 5501000 | 196800 | 0 | 84105 | 22800 | 1723745 | 0 | 0 | 43320 | 0 |  | 7737454 | 0 | 0 | 0 | 405120 | 0 | 0 | 0 | 0 | 0 | 43125 | 2784594 | 344400 | 188160 | 0 | 0 | 0 | 0 | 0 | 0 | 153720 | 0 | 0 | 0 | 0 | 293520 | 55332 | 245502 | 2920581 | 0 | 5667400 | 0 | 0 | 4384309 | 0 | 4111036 | 0 | 361853 | 0 | 0 | 0 | 8840363 | 0 | 0 | 0 | 484704 | 479040 | 0 | 20165 | 314112 | 5741300 |  | 121880205 | 45575790 | 167455995 | 93892717 | 7737454 | 40437403 | 8100225 | 14329281 | 893640 | 0 | 1899840 | 165435 | 0
Fuel Cost | 1891680 | 0 | 2866530 | 0 | 4986657.98 | 0 | 0 | 5849575.2 | 5503920 |  | 0 | 6839400 | 0 | 5689152 | 1224223.2 | 932274.9 | 7404573.2 | 0 | 0 | 0 | 884448 | 519054.08 | 0 | 596605.44 | 0 | 0 | 1033793.28 | 5133718.8 | 4803895.62 | 0 | 249048 | 450000 | 0 | 0 | 0 | 0 | 0 | 232346.4 | 0 | 0 | 4590000 | 0 | 3831437.4 | 0 | 3993856.63 | 0 |  | 0 | 0 | 0 | 367970.4 | 839923.2 | 2048716.8 | 407773.44 | 1503868.8 | 0 | 0 | 2577130.5 | 5399262 | 6308400 | 3905400 | 196712.46 | 2818682.3 | 609942.24 | 213580.8 | 0 | 1137427.72 | 0 | 0 | 0 | 377922.24 | 108945 | 661500 | 226860 | 13108896 | 2678841.6 | 9695635.2 | 326440.8 | 188600 | 973760 | 2125843.2 | 501840 | 1031400 | 4048542.96 | 3043360 | 2051908.8 | 1703116.8 | 0 | 2206857.6 | 494490 | 0 | 379008 | 5266922 | 297936 | 106479.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1280593.8 | 3086784 | 1094083.2 | 705298.64 | 5170940 | 1725936 | 0 | 794792.25 | 0 | 15892928.9 | 0 | 0 | 0 | 0 |  | 20891125.8 | 0 | 0 | 0 | 3905356.8 | 0 | 0 | 0 | 0 | 0 | 426506.25 | 2227675.2 | 533820 | 2020838.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1594076.4 | 0 | 0 | 0 | 0 | 322872 | 91297.8 | 185845.014 | 18604100.97 | 0 | 23179666 | 0 | 0 | 3858191.92 | 0 | 3823263.48 | 0 | 575346.27 | 0 | 0 | 0 | 6453464.99 | 0 | 0 | 0 | 4318712.64 | 4474233.6 | 0 | 0 | 0 | 0 |  | 179197442.82 | 97486393.534 | 276683836.354 | 89087008.784 | 20891125.8 | 36302540.6 | 73808958 | 41783766.97 | 232346.4 | 0 | 13108896 | 1469193.8 | 0
Yesterday Day Peak | 71 | 0 | 100 | 0 | 270 | 0 | 0 | 356 | 290 |  | 0 | 330 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 42 | 0 | 0 | 120 | 0 | 151 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 19 | 3 | 0 | 0 | 100 | 305 | 305 | 180 | 8 | 89 | 37 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 16 | 5 | 80 | 147 | 48 | 17 | 2 | 30 | 66 | 2 | 50 | 100 | 144 | 64 | 50 | 0 | 18 | 17 | 0 | 9 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.22 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 3.98 | 85 | 0 | 0 | 0 | 0 |  | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 123 | 0 | 260 | 0 | 0 | 200 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 401 |  | 6999.4 | DayPeak
Yesterday Evening Peak | 71 | 0 | 100 | 0 | 343 | 0 | 0 | 330 | 317 | 0 | 0 | 450 | 0 | 100 | 15 | 15 | 310 | 0 | 0 | 0 | 45 | 100 | 0 | 0 | 0 | 0 | 36 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 151 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 19 | 28 | 0 | 0 | 135 | 345 | 340 | 172 | 8 | 89 | 43 | 42 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 92 | 128 | 95 | 22 | 0 | 30 | 66 | 53 | 50 | 130 | 150 | 67 | 74 | 0 | 122 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 80 | 40 | 231 | 70 | 0 | 17 | 0 | 194 | 0 | 0 | 0 | 0 |  | 647 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 16 | 98 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 122 | 0 | 300 | 0 | 0 | 180 | 0 | 182 | 0 | 44 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 105 | 102 | 0 | 0 | 108 | 0 |  | 9009 | EvPeak
Forecast for Evening | 71 | 0 | 150 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 0 | 0 | 120 | 25 | 150 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 22 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 90 | 43 | 42 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 14 | 104 | 150 | 95 | 22 | 0 | 30 | 66 | 51 | 44 | 163 | 160 | 66 | 74 | 0 | 122 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 658 | 40 | 0 | 0 | 115 | 230 | 0 | 0 | 36 | 70 | 40 | 100 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 120 | 0 | 275 | 17 | 17 | 210 | 0 | 220 | 0 | 95 | 100 | 220 | 0 | 430 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113
Forecast for Day | 71 | 0 | 150 | 0 | 360 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 0 | 0 | 120 | 25 | 150 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 12 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 90 | 40 | 42 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 86 | 150 | 95 | 22 | 1.6 | 30 | 66 | 51 | 44 | 163 | 160 | 66 | 74 | 0 | 100 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 0 | 100 | 230 | 0 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 312 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 100 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 120 | 0 | 200 | 0 | 0 | 210 | 0 | 220 |  | 95 | 80 | 220 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 71 | 0 | 150 | 0 | 355 | 0 | 0 | 385 | 342 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 33 | 0 | 0 | 41 | 0 | 0 | 120 | 0 | 151 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 100 | 345 | 340 | 201 | 8 | 89 | 40 | 5 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 68 | 130 | 13 | 20 | 0.2 | 30 | 66 | 29 | 18 | 130 | 159 | 69 | 74 | 0 | 99 | 16 | 0 | 10 | 330 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.43 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 121 | 0 | 196 | 0 | 0 | 130 | 0 | 133 | 0 | 19 | 0 | 130 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 252 | 0
199
| Minimum Generation |  | 5479 | 5:00
| Highest Generation |  | 9009 | 19:00
| Day Peak Generation |  | 6999.4 | 12:00
| Evening Peak Generation |  | 9009 | 19:00
| HVDC Max Flow |  | 648 | 19:30
| HVDC EvPeak Flow |  | 647 | 19:00
| Load factor L.F |  | 77.45%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-01-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-01-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6999.4 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5382 | MW
Evening Peak Generation : |  | 9009 | MW Hour : | 19:00 | Available Max Generation : |  | 14600 | MW
E.P. Demand (at gen end) : |  | 9009 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9100 | MW
Maximum Generation : |  | 9009 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5500 | MW
Total Gen. (MKWH) : |  | 167.456 | System Load Factor : | 77.45% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -575 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-01-22
Actual : | 94.83 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : | Total = | 1073.84 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 125389549.384
: |  | Coal : | 41783766.97 | Oil : | 73808958 | Total : | 240982274.354
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3195.5127 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1081.196 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 967.7438 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 874.093 |  |  | 0 | 0%
) | 0 | 0:00 | 790.0955 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 637.5654 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 363.5151 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 164.3417 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 491.6885 |  |  | 0 | 0%
Total | 0 |  | 8565.7518 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Summit Meghna 305 MW
3) Ghorasal Unit-3,5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3
6) Bheramara 410 MW
7)Shajibazar 330 MW GT-1
8) Ashuganj unit-4
9) Bhola 225 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Tongi 132/33 kV T-2 transformer was under shut down from 08:32 to 16:57 for A/M.
b) Tongi-Uttara 3rd phase 132 kV Ckt was under shut down from 10:40 to 14:40 for A/M.
c) Tongi-Uttara 132 kV Ckt was under shut down from 10:41 to 13:20 for A/M.
d) Hathazari 230 kV Bus-2 was under shut down from 09:28 to 13:15 for A/M.
e) Savar 132/33 kV T-2 transformer was under shut down from 08:15 to 15:17 for A/M.
f) Matarbari 132/33 kV T-2 transformer was under shut down from 10:28 to 14:56 for A/M.
g) Rampura-Moghbazar 132 kV Ckt-2 was under shut down from 08:32 to 15:41 for A/M.
h) Kaliakoir-Bibiyana 400 kV Ckt-1 was under shut down from 09:02 to 13:52 for A/M.
i) Cumilla(N)-Ashuganj 230 kV Ckt-2 was under shut down from 09:06 to 15:18 for A/M.
j) Cumilla(N)-BSRM 230 kV Ckt-1 was under shut down from 10:40 to 11:04 for removing nest.
k) Cumilla(N)-BSRM 230 kV Ckt-2 was under shut down from 11:09 to 11:25 for removing nest.
l) Mymensing 132/33 kV T-1 transformer was under shut down from 09:20 to 16:35 for A/M.
m) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:10 to 16:30 for A/M.
n) Fenchuganj-Srimongal 132 kV Ckt-1 was under shut down from 09:45 to 12:28 for A/M.
o) Bhulta-Ghorasal 230 kV Ckt-2 was under shut down from 08:17 to 16:14 for A/M.
p) Kamrangirchar 132/33 kV T-3 transformer was under shut down from 09:13 to 21:30 for A/M.
q) Bhaluka 132/33 kV T-2 transformer was under shut down from 08:12 to 14:09 for C/M.
r) Savar-Aminbazar 132 kV Ckt-1 was under shut down from 08:55 to 22:07 for A/M.
s) Bogura(O)-Bogura(N) 132 kV Ckt-1 was under shut down from 08:55 to 13:25 for D/W.
t) Barapukuria 132/33 kV T-4 transformer was shut down at 10:07 for D/W.
u) Fenchuganj-Srimongal 132 kV Ckt-2 was under shut down from 12:31 to 15:10 for A/M.
v) Ishurdi-Ghorasal 230 kV Ckt-2 was under shut down from 08:53 to 18:09 for A/M.
w) Bogura(O)-Natore 132 kV Ckt-2 was under shut down from 12:05 to 17:30 for D/W.
x) Bogura(O)-Naogaon 132 kV Ckt-2 was under shut down from 12:05 to 17:29 for D/W.
y) Bakulia 132/33 kV T-1 transformer was under shut down from 14:14 to 16:17 for C/M.
z) Payra-660 MW tripped at 16:44 due to boiler trip and was synchronized at 01:15(22/01/20).
aa) Bogura(O)-Bogura(N) 132 kV Ckt-1 & 2 tripped at 22:50 showing E/F & O/C relays due to fault of 33 kV |  |  |  |  | About 46 MW power interruption occurred under Bogura, Naogaon
Dupchachia feeder and were switched on at 23:29. At the same time GT-3 & GT-4 transformers also tripped |  |  |  |  | Niamatpur & Joypurhat S/S areas from 22:50 to 23:29.
and were switched on at 23:43.
ab) Sirajganj #3 CCPP GT & ST were synchronized at 00:18 & 02:22(22/01/20) respectively.
ac) Bibiyana #3 CCPP ST tripped at 04:50(22/1/20) due to drain line problem at cooling water line.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-01-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 71 | 1689000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2679000 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 343 | 6738727 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8124410 | Gas shortage.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 317 | 7242000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8549250
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 557760
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 113040 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 90865 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 56928 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 332064
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 45 | 79680 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 5971430 | Gas shortage.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 100 | 51088
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 36 | 110448 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 535320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 503553
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1292460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 799100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2477 | 46130723
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110970
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 218880
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 893640 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 3648988 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 141 | 3144769 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 84105 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 35760 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 331200 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 443232
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 540960
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 88320 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 194 | 1723745 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 875 | 14287369
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 135 | 2454410
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 172 | 4245000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7296300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 340 | 7510000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 743832 | Machine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 42 | 207360 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 795404 | Machine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 75272 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2119310 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 80 | 116640 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 370512
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 145260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 1899840
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 350000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 302480 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 43320 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1506 | 28875667
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 128 | 3266880 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 320040
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1019520
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 0 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 70 | 196800 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 315 | 4814740
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Gas shortage.
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1563120
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3264954
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 150 | 3308000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 369000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 825120
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 140104
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1377120 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 967680 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 122 | 1451880 | Machine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 311000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 397248
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7418200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 231 | 5501000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 161280
| Sylhet Area Total |  |  |  | 1949 | 1345 | 27771706
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 647 | 7737454
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 405120 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 16 | 43125 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 105 | 484704
| Khulna Area Total |  |  |  | 2314 | 851 | 8670403
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 188160 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 19 | 344400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 98 | 2784594 | ST Under S/D.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 44 | 361853 | Machine problem
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 5741300 | On test
| Barisal Area Total |  |  |  | 462 | 193 | 9420307
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 32 | 153720 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4384309 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4111036 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 385 | 8840363 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 293520
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 3 | 55332 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245502
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 108 | 314112
| Rajshahi Area Total |  |  |  | 2183 | 923 | 18397894
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 122 | 2920581
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 300 | 5667400
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 102 | 479040 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20165
| Rangpur Area Total |  |  |  | 605 | 524 | 9087186
| Total |  |  |  | 19107 | 9009 | 167455995
| Eastern Grid Total |  |  |  | 13543 | 6518 | 121880205
| Western Grid Total |  |  |  | 5564 | 2491 | 45575790
| National Grid Total |  |  |  | 19107 | 9009 | 167455995
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-01-21
(a) ENTIRE EASTERN GRID : |  | 5626 | MW | (b) ENTIRE WESTERN GRID : |  | 2840 | MW
i) Dhaka area |  | 2978 | MW | i) Khulna area |  | 1075 | MW
ii) Chittagong area |  | 926 | MW | ii) Rajshahi area |  | 937 | MW
iii) Comilla area |  | 703 | MW | iii) Barisal area |  | 237 | MW
iv) Mymensingh area |  | 697 | MW | iv) Rangpur area |  | 591 | MW
v) Sylhet area |  | 322 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8466 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 104 | 19:00 | Shahjibazar | 78 | 19:30 | Bottail | 106 | 18:30
Munsiganj | 72 | 18:30 | Fenchuganj | 25 | 18:00 | G.K Project | 30 | 18:30
Sonargaon | 75 | 19:00 | Kulawara | 26 | 18:00 | Faridpur | 132 | 19:30
Shyampur | 174 | 0:00 | Sylhet | 101 | 19:00 | Madaripur | 59 | 21:00
Bhulta | 158 | 13:00 | Chatak | 20 | 18:00 | Sariatpur | 38 | 18:30
Madanganj | 52 | 19:30 | Sunamganj | 26 | 19:00 | Gopalganj | 68 | 19:00
Shitalakhya | 96 | 15:00 | Biani Bazar | 28 | 19:30 | Bagerhat | 65 | 19:00
Rahim steel | 27 | 16:00 | Comilla (S) | 104 | 21:00 | Mongla | 38 | 11:00
Matuail | 74 | 10:00 | Comilla(N) | 79 | 19:00 | Satkhira | 71 | 19:30
Ghorasal | 60 | 19:00 | Chandpur | 52 | 18:30 | Gallamari | 35 | 13:00
Narsingdi | 116 | 18:30 | Feni | 88 | 18:00 | Magura | 36 | 18:30
Haripur (SBU) | 96 | 15:00 | Chowmuhani | 104 | 18:30 | Norail | 27 | 18:30
Ullon | 42 | 20:00 | Ashuganj | 32 | 18:30 | Chuadanga | 63 | 18:30
Hasnabad | 120 | 21:00 | Daudkandi | 92 | 21:00 | Barisal(N) | 28 | 19:30
Magbazar | 70 | 13:00 | B.Baria | 95 | 18:00 | Barisal (S) | 68 | 20:00
Maniknagar | 74 | 18:00 | Ramganj | 66 | 19:30 | Patuakhali | 86 | 19:00
Bangabhaban | 16 | 12:00 | Chaddagram | 24 | 18:00 | Bhandaria | 40 | 19:00
Narinda | 66 | 12:00 | PHP | 3 | 19:30 | Borhan Uddin | 25 | 21:00
Dhanmondi | 78 | 12:00 | Madunaghat | 41 | 18:00 | Ishurdi | 43 | 18:30
Lalbag | 81 | 13:00 | Hathazari | 68 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Madartek | 42 | 21:00 | Khulshi | 140 | 13:00 | Natore | 93 | 18:30
Mirpur | 70 | 18:30 | Halishahar | 87 | 18:00 | Bogra | 121 | 19:30
Kalyanpur | 72 | 18:30 | Baraulia | 133 | 15:00 | Noagaon | 89 | 19:00
Gulshan | 90 | 18:00 | Sikalbaha | 19 | 20:00 | Rajshahi | 92 | 19:30
Uttara | 42 | 18:00 | Dohazari | 64 | 18:30 | Rajshahi New | 10 | 18:00
Uttara New | 22 | 18:00 | Cox'sbazar | 71 | 18:30 | C.Nawabganj | 63 | 19:30
Kamrangirchar | 66 | 18:00 | Chandraghona | 22 | 8:00 | Amnura | 27 | 18:30
Savar | 95 | 18:00 | Kaptai | 3.5 | 18:00 | Pabna | 73 | 18:30
Bhasantec | 100 | 18:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 80 | 18:30
Agargaon | 38 | 18:00 | Bakulia | 71 | 18:00 | Serajganj | 67 | 19:00
Satmosjid | 54 | 18:00 | Julda | 20 | 1:00 | Niyamatpur | 77 | 19:30
Tongi | 96 | 18:00 | TK chemical | 10.4 | 18:00 | Joypurhat | 51 | 19:00
Kabirpur | 162 | 18:00 | Modern Steel | 13 | 4:00 | Sherpur(Bogura) | 38 | 19:00
Basundhara | 84 | 18:00 | Shahmirpur | 24 | 18:00 | Mohastangor | 30 | 18:30
Manikganj | 86 | 21:00 | Khagrachhari | 16 | 18:30 | Rangpur | 109 | 20:00
Joydevpur | 161 | 18:30 | Matarbari | 22 | 18:30 | Lalmonirhat | 55 | 18:30
New Tongi | 73 | 12:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 86 | 18:30
Korda | 172 | 19:00 | Rangamati | 9 | 18:30 | Purbasadipur | 91 | 18:30
Dhamrai | 44 | 18:30 | Abul Khair 230 | 112 | 10:00 | Thakurgaon | 60 | 19:00
Valuka | 76 | 18:30 | BSRM | 100 | 4:00 | Palashbari | 84 | 18:30
Tangail | 133 | 21:00 | GPH Ispat | 8 | 1:00 | Barapukuria | 41 | 19:30
Mymensing | 163 | 18:30 | Goalpara | 18 | 18:30 | Panchagar | 38 | 18:30
Kishorganj | 88 | 20:00 | Central s/s | 66 | 18:30 | Joldhaka | 13 | 18:30
Netrokona | 102 | 19:30 | Noapara | 41 | 19:00 | Kurigram | 33 | 8:00
Jamalpur | 91 | 18:30 | Jessore | 101 | 19:00
Sherpur | 82 | 18:30 | Benapol | 36 | 8:00
Srimongal | 23 | 18:00 | Jhenida | 83 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-01-21 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.083333 | 395 | 0.66667 | Kaliakoir | 387 | 0.16667 | 364 | 0.5
Bheramara | 408 | 0.125 | 394 | 0.45833 | Bhulta | 394 | 0.16667 | 382 | 0.5
Ashuganj(N) | 398 | 0.125 | 388 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 236 | 0.91667 | 234 | 0.041667 | Hathazari | 224 | 0.77083 | 216 | 0.45833
Ishurdi | 241 | 0.125 | 226 | 0.54167 | Megnaghat | 234 | 0.16667 | 227 | 0.41667
Ashuganj | 242 | 0.25 | 237 | 0.5 | Fenchuganj | 243 | 0.125 | 239 | 0.41667
Serajganj | 235 | 0.125 | 230 | 0.29167 | Siddhirganj | 234 | 0.16667 | 226 | 0.54167
Baghabari | 241 | 0.041667 | 236 | 0.29167 | Maniknagar | 233 | 0.20833 | 225 | 0.45833
Barapukuria | 234 | 0.125 | 229 | 0.375 | Old Airport | 233 | 0.125 | 222 | 0.5
Bogra | 232 | 0.20833 | 224 | 0.33333 | Barisal | 240 | 0.125 | 224 | 0.75
Khulna South | 240 | 0.125 | 217 | 0.54167 | AKSML | 221 | 0.083333 | 214 | 0.41667
Rampura | 231 | 0.16667 | 227 | 0.54167 | BSRM | 225 | 0.125 | 216 | 0.45833
Haripur | 232 | 0.29167 | 225 | 0.5 | Bibiyana | 242 | 0.041667 | 235 | 0.54167
Hasnabad | 232 | 0.16667 | 223 | 0.5 | Bhulta | 236 | 0.20833 | 227 | 0.5
Aminbazar | 233 | 0.083333 | 224 | 0.5 | Ashuganj (S) | 239 | 0.16667 | 233 | 0.54167
Tongi | 231 | 0.16667 | 223 | 0.45833 | Kaliakoir | 236 | 0.16667 | 225 | 0.41667
Comilla (N) | 239 | 0.25 | 230 | 0.45833 | GPH | 222 | 0.875 | 214 | 0.45833
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.125 | 128 | 0.5 | Halishahar | 135 | 0.77083 | 126 | 0.45833
Munsiganj | 138 | 0.77083 | 128 | 0.45833 | Baraulia | 132 | 0.75 | 127 | 0.375
Sonargaon | 133 | 0.375 | 128 | 0.5 | Sikalbaha | 133 | 0.75 | 127 | 0.41667
Shyampur | 134 | 0.20833 | 128 | 0.45833 | Dohazari | 131 | 0.77083 | 127 | 0.45833
Bhulta | 128 | 0.75 | 123 | 0.54167 | Cox'sbazar | 125 | 0.16667 | 122 | 0.41667
Madanganj | 135 | 0.75 | 126 | 0.45833 | Chandraghona | 133 | 0.75 | 128 | 0.41667
Shitalakhya | 137 | 0.75 | 126 | 0.45833 | Kaptai | 132 | 0.041667 | 128 | 0.41667
Rahim steal | 134 | 4:00 | 129 | 0.5 | A. Khaer Stl. | 131 | 0.875 | 128 | 0.41667
Matuail | 136 | 0.875 | 127 | 0.5 | Bakulia | 132 | 0.77083 | 125 | 0.45833
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | Julda | 131 | 0.75 | 126 | 0.41667
Narsinghdi | 134 | 0.20833 | 130 | 0.8125 | TK Chemical | 133 | 0.8125 | 127 | 0.41667
Haripur (SBU) | 134 | 0.041667 | 127 | 0.54167 | Modern Steel | 132 | 0.77083 | 126 | 0.41667
Ullon | 129 | 0.25 | 124 | 0.5 | Shahmirpur | 132 | 0.77083 | 127 | 0.41667
Hasnabad | 135 | 0.25 | 126 | 0.5 | Khagrachhari | 132 | 0.77083 | 128 | 0.375
Magbazar | 130 | 0.25 | 124 | 0.5 | Matarbari | 128 | 0.083333 | 124 | 0.41667
Maniknagar | 137 | 0.25 | 132 | 0.45833 | Baroiar Hat | 133 | 0.70833 | 129 | 0.45833
Bangabhaban | 137 | 0.25 | 132 | 0.45833 | Rangamati | 132 | 0.16667 | 128 | 0.45833
Narinda | 137 | 0.25 | 132 | 0.45833 | Goalpara | 137 | 0.083333 | 121 | 13:00
Dhanmondi | 129 | 0.25 | 124 | 0.5 | Central s/s | 135 | 0.083333 | 121 | 18:00
Lalbag | 134 | 0.20833 | 124 | 0.45833 | Noapara | 134 | 0.125 | 122 | 0.54167
Madartek | 130 | 0.25 | 123 | 0.5 | Jessore | 136 | 0.16667 | 118 | 0.54167
Mirpur | 135 | 0.25 | 129 | 0.54167 | Benapol | 134 | 0.125 | 117 | 0.29167
Kalyanpur | 137 | 0.25 | 131 | 12;00 | Jhenida | 132 | 0.16667 | 116 | 0.75
Gulshan | 128 | 0.25 | 123 | 12;00 | Bottail | 136 | 0.20833 | 120 | 0.75
Uttara | 137 | 0.95833 | 129 | 12;00 | G.K Project | 137 | 0.083333 | 126 | 0.5
Uttara New | 137 | 0.95833 | 128 | 12;00 | Faridpur | 138 | 0.20833 | 124 | 0.66667
Kamrangirchar | 133 | 0.25 | 124 | 12;00 | Madaripur | 139 | 0.375 | 125 | 0.75
Savar | 134 | 0.25 | 127 | 12;00 | Sariatpur | 140 | 0.16667 | 130 | 0.75
Bhasantec | 135 | 0.25 | 127 | 12;00 | Gopalganj | 145 | 0.8125 | 132 | 0.54167
Agargaon | 136 | 0.25 | 129 | 0.45833 | Bagerhat | 133 | 0.041667 | 120 | 0.54167
Satmosjid | 136 | 0.20833 | 129 | 0.45833 | Mongla | 132 | 0.125 | 117 | 0.75
Tongi | 138 | 0.16667 | 132 | 0.45833 | Satkhira | 135 | 0.083333 | 119 | 0.29167
Kabirpur | 133 | 0.083333 | 125 | 0.54167 | Gallamari | 137 | 0.125 | 124 | 0.54167
Basundhara | 130 | 23:00 | 124 | 0.54167 | Magura | 133 | 0.20833 | 115 | 0.75
Manikganj | 139 | 3:00 | 131 | 0.54167 | Norail | 130 | 0.125 | 115 | 0.77083
Joydevpur | 142 | 0.83333 | 134 | 0.77083 | Chuadanga | 131 | 0.041667 | 110 | 0.77083
New Tongi | 138 | 0.16667 | 131 | 0.5 | Barisal(N) | 140 | 0.083333 | 125 | 0.75
Kodda | 135 | 0.66667 | 126 | 0.625 | Barisal (S) | 139 | 0.375 | 126 | 0.75
Dhamrai | 133 | 0.083333 | 125 | 0.54167 | Patuakhali | 136 | 0.16667 | 119 | 0.75
Valuka | 126 | 0.083333 | 119 | 0.58333 | Bhandaria | 138 | 0.375 | 123 | 0.75
Tangail | 131 | 0.16667 | 124 | 0.54167 | Ishurdi | 137 | 0.125 | 127 | 0.54167
Mymensing | 128 | 0.16667 | 119 | 0.8125 | Ruppur Paromanobik | 135 | 0.083333 | 129 | 0.5
Kishorganj | 131 | 0.16667 | 125 | 0.875 | Natore | 133 | 0.20833 | 124 | 0.54167
Netrokona | 127 | 0.20833 | 116 | 0.8125 | Bogra | 136 | 0.16667 | 129 | 0.33333
Jamalpur | 133 | 0.75 | 117 | 0.33333 | Noagaon | 132 | 0.16667 | 122 | 0.54167
Sherpur | 132 | 0.75 | 118 | 0.54167 | Rajshahi | 132 | 0.041667 | 120 | 0.5
Srimongal | 140 | 0.375 | 137 | 0.75 | Rajshahi New | 133 | 0.125 | 117 | 0.54167
Shahjibazar | 137 | 0.16667 | 134 | 0.8125 | C.Nawabganj | 129 | 0.041667 | 117 | 0.54167
Fenchuganj | 139 | 0.125 | 137 | 0.41667 | Amnura | 131 | 0.16667 | 117 | 0.54167
Khulawara | 138 | 0.125 | 137 | 1:00 | Pabna | 137 | 0.083333 | 126 | 0.75
Sylhet | 137 | 0.083333 | 135 | 0.5 | Shahjadpur | 144 | 0.125 | 135 | 0.75
Chatak | 137 | 0.125 | 135 | 0.41667 | Serajganj | 138 | 0.125 | 130 | 0.5
Sunamganj | 137 | 0.041667 | 135 | 0.375 | Niyamatpur | 130 | 0.16667 | 120 | 0.54167
Biani Bazar | 137 | 0.041667 | 135 | 0.54167 | Joypurhat | 134 | 0.083333 | 122 | 0.54167
Comilla(s) | 134 | 0.041667 | 129 | 0.75 | Sherpur(Bogura) | 137 | 0.16667 | 130 | 0.33333
Comilla(n) | 138 | 0.29167 | 136 | 0.75 | Mohastangor | 135 | 0.16667 | 129 | 0.33333
Chandpur | 136 | 21:00 | 135 | 0.041667 | Rangpur | 131 | 0.083333 | 124 | 0.375
Feni | 138 | 0.77083 | 130 | 0.45833 | Lalmonirhat | 128 | 0.25 | 118 | 0.54167
Chowmuhani | 131 | 0.29167 | 127 | 0.83333 | Saidpur | 132 | 0.20833 | 122 | 0.77083
Ashuganj | 138 | 0.25 | 135 | 0.66667 | Purbasadipur | 131 | 0.16667 | 118 | 0.77083
Daudkandi | 135 | 0.91667 | 130 | 0.45833 | Thakurgaon | 130 | 0.25 | 117 | 0.77083
B.Baria | 135 | 0.375 | 131 | 0.8125 | Palashbari | 130 | 0.125 | 118 | 0.54167
Ramganj | 132 | 0.75 | 130 | 0.79167 | Barapukuria | 134 | 0.16667 | 129 | 0.375
Chaddagram | 136 | 0.70833 | 133 | 0.41667 | Panchagar | 127 | 0.25 | 110 | 0.77083
PHP | 132 | 0.75 | 130 | 0.79167 | Joldhaka | 131 | 0.16667 | 121 | 0.77083
Madanhat | 133 | 0.75 | 130 | 0.45833 | Kurigram | 132 | 0.20833 | 122 | 0.54167
Hathazari | 135 | 0.77083 | 130 | 0.41667
Khulshi | 131 | 0.83333 | 125 | 0.41667

## L-Curve
Date | 2020-01-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 497 | 5092 | 1513 | 6605 |  |  |  | QF-LDC-12
0:30 | 442 | 4833.5 | 1509 | 6342.5 | Date: | 2020-01-21
1:00 | 387 | 4575 | 1505 | 6080
1:30 | 358 | 4501 | 1517.5 | 6018.5
2:00 | 329 | 4427 | 1530 | 5957
2:30 | 313.5 | 4333.5 | 1506 | 5839.5 | [5 empty] | Gen. at Eve. Peak | 9009 | 9009 MW (19:00 )
3:00 | 298 | 4240 | 1482 | 5722 | [6 empty] | 19:00
3:30 | 293 | 4173.5 | 1449.5 | 5623 | [5 empty] | Gen. at Day Peak | 6999.4 | 6999.4 MW (12:00 )
4:00 | 288 | 4107 | 1417 | 5524 | [6 empty] | 12:00
4:30 | 285.5 | 4088.5 | 1413 | 5501.5 | [5 empty] | Highest Generation | 9009
5:00 | 283 | 4070 | 1409 | 5479 | [6 empty] | 19:00
5:30 | 309.5 | 4176 | 1448 | 5624
6:00 | 336 | 4282 | 1487 | 5769
6:30 | 357.5 | 4476.92 | 1524 | 6000.92
7:00 | 379 | 4671.84 | 1561 | 6232.84
7:30 | 386.5 | 4817.77 | 1676.6 | 6494.37
8:00 | 394 | 4963.7 | 1792.2 | 6755.9
8:30 | 338.5 | 5027.32 | 1838.5 | 6865.82
9:00 | 283 | 5090.94 | 1884.8 | 6975.74
9:30 | 160 | 4988.405 | 1914.05 | 6902.455
10:00 | 37 | 4885.87 | 1943.3 | 6829.17
10:30 | 35.5 | 4901.3985 | 1945.1 | 6846.4985
11:00 | 34 | 4916.927 | 1946.9 | 6863.827
11:30 | 26 | 4935.5635 | 1996.05 | 6931.6135
12:00 | 18 | 4954.2 | 2045.2 | 6999.4
12:30 | 44.5 | 4958.68 | 2059.95 | 7018.63
13:00 | 71 | 4963.16 | 2074.7 | 7037.86
13:30 | 40 | 4863.33 | 2065.3 | 6928.63
14:00 | 9 | 4763.5 | 2055.9 | 6819.4
14:30 | 78 | 4752.65 | 2050.15 | 6802.8
15:00 | 147 | 4741.8 | 2044.4 | 6786.2
15:30 | 143.5 | 4647.25 | 2022.8 | 6670.05
16:00 | 140 | 4552.7 | 2001.2 | 6553.9
16:30 | 165.5 | 4714.05 | 1791.7 | 6505.75
17:00 | 191 | 4875.4 | 1582.2 | 6457.6
17:30 | 336.5 | 5352.2 | 1844.6 | 7196.8
18:00 | 482 | 5829 | 2107 | 7936
18:30 | 528.5 | 6173.5 | 2299 | 8472.5
19:00 | 575 | 6518 | 2491 | 9009
19:30 | 560 | 6353 | 2508 | 8861
20:00 | 510 | 6385 | 2511 | 8896 |  |  |  | Executive Engineer
20:30 | 485 | 6281 | 2456.5 | 8737.5 |  |  |  | Network Operation Division
21:00 | 460 | 6177 | 2402 | 8579
21:30 | 427 | 6017 | 2278 | 8295
22:00 | 394 | 5857 | 2154 | 8011 |  |  |  |  | Page 6 of 7
22:30 | 409.5 | 5681 | 1915.5 | 7596.5
23:00 | 425 | 5505 | 1677 | 7182
23:30 | 461 | 5298.5 | 1595 | 6893.5
24:00 | 497 | 5092 | 1513 | 6605
9009 MW (19:00 )
6999.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-01-21 |  | Energy | 167455995
[10 empty] | 2020-01-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4029 | 210 | 1767 | 392 | 417 | 40 | 0 | 0 | 70
0:30 | 3931.5 | 173.5 | 1607.5 | 196 | 479.5 | 40.5 | 0 | 0 | 74 | Date: | 2020-01-21
1:00 | 3834 | 137 | 1448 | 0 | 542 | 41 | 0 | 0 | 78
1:30 | 3760.5 | 136.5 | 1460.5 | 0 | 544 | 41 | 0 | 0 | 76 | [7 empty] | Total Energy | 167.456 | Total Energy Gen 167.456 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.456 MKWHr
2:00 | 3687 | 136 | 1473 | 0 | 546 | 41 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3613.5 | 136 | 1431.5 | 0 | 544 | 41.5 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 167.456
3:00 | 3540 | 136 | 1390 | 0 | 542 | 42 | 0 | 0 | 72
3:30 | 3487.5 | 135.5 | 1344 | 0 | 542 | 42 | 0 | 0 | 72 | [6 empty] | Shortage
4:00 | 3435 | 135 | 1298 | 0 | 542 | 42 | 0 | 0 | 72
4:30 | 3401 | 137 | 1307 | 0 | 542 | 42.5 | 0 | 0 | 72
5:00 | 3367 | 139 | 1316 | 0 | 542 | 43 | 0 | 0 | 72
5:30 | 3404.5 | 139.5 | 1422.5 | 0 | 542.5 | 43 | 0 | 0 | 72
6:00 | 3442 | 140 | 1529 | 0 | 543 | 43 | 0 | 0 | 72
6:30 | 3566.5 | 139.5 | 1635.5 | 0 | 544 | 43 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3691 | 139 | 1742 | 0 | 545 | 43 | 0 | 0 | 72
7:30 | 3823 | 223.5 | 1733 | 22 | 572 | 43 | 0 | 0 | 75 |  |  |  | Oil |  |  |  | ,
8:00 | 3955 | 308 | 1724 | 44 | 599 | 43 | 0 | 0 | 78
8:30 | 3941 | 308 | 1778.5 | 80 | 629.5 | 42.5 | 0 | 0 | 78
9:00 | 3927 | 308 | 1833 | 116 | 660 | 42 | 0 | 0 | 78
9:30 | 3902.5 | 308 | 1726.5 | 116 | 712 | 42 | 0 | 0 | 80
10:00 | 3878 | 308 | 1620 | 116 | 764 | 42 | 0 | 0 | 82
10:30 | 3877.5 | 306.5 | 1609 | 133 | 773 | 42 | 0 | 0 | 84
11:00 | 3877 | 305 | 1598 | 150 | 782 | 42 | 0 | 0 | 86
11:30 | 3890.5 | 305 | 1634 | 168.5 | 783 | 42 | 0 | 0 | 83
12:00 | 3904 | 305 | 1670 | 187 | 784 | 42 | 0 | 0 | 80
12:30 | 3905.5 | 305 | 1660 | 186 | 815 | 40 | 0 | 0 | 80
13:00 | 3907 | 305 | 1650 | 185 | 846 | 38 | 0 | 0 | 80
13:30 | 3907 | 305 | 1650 | 185 | 846 | 38 | 0 | 0 | 80
14:00 | 3907 | 305 | 1650 | 185 | 846 | 38 | 0 | 0 | 80
14:30 | 3815 | 304.5 | 1590.5 | 187 | 876.5 | 38 | 0 | 0 | 79
15:00 | 3723 | 304 | 1531 | 189 | 907 | 38 | 0 | 0 | 78
15:30 | 3715.5 | 304 | 1475 | 153 | 894.5 | 38 | 0 | 0 | 77
16:00 | 3708 | 304 | 1419 | 117 | 882 | 38 | 0 | 0 | 76
16:30 | 3758 | 304 | 1549.5 | 143.5 | 631 | 38 | 0 | 0 | 76
17:00 | 3808 | 304 | 1680 | 170 | 380 | 38 | 0 | 0 | 76
17:30 | 3892 | 425.5 | 1718 | 651 | 386.5 | 38 | 0 | 0 | 85
18:00 | 3976 | 547 | 1756 | 1132 | 393 | 38 | 0 | 0 | 94
18:30 | 4119 | 597 | 1872 | 1345 | 407.5 | 39 | 0 | 0 | 93
19:00 | 4262 | 647 | 1988 | 1558 | 422 | 40 | 0 | 0 | 92
19:30 | 4283 | 648 | 2032 | 1344 | 422 | 40 | 0 | 0 | 92
20:00 | 4337 | 648 | 2042 | 1321 | 422 | 40 | 0 | 0 | 86
20:30 | 4275 | 648 | 2025 | 1232 | 422.5 | 40 | 0 | 0 | 95
21:00 | 4213 | 648 | 2008 | 1143 | 423 | 40 | 0 | 0 | 104
21:30 | 4168 | 598.5 | 1995 | 976 | 420.5 | 40 | 0 | 0 | 97
22:00 | 4123 | 549 | 1982 | 809 | 418 | 40 | 0 | 0 | 90
22:30 | 4122 | 427.5 | 1906 | 600.5 | 417.5 | 40 | 0 | 0 | 83
23:00 | 4121 | 306 | 1830 | 392 | 417 | 40 | 0 | 0 | 76
23:30 | 4075 | 258 | 1798.5 | 392 | 417 | 40 | 0 | 0 | 73 | Max Temp. in Dhaka |  | 23.7° C
24:00 | 4029 | 210 | 1767 | 392 | 417 | 40 | 0 | 0 | 70
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
HVDC
COAL
HYDRO
Total Energy Gen 167.456 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 167.456 MKWHr
Note on W13: Author:

## Generation
2020-01-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 41 | 41 | 42 | 42 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 38 | 40 | 38 | 38 | 38 | 38 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 893640
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.6 | 3.91 | 9.22 | 13.27 | 16.48 | 18.22 | 17.36 | 15 | 10 | 5.9 | 1 | [9 empty] | 110970
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 153 | 151 | 151 | 150 | 151 | 151 | 151 | 151 | 151 |  | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 3648988
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 145 | 140 | 104 | 104 | 103 | 104 | 105 | 104 | 106 | 140 | 150 | 140 | 139 | 139 | 139 | 139 | 140 | 139 |  | 141 | 139 | 140 | 139 | 139 | 141 | 142 | 3144769
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 |  |  |  | 84105
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 230 | 230 | 210 | 210 | 210 | 210 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 310 | 326 | 330 | 315 | 270 | 260 | 222 | 5971430
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1689000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 106 | 100 | 100 | 100 | 100 | 101 | 100 | 100 | 100 | 101 |  | 100 | 152 | 150 | 150 | 151 | 150 | 150 | 2679000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 288 | 290 | 290 | 250 | 200 | 230 | 290 | 290 | 290 | 270 | 270 | 270 | 270 | 250 | 250 | 250 | 290 | 270 |  | 343 | 330 | 335 | 325 | 320 | 320 | 335 | 6738727
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 |  | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 2454410
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 40 | 40 | 37 | 37 | 37 | 40 | 40 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 743832
33 | Ashuganj 225 MW CCPP | 194 | 166 | 159 | 141 | 131 | 160 | 191 | 237 | 185 | 175 | 178 | 180 | 162 | 167 | 161 | 162 | 160 | 198 |  | 172 | 194 | 200 | 174 | 180 | 181 | 199 | 4245000
34 | Ashuganj 450 MW CCPP(South) | 310 | 270 | 270 | 270 | 275 | 270 | 270 | 295 | 295 | 295 | 310 | 305 | 360 | 325 | 320 | 320 | 320 | 345 |  | 340 | 330 | 345 | 330 | 320 | 325 | 310 | 7510000
| Ashuganj 450 MW CCPP(North) | 300 | 260 | 260 | 260 | 265 | 265 | 290 | 290 | 290 | 310 | 295 | 305 | 270 | 265 | 260 | 260 | 260 | 285 |  | 345 | 330 | 345 | 320 | 310 | 310 | 285 | 7296300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 42 | 20 | 20 | 5 | 5 | 5 | 5 | 207360
36 | Chandpur 150 MW CCPP | 89 | 89 | 88 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 88 | 90 | 88 |  | 89 | 89 | 89 | 88 | 88 | 90 | 90 | 2119310
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 362 | 362 | 305 | 275 | 260 | 270 | 335 | 370 | 370 | 370 | 370 | 356 | 369 | 305 | 300 | 300 | 300 | 300 |  | 330 | 342 | 355 | 352 | 340 | 335 | 352 | 8124410
40 | Meghnaghat 450 MW CCPP(MPL) | 310 | 310 | 310 | 300 | 300 | 360 | 420 | 420 | 420 | 350 | 330 | 330 | 330 | 300 | 300 | 260 | 400 | 370 |  | 450 | 450 | 450 | 450 | 450 | 350 | 350 | 8549250
41 | Haripur 360MW CCPP(HPL) | 314 | 314 | 252 | 254 | 254 | 316 | 374 | 372 | 370 | 289 | 290 | 290 | 290 | 260 | 260 | 260 | 305 | 290 |  | 317 | 333 | 344 | 332 | 322 | 332 | 313 | 7242000
42 | RPCL 210MW CCPP | 149 | 151 | 151 | 151 | 152 | 165 | 165 | 165 | 164 | 162 | 146 | 147 | 126 | 127 | 127 | 127 | 127 | 127 |  | 128 | 127 | 126 | 126 | 106 | 109 | 128 | 3266880
43
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1563120
46 | Shajibazar 330 MW CCPP | 155 | 152 | 146 | 146 | 150 | 146 | 150 | 149 | 151 | 145 | 147 | 144 | 142 | 142 | 142 | 143 | 143 | 150 |  | 150 | 148 | 150 | 150 | 148 | 144 | 140 | 3308000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 69 | 67 | 66 | 64 | 64 | 64 | 64 | 65 | 45 | 45 | 45 |  | 67 | 67 | 68 | 69 | 69 | 69 | 69 | 1377120
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 30 | 967680
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 38 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 77 | 118 |  | 122 | 127 | 122 | 117 | 117 | 119 | 77 | 1451880
51 | Sylhet 20 MW GTPP | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 311000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 161280
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 11 | 11 | 5 | 0 | 5 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 140104
55 | Fenchugonj 51 MW PP (Barakatullah) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 28 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 369000
56 | Shahjahanulla 25 MW PP | [7 empty] | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 10 | 397248
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 280 | 275 | 290 | 305 | 305 | 295 | 295 | 280 | 300 | 310 | 320 | 290 | 300 | 280 | 290 | 260 |  | 310 | 320 | 320 | 310 | 310 | 290 | 270 | 7418200
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 443232
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 332064
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 17 | 14 | 14 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 320040
63 | Impoprt (Tripura) | 78 | 74 | 72 | 72 | 72 | 72 | 72 | 78 | 78 | 82 | 86 | 80 | 80 | 82 | 78 | 76 | 76 | 94 |  | 92 | 92 | 86 | 104 | 90 | 76 | 70 | 1899840
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 37 | 37 | 42 | 42 | 38 | 10 | 3 | 3 | 2 | 3 | 10 | 5 | 3 | 3 | 4 | 17 |  | 28 | 32 | 33 | 36 | 40 | 36 | 37 | 540960
65 | Feni 22MW PP (Doreen) | [6 empty] | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 370512
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 145260
67 | Jangalia 33MW PP (Summit) | [7 empty] | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 0 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 350000
68 | Cumilla 25 MW PP (Summit) | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 302480
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 32 | 32 | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 17 |  | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 692460
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 18 | 18 | 614600
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 |  | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 799100
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [16 empty] | 5 | 18 | [7 empty] | 0 | 43320
| Chowmuhani 113 MW | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 2 | 24 |  | 45 | 7 |  |  |  |  | 0 | 79680
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 32 | 65 |  | 95 | 95 | 95 | 95 | 95 | 50 | 24 | 1019520
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.24 | 0.59 | 1.22 | 2.1 | 3.747 | 3.98 | 3.8 | 3.2 | 2.3 | 1.2 | 0.2 | 0 | [8 empty] | 22800
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 30 |  | 15 | 15 | 0 | 0 |  |  |  | 113040
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 21 | [7 empty] | 0 | 56928
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 2 | 60 |  | 100 | 100 | 100 | 100 | 96 | 55 | 0 | 557760
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 10 |  | 0 | 0 | [5 empty] | 35760
92 | Fenchuganj 44MW (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 26 | 50 | 50 | 50 | 50 | 46 | 46 | 46 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 825120
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 795404
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 16 | 85 |  | 100 | 93 | 93 | 93 | 93 | 50 | 0 | 51088
95 | Patenga 50MW PP (Baraka) | [17 empty] | 32 |  | 50 | 50 | 50 | 50 |  |  | 0 | 218880
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 2 |  |  |  |  | 3 | 46 |  | 25 | [5 empty] | 0 | 88320
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 4 |  | 36 | 47 | 48 |  |  |  | 0 | 110448
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 33 |  | 15 | 15 | 0 | 0 |  |  |  | 90865
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 35 |  | 55 | 55 | 55 | 35 |  |  | 0 | 503553
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3264954
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.2 | 0.5 | 1.5 | 1.7 | 2 | 2 | 1.3 | 1.5 | 0.6 | 0.2 | 0 | [8 empty] | 11500
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 535320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [25 empty] | 0 | 0
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 80 |  | 90 | 90 | 90 | 90 | 0 | 0 |  | 331200
116 | Chandpur 200MW (Desh energy) | [17 empty] | 32 |  | 80 | 0 | 0 |  |  |  |  | 116640
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 20 |  | 40 | [5 empty] | 0 | 75272
118 | Bibiyana-III 400 MW CCPP | 229 | 229 | 230 | 230 | 230 | 230 | 228 | 228 | 229 | 229 | 229 | 229 | 229 | 230 | 230 | 230 | 230 | 230 |  | 231 | 229 | 229 | 228 | 229 | 229 | 229 | 5501000
| Jamalpur 115 MW PP (United) | [16 empty] | 5 | 38 |  | 70 | 16 | 16 | 16 |  |  | 0 | 196800
| Anwara 300 MW PP (United) | [7 empty] | 5 | 16 | 16 | 50 | 85 | 85 | 89 | 89 | 51 | 51 | 188 |  | 194 | 194 | 199 | 197 | 199 | 105 | 16 | 1723745
120 | Eastern Zone Total | 4575 | 4427 | 4240 | 4107 | 4070 | 4282 | 4671.84 | 4963.7 | 5090.94 | 4885.87 | 4916.927 | 4954.2 | 4963.16 | 4763.5 | 4741.8 | 4552.7 | 4875.4 | 5829 |  | 6518 | 6353 | 6385 | 6177 | 5857 | 5505 | 5092 | 121880205
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [16 empty] | 8 | 49 |  | 83 | 83 | 83 | 83 | 83 | 32 | 0 | 405120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 0 | 0 |  | 32 | 40 | 48 | 48 | 48 | 0 |  | 188160
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [7 empty] | 0 | 25 | 24 | 0 | [5 empty] | 10 | 43 |  | 44 | 44 | 43 | 43 | 44 | 43 | 44 | 361853
| Bhola 225 MW CCPP | 155 | 155 | 155 | 155 | 155 | 155 | 156 | 155 | 100 | 99 | 98 | 96 | 96 | 84 | 79 | 78 | 90 | 97 |  | 98 | 97 | 97 | 97 | 97 | 97 | 97 | 2784594
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 12 | 12 | 10 | 11 | 13 | 13 | 14 | 12 | 11 | 12 | 18 |  | 19 | 20 | 21 | 21 | 20 | 18 | 16 | 344400
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [17 empty] | 0 |  | 16 | 16 | 16 | 16 | 0 |  |  | 43125
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 50 |  | 105 | 105 | 105 | 105 | 50 | 32 | 15 | 484704
146 | Bheramara HVDC | 137 | 136 | 136 | 135 | 139 | 140 | 139 | 308 | 308 | 308 | 305 | 305 | 305 | 305 | 304 | 304 | 304 | 547 |  | 647 | 648 | 648 | 648 | 549 | 306 | 210 | 7737454
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 260 | 263 | 260 | 259 | 260 | 261 | 260 | 288 | 306 | 382 | 401 | 401 | 462 | 493 | 523 | 500 | 0 | [9 empty] | 5741300
149
150 | Barapukuria TPP Unit-1 | 122 | 123 | 122 | 123 | 122 | 122 | 120 | 121 | 121 | 122 | 121 | 123 | 124 | 124 | 123 | 122 | 120 | 121 |  | 122 | 122 | 122 | 123 | 123 | 122 | 122 | 2920581
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 165 | 190 | 233 | 260 | 260 | 260 | 260 | 260 | 261 | 260 | 260 | 272 |  | 300 | 300 | 300 | 300 | 295 | 295 | 295 | 5667400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 150 | 150 | 140 | 130 | 130 | 130 | 145 | 170 | 170 | 170 | 200 | 200 | 195 | 170 | 170 | 175 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4384309
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 158 | 160 | 138 | 133 | 133 | 133 | 133 | 165 | 189 | 159 | 171 | 176 | 180 | 171 | 167 | 172 | 171 | 167 |  | 182 | 177 | 174 | 172 | 172 | 171 | 159 | 4111036
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 336 | 356 | 336 | 287 | 285 | 361 | 430 | 394 | 396 | 371 | 372 | 432 | 395 | 371 | 367 | 346 | 396 | 385 |  | 385 | 387 | 385 | 385 | 365 | 355 | 375 | 8840363
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [8 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  |  | 293520
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 |  |  | 55332
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 245502
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 32 |  | 32 | 32 | 32 | 32 | 18 |  |  | 153720
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 40 |  | 108 | 108 | 108 | 0 |  |  |  | 314112
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 70 |  | 102 | 113 | 113 | 113 | 74 | 15 |  | 479040
177 | Sympa Solar Power 8MW | [7 empty] | 0.2 | 0.8 | 2.3 | 1.9 | 3.2 | 3.7 | 2.9 | 2.4 | 2.2 | 0.2 | [9 empty] | 20165
178
178