## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-02 | Sunday
|  | Date (day): | 2020-02-02 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11695.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14564 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-01 | 2020-02-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 240 | 171 | 220 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 360 | 360 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | .
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 347 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 320 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 66 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 | 305 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 23 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 300 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 48 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 31 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 53 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 44 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2070 | 2435 | 3800 | 4451 | 806 | 575
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3.13 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 36 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 80 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 26 | 155 | 155
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 103 | 144 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 16 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 27 | 20 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100 |  |  | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0.7 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 33 | 223 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 286.83 | 769 | 1420 | 1565 | 420 | 108
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 135 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  | 129 | Under maint
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 100 | 135 | 135
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 165 | 225 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 43 | 43 | 43
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 112 | 55 | 110 | 85 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 52 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 90 |  | 73 | ST Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 106 | 89 | 100
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1067 | 1274 | 1452 | 2182 | 135 | 202
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 165 | 158 | 160 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 92 | 93 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 134 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 24 | 115 | 50 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 301.7 | 520 | 428.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 58 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 22 | 22
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 141 | 155 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 44 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 66 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 77 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 98 | 127 | 140 | 140 | 2
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 146 | 145 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1032 | 1220 | 1398 | 1398 | 2 | 370
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 299 | 640 | 402 | 747
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 310 | 325 | 340 | 340 | 70 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 15 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 609 | 1062 | 1100 | 1916 | 70 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 0 | 19 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 144 | 150 | 150 |  | 44 | ST under shut down
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 60 | 95 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 144 | 306 | 335 | 405 | 0 | 57
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 40 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 210 | 210
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 385 | 432 | 410 | 410 | ` |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 5 | 3 | 4 |  | 6 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 34 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 87 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 414 | 631 | 1231 | 1498 | 171 | 16
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 119 | 121 | 125 | 125
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 285 | 285
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 469.8 | 514 | 531 | 557 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 6394.33 | 8731 | 11695.6 | 14564 | 1646 | 1420
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6006.9058 | 8202 | 10986.9787 | 13681.5861
A. |  | 2020-02-01 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8731 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5350 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8731 | MW
3 | Day peak Generation : |  |  | 6394.33 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8202 | MW
4 | Evening peak Generation : |  |  | 8731 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 160.7677 | MKWHr | By Solar | 0.14208 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 130.4962 | MKWHr |  | By Oil: | 9.5587 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 9.608 | MKWHr |  | By Hydro: | 1.3558 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1646 | MW | Dhaka | 2652 | 2652 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1420 | MW | Chittagong | 831 | 831 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3066 | MW | Khulna | 1065 | 1065 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1075.26 | MMCFD |  |  | Rajshahi | 962 | 962 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 122557571.22 | ii) Oil : | Taka | 87044453.77 | Comilla | 736 | 736 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 45772540.3 | Total | Taka | 255374565.29 | Mymensingh | 767 | 767 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6.9455 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -591 | MW (E to W) at | 19:00 | hrs | Barisal | 220 | 220 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -662 | MW at | 7:00 | hrs | Rangpur | 647 | 647 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.0° C |  |  | Total | 8202 | 8202 |  | 0
B. |  | 2020-02-02 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 24.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14564 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 5564 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 165.721 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5467 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.6284 | MKWHr. | ii) HVDC Flow at Peak Time |  | 640 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9786 | MKWHr. | iii) Maximum HVDC Flow : |  | 640 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.21 |  | (b) Today: | 94.14 |  | (c) Rule Curve: |  | 96.86
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-02-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 149 | 0 | 380 | 0 | 0 | 342 | 314 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 125 | 0 | 310 | 182 | 26 | 90 | 43 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 66 | 161 | 0 | 22 | 0 | 59 | 42 | 5 | 5 | 130 | 150 | 45 | 5 | 0 | 69 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 123 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4544 | 1371 | 5915 | 3614 | 137 | 1663 | 0 | 403 | 32 | 0 | 66 | 0 | 0 | 94.21
2:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 343 | 314 |  | 0 | 360 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 80 | 0 | 270 | 192 | 26 | 90 | 10 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 21 | 66 | 161 | 0 | 22 | 0 | 60 | 42 | 5 | 5 | 100 | 154 | 45 | 5 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 122 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4306 | 1362 | 5668 | 3404 | 137 | 1627 | 0 | 402 | 32 | 0 | 66 | 0 | 0 | 94.21
3:00 | 72 | 0 | 151 | 0 | 380 | 0 | 0 | 341 | 314 |  | 0 | 360 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 102 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 80 | 0 | 270 | 163 | 26 | 89 | 10 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 64 | 162 | 0 | 22 | 0 | 60 | 42 | 5 | 5 | 100 | 151 | 45 | 5 | 0 | 67 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 116 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4211 | 1347 | 5558 | 3320 | 137 | 1609 | 0 | 396 | 32 | 0 | 64 | 0 | 0 | 94.21
4:00 | 72 | 0 | 149 | 0 | 380 | 0 | 0 | 342 | 293 |  | 0 | 300 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 80 | 0 | 265 | 163 | 26 | 89 | 10 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 64 | 165 | 0 | 22 | 0 | 60 | 42 | 5 | 5 | 100 | 144 | 45 | 5 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 119 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4071 | 1289 | 5360 | 3252 | 136 | 1477 | 0 | 399 | 32 | 0 | 64 | 0 | 0 | 94.21
5:00 | 72 | 0 | 152 | 0 | 380 | 0 | 0 | 341 | 293 |  | 0 | 300 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 80 | 0 | 270 | 163 | 26 | 89 | 10 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 64 | 165 | 0 | 22 | 0 | 60 | 42 | 5 | 5 | 100 | 144 | 45 | 5 | 0 | 68 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 119 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4078 | 1272 | 5350 | 3259 | 137 | 1459 | 0 | 399 | 32 | 0 | 64 | 0 | 0 | 94.21
6:00 | 72 | 0 | 152 | 0 | 380 | 0 | 0 | 367 | 302 |  | 0 | 340 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 29 | 0 | 0 | 32 | 0 | 110 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 80 | 0 | 330 | 204 | 26 | 89 | 10 | 5 | 0 | 14 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 68 | 162 | 0 | 22 | 0 | 60 | 0 | 5 | 5 | 100 | 150 | 45 | 5 | 0 | 100 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 116 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4386 | 1273 | 5659 | 3454 | 136 | 1573 | 0 | 396 | 32 | 0 | 68 | 0 | 0 | 94.21
7:00 | 71 | 0 | 259 | 0 | 380 | 0 | 0 | 366 | 328 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 29 | 0 | 0 | 30 | 0 | 110 | 0 | 0 | 0 | 0 | 85 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 100 | 0 | 135 | 0 | 345 | 203 | 26 | 89 | 43 | 5 | 0 | 20 | 0 | 0 | 0 | 22 | 0 | 0 | 14 | 72 | 161 | 4 | 22 | 0 | 60 | 0 | 5 | 10 | 130 | 157 | 57 | 5 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 117 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4719.2 | 1411.1 | 6130.3 | 3787 | 136 | 1704 | 4 | 397 | 30 | 0 | 72 | 0.3 | 0 | 94.2
8:00 | 72 | 0 | 237 | 0 | 368 | 0 | 0 | 350 | 330 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 17 | 0 | 0 | 30 | 0 | 110 | 0 | 0 | 0 | 0 | 85 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 100 | 0 | 135 | 0 | 330 | 198 | 26 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 70 | 164 | 72 | 22 | 0.4 | 60 | 0 | 50 | 50 | 130 | 155 | 57 | 50 | 0 | 98 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 0 | 0 | 0 | 145 | 2 | 0 | 0 | 0.3 | 5 | 0 | 0 | 0 | 0 |  | 299 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 119 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 5 | 0 | 0.2 | 0 | 0 |  | 4878.76 | 1600.2 | 6478.96 | 3721 | 299 | 1874 | 84 | 399 | 30 | 0 | 70 | 1.96 | 0 | 94.2
9:00 | 72 | 0 | 240 | 0 | 360 | 0 | 0 | 345 | 300 |  | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 17 | 0 | 0 | 30 | 0 | 110 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 100 | 0 | 135 | 0 | 305 | 165 | 26 | 90 | 43 | 5 | 0 | 52 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 74 | 165 | 92 | 20 | 0.7 | 60 | 0 | 50 | 50 | 100 | 141 | 57 | 50 | 0 | 98 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 0 | 0 | 0 | 146 | 24 | 0 | 0 | 0.7 | 33 | 0 | 0 | 0 | 0 |  | 299 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 119 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 70 | 0 | 0.8 | 0 | 0 |  | 4757.53 | 1636.8 | 6394.33 | 3605 | 299 | 1745 | 237 | 399 | 30 | 0 | 74 | 5.33 | 0 | 94.2
10:00 | 72 | 0 | 240 | 0 | 360 | 0 | 0 | 300 | 280 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 17 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 100 | 0 | 135 | 0 | 285 | 175 | 26 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 78 | 161 | 92 | 20 | 1.3 | 60 | 0 | 11 | 10 | 100 | 142 | 45 | 10 | 0 | 69 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 12.86 | 0 | 0 | 0 | 144 | 24 | 0 | 0 | 1.2 | 65 | 0 | 0 | 0 | 0 |  | 299 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 122 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 74 | 0 | 1.7 | 0 | 0 |  | 4530.36 | 1662.7 | 6193.06 | 3500 | 299 | 1529 | 287 | 403 | 80 | 0 | 78 | 17.06 | 0 | 94.2
11:00 | 72 | 0 | 150 | 0 | 360 | 0 | 0 | 300 | 280 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 100 | 0 | 115 | 0 | 280 | 171 | 26 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 33 | 17 | 78 | 158 | 92 | 20 | 1.7 | 60 | 0 | 11 | 10 | 100 | 146 | 45 | 10 | 0 | 68 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 17.2 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 2.1 | 71 | 0 | 0 | 0 | 0 |  | 299 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 122 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 70 | 0 | 2.8 | 0 | 0 |  | 4494 | 1639.8 | 6133.8 | 3404 | 299 | 1533 | 314 | 402 | 80 | 0 | 78 | 23.8 | 0 | 94.2
12:00 | 72 | 0 | 0 | 0 | 360 | 0 | 0 | 348 | 242 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 20 | 25 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 0 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 125 | 0 | 100 | 0 | 345 | 222 | 26 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 33 | 14 | 84 | 156 | 92 | 20 | 1.8 | 60 | 0 | 11 | 10 | 100 | 165 | 52 | 10 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 18.55 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 4.1 | 71 | 0 | 0 | 0 | 0 |  | 300 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 114 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 71 | 0 | 4.1 | 0 | 0 |  | 4602.45 | 1758.1 | 6360.55 | 3567 | 300 | 1580 | 327 | 394 | 80 | 0 | 84 | 28.55 | 0 | 94.19
13:00 | 72 | 0 | 0 | 0 | 360 | 0 | 0 | 370 | 242 |  | 0 | 350 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 20 | 25 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 135 | 0 | 100 | 0 | 320 | 195 | 26 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 78 | 156 | 92 | 20 | 1.3 | 66 | 0 | 50 | 36 | 163 | 157 | 63 | 76 | 0 | 140 | 0 | 0 | 0 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 5.9 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 3.8 | 71 | 0 | 0 | 0 | 0 |  | 299 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 114 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 436 | 0 | 0 | 0 | 0 | 71 | 0 | 4.7 | 0 | 0 |  | 4969 | 1677.7 | 6646.7 | 3650 | 299 | 1806 | 325 | 393 | 80 | 0 | 78 | 15.7 | 0 | 94.19
14:00 | 72 | 0 | 0 | 0 | 360 | 0 | 0 | 343 | 255 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 20 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 16 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 135 | 0 | 100 | 0 | 270 | 163 | 26 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 86 | 157 | 84 | 20 | 1.3 | 48 | 20 | 50 | 44 | 130 | 145 | 63 | 76 | 0 | 80 | 0 | 0 | 0 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 14 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 3.14 | 71 | 0 | 0 | 0 | 0 |  | 299 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 123 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 71 | 0 | 3.8 | 0 | 0 |  | 4825.44 | 1629.8 | 6455.24 | 3495 | 299 | 1750 | 320 | 403 | 80 | 0 | 86 | 22.24 | 0 | 94.19
15:00 | 72 | 0 | 0 | 0 | 360 | 0 | 0 | 340 | 255 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 20 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 135 | 0 | 100 | 0 | 270 | 178 | 26 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 84 | 157 | 84 | 20 | 0.58 | 58 | 20 | 53 | 44 | 100 | 151 | 45 | 10 | 0 | 77 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 10 | 0 | 0 | 0 | 144 | 24 | 0 | 0 | 1.21 | 70 | 0 | 0 | 0 | 0 |  | 296 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 72 | 0 | 3 | 0 | 0 |  | 4755.79 | 1634 | 6389.79 | 3504 | 296 | 1692 | 319 | 400 | 80 | 0 | 84 | 14.79 | 0 | 94.19
16:00 | 72 | 0 | 100 | 0 | 360 | 0 | 0 | 295 | 255 |  | 0 | 420 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 20 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 27 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 135 | 0 | 100 | 0 | 280 | 175 | 26 | 89 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 80 | 156 | 84 | 20 | 0.4 | 35 | 20 | 53 | 44 | 100 | 154 | 45 | 10 | 0 | 78 | 0 | 0 | 10 | 290 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 4 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 1.21 | 71 | 0 | 0 | 0 | 0 |  | 297 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 71 | 0 | 1.6 | 0 | 0 |  | 4713.61 | 1723.6 | 6437.21 | 3550 | 297 | 1703 | 319 | 401 | 80 | 0 | 80 | 7.21 | 0 | 94.18
17:00 | 72 | 0 | 102 | 0 | 360 | 0 | 0 | 280 | 255 |  | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 22 | 25 | 22 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 11 | 135 | 0 | 100 | 0 | 275 | 168 | 26 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 78 | 158 | 93 | 20 | 0.1 | 33 | 20 | 53 | 44 | 100 | 152 | 45 | 10 | 0 | 78 | 0 | 0 | 10 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 0.28 | 71 | 0 | 0 | 0 | 0 |  | 299 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 135 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 71 | 0 | 0.4 | 0 | 0 |  | 4679.38 | 1702.4 | 6381.78 | 3493 | 299 | 1683 | 339 | 401 | 80 | 7 | 78 | 1.78 | 0 | 94.18
18:00 | 72 | 0 | 160 | 0 | 360 | 0 | 0 | 328 | 260 |  | 0 | 350 | 0 | 15 | 10 | 10 | 280 | 0 | 0 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 11 | 53 | 17 | 0 | 19 | 25 | 16 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 111 | 0 |  | 0 | 0 | 0 | 0 | 10 | 6 | 16 | 16 | 135 | 0 | 100 | 0 | 335 | 160 | 112 | 90 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 108 | 158 | 90 | 20 | 0 | 60 | 20 | 53 | 44 | 100 | 163 | 65 | 40 | 0 | 77 | 0 | 0 | 10 | 275 | 16 | 11 | 0 | 2 | 0 | 0 | 40 | 0 | 44 | 0 | 50 | 15 | 8 | 145 | 85 | 17 | 13 | 0 | 105 | 0 | 0 | 17 | 0 |  | 640 | 0 | 350 | 0 | 37 | 0 | 0 | 0 | 0 | 7 | 0 | 144 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 10 | 71 | 0 | 0 | 22 | 0 |  | 5402 | 2283 | 7685 | 3764 | 640 | 1816 | 839 | 401 | 80 | 37 | 108 | 0 | 0 | 94.18
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 171 | 0 | 360 | 0 | 0 | 347 | 320 |  | 0 | 420 | 0 | 66 | 0 | 0 | 300 | 0 | 0 | 0 | 23 | 48 | 0 | 0 | 0 | 0 | 31 | 53 | 35 | 0 | 19 | 25 | 28 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 16 | 27 | 135 | 0 | 100 | 0 | 320 | 225 | 112 | 91 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 106 | 158 | 93 | 20 | 0 | 58 | 20 | 53 | 44 | 130 | 155 | 66 | 77 | 0 | 127 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 134 | 0 | 44 | 0 | 90 | 0 | 0 | 145 | 115 | 17 | 17 | 0 | 223 | 0 | 0 | 0 | 0 |  | 640 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 144 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 15 | 113 | 0 | 0 | 87 | 0 |  | 6218 | 2513 | 8731 | 3938 | 640 | 2122 | 1410 | 401 | 80 | 34 | 106 | 0 | 0 | 94.17
19:30 | 72 | 0 | 170 | 0 | 360 | 0 | 0 | 345 | 320 |  | 0 | 420 | 0 | 50 | 0 | 0 | 335 | 0 | 0 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 18 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 31 | 0 | 0 | 33 | 50 | 110 | 0 | 0 | 26 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 16 | 28 | 135 | 0 | 100 | 0 | 320 | 225 | 112 | 91 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 106 | 159 | 93 | 20 | 0 | 58 | 20 | 53 | 44 | 130 | 152 | 66 | 77 | 0 | 122 | 0 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 145 | 0 | 44 | 0 | 90 | 0 | 0 | 145 | 115 | 17 | 17 | 0 | 228 | 0 | 0 | 0 | 0 |  | 640 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 144 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 15 | 113 | 0 | 0 | 95 | 0 |  | 6201 | 2529 | 8730 | 3972 | 640 | 2150 | 1343 | 402 | 83 | 34 | 106 | 0 | 0 | 0
20:00 | 72 | 0 | 170 | 0 | 360 | 0 | 0 | 345 | 320 |  | 0 | 420 | 0 | 50 | 0 | 0 | 335 | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 18 | 53 | 17 | 0 | 19 | 25 | 31 | 25 | 31 | 0 | 0 | 33 | 50 | 110 | 0 | 0 | 26 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 32 | 135 | 0 | 100 | 0 | 310 | 228 | 112 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 158 | 95 | 20 | 0 | 58 | 20 | 53 | 44 | 130 | 151 | 67 | 77 | 0 | 123 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 145 | 0 | 44 | 0 | 90 | 0 | 0 | 145 | 115 | 17 | 17 | 0 | 217 | 0 | 0 | 0 | 0 |  | 640 | 0 | 310 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 144 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 6 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 14 | 113 | 0 | 0 | 96 | 0 |  | 6176 | 2503 | 8679 | 3953 | 640 | 2128 | 1332 | 401 | 83 | 34 | 108 | 0 | 0 | 94.17
21:00 | 72 | 0 | 171 | 0 | 360 | 0 | 0 | 350 | 332 |  | 0 | 420 | 0 | 26 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 36 | 135 | 0 | 100 | 0 | 305 | 224 | 112 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 106 | 160 | 95 | 20 | 0 | 58 | 20 | 53 | 47 | 130 | 150 | 67 | 77 | 0 | 122 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 21 | 0 | 30 | 0 | 0 | 145 | 115 | 17 | 0 | 0 | 217 | 0 | 0 | 0 | 0 |  | 640 | 0 | 315 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 144 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 20 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 15 | 113 | 0 | 0 | 109 | 0 |  | 5906 | 2537 | 8443 | 3968 | 640 | 2153 | 1060 | 402 | 80 | 34 | 106 | 0 | 0 | 94.17
22:00 | 72 | 0 | 170 | 0 | 360 | 0 | 0 | 343 | 332 |  | 0 | 420 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 27 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 135 | 0 | 100 | 0 | 310 | 229 | 55 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 162 | 95 | 20 | 0 | 60 | 20 | 53 | 47 | 130 | 145 | 67 | 77 | 0 | 122 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 0 | 0 | 145 | 115 | 3 | 0 | 0 | 163 | 0 | 0 | 0 | 0 |  | 542 | 0 | 310 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 18 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 35 | 0 |  | 5656 | 2159 | 7815 | 3916 | 542 | 2065 | 710 | 402 | 80 | 0 | 100 | 0 | 0 | 94.16
23:00 | 72 | 0 | 168 | 0 | 360 | 0 | 0 | 337 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 31 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 135 | 0 | 100 | 0 | 325 | 194 | 55 | 88 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 160 | 95 | 20 | 0 | 60 | 20 | 53 | 47 | 130 | 154 | 67 | 77 | 0 | 122 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 90 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 |  | 299 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 123 | 0 | 280 | 0 | 0 | 18 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5462 | 1736 | 7198 | 3913 | 299 | 2068 | 345 | 403 | 80 | 0 | 90 | 0 | 0 | 94.16
24:00 | 72 | 0 | 169 | 0 | 360 | 0 | 0 | 342 | 332 |  | 0 | 400 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 135 | 0 | 100 | 0 | 310 | 185 | 55 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 86 | 160 | 93 | 20 | 0 | 60 | 22 | 53 | 47 | 130 | 149 | 67 | 77 | 0 | 93 | 0 | 0 | 10 | 310 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 25 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5143 | 1620 | 6763 | 3748 | 203 | 2082 | 163 | 401 | 80 | 0 | 86 | 0 | 0 | 94.16
KWH | 1673000 | 0 | 3518000 | 0 | 8750864 | 0 | 0 | 8270850 | 7184000 |  | 0 | 8975750 | 0 | 164160 | 29568 | 312000 | 7039258 | 0 | 0 | 0 | 41280 | 144288 | 0 | 0 | 0 | 0 | 74160 | 316764 | 79054 | 0 | 200448 | 600000 | 647460 | 615600 | 719800 | 0 | 0 | 651840 | 704000 | 2600000 | 0 | 0 | 248313 | 0 | 2870820 | 0 |  | 0 | 0 | 0 | 0 | 21120 | 55200 | 262272 | 625440 | 2906484 | 0 | 2514518 | 0 | 7312000 | 4562000 | 1037090 | 2121380 | 832392 | 134880 | 0 | 997132 | 0 | 0 | 0 | 503460 | 120780 | 567500 | 457120 | 1978560 | 3771560 | 1517760 | 476820 | 9900 | 1353000 | 435690 | 790800 | 759744 | 3044782 | 3443000 | 1306080 | 884160 | 0 | 2218110 | 0 | 0 | 93960 | 7483500 | 233520 | 123008 | 0 | 15050 | 0 | 0 | 528000 | 0 | 492480 | 91260 | 250560 | 30720 | 18400 | 3485000 | 999600 | 77844 | 52690 | 18120 | 1634454 | 0 | 0 | 21660 | 0 |  | 7628363 | 0 | 7566912 | 0 | 236160 | 0 | 0 | 0 | 0 | 10368 | 89250 | 2435924 | 254800 | 152544 | 0 | 0 | 0 | 0 | 0 | 136748 | 427410 | 0 | 0 | 0 | 0 | 216240 | 77220 | 244800 | 2840290 | 0 | 6767700 | 0 | 0 | 124373 | 0 | 0 | 0 | 922543 | 0 | 0 | 0 | 9882054 | 0 | 0 | 0 | 58175 | 1179840 | 0 | 22803 | 391392 | 0 |  | 119101837 | 41665909 | 160767746 | 87132116 | 7628363 | 43364095 | 9411583 | 9607990 | 1355840 | 147116 | 1978560 | 142083 | 0
Fuel Cost | 1873760 | 0 | 3764260 | 0 | 6475639.36 | 0 | 0 | 5955012 | 5459840 |  | 0 | 7180600 | 0 | 1674432 | 320221.44 | 3201120 | 8728679.92 | 0 | 0 | 0 | 458208 | 1465966.08 | 0 | 0 | 0 | 0 | 694137.6 | 3037766.76 | 754175.16 | 0 | 150336 | 450000 | 0 | 0 | 0 | 0 | 0 | 169478.4 | 183040 | 3978000 | 0 | 0 | 260728.65 | 0 | 3645941.4 | 0 |  | 0 | 0 | 0 | 0 | 200851.2 | 516672 | 241290.24 | 1738723.2 | 3051808.2 | 0 | 2640243.9 | 0 | 6142080 | 4197040 | 1016348.2 | 2821435.4 | 682561.44 | 138926.4 | 0 | 1425898.76 | 0 | 0 | 0 | 513529.2 | 90585 | 1072575 | 342840 | 13652064 | 3092679.2 | 14433897.6 | 486356.4 | 162360 | 1840080 | 592538.4 | 1075488 | 949680 | 3775529.68 | 3167560 | 1946059.2 | 1556121.6 | 0 | 3371527.2 | 0 | 0 | 220806 | 5313285 | 175140 | 93486.08 | 0 | 157573.5 | 0 | 0 | 5079360 | 0 | 4969123.2 | 1053140.4 | 2335219.2 | 288153.6 | 172408 | 3275900 | 8766492 | 693590.04 | 497920.5 | 0 | 15069665.88 | 0 | 0 | 0 | 0 |  | 20596580.1 | 0 | 5902191.36 | 0 | 2276582.4 | 0 | 0 | 0 | 0 | 135820.8 | 882682.5 | 1948739.2 | 394940 | 1638322.56 | 0 | 0 | 0 | 0 | 0 | 1353805.2 | 4432241.7 | 0 | 0 | 0 | 0 | 237864 | 127413 | 185313.6 | 18092647.3 | 0 | 27679893 | 0 | 0 | 109448.24 | 0 | 0 | 0 | 1466843.37 | 0 | 0 | 0 | 7213899.42 | 0 | 0 | 0 | 518339.25 | 11019705.6 | 0 | 0 | 0 | 0 |  | 184977955.59 | 106213272.6 | 291191228.19 | 83265364.59 | 20596580.1 | 39292206.63 | 85554827.77 | 45772540.3 | 352518.4 | 1489626 | 13652064 | 1215500.4 | 0
Yesterday Day Peak | 72 | 0 | 240 | 0 | 360 | 0 | 0 | 345 | 300 |  | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 20 | 17 | 0 | 0 | 30 | 0 | 110 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 100 | 0 | 135 | 0 | 305 | 165 | 26 | 90 | 43 | 5 | 0 | 52 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 74 | 165 | 92 | 20 | 0.7 | 60 | 0 | 50 | 50 | 100 | 141 | 57 | 50 | 0 | 98 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 0 | 0 | 0 | 146 | 24 | 0 | 0 | 0.7 | 33 | 0 | 0 | 0 | 0 |  | 299 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 119 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 70 | 0 | 0.8 | 0 | 0 |  | 6394.33 | DayPeak
Yesterday Evening Peak | 72 | 0 | 171 | 0 | 360 | 0 | 0 | 347 | 320 | 0 | 0 | 420 | 0 | 66 | 0 | 0 | 300 | 0 | 0 | 0 | 23 | 48 | 0 | 0 | 0 | 0 | 31 | 53 | 35 | 0 | 19 | 25 | 28 | 25 | 31 | 0 | 0 | 30 | 50 | 110 | 0 | 0 | 26 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 16 | 27 | 135 | 0 | 100 | 0 | 320 | 225 | 112 | 91 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 106 | 158 | 93 | 20 | 0 | 58 | 20 | 53 | 44 | 130 | 155 | 66 | 77 | 0 | 127 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 134 | 0 | 44 | 0 | 90 | 0 | 0 | 145 | 115 | 17 | 17 | 0 | 223 | 0 | 0 | 0 | 0 |  | 640 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 144 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 15 | 113 | 0 | 0 | 87 | 0 |  | 8731 | EvPeak
Forecast for Evening | 72 | 0 | 220 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 30 | 100 | 0 | 25 | 155 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 40 | 100 | 0 | 135 | 0 | 360 | 225 | 110 | 90 | 43 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 100 | 160 | 95 | 22 | 0 | 60 | 22 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 140 | 0 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 747 | 40 | 340 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 150 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 4 | 11 | 125 | 0 | 285 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113
Forecast for Day | 72 | 0 | 220 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 0 | 100 | 100 | 55 | 335 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 40 | 30 | 100 | 0 | 25 | 155 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 20 | 100 | 0 | 135 | 0 | 360 | 225 | 55 | 90 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 89 | 160 | 95 | 22 | 1.6 | 60 | 22 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 140 | 0 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 90 | 0 | 100 | 230 | 50 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 402 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 150 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 3 | 11 | 125 | 0 | 285 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 72 | 0 | 130 | 0 | 295 | 0 | 0 | 354 | 332 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 28 | 25 | 31 | 0 | 0 | 30 | 0 | 110 | 0 | 0 | 45 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 14 | 135 | 0 | 100 | 0 | 275 | 181 | 8 | 89 | 43 | 5 | 0 | 28 | 0 | 0 | 0 | 22 | 5 | 33 | 18 | 82 | 165 | 95 | 20 | 0.5 | 40 | 22 | 48 | 29 | 130 | 147 | 68 | 5 | 0 | 140 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 14 | 0 | 26 | 4.66 | 0 | 0 | 0 | 145 | 108 | 0 | 0 | 0.52 | 50 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 50 | 0 | 0
199
| Minimum Generation |  | 5350 | 5:00
| Highest Generation |  | 8731 | 19:00
| Day Peak Generation |  | 6394.33 | 9:00
| Evening Peak Generation |  | 8731 | 19:00
| HVDC Max Flow |  | 640 | 18:00
| HVDC EvPeak Flow |  | 640 | 19:00
| Load factor L.F |  | 76.72%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6394.33 | MW Hour : | 9:00 | Min. Gen. at | 5:00 | 5467 | MW
Evening Peak Generation : |  | 8731 | MW Hour : | 19:00 | Available Max Generation : |  | 14564 | MW
E.P. Demand (at gen end) : |  | 8731 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8731 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5564 | MW
Total Gen. (MKWH) : |  | 160.7677 | System Load Factor : | 76.72% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -662 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-02
Actual : | 94.14 | Ft.(MSL) , | Rule curve : | 96.86 | Ft.( MSL )
Gas Consumed : | Total = | 1075.26 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 122557571.22
: |  | Coal : | 45772540.3 | Oil : | 87044453.77 | Total : | 255374565.29
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3159.9725 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1068.8527 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 956.6386 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 864.0423 |  |  | 0 | 0%
) | 0 | 0:00 | 781.0218 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 630.2426 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 359.7521 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 162.4651 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 486.0392 |  |  | 0 | 0%
Total | 0 |  | 8469.0268 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Summit Meghna 305 MW
3) Ghorasal Unit-3,5
4) Baghabari 100 MW & 71 MW
5) Bhola 225 MW ST
6) Sirajganj unit-2&3
7)Shajibazar 330 MW GT-1
8) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorashal unit-4 tripped at 11:51 due to gas valve problem.
b) Rangamati-Khagrachari 132 kV Ckt-1 was under shut down from 08:23 to 16:58 for A/M.
c) Chowmuhuni-Ramganj 132 kV Ckt-1 was under shut down from 08:55 to 17:12 for A/M.
d) Bibiyana-Shahjibazar 230 kV Ckt-2 was under shut down from 09:39 to 17:13 for A/M.
e) Ramganj 132/33 kV T1 transformer was under shut down from 08:15 to 12:57 for D/W.
f) Ashuganj-Kishoreganj 132 kV Ckt-1 was under shut down from 08:52 to 12:14 for D/W.
g) Ashuganj-Kishoreganj 132 kV Ckt-2 was under shut down from 12:15 to 14:25 for D/W.
h) Netrokona 132 kV main bus & transformer bus was under shut down from 09:00 to 14:20 for C/M. |  |  |  |  | About 90 MW power interruption occurred under Netrokona S/S area
from 09:00 to 14:20.
i) Mymensingh-Netrokona 132 kV Ckt-1&2 was under shut down from 09:00 to 14:20 for C/M.
j) Faridpur 132/33 kV T2 transformer was under shut down from 09:39 to 17:55 for C/M.
k) Sikalbaha 225 MW CCPP GT was synchronized at 13:59.
l) Ghorashal unit-4 GT was synchronized at 16:10.
m) Bhola CCPP GT-2 was synchronized at 15:20.
n) Hathazari 132/33 kV T1 transformer was switched on at 16:23.
o) Sirajganj unit-1 GT & ST was synchronized at 19:53 & 23:09 respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 72 | 1673000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 171 | 3518000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 360 | 8750864
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8270850 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7184000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8975750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 66 | 164160 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 29568 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 312000 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 200448
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 23 | 41280 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7039258 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 144288 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 31 | 74160 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 316764
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 79054 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1247460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 615600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 719800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 15050 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 44 | 492480 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 77844 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2435 | 49941678
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 91260
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 36 | 55200 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1355840 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 26 | 248313
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 144 | 2870820 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 52690 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 250560 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 262272 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 625440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 21120 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18120
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 223 | 1634454 | Transformer overload.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 769 | 10086089
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2906484
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2514518 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 225 | 4562000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7312000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 832392
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 134880 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 112 | 1037090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 997132
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 18400 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2121380 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 30720 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 503460
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 120780
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 1978560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 567500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 457120
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 21660 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1274 | 26116076
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3771560 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 476820
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 93 | 1517760
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9900
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 134 | 528000 | High voltage
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 999600
| Mymensingh Area Total |  |  |  | 637 | 520 | 7303640
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1353000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 435690
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3044782 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 155 | 3443000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 790800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 44 | 759744
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 123008
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1306080 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 884160 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 127 | 2218110
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 233520
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7483500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 145 | 3485000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 93960
| Sylhet Area Total |  |  |  | 1949 | 1220 | 25654354
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 640 | 7628363
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 236160 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 10368 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 325 | 7566912 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 89250 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 15 | 58175 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1062 | 15589228
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 152544 | Line overload
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 19 | 254800 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 144 | 2435924 | ST Under S/D.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 922543
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 306 | 3765811
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 427410 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 124373 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 432 | 9882054 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 216240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 77220 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244800
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 34 | 136748 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 87 | 391392 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 631 | 11500237
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 121 | 2840290
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6767700
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1179840
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22803
| Rangpur Area Total |  |  |  | 605 | 514 | 10810633
| Total |  |  |  | 19107 | 8731 | 160767746
| Eastern Grid Total |  |  |  | 13543 | 6218 | 119101837
| Western Grid Total |  |  |  | 5564 | 2513 | 41665909
| National Grid Total |  |  |  | 19107 | 8731 | 160767746
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-01
(a) ENTIRE EASTERN GRID : |  | 5308 | MW | (b) ENTIRE WESTERN GRID : |  | 2894 | MW
i) Dhaka area |  | 2652 | MW | i) Khulna area |  | 1065 | MW
ii) Chittagong area |  | 831 | MW | ii) Rajshahi area |  | 962 | MW
iii) Comilla area |  | 736 | MW | iii) Barisal area |  | 220 | MW
iv) Mymensingh area |  | 767 | MW | iv) Rangpur area |  | 647 | MW
v) Sylhet area |  | 322 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8202 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 74 | 21:00 | Srimongal | 23 | 18:30 | Jhenida | 82 | 18:30
Munsiganj | 83 | 21:00 | Shahjibazar | 77 | 19:00 | Bottail | 100 | 18:30
Sonargaon | 63 | 18:30 | Fenchuganj | 30 | 19:30 | G.K Project | 37 | 18:30
Shyampur | 156 | 0:00 | Kulawara | 28 | 18:30 | Faridpur | 132 | 20:00
Bhulta | 140 | 6:00 | Sylhet | 101 | 18:00 | Madaripur | 60 | 19:30
Madanganj | 46 | 19:00 | Chatak | 20 | 18:00 | Sariatpur | 40 | 20:00
Shitalakhya | 93 | 10:00 | Sunamganj | 26 | 20:00 | Gopalganj | 66 | 19:00
Rahim steel | 14 | 12:00 | Biani Bazar | 30 | 18:30 | Bagerhat | 70 | 18:30
Matuail | 78 | 10:00 | Comilla (S) | 108 | 18:00 | Mongla | 32 | 8:00
Ghorasal | 54 | 19:00 | Comilla(N) | 79 | 19:30 | Satkhira | 69 | 19:30
Narsingdi | 116 | 19:30 | Chandpur | 59 | 19:30 | Gallamari | 34 | 13:00
Haripur (SBU) | 77 | 9:00 | Feni | 82 | 18:30 | Magura | 40 | 18:30
Ullon | 39 | 18:00 | Chowmuhani | 108 | 19:30 | Norail | 27 | 20:00
Hasnabad | 120 | 20:00 | Ashuganj | 35 | 20:00 | Chuadanga | 65 | 18:30
Magbazar | 53 | 20:00 | Daudkandi | 112 | 19:30 | Barisal(N) | 31 | 18:30
Maniknagar | 50 | 19:00 | B.Baria | 93 | 19:30 | Barisal (S) | 68 | 18:30
Bangabhaban | 12 | 17:00 | Ramganj | 62 | 20:00 | Patuakhali | 73 | 20:00
Narinda | 52 | 19:00 | Chaddagram | 22 | 12:00 | Bhandaria | 40 | 20:00
Dhanmondi | 62 | 19:00 | PHP | 4 | 17:00 | Borhan Uddin | 25 | 20:00
Lalbag | 24 | 18:00 | Madunaghat | 39 | 18:00 | Ishurdi | 45 | 18:30
Madartek | 40 | 18:30 | Hathazari | 70 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 138 | 14:00 | Natore | 93 | 18:30
Mirpur | 54 | 18:30 | Halishahar | 84 | 20:00 | Bogra | 122 | 19:00
Kalyanpur | 63 | 18:30 | Baraulia | 108 | 22:00 | Noagaon | 85 | 19:00
Gulshan | 68 | 18:30 | Sikalbaha | 21 | 18:30 | Rajshahi | 92 | 19:00
Uttara | 32 | 13:00 | Dohazari | 66 | 18:30 | Rajshahi New | 10 | 19:30
Uttara New | 23 | 19:00 | Cox'sbazar | 75 | 18:30 | C.Nawabganj | 66 | 18:30
Kamrangirchar | 44 | 18:30 | Chandraghona | 22 | 18:00 | Amnura | 32 | 18:30
Savar | 86 | 18:30 | Kaptai | 3.8 | 18:30 | Pabna | 70 | 18:30
Bhasantec | 82 | 18:30 | A. Khaer Stl. | 8 | 1:00 | Shahjadpur | 75 | 19:00
Agargaon | 34 | 19:30 | Bakulia | 70 | 18:30 | Serajganj | 65 | 19:00
Satmosjid | 55 | 13:00 | Julda | 20 | 12:00 | Niyamatpur | 90 | 8:00
Tongi | 90 | 18:00 | TK chemical | 10 | 18:00 | Joypurhat | 51 | 18:30
Kabirpur | 161 | 16:00 | Modern Steel | 14 | 11:00 | Sherpur(Bogura) | 40 | 18:30
Basundhara | 58 | 19:30 | Shahmirpur | 24 | 19:30 | Mohastangor | 32 | 18:30
Manikganj | 61 | 19:00 | Khagrachhari | 16 | 18:00 | Rangpur | 104 | 19:30
Joydevpur | 165 | 18:30 | Matarbari | 22 | 18:30 | Lalmonirhat | 51 | 18:30
New Tongi | 71 | 18:30 | Baroiar Hat | 30 | 18:30 | Saidpur | 92 | 18:30
Korda | 179 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 97 | 19:30
Dhamrai | 42 | 18:30 | Abul Khair 230 | 124 | 2:00 | Thakurgaon | 58 | 19:00
Valuka | 86 | 9:00 | BSRM | 136 | 7:00 | Palashbari | 105 | 18:30
Tangail | 136 | 19:30 | GPH Ispat | 9 | 12:00 | Barapukuria | 48 | 18:30
Mymensing | 179 | 18:00 | Goalpara | 18 | 18:30 | Panchagar | 38 | 19:00
Kishorganj | 92 | 19:00 | Central s/s | 66 | 19:00 | Joldhaka | 21 | 18:30
Netrokona | 111 | 19:00 | Noapara | 44 | 19:00 | Kurigram | 48 | 0.79167
Jamalpur | 103 | 20:00 | Jessore | 94 | 19:00
Sherpur | 96 | 18:30 | Benapol | 30 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-01 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 394 | 0.16667 | 384 | 0.54167 | Kaliakoir | 392 | 24:00 | 366 | 0.77083
Bheramara | 407 | 0.16667 | 400 | 0.375 | Bhulta | 395 | 0.125 | 388 | 0.5
Ashuganj(N) | 394 | 0.125 | 385 | 0.375 | Gopalganj | 397 | 24:00 | 369 | 0.77083
Payra | 234 | 0.16667 | 228 | 0.5
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 236 | 0.54167 | Hathazari | 240 | 0.29167 | 235 | 0.41667
Ishurdi | 240 | 0.20833 | 226 | 0.77083 | Megnaghat | 243 | 0.125 | 240 | 0.66667
Ashuganj | 240 | 0.041667 | 238 | 0.33333 | Fenchuganj | 237 | 0.083333 | 233 | 0.5
Serajganj | 235 | 0.083333 | 227 | 0.77083 | Siddhirganj | 235 | 0.041667 | 231 | 0.5
Baghabari | 244 | 0.083333 | 235 | 0.77083 | Maniknagar | 236 | 0.16667 | 229 | 0.5
Barapukuria | 233 | 0.125 | 224 | 0.33333 | Old Airport | 247 | 0.375 | 238 | 0.75
Bogra | 230 | 0.041667 | 230 | 0.77083 | Barisal | 224 | 0.8125 | 218 | 0.083333
Khulna South | 241 | 24:00 | 223 | 0.29167 | AKSML | 228 | 0.83333 | 221 | 0.33333
Rampura | 233 | 0.125 | 230 | 0.5 | BSRM | 223 | 0.54167 | 218 | 0.083333
Haripur | 234 | 0.125 | 230 | 0.5 | Bibiyana | 237 | 0.16667 | 230 | 0.5
Hasnabad | 236 | 0.20833 | 231 | 0.58333 | Bhulta | 239 | 0.20833 | 235 | 0.33333
Shyampur | 236 | 0.083333 | 232 | 0.45833 | Ashuganj (S) | 240 | 0.16667 | 233 | 0.5
Aminbazar | 234 | 0.041667 | 228 | 0.625 | Kaliakoir | 406 | 0.041667 | 390 | 0.79167
Tongi | 239 | 0.29167 | 233 | 0.375 | GPH | 242 | 0.041667 | 238 | 0.5
Comilla (N) | 226 | 0.8125 | 221 | 0.041667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.041667 | 132 | 0.5 | Khulshi | 131 | 0.77083 | 127 | 0.375
Munsiganj | 138 | 0.77083 | 130 | 0.5 | Halishahar | 135 | 0.77083 | 130 | 0.041667
Sonargaon | 135 | 0.041667 | 132 | 0.45833 | Baraulia | 135 | 0.77083 | 129 | 0.375
Shyampur | 138 | 0.041667 | 134 | 0.5 | Sikalbaha | 134 | 0.77083 | 128 | 0.33333
Bhulta | 130 | 0.041667 | 127 | 0.29167 | Dohazari | 132 | 0.77083 | 128 | 0.041667
Madanganj | 136 | 0.79167 | 130 | 0.41667 | Cox'sbazar | 126 | 0.70833 | 122 | 0.75
Shitalakhya | 132 | 0.79167 | 132 | 0.5 | Chandraghona | 134 | 0.77083 | 131 | 0.041667
Rahim steal | 136 | 3:00 | 133 | 0.41667 | Kaptai | 135 | 0.8125 | 132 | 0.29167
Matuail | 135 | 0.041667 | 131 | 0.5 | A. Khaer Stl. | 132 | 0.125 | 130 | 0.041667
Ghorasal | 142 | 0.041667 | 142 | 0.041667 | Bakulia | 132 | 0.77083 | 127 | 0.33333
Narsinghdi | 135 | 0.54167 | 130 | 0.79167 | Julda | 133 | 0.77083 | 128 | 0.29167
Haripur (SBU) | 136 | 0.125 | 132 | 0.5 | TK Chemical | 133 | 0.77083 | 129 | 0.29167
Ullon | 131 | 0.25 | 127 | 0.5 | Modern Steel | 133 | 0.83333 | 129 | 0.25
Hasnabad | 137 | 0.25 | 133 | 0.54167 | Shahmirpur | 133 | 0.77083 | 129 | 0.29167
Magbazar | 132 | 0.25 | 128 | 0.5 | Khagrachhari | 133 | 0.125 | 130 | 0.375
Maniknagar | 138 | 0.25 | 136 | 0.54167 | Matarbari | 129 | 0.125 | 123 | 0.29167
Bangabhaban | 138 | 0.25 | 136 | 0.54167 | Baroiar Hat | 134 | 0.041667 | 132 | 0.29167
Narinda | 138 | 0.25 | 136 | 0.54167 | Rangamati | 133 | 0.77083 | 130 | 7:00
Dhanmondi | 131 | 0.25 | 127 | 0.5 | Goalpara | 135 | 0.041667 | 127 | 18:00
Lalbag | 138 | 0.20833 | 133 | 0.5 | Central s/s | 135 | 0.20833 | 125 | 0.77083
Madartek | 131 | 0.25 | 128 | 0.5 | Noapara | 135 | 0.041667 | 125 | 0.33333
Dhaka University |  |  |  |  | Jessore | 132 | 0.041667 | 122 | 0.77083
Mirpur | 136 | 0.16667 | 133 | 0.54167 | Benapol | 134 | 0.16667 | 124 | 0.33333
Kalyanpur | 140 | 0.125 | 136 | 0.41667 | Jhenida | 134 | 0.125 | 119 | 0.77083
Gulshan | 130 | 0.041667 | 127 | 0.41667 | Bottail | 138 | 0.625 | 127 | 0.77083
Uttara | 137 | 0.16667 | 133 | 0.5 | G.K Project | 140 | 0.041667 | 133 | 0.77083
Uttara New | 137 | 0.16667 | 133 | 0.41667 | Faridpur | 139 | 0.375 | 128 | 0.75
Kamrangirchar | 136 | 0.041667 | 133 | 0.41667 | Madaripur | 140 | 0.375 | 130 | 0.77083
Savar | 136 | 0.041667 | 132 | 0.5 | Sariatpur | 140 | 0.41667 | 131 | 0.33333
Bhasantec | 137 | 0.125 | 132 | 0.5 | Gopalganj | 142 | 0.16667 | 133 | 0.77083
Agargaon | 138 | 0.16667 | 133 | 0.5 | Bagerhat | 135 | 0.041667 | 125 | 0.33333
Satmosjid | 137 | 0.041667 | 133 | 0.54167 | Mongla | 132 | 0.083333 | 123 | 0.77083
Tongi | 140 | 0.041667 | 135 | 0.375 | Satkhira | 134 | 0.125 | 123 | 0.77083
Kabirpur | 134 | 22:00 | 129 | 0.41667 | Gallamari | 135 | 0.125 | 126 | 0.29167
Basundhara | 131 | 24:00 | 128 | 0.54167 | Magura | 134 | 0.125 | 120 | 0.77083
Manikganj | 137 | 0.041667 | 133 | 0.79167 | Norail | 132 | 0.083333 | 117 | 0.77083
Joydevpur | 143 | 0.25 | 138 | 0.83333 | Chuadanga | 130 | 0.16667 | 115 | 0.77083
New Tongi | 138 | 0.041667 | 133 | 0.5 | Barisal(N) | 140 | 0.375 | 136 | 0.25
Kodda | 136 | 0.125 | 126 | 0.41667 | Barisal (S) | 140 | 0.375 | 130 | 0.77083
Dhamrai | 136 | 0.125 | 131 | 0.33333 | Patuakhali | 137 | 0.083333 | 129 | 0.77083
Valuka | 131 | 0.41667 | 112 | 0.33333 | Bhandaria | 135 | 0.375 | 128 | 0.29167
Tangail | 136 | 0.16667 | 128 | 0.33333 | Ishurdi | 138 | 0.125 | 130 | 0.77083
Mymensing | 134 | 0.45833 | 116 | 0.33333 | Ruppur Paromanobik | 136 | 0.041667 | 129 | 0.77083
Kishorganj | 133 | 0.41667 | 123 | 0.29167 | Natore | 135 | 0.125 | 126 | 0.77083
Netrokona | 130 | 0.625 | 110 | 0.29167 | Bogra | 136 | 0.125 | 128 | 0.75
Jamalpur | 139 | 0.77083 | 115 | 0.29167 | Noagaon | 132 | 0.125 | 116 | 0.58333
Sherpur | 138 | 0.75 | 116 | 0.29167 | Rajshahi | 131 | 0.041667 | 121 | 0.33333
Srimongal | 140 | 0.41667 | 138 | 0.041667 | Rajshahi New | 130 | 0.125 | 120 | 0.33333
Shahjibazar | 138 | 0.041667 | 135 | 0.79167 | C.Nawabganj | 132 | 0.041667 | 117 | 0.33333
Fenchuganj | 139 | 0.083333 | 137 | 12:00 | Amnura | 128 | 0.70833 | 121 | 0.29167
Khulawara | 139 | 0.041667 | 136 | 0.83333 | Pabna | 137 | 0.16667 | 128 | 0.77083
Sylhet | 137 | 0.125 | 135 | 0.8125 | Shahjadpur | 144 | 0.16667 | 135 | 0.33333
Chatak | 136 | 0.041667 | 135 | 0.41667 | Serajganj | 136 | 0.083333 | 130 | 0.79167
Sunamganj | 136 | 0.083333 | 134 | 0.45833 | Niyamatpur | 128 | 0.041667 | 112 | 0.58333
Biani Bazar | 138 | 0.16667 | 134 | 0.83333 | Joypurhat | 131 | 0.041667 | 116 | 0.58333
Comilla(s) | 132 | 0.041667 | 128 | 0.375 | Sherpur(Bogura) | 137 | 0.083333 | 129 | 0.33333
Comilla(n) | 141 | 7:00 | 139 | 0.45833 | Mohastangor | 135 | 0.16667 | 112 | 0.33333
Chandpur | 137 | 0.33333 | 135 | 0.91667 | Rangpur | 130 | 0.041667 | 115 | 0.33333
Feni | 135 | 0.41667 | 133 | 0.625 | Lalmonirhat | 127 | 0.125 | 116 | 0.29167
Chowmuhani | 133 | 0.29167 | 130 | 0.58333 | Saidpur | 132 | 0.25 | 120 | 0.33333
Ashuganj | 140 | 0.16667 | 136 | 0.77083 | Purbasadipur | 128 | 0.083333 | 114 | 0.77083
Daudkandi | 135 | 0.29167 | 134 | 0.375 | Thakurgaon | 127 | 0.125 | 112 | 0.77083
B.Baria | 136 | 0.58333 | 132 | 0.77083 | Palashbari | 130 | 0.125 | 109 | 0.33333
Ramganj | 132 | 0.375 | 127 | 0.875 | Barapukuria | 133 | 0.125 | 124 | 0.33333
Chaddagram | 138 | 0.125 | 133 | 0.83333 | Panchagar | 126 | 0.20833 | 106 | 0.77083
PHP | 133 | 0.45833 | 132 | 0.875 | Joldhaka | 130 | 0.125 | 116 | 0.33333
Madanhat | 135 | 0.125 | 132 | 0.29167 | Kurigram | 129 | 0.083333 | 120 | 0.79167
Hathazari | 136 | 0.8125 | 132 | 0.29167

## L-Curve
Date | 2020-02-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 537 | 5143 | 1620 | 6763 |  |  |  | QF-LDC-12
0:30 | 524.5 | 4843.5 | 1495.5 | 6339 | Date: | 2020-02-01
1:00 | 512 | 4544 | 1371 | 5915
1:30 | 476.5 | 4425 | 1366.5 | 5791.5
2:00 | 441 | 4306 | 1362 | 5668
2:30 | 445.5 | 4258.5 | 1354.5 | 5613 | [5 empty] | Gen. at Eve. Peak | 8731 | 8731 MW (19:00 )
3:00 | 450 | 4211 | 1347 | 5558 | [6 empty] | 19:00
3:30 | 445 | 4141 | 1318 | 5459 | [5 empty] | Gen. at Day Peak | 6394.33 | 6394.33 MW (09:00 )
4:00 | 440 | 4071 | 1289 | 5360 | [6 empty] | 9:00
4:30 | 448.5 | 4074.5 | 1280.5 | 5355 | [5 empty] | Highest Generation | 8731
5:00 | 457 | 4078 | 1272 | 5350 | [6 empty] | 19:00
5:30 | 484 | 4232 | 1272.5 | 5504.5
6:00 | 511 | 4386 | 1273 | 5659
6:30 | 586.5 | 4552.6 | 1342.05 | 5894.65
7:00 | 662 | 4719.2 | 1411.1 | 6130.3
7:30 | 621 | 4798.98 | 1505.65 | 6304.63
8:00 | 580 | 4878.76 | 1600.2 | 6478.96
8:30 | 507 | 4818.145 | 1618.5 | 6436.645
9:00 | 434 | 4757.53 | 1636.8 | 6394.33
9:30 | 382.5 | 4643.945 | 1649.75 | 6293.695
10:00 | 331 | 4530.36 | 1662.7 | 6193.06
10:30 | 289.5 | 4512.18 | 1651.25 | 6163.43
11:00 | 248 | 4494 | 1639.8 | 6133.8
11:30 | 239 | 4548.225 | 1698.95 | 6247.175
12:00 | 230 | 4602.45 | 1758.1 | 6360.55
12:30 | 320.5 | 4785.725 | 1717.9 | 6503.625
13:00 | 411 | 4969 | 1677.7 | 6646.7
13:30 | 381.5 | 4897.22 | 1653.75 | 6550.97
14:00 | 352 | 4825.44 | 1629.8 | 6455.24
14:30 | 299 | 4790.615 | 1631.9 | 6422.515
15:00 | 246 | 4755.79 | 1634 | 6389.79
15:30 | 228 | 4734.7 | 1678.8 | 6413.5
16:00 | 210 | 4713.61 | 1723.6 | 6437.21
16:30 | 241 | 4696.495 | 1713 | 6409.495
17:00 | 272 | 4679.38 | 1702.4 | 6381.78
17:30 | 357.5 | 5040.69 | 1992.7 | 7033.39
18:00 | 443 | 5402 | 2283 | 7685
18:30 | 517 | 5810 | 2398 | 8208
19:00 | 591 | 6218 | 2513 | 8731
19:30 | 533 | 6201 | 2529 | 8730
20:00 | 540 | 6176 | 2503 | 8679 |  |  |  | Executive Engineer
20:30 | 456 | 6041 | 2520 | 8561 |  |  |  | Network Operation Division
21:00 | 372 | 5906 | 2537 | 8443
21:30 | 416.5 | 5781 | 2348 | 8129
22:00 | 461 | 5656 | 2159 | 7815 |  |  |  |  | Page 6 of 7
22:30 | 523.5 | 5559 | 1947.5 | 7506.5
23:00 | 586 | 5462 | 1736 | 7198
23:30 | 561.5 | 5302.5 | 1678 | 6980.5
24:00 | 537 | 5143 | 1620 | 6763
8731 MW (19:00 )
6394.33 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-01 |  | Energy | 160767746
[10 empty] | 2020-02-01 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3748 | 203 | 2082 | 345 | 401 | 80 | 0 | 0 | 86
0:30 | 3681 | 170 | 1872.5 | 172.5 | 402 | 56 | 0 | 0 | 76 | Date: | 2020-02-01
1:00 | 3614 | 137 | 1663 | 0 | 403 | 32 | 0 | 0 | 66
1:30 | 3509 | 137 | 1645 | 0 | 402.5 | 32 | 0 | 0 | 66 | [7 empty] | Total Energy | 160.7677 | Total Energy Gen 160.768 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 160.768 MKWHr
2:00 | 3404 | 137 | 1627 | 0 | 402 | 32 | 0 | 0 | 66 | [7 empty] | Energy not Served | 0
2:30 | 3362 | 137 | 1618 | 0 | 399 | 32 | 0 | 0 | 65 | [7 empty] | Energy Requirement | 160.7677
3:00 | 3320 | 137 | 1609 | 0 | 396 | 32 | 0 | 0 | 64
3:30 | 3286 | 136.5 | 1543 | 0 | 397.5 | 32 | 0 | 0 | 64 | [6 empty] | Shortage
4:00 | 3252 | 136 | 1477 | 0 | 399 | 32 | 0 | 0 | 64
4:30 | 3255.5 | 136.5 | 1468 | 0 | 399 | 32 | 0 | 0 | 64
5:00 | 3259 | 137 | 1459 | 0 | 399 | 32 | 0 | 0 | 64
5:30 | 3356.5 | 136.5 | 1516 | 0 | 397.5 | 32 | 0 | 0 | 66
6:00 | 3454 | 136 | 1573 | 0 | 396 | 32 | 0 | 0 | 68
6:30 | 3620.5 | 136 | 1638.5 | 2 | 396.5 | 31 | 0 | 0 | 70 |  |  |  |  | Coal
7:00 | 3787 | 136 | 1704 | 4 | 397 | 30 | 0 | 0 | 72
7:30 | 3754 | 217.5 | 1789 | 44 | 398 | 30 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 3721 | 299 | 1874 | 84 | 399 | 30 | 0 | 0 | 70
8:30 | 3663 | 299 | 1809.5 | 160.5 | 399 | 30 | 0 | 0 | 72
9:00 | 3605 | 299 | 1745 | 237 | 399 | 30 | 0 | 0 | 74
9:30 | 3552.5 | 299 | 1637 | 262 | 401 | 55 | 0 | 0 | 76
10:00 | 3500 | 299 | 1529 | 287 | 403 | 80 | 0 | 0 | 78
10:30 | 3452 | 299 | 1531 | 300.5 | 402.5 | 80 | 0 | 0 | 78
11:00 | 3404 | 299 | 1533 | 314 | 402 | 80 | 0 | 0 | 78
11:30 | 3485.5 | 299.5 | 1556.5 | 320.5 | 398 | 80 | 0 | 0 | 81
12:00 | 3567 | 300 | 1580 | 327 | 394 | 80 | 0 | 0 | 84
12:30 | 3608.5 | 299.5 | 1693 | 326 | 393.5 | 80 | 0 | 0 | 81
13:00 | 3650 | 299 | 1806 | 325 | 393 | 80 | 0 | 0 | 78
13:30 | 3650 | 299 | 1806 | 325 | 393 | 80 | 0 | 0 | 78
14:00 | 3650 | 299 | 1806 | 325 | 393 | 80 | 0 | 0 | 78
14:30 | 3577 | 297.5 | 1749 | 322 | 396.5 | 80 | 0 | 0 | 81
15:00 | 3504 | 296 | 1692 | 319 | 400 | 80 | 0 | 0 | 84
15:30 | 3527 | 296.5 | 1697.5 | 319 | 400.5 | 80 | 0 | 0 | 82
16:00 | 3550 | 297 | 1703 | 319 | 401 | 80 | 0 | 0 | 80
16:30 | 3521.5 | 298 | 1693 | 329 | 401 | 80 | 3.5 | 0 | 79
17:00 | 3493 | 299 | 1683 | 339 | 401 | 80 | 7 | 0 | 78
17:30 | 3628.5 | 469.5 | 1749.5 | 589 | 401 | 80 | 22 | 0 | 93
18:00 | 3764 | 640 | 1816 | 839 | 401 | 80 | 37 | 0 | 108
18:30 | 3851 | 640 | 1969 | 1124.5 | 401 | 80 | 35.5 | 0 | 107
19:00 | 3938 | 640 | 2122 | 1410 | 401 | 80 | 34 | 0 | 106
19:30 | 3972 | 640 | 2150 | 1343 | 402 | 83 | 34 | 0 | 106
20:00 | 3953 | 640 | 2128 | 1332 | 401 | 83 | 34 | 0 | 108
20:30 | 3960.5 | 640 | 2140.5 | 1196 | 401.5 | 81.5 | 34 | 0 | 107
21:00 | 3968 | 640 | 2153 | 1060 | 402 | 80 | 34 | 0 | 106
21:30 | 3942 | 591 | 2109 | 885 | 402 | 80 | 17 | 0 | 103
22:00 | 3916 | 542 | 2065 | 710 | 402 | 80 | 0 | 0 | 100
22:30 | 3914.5 | 420.5 | 2066.5 | 527.5 | 402.5 | 80 | 0 | 0 | 95
23:00 | 3913 | 299 | 2068 | 345 | 403 | 80 | 0 | 0 | 90
23:30 | 3830.5 | 251 | 2075 | 345 | 402 | 80 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 25.0° C
24:00 | 3748 | 203 | 2082 | 345 | 401 | 80 | 0 | 0 | 86
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 160.768 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 160.768 MKWHr
Note on W13: Author:

## Generation
2020-02-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 33 | 33 | 30 | 30 | 30 | 30 | 651840
2 | Karnaphuli Hydro PP Unit-4 & 5 | [9 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 704000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.2 | 1.06 | 3.13 | 12.86 | 17.2 | 18.55 | 5.9 | 14 | 10 | 4 | 1 | [9 empty] | 91260
6 | Sikalbaha 225MW CCPP (Gas) | [13 empty] | 16 | 26 | 27 | 26 | 26 |  | 26 | 26 | 26 | 26 | 27 | 26 | 26 | 248313
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 104 | 102 | 105 | 105 | 140 | 85 | 85 | 103 | 100 | 140 | 150 | 140 | 140 | 140 | 105 | 104 | 111 |  | 144 | 145 | 145 | 144 | 139 | 140 | 115 | 2870820
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 13 |  | 17 | 17 | 17 |  |  |  |  | 52690
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 270 | 230 | 170 | 170 | 260 | 300 | 300 | 280 | 260 | 260 | 280 | 340 | 335 | 335 | 300 | 280 | 280 |  | 300 | 335 | 335 | 335 | 338 | 338 | 300 | 7039258
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 2 |  | 0 | [6 empty] | 15050
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 112 |  | 112 | 112 | 112 | 112 | 55 | 55 | 55 | 1037090
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1673000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 149 | 150 | 151 | 149 | 152 | 152 | 259 | 237 | 240 | 240 | 150 |  |  |  | 0 | 100 | 102 | 160 |  | 171 | 170 | 170 | 171 | 170 | 168 | 169 | 3518000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 368 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8750864
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 125 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2906484
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 125 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2514518
32 | Ashuganj 50 MW PP | 43 | 10 | 10 | 10 | 10 | 10 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 832392
33 | Ashuganj 225 MW CCPP | 182 | 192 | 163 | 163 | 163 | 204 | 203 | 198 | 165 | 175 | 171 | 222 | 195 | 163 | 178 | 175 | 168 | 160 |  | 225 | 225 | 228 | 224 | 229 | 194 | 185 | 4562000
34 | Ashuganj 450 MW CCPP(South) | 310 | 270 | 270 | 265 | 270 | 330 | 345 | 330 | 305 | 285 | 280 | 345 | 320 | 270 | 270 | 280 | 275 | 335 |  | 320 | 320 | 310 | 305 | 310 | 325 | 310 | 7312000
| Ashuganj 450 MW CCPP(North) | [26 empty] | 0
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 134880
36 | Chandpur 150 MW CCPP | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 89 | 89 | 90 | 90 | 89 | 90 | 89 | 89 | 90 |  | 91 | 91 | 89 | 89 | 89 | 88 | 89 | 2121380
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 343 | 341 | 342 | 341 | 367 | 366 | 350 | 345 | 300 | 300 | 348 | 370 | 343 | 340 | 295 | 280 | 328 |  | 347 | 345 | 345 | 350 | 343 | 337 | 342 | 8270850
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 360 | 360 | 300 | 300 | 340 | 380 | 380 | 380 | 320 | 320 | 350 | 350 | 420 | 420 | 420 | 380 | 350 |  | 420 | 420 | 420 | 420 | 420 | 400 | 400 | 8975750
41 | Haripur 360MW CCPP(HPL) | 314 | 314 | 314 | 293 | 293 | 302 | 328 | 330 | 300 | 280 | 280 | 242 | 242 | 255 | 255 | 255 | 255 | 260 |  | 320 | 320 | 320 | 332 | 332 | 332 | 332 | 7184000
42 | RPCL 210MW CCPP | 161 | 161 | 162 | 165 | 165 | 162 | 161 | 164 | 165 | 161 | 158 | 156 | 156 | 157 | 157 | 156 | 158 | 158 |  | 158 | 159 | 158 | 160 | 162 | 160 | 160 | 3771560
43
44 | Fenchugonj CCPP Phase-1 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 66 | 48 | 58 | 35 | 33 | 60 |  | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 1353000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 0 | 0 | [6 empty] | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 435690
46 | Shajibazar 330 MW CCPP | 150 | 154 | 151 | 144 | 144 | 150 | 157 | 155 | 141 | 142 | 146 | 165 | 157 | 145 | 151 | 154 | 152 | 163 |  | 155 | 152 | 151 | 150 | 145 | 154 | 149 | 3443000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 57 | 57 | 57 | 45 | 45 | 52 | 63 | 63 | 45 | 45 | 45 | 65 |  | 66 | 66 | 67 | 67 | 67 | 67 | 67 | 1306080
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 10 | 10 | 10 | 76 | 76 | 10 | 10 | 10 | 40 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 884160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 69 | 68 | 67 | 68 | 68 | 100 | 100 | 98 | 98 | 69 | 68 | 70 | 140 | 80 | 77 | 78 | 78 | 77 |  | 127 | 122 | 123 | 122 | 122 | 122 | 93 | 2218110
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [14 empty] | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 93960
54 | Hobiganj 11MW PP Cofidence-E | [12 empty] | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 123008
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 11 | 11 | 11 | 50 | 50 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 790800
56 | Shahjahanulla 25 MW PP | [12 empty] | 16 | 16 | 16 | 8 | 8 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 1 | 233520
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 290 | 300 | 300 | 310 | 320 | 315 | 280 | 285 | 290 | 305 | 320 | 275 | 290 | 290 | 295 | 275 |  | 300 | 325 | 310 | 300 | 300 | 290 | 310 | 7483500
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [8 empty] | 16 | 16 |  | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 262272
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 22 | 22 | 22 | 22 | 22 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 200448
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 476820
63 | Impoprt (Tripura) | 66 | 66 | 64 | 64 | 64 | 68 | 72 | 70 | 74 | 78 | 78 | 84 | 78 | 86 | 84 | 80 | 78 | 108 |  | 106 | 106 | 108 | 106 | 100 | 90 | 86 | 1978560
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 15 | 7 | 4 | 2 | 6 | 15 | 8 | 3 | 4 | 11 | 16 |  | 27 | 28 | 32 | 36 | 40 | 42 | 42 | 625440
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503460
66 | Feni 11 MW PP (Doreen) | [12 empty] | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 120780
67 | Jangalia 33MW PP (Summit) | [7 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 567500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 17 | 14 | 14 | 18 | 15 | 16 | 16 | 16 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 457120
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 28 | 31 | 31 | 28 | 24 | 24 | 22 | 22 | 22 | 22 | 16 |  | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 647460
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615600
72 | Rupganj 33 MW PP(Summit) | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 17 | 17 | 17 | 25 | 25 | 25 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 719800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [17 empty] | 17 | [8 empty] | 21660
Chowmuhani 113 MW
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 5 |  | 23 | 7 | 7 |  |  |  |  | 41280
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 4 | 72 | 92 | 92 | 92 | 92 | 92 | 84 | 84 | 84 | 93 | 90 |  | 93 | 93 | 95 | 95 | 95 | 95 | 93 | 1517760
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 3 |  |  | 77844
| Kaptai 7 MW Solar PP | [7 empty] | 0.3 | 0.7 | 1.2 | 2.1 | 4.1 | 3.8 | 3.14 | 1.21 | 1.21 | 0.28 | [9 empty] | 18120
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [17 empty] | 10 |  | 0 | [6 empty] | 29568
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 15 |  | 66 | 50 | 50 | 26 |  |  |  | 164160
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 50 | 50 | 10 | 10 | 10 | 36 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 759744
93 | Ashuganj 51 MW PP (Midland) | 14 | 14 | 14 | 14 | 14 | 14 | 20 | 51 | 52 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 997132
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 16 |  | 48 | 50 | 48 | 7 | 0 |  |  | 144288
95 | Patenga 50MW PP (Baraka) | [17 empty] | 6 |  | 36 | 6 | 6 | 6 |  |  |  | 55200
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 10 | [8 empty] | 21120
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 11 |  | 31 | 18 | 18 |  |  |  |  | 74160
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 10 |  | 0 | [6 empty] | 312000
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 11 | 17 |  | 35 | 17 | 17 |  |  |  |  | 79054
101 | Kushiara 163 MW CCPP (KP) | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 163 | 130 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3044782
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0.4 | 0.7 | 1.3 | 1.7 | 1.8 | 1.3 | 1.3 | 0.58 | 0.4 | 0.1 | [9 empty] | 9900
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 53 |  | 53 | 53 | 53 | 35 | 35 | 53 |  | 316764
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 40 |  | 134 | 145 | 145 | 100 | 50 | 0 |  | 528000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 7 | 32 | 44 | 42 | 45 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 21 | 17 | 0 |  | 492480
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 50 |  | 90 | 90 | 90 | 30 | 0 |  |  | 250560
116 | Chandpur 200MW (Desh energy) | [17 empty] | 15 |  | 0 | [6 empty] | 30720
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 8 | [8 empty] | 18400
118 | Bibiyana-III 400 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 146 | 144 | 145 | 145 | 145 | 145 | 144 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 144 | 145 | 3485000
| Jamalpur 115 MW PP (United) | [7 empty] | 2 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 85 |  | 115 | 115 | 115 | 115 | 115 | 90 | 70 | 999600
| Anwara 300 MW PP (United) | [7 empty] | 5 | 33 | 65 | 71 | 71 | 71 | 71 | 70 | 71 | 71 | 105 |  | 223 | 228 | 217 | 217 | 163 | 107 | 0 | 1634454
120 | Eastern Zone Total | 4544 | 4306 | 4211 | 4071 | 4078 | 4386 | 4719.2 | 4878.76 | 4757.53 | 4530.36 | 4494 | 4602.45 | 4969 | 4825.44 | 4755.79 | 4713.61 | 4679.38 | 5402 |  | 6218 | 6201 | 6176 | 5906 | 5656 | 5462 | 5143 | 119101837
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 37 |  | 49 | 49 | 49 | 49 | 49 | 0 |  | 236160
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 20 |  | 48 | 48 | 48 | 32 | 0 |  |  | 152544
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [5 empty] | 0 | 1 | 42 | 60 | 35 | 32 | 32 | 32 | 32 | 32 | 12 | 12 | 22 |  | 95 | 95 | 95 | 98 | 97 | 97 | 96 | 922543
| Bhola 225 MW CCPP | 96 | 84 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 134 | 135 | 144 |  | 144 | 144 | 144 | 144 | 99 | 99 | 100 | 2435924
140 | Bhola 33 MW PP (Venture) | 15 | 14 | 14 | 0 | [6 empty] | 4 | 10 | 12 | 12 | 12 | 11 | 12 | 18 |  | 19 | 20 | 21 | 21 | 20 | 19 | 17 | 254800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 33 | 33 | 33 | 33 | 0 |  |  | 89250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 7 | 7 |  | 0 | [6 empty] | 10368
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 10 |  | 15 | 15 | 14 | 15 | 0 |  |  | 58175
146 | Bheramara HVDC | 137 | 137 | 137 | 136 | 137 | 136 | 136 | 299 | 299 | 299 | 299 | 300 | 299 | 299 | 296 | 297 | 299 | 640 |  | 640 | 640 | 640 | 640 | 542 | 299 | 203 | 7628363
147 | Bheramara 410 MW CCPP | 310 | 280 | 280 | 280 | 280 | 230 | 350 | 330 | 310 | 330 | 310 | 397 | 310 | 315 | 310 | 340 | 310 | 350 |  | 325 | 330 | 310 | 315 | 310 | 330 | 310 | 7566912
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 123 | 122 | 116 | 119 | 119 | 116 | 117 | 119 | 119 | 122 | 122 | 114 | 114 | 123 | 120 | 121 | 121 | 121 |  | 121 | 122 | 121 | 122 | 122 | 123 | 121 | 2840290
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 281 | 280 | 280 | 279 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6767700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [21 empty] | 6 | 20 | 18 | 18 | 25 | 124373
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 397 | 432 | 424 | 377 | 359 | 414 | 432 | 430 | 385 | 400 | 400 | 430 | 436 | 354 | 363 | 394 | 393 | 433 |  | 432 | 433 | 421 | 434 | 401 | 433 | 430 | 9882054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [13 empty] | 20 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 216240
163 | Bogura 20 MW PP (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | [5 empty] | 0 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 77220
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244800
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 |  | 40 | 40 | 40 | 40 | 40 |  |  | 427410
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 0 | 30 |  | 34 | 34 | 34 | 34 | 0 |  |  | 136748
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 0 | 22 |  | 87 | 95 | 96 | 109 | 35 |  |  | 391392
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 5 | 70 | 74 | 70 | 71 | 71 | 71 | 72 | 71 | 71 | 71 |  | 113 | 113 | 113 | 113 | 108 |  |  | 1179840
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.2 | 0.8 | 1.7 | 2.8 | 4.1 | 4.7 | 3.8 | 3 | 1.6 | 0.4 | [9 empty] | 22803
178
178