## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-05 | Wednesday
|  | Date (day): | 2020-02-05 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11311.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14493 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-04 | 2020-02-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 150 |  | 170
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 150 | 0 | 0 |  |  | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 350 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 342 | 365 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint |  | 2020-10-02
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  |  | GT-2 Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 55 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 210 | 270 | 230 | 335
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 60 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 43 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 83 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 65 | 0 | 0 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 240 | 240 |  |  | ST Under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 59 | 49 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 75 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 142 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1997 | 2494 | 3130 | 4036 | 401 | 575
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.6 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 71 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 202 | 203 | 210 | 220
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 104 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 31 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 25 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 85 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.8 | 0 | 5 | 0 |  |  | Engine problem
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 209 | 217 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 778.4 | 1015 | 1495 | 1650 | 390 | 108
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 100 | 100 | 100
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 194 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 17 | 310 | 320 | 360
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 295 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 43 | 43
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 10 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 55 | 110 | 85 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 130 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 0 | 0 |  | 163 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 108 | 94 | 104
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1068 | 1423 | 1552 | 2321 | 399 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 127 | 126 | 110 | 130 | 72 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 92 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 40 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 105 | 99 | 60 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 350.1 | 377 | 388.6 | 562 | 72 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 44 | 44 | 44
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 153 | 148 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 41 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 56 | 59 | 76 | 76 |  | 10 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 146 | 0 | 0 | 0 |  |  | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 145 | 145 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1274 | 1106 | 1280 | 1280 | 0 | 370
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 390 | 556 | 400 | 745
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 245 | 265 | 340 | 340 | 70 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 15 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 684 | 951 | 1098 | 1914 | 70 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 65 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 189 | 194 | 194
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 97 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 297 | 371 | 379 | 449 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 130 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 225 | 225 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 342 | 255 | 410 | 410 | ` |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 46 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 789 | 875 | 1458 | 1724 | 171 | 15
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 121 | 122 | 125 | 125
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 285 | 285
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 112 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 405.8 | 514 | 531 | 557 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7643.3 | 9126 | 11311.6 | 14493 | 1503 | 1336
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7255.5235 | 8663 | 10737.7154 | 13757.7097
A. |  | 2020-02-04 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9126 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5498 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9126 | MW
3 | Day peak Generation : |  |  | 7643.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8663 | MW
4 | Evening peak Generation : |  |  | 9126 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 174.1133 | MKWHr | By Solar | 0.20358 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 127.3332 | MKWHr |  | By Oil: | 24.4944 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 9.629 | MKWHr |  | By Hydro: | 1.6754 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1503 | MW | Dhaka | 3015 | 3015 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1336 | MW | Chittagong | 869 | 869 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2839 | MW | Khulna | 1053 | 1053 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1137.66 | MMCFD |  |  | Rajshahi | 986 | 986 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 120209432.77 | ii) Oil : | Taka | 180767646.01 | Comilla | 744 | 744 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 45950151.32 | Total | Taka | 346927230.1 | Mymensingh | 771 | 771 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.497 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -425 | MW (E to W) at | 19:00 | hrs | Barisal | 227 | 227 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -452 | MW at | 18:30 | hrs | Rangpur | 684 | 684 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.7° C |  |  | Total | 8663 | 8663 |  | 0
B. |  | 2020-02-05 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14493 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve(Generation end) |  |  |  | 5293 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 175.5251 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5624 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.608 | MKWHr. | ii) HVDC Flow at Peak Time |  | 556 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1696 | MKWHr. | iii) Maximum HVDC Flow : |  | 561 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.83 |  | (b) Today: | 93.59 |  | (c) Rule Curve: |  | 96.44
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-02-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 201 | 0 | 360 | 0 | 0 | 335 | 0 |  | 0 | 225 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 20 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 216 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 33 | 0 | 0 | 100 | 190 | 305 | 0 | 8 | 89 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 20 | 14 | 80 | 130 | 90 | 17 | 0 | 60 | 42 | 5 | 47 | 100 | 148 | 45 | 5 | 0 | 153 | 0 | 0 | 0 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 32 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 |  | 136 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 122 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 180 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4391 | 1911 | 6302 | 4061 | 136 | 1268 | 275 | 402 | 80 | 0 | 80 | 0 | 0 | 93.88
2:00 | 72 | 0 | 200 | 0 | 300 | 0 | 0 | 352 | 0 |  | 0 | 225 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 20 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 201 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 100 | 35 | 275 | 0 | 8 | 88 | 43 | 52 | 0 | 5 | 0 | 0 | 0 | 19 | 0 | 0 | 14 | 78 | 148 | 48 | 17 | 0 | 60 | 42 | 5 | 47 | 100 | 166 | 45 | 5 | 0 | 152 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 145 | 0 | 0 | 0 | 80 | 0 | 175 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4012 | 1847 | 5859 | 3716 | 136 | 1280 | 168 | 401 | 80 | 0 | 78 | 0 | 0 | 93.87
3:00 | 72 | 0 | 200 | 0 | 300 | 0 | 0 | 362 | 0 |  | 0 | 225 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 20 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 206 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 100 | 20 | 300 | 0 | 8 | 89 | 40 | 56 | 0 | 5 | 0 | 0 | 0 | 19 | 0 | 0 | 14 | 76 | 149 | 8 | 17 | 0 | 60 | 42 | 5 | 5 | 100 | 149 | 45 | 5 | 0 | 153 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3993 | 1750 | 5743 | 3708 | 136 | 1214 | 128 | 401 | 80 | 0 | 76 | 0 | 0 | 93.86
4:00 | 72 | 0 | 130 | 0 | 300 | 0 | 0 | 353 | 0 |  | 0 | 225 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 202 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 100 | 20 | 275 | 0 | 8 | 89 | 40 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 151 | 0 | 17 | 0 | 60 | 42 | 5 | 5 | 100 | 162 | 45 | 5 | 0 | 153 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3832 | 1705 | 5537 | 3546 | 136 | 1179 | 120 | 400 | 80 | 0 | 76 | 0 | 0 | 93.85
5:00 | 72 | 0 | 130 | 0 | 300 | 0 | 0 | 339 | 0 |  | 0 | 225 | 120 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 201 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 100 | 20 | 270 | 27 | 8 | 89 | 40 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 151 | 0 | 17 | 0 | 60 | 42 | 5 | 5 | 100 | 150 | 45 | 5 | 0 | 153 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 135 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 118 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3823 | 1675 | 5498 | 3518 | 135 | 1173 | 120 | 398 | 80 | 0 | 74 | 0 | 0 | 93.84
6:00 | 72 | 0 | 130 | 0 | 330 | 0 | 0 | 356 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 215 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 100 | 20 | 345 | 49 | 8 | 90 | 36 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 162 | 0 | 17 | 0 | 60 | 42 | 5 | 5 | 100 | 159 | 45 | 5 | 0 | 153 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 118 | 0 | 280 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4040 | 1781 | 5821 | 3790 | 136 | 1191 | 150 | 398 | 80 | 0 | 76 | 0 | 0 | 93.83
7:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 380 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 215 | 0 | 151 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 39 | 0 | 0 | 100 | 20 | 345 | 61 | 8 | 89 | 43 | 30 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 76 | 163 | 6 | 17 | 0 | 60 | 42 | 5 | 10 | 100 | 163 | 45 | 5 | 0 | 155 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1.1 | 0 | 0 | 0 | 145 | 3 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 |  | 389 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 119 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4265.3 | 2223.1 | 6488.4 | 4163 | 389 | 1206 | 174 | 399 | 80 | 0 | 76 | 1.4 | 0 | 93.82
8:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 375 | 0 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 18 | 20 | 25 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 214 | 0 | 151 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 0 | 0 | 100 | 20 | 330 | 63 | 8 | 89 | 36 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 80 | 151 | 73 | 17 | 0.5 | 60 | 42 | 48 | 47 | 130 | 156 | 68 | 61 | 0 | 153 | 0 | 0 | 10 | 325 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 12 | 6.2 | 0 | 0 | 0 | 145 | 55 | 0 | 0 | 0.9 | 16 | 0 | 0 | 0 | 0 |  | 390 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 3 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 220 | 0 | 0 | 0 | 23 | 0 | 206 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 17 | 0 |  | 4708.6 | 2341.8 | 7050.4 | 4244 | 390 | 1422 | 426 | 400 | 80 | 0 | 80 | 8.4 | 0 | 93.81
9:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 364 | 0 |  | 0 | 225 | 150 | 17 | 0 | 0 | 0 | 0 | 92 | 0 | 55 | 7 | 20 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 18 | 20 | 33 | 0 | 0 | 30 | 50 | 120 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 0 | 0 | 100 | 20 | 310 | 136 | 8 | 90 | 36 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 15 | 85 | 130 | 95 | 17 | 0.1 | 60 | 42 | 45 | 47 | 130 | 148 | 69 | 61 | 0 | 132 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 31 | 12.2 | 0 | 0 | 0 | 145 | 92 | 0 | 0 | 2.8 | 100 | 0 | 0 | 0 | 0 |  | 390 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 11 | 5 | 11 | 122 | 0 | 279 | 0 | 0 | 214 | 0 | 0 | 0 | 70 | 0 | 192 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 82 | 0 |  | 4961.1 | 2394.2 | 7355.3 | 4161 | 390 | 1406 | 795 | 401 | 80 | 20 | 85 | 17.3 | 0 | 93.8
10:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 335 | 0 |  | 0 | 225 | 160 | 40 | 0 | 0 | 0 | 0 | 32 | 0 | 88 | 24 | 32 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 201 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0 | 0 | 100 | 16 | 310 | 211 | 8 | 90 | 36 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 90 | 131 | 92 | 17 | 1.5 | 58 | 42 | 45 | 47 | 130 | 148 | 67 | 76 | 0 | 130 | 0 | 0 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 71 | 17.4 | 0 | 0 | 0 | 145 | 105 | 0 | 0 | 3.9 | 100 | 0 | 0 | 0 | 0 |  | 390 | 0 | 285 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 5 | 8 | 120 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 73 | 0 | 168 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 109 | 0 |  | 5094.8 | 2332.8 | 7427.6 | 4056 | 390 | 1433 | 930 | 400 | 70 | 32 | 90 | 26.6 | 0 | 93.79
11:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 338 | 0 |  | 0 | 225 | 160 | 40 | 0 | 0 | 0 | 0 | 37 | 0 | 93 | 24 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 34 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 135 | 17 | 310 | 190 | 8 | 90 | 36 | 30 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 19 | 95 | 129 | 92 | 17 | 1.9 | 60 | 42 | 47 | 44 | 163 | 152 | 65 | 56 | 0 | 147 | 0 | 0 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 103 | 19.5 | 0 | 0 | 0 | 145 | 105 | 0 | 0 | 4.6 | 121 | 0 | 0 | 0 | 0 |  | 390 | 0 | 260 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 124 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 90 | 0 | 130 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 109 | 0 |  | 5205 | 2191.3 | 7396.3 | 3985 | 390 | 1410 | 996 | 404 | 70 | 16 | 95 | 30.3 | 0 | 93.78
12:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 342 | 0 |  | 0 | 225 | 210 | 55 | 0 | 0 | 0 | 0 | 62 | 0 | 100 | 48 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 34 | 20 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 135 | 17 | 305 | 185 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 100 | 127 | 92 | 17 | 2.1 | 60 | 42 | 53 | 44 | 163 | 153 | 65 | 56 | 0 | 146 | 0 | 0 | 10 | 305 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 19.6 | 0 | 0 | 0 | 145 | 105 | 0 | 0 | 4.8 | 209 | 0 | 0 | 0 | 0 |  | 390 | 0 | 245 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 130 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 109 | 0 |  | 5467.5 | 2175.8 | 7643.3 | 4006 | 390 | 1452 | 1177 | 401 | 70 | 16 | 100 | 31.3 | 0 | 93.77
13:00 | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 347 | 0 |  | 0 | 225 | 300 | 53 | 0 | 0 | 0 | 0 | 34 | 0 | 100 | 72 | 32 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 34 | 25 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7 | 19 | 10 | 0 | 0 | 135 | 24 | 260 | 183 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 100 | 124 | 92 | 17 | 2 | 60 | 42 | 53 | 44 | 163 | 148 | 64 | 59 | 0 | 152 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 120 | 19.7 | 0 | 0 | 0 | 144 | 115 | 0 | 0 | 4.7 | 214 | 0 | 0 | 0 | 0 |  | 390 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 130 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 109 | 0 |  | 5538.4 | 2179.7 | 7718.1 | 3892 | 390 | 1404 | 1397 | 402 | 70 | 32 | 100 | 31.1 | 0 | 93.76
14:00 | 72 | 0 | 100 | 0 | 380 | 0 | 0 | 338 | 0 |  | 0 | 225 | 260 | 93 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 7 | 0 | 0 | 80 | 75 | 260 | 165 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 99 | 105 | 92 | 17 | 1.7 | 60 | 42 | 11 | 44 | 100 | 149 | 45 | 20 | 0 | 152 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 17.39 | 0 | 0 | 0 | 145 | 55 | 0 | 0 | 4.1 | 215 | 0 | 0 | 0 | 0 |  | 388 | 0 | 235 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 57 | 0 | 130 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 109 | 0 |  | 5139.19 | 2076.4 | 7215.59 | 3732 | 388 | 1153 | 1328 | 402 | 70 | 16 | 99 | 27.59 | 0 | 93.75
15:00 | 72 | 0 | 101 | 0 | 385 | 0 | 0 | 275 | 0 |  | 0 | 225 | 260 | 100 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 26 | 33 | 17 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 4 | 0 | 0 | 80 | 95 | 260 | 166 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 25 | 17 | 97 | 105 | 95 | 17 | 1.1 | 58 | 42 | 51 | 44 | 100 | 150 | 45 | 50 | 0 | 150 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13.62 | 0 | 0 | 0 | 145 | 55 | 0 | 0 | 2.9 | 216 | 0 | 0 | 0 | 0 |  | 388 | 0 | 225 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 20 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 52 | 0 | 130 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 108 | 0 |  | 5101.62 | 1956.2 | 7057.82 | 3653 | 388 | 1125 | 1288 | 400 | 70 | 16 | 97 | 20.82 | 0 | 93.74
16:00 | 72 | 0 | 100 | 0 | 380 | 0 | 0 | 315 | 0 |  | 0 | 225 | 245 | 65 | 0 | 0 | 0 | 0 | 41 | 0 | 72 | 48 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 33 | 17 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 213 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 4 | 0 | 0 | 80 | 118 | 290 | 186 | 8 | 90 | 20 | 10 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 89 | 105 | 95 | 17 | 0.7 | 60 | 40 | 53 | 44 | 100 | 160 | 45 | 59 | 0 | 66 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 8.13 | 0 | 0 | 0 | 145 | 55 | 0 | 0 | 1.7 | 125 | 0 | 0 | 0 | 0 |  | 388 | 0 | 225 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 53 | 0 | 130 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 70 | 0 |  | 4912.53 | 1950.4 | 6862.93 | 3701 | 388 | 1193 | 993 | 401 | 70 | 16 | 89 | 11.93 | 0 | 93.73
17:00 | 72 | 0 | 100 | 0 | 380 | 0 | 0 | 358 | 0 |  | 0 | 225 | 250 | 55 | 1 | 1 | 0 | 0 | 67 | 0 | 60 | 48 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 33 | 17 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 6 | 0 | 0 | 80 | 135 | 270 | 174 | 8 | 90 | 20 | 10 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 17 | 96 | 104 | 92 | 17 | 0.2 | 60 | 40 | 53 | 44 | 130 | 150 | 45 | 59 | 0 | 0 | 0 | 0 | 10 | 325 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 2.41 | 20 | 0 | 3 | 145 | 55 | 0 | 1 | 0.34 | 126 | 0 | 0 | 0 | 0 |  | 386 | 0 | 225 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 54 | 0 | 130 | 0 | 256 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 70 | 0 |  | 4972.95 | 1967 | 6939.95 | 3683 | 386 | 1270 | 1014 | 402 | 70 | 16 | 96 | 2.95 | 0 | 93.72
18:00 | 72 | 0 | 150 | 0 | 320 | 0 | 0 | 351 | 0 |  | 0 | 225 | 260 | 75 | 22 | 18 | 0 | 0 | 67 | 0 | 75 | 72 | 16 | 22 | 0 | 0 | 12 | 53 | 55 | 0 | 22 | 25 | 14 | 33 | 17 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 32 | 26 | 19 | 12 | 0 | 0 | 84 | 240 | 290 | 202 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 126 | 95 | 17 | 0 | 60 | 44 | 53 | 44 | 130 | 163 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 15 | 0 | 0 | 21 | 0 | 95 | 0 | 80 | 0 | 40 | 145 | 80 | 0 | 20 | 0 | 213 | 0 | 0 | 0 | 0 |  | 555 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 0 | 6 | 0 | 189 | 18 | 27 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 54 | 0 | 130 | 0 | 256 | 0 | 0 | 4 | 15 | 70 | 0 | 0 | 109 | 0 |  | 5688 | 2456 | 8144 | 3906 | 555 | 1267 | 1761 | 400 | 71 | 72 | 112 | 0 | 0 | 93.71
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 365 | 0 |  | 0 | 225 | 270 | 100 | 60 | 43 | 0 | 0 | 65 | 0 | 100 | 102 | 0 | 83 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 85 | 50 | 19 | 25 | 0 | 0 | 100 | 310 | 295 | 194 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 126 | 95 | 17 | 0 | 59 | 44 | 53 | 41 | 130 | 148 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 315 | 24 | 11 | 0 | 75 | 0 | 0 | 40 | 0 | 142 | 0 | 90 | 0 | 130 | 145 | 99 | 0 | 31 | 0 | 217 | 0 | 0 | 0 | 0 |  | 556 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 20 | 65 | 0 | 0 | 0 | 25 | 0 | 102 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 130 | 0 | 255 | 0 | 0 | 46 | 15 | 112 | 0 | 0 | 109 | 0 |  | 6415 | 2711 | 9126 | 4067 | 556 | 1326 | 2469 | 402 | 71 | 127 | 108 | 0 | 0 | 93.7
19:30 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 342 | 0 |  | 0 | 225 | 255 | 100 | 80 | 30 | 0 | 0 | 63 | 0 | 100 | 102 | 0 | 30 | 0 | 0 | 24 | 53 | 55 | 0 | 22 | 0 | 31 | 33 | 33 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 87 | 50 | 19 | 28 | 0 | 0 | 100 | 345 | 295 | 228 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 108 | 95 | 17 | 0 | 60 | 44 | 53 | 44 | 130 | 145 | 68 | 59 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 30 | 0 | 0 | 40 | 0 | 149 | 0 | 90 | 0 | 150 | 145 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 556 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 20 | 80 | 0 | 0 | 0 | 25 | 0 | 102 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 98 | 0 | 130 | 0 | 257 | 0 | 0 | 30 | 0 | 113 | 0 | 0 | 109 | 0 |  | 6331 | 2696 | 9027 | 4070 | 556 | 1320 | 2373 | 402 | 71 | 127 | 108 | 0 | 0 | 0
20:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 337 | 0 |  | 0 | 225 | 250 | 100 | 85 | 30 | 0 | 0 | 65 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 24 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 202 | 0 | 125 | 0 |  | 0 | 0 | 0 | 0 | 89 | 50 | 19 | 30 | 0 | 0 | 100 | 360 | 295 | 228 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 107 | 95 | 17 | 0 | 60 | 44 | 53 | 44 | 130 | 150 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 0 | 90 | 0 | 100 | 145 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 555 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 80 | 0 | 0 | 0 | 25 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 98 | 0 | 130 | 0 | 258 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 0 |  | 6281 | 2623 | 8904 | 4139 | 555 | 1313 | 2227 | 402 | 71 | 85 | 112 | 0 | 0 | 93.69
21:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 350 | 0 |  | 0 | 225 | 253 | 100 | 82 | 30 | 0 | 0 | 67 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 24 | 53 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 210 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 65 | 50 | 19 | 36 | 0 | 0 | 100 | 360 | 310 | 228 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 101 | 95 | 17 | 0 | 59 | 44 | 53 | 50 | 130 | 157 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 90 | 0 | 50 | 145 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 556 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 26 | 24 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 130 | 0 | 256 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 109 | 0 |  | 6223 | 2512 | 8735 | 4206 | 556 | 1342 | 2025 | 402 | 70 | 26 | 108 | 0 | 0 | 93.68
22:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 361 | 0 |  | 0 | 225 | 254 | 100 | 0 | 0 | 0 | 0 | 42 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 18 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 215 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 18 | 45 | 19 | 41 | 0 | 0 | 100 | 340 | 320 | 196 | 8 | 89 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 103 | 95 | 17 | 0 | 60 | 44 | 53 | 50 | 130 | 153 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 10 | 0 | 0 | 145 | 90 | 0 | 17 | 0 | 217 | 0 | 0 | 0 | 0 |  | 561 | 0 | 275 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 98 | 0 | 130 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5740 | 2335 | 8075 | 4145 | 561 | 1357 | 1442 | 402 | 70 | 0 | 98 | 0 | 0 | 93.91
23:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 343 | 0 |  | 0 | 225 | 245 | 55 | 0 | 0 | 0 | 0 | 42 | 0 | 90 | 48 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 19 | 42 | 0 | 0 | 100 | 330 | 275 | 189 | 8 | 50 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 103 | 95 | 17 | 0 | 60 | 44 | 53 | 50 | 163 | 162 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 144 | 50 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 |  | 538 | 0 | 275 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 119 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 130 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 5267 | 2213 | 7480 | 4032 | 538 | 1373 | 978 | 399 | 70 | 0 | 90 | 0 | 0 | 93.9
24:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 359 | 0 |  | 0 | 225 | 232 | 50 | 0 | 0 | 0 | 0 | 37 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 19 | 42 | 0 | 0 | 100 | 285 | 270 | 180 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 82 | 104 | 95 | 17 | 0 | 60 | 44 | 53 | 50 | 163 | 148 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 |  | 295 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 130 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 4857 | 1961 | 6818 | 3926 | 295 | 1417 | 627 | 401 | 70 | 0 | 82 | 0 | 0 | 93.89
KWH | 1640000 | 0 | 3789000 | 0 | 8430873 | 0 | 0 | 8464390 | 0 |  | 0 | 5186750 | 4771287 | 1158720 | 286536 | 150818 | 0 | 0 | 1573000 | 0 | 1435200 | 1100304 | 224640 | 153931 | 0 | 0 | 146688 | 868320 | 225286 | 0 | 339264 | 600000 | 687420 | 661600 | 721800 | 0 | 0 | 607440 | 1068000 | 2800000 | 0 | 0 | 4888927 | 0 | 3084664 | 0 |  | 0 | 0 | 0 | 0 | 338880 | 324960 | 442704 | 548640 | 0 | 0 | 2404320 | 3350900 | 7303000 | 3198000 | 200727 | 2022130 | 851832 | 646080 | 0 | 992688 | 0 | 0 | 0 | 339084 | 158940 | 580900 | 476380 | 2169600 | 2973960 | 1798080 | 397512 | 12350 | 1411000 | 1024440 | 872400 | 961056 | 3234845 | 3563000 | 1353312 | 998400 | 0 | 2449550 | 0 | 0 | 159840 | 7604000 | 375622 | 155184 | 0 | 150545 | 0 | 0 | 211200 | 0 | 1464480 | 137298 | 358080 | 0 | 429890 | 3481000 | 1585200 | 0 | 152218 | 31200 | 2797636 | 0 | 0 | 0 | 0 |  | 8608000 | 0 | 6814944 | 0 | 1221120 | 0 | 0 | 0 | 0 | 4480 | 0 | 4705873 | 343700 | 257184 | 0 | 0 | 0 | 52622 | 0 | 244660 | 449140 | 0 | 0 | 0 | 0 | 309600 | 114480 | 249480 | 2880436 | 0 | 6748600 | 0 | 0 | 3866227 | 0 | 0 | 0 | 1476383 | 0 | 3802255 | 0 | 8251145 | 0 | 0 | 93120 | 33840 | 379200 | 0 | 22728 | 1626144 | 0 |  | 121557921 | 52555361 | 174113282 | 95432487 | 8608000 | 31900734 | 23968007 | 9629036 | 1675440 | 526402 | 2169600 | 203576 | 0
Fuel Cost | 1836800 | 0 | 4054230 | 0 | 6238846.02 | 0 | 0 | 6094360.8 | 0 |  | 0 | 4149400 | 4294158.3 | 11818944 | 3103184.88 | 1547392.68 | 0 | 0 | 1966250 | 0 | 15930720 | 11179088.64 | 2226182.4 | 1613196.88 | 0 | 0 | 1372999.68 | 8327188.8 | 2149228.44 | 0 | 254448 | 450000 | 0 | 0 | 0 | 0 | 0 | 157934.4 | 277680 | 4284000 | 0 | 0 | 5133373.35 | 0 | 3917523.28 | 0 |  | 0 | 0 | 0 | 0 | 3222748.8 | 3041625.6 | 407287.68 | 1525219.2 | 0 | 0 | 2524536 | 2479666 | 6134520 | 2942160 | 196712.46 | 2689432.9 | 698502.24 | 665462.4 | 0 | 1419543.84 | 0 | 0 | 0 | 345865.68 | 119205 | 1097901 | 357285 | 14970240 | 2438647.2 | 17099740.8 | 405462.24 | 202540 | 1918960 | 1393238.4 | 1186464 | 1201320 | 4011207.8 | 3277960 | 2016434.88 | 1757184 | 0 | 3723316 | 0 | 0 | 375624 | 5398840 | 281716.5 | 117939.84 | 0 | 1576206.15 | 0 | 0 | 2031744 | 0 | 14776603.2 | 1584418.92 | 3337305.6 | 0 | 4028069.3 | 3272140 | 13902204 | 0 | 1438460.1 | 0 | 25794203.92 | 0 | 0 | 0 | 0 |  | 23241600 | 0 | 5315656.32 | 0 | 11771596.8 | 0 | 0 | 0 | 0 | 58688 | 0 | 3764698.4 | 532735 | 2762156.16 | 0 | 0 | 0 | 586209.08 | 0 | 2422134 | 4657581.8 | 0 | 0 | 0 | 0 | 340560 | 188892 | 188856.36 | 18348377.32 | 0 | 27601774 | 0 | 0 | 3402279.76 | 0 | 0 | 0 | 2347448.97 | 0 | 3345984.4 | 0 | 6023335.85 | 0 | 0 | 854841.6 | 301514.4 | 3541728 | 0 | 0 | 0 | 0 |  | 265762995.2 | 121598648.22 | 387361643.42 | 88889483.25 | 23241600 | 31319949.52 | 175474432.53 | 45950151.32 | 435614.4 | 5293213.48 | 14970240 | 1786958.92 | 0
Yesterday Day Peak | 72 | 0 | 200 | 0 | 380 | 0 | 0 | 342 | 0 |  | 0 | 225 | 210 | 55 | 0 | 0 | 0 | 0 | 62 | 0 | 100 | 48 | 16 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 34 | 20 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 135 | 17 | 305 | 185 | 8 | 90 | 40 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 100 | 127 | 92 | 17 | 2.1 | 60 | 42 | 53 | 44 | 163 | 153 | 65 | 56 | 0 | 146 | 0 | 0 | 10 | 305 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 19.6 | 0 | 0 | 0 | 145 | 105 | 0 | 0 | 4.8 | 209 | 0 | 0 | 0 | 0 |  | 390 | 0 | 245 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 130 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 109 | 0 |  | 7643.3 | DayPeak
Yesterday Evening Peak | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 365 | 0 | 0 | 0 | 225 | 270 | 100 | 60 | 43 | 0 | 0 | 65 | 0 | 100 | 102 | 0 | 83 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 203 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 50 | 19 | 25 | 0 | 0 | 100 | 310 | 295 | 194 | 8 | 90 | 40 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 126 | 95 | 17 | 0 | 59 | 44 | 53 | 41 | 130 | 148 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 315 | 24 | 11 | 0 | 75 | 0 | 0 | 40 | 0 | 142 | 0 | 90 | 0 | 130 | 145 | 99 | 0 | 31 | 0 | 217 | 0 | 0 | 0 | 0 |  | 556 | 0 | 265 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 20 | 65 | 0 | 0 | 0 | 25 | 0 | 102 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 130 | 0 | 255 | 0 | 0 | 46 | 15 | 112 | 0 | 0 | 109 | 0 |  | 9126 | EvPeak
Forecast for Evening | 72 | 150 | 0 | 0 | 365 | 0 | 0 | 412 | 0 | 0 | 0 | 225 | 335 | 100 | 100 | 55 | 240 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 30 | 50 | 120 | 0 | 25 | 220 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 0 | 100 | 360 | 360 | 225 | 110 | 0 | 43 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 104 | 130 | 95 | 22 | 0 | 60 | 44 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 0 | 0 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 745 | 40 | 340 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 194 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 5 | 11 | 125 | 0 | 285 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113
Forecast for Day | 72 | 0 | 0 | 0 | 365 | 0 | 0 | 412 | 0 | 0 | 0 | 225 | 230 | 100 | 100 | 55 | 240 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 30 | 50 | 120 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 320 | 360 | 225 | 55 | 0 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 94 | 110 | 95 | 22 | 1.6 | 60 | 44 | 51 | 44 | 163 | 160 | 66 | 76 | 0 | 0 | 0 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 90 | 0 | 100 | 230 | 60 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 400 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 194 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 5 | 11 | 125 | 0 | 285 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 225 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 377 | 0 | 0 | 0 | 225 | 230 | 3 | 0 | 0 | 238 | 0 | 0 | 0 | 20 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 28 | 0 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 0 | 0 | 100 | 320 | 315 | 180 | 55 | 0 | 32 | 5 | 0 | 32 | 0 | 0 | 0 | 22 | 11 | 25 | 17 | 78 | 105 | 95 | 17 | 0.4 | 60 | 44 | 51 | 38 | 130 | 147 | 69 | 59 | 0 | 0 | 0 | 0 | 10 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5.92 | 0 | 0 | 0 | 145 | 70 | 0 | 0 | 1.4 | 66 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 0 | 120 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 82 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 17 | 0 | 0
199
| Minimum Generation |  | 5498 | 5:00
| Highest Generation |  | 9126 | 19:00
| Day Peak Generation |  | 7643.3 | 12:00
| Evening Peak Generation |  | 9126 | 19:00
| HVDC Max Flow |  | 561 | 22:00
| HVDC EvPeak Flow |  | 556 | 19:00
| Load factor L.F |  | 79.5%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7643.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5624 | MW
Evening Peak Generation : |  | 9126 | MW Hour : | 19:00 | Available Max Generation : |  | 14493 | MW
E.P. Demand (at gen end) : |  | 9126 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 9126 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5293 | MW
Total Gen. (MKWH) : |  | 174.1133 | System Load Factor : | 79.5% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -452 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-05
Actual : | 93.59 | Ft.(MSL) , | Rule curve : | 96.44 | Ft.( MSL )
Gas Consumed : | Total = | 1137.66 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120209432.77
: |  | Coal : | 45950151.32 | Oil : | 180767646.01 | Total : | 346927230.1
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3261.4044 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1104.0806 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 988.3327 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 892.727 |  |  | 0 | 0%
) | 0 | 0:00 | 806.9182 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 651.1418 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 370.4916 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 167.821 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 502.1623 |  |  | 0 | 0%
Total | 0 |  | 8745.0796 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Haripur 360 MW CCPP
3) Ghorasal Unit-3,4,5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,4
6) Sirajganj unit-2
7)Shajibazar 330 MW GT-1
8) Chandpur 150 MW
9) Sylhet 150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorashal-Joydevpur 132 kV Ckt-2 was under shut down from 09:32 to 16:43 for A/M.
b) Rangamati-Chandraghona 132 kV Ckt-2 was under shut down from 08:49 to 16:29 for A/M.
c) Ullon-Dhanmondi 132 kV Ckt-2 was under shut down from 12:13 to 14:29 for A/M.
d) Comilla(N)-Tripura 132 kV Ckt-1 was under shut down from 08:41 to 16:31 for A/M.
e) Bibiyana-Shahjibazar 230 kV Ckt-2 was under shut down from 08:44 to 15:47 for A/M.
f) Valuka-Mymensing 132 kV Ckt-2 was under shut down from 08:40 to 15:12 for C/M.
g) Meghnaghat Summit 305 MW GT-1 was synchronized at 09:32.
h) Ashuganj 225 MW ST was synchronized at 08:04.
i) Bogura-Naogaon 132 kV Ckt-2 was under shut down from 11:18 to 11:41 due to red hot maintenance
at CT of Bogura end.
j) Haripur-Rahim steel 132 kV Ckt-1 was under shut down from 11:45 to 15:42 due to red hot
maintenance at Rahim steel end.
k) Matuail 132/33 kV T2 transformer tripped at 09:57 showing O/C relay at 33 kV end and was switched |  |  |  |  | About 30 MW power interruption occurred under Matuail S/S area
on at 10:55. |  |  |  |  | from 09:57 to 10:55.
l) Ashuganj (North) 450 MW ST was synchronized at 12:46.
m) Sylhet 132/33 kV T2 transformer was shut down from 10:46 to 13:03 due to maintenance work.
n) Raozan-Hathazari 230 kV Cklt-2 was under shut down from 10:08 to 12:50 due to maintenance by P/P.
o) Polashbari 132/33 kV T3 & T4 transformers were under shut down from 14:42 to 16:24 due to
replace at 33 kV Bus isolator.
p) Chandpur CCPP 150 MW was shut down at 23:05.
q) B.Baria-Shahjibazar 132 kV Ckt-2 was shut down at 07:35(05/02/2020) for A/M.
r) Rampura230/132 kV T3 transformer was shut down at 07:51(05/02/2020) for C/M.
s) Ghorashal unit-4 GT tripped at 05:43(05/02/2020) due to gas shortage.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 72 | 1640000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3789000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 8430873
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 8464390 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5186750 | GT-2 Under maint
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1158720
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 4771287 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 60 | 286536 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 43 | 150818 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 83 | 153931 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 339264
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 65 | 1573000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1435200
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1100304
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 146688
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 868320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 224640 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 225286
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1287420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 661600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 721800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 75 | 150545 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 142 | 1464480 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2494 | 44230852
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137298
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 324960
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 71 | 1675440 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4888927
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 3084664 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 31 | 152218 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 358080 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 442704
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 548640
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 338880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31200
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 217 | 2797636 | Transformer overload.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1015 | 17580647
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Machine problem
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2404320 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 3198000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 3350900 | Delayed in Synchronizing
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7303000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 851832
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 646080 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 992688
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 130 | 429890 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2022130 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 339084
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 158940
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2169600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 580900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 476380
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1423 | 25124471
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 2973960 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 397512 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1798080 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12350
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 211200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 99 | 1585200 | Engine problem
| Mymensingh Area Total |  |  |  | 637 | 377 | 6978302
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1411000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 44 | 1024440
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3234845
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 148 | 3563000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 872400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 41 | 961056
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 155184
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1353312 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 59 | 998400 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 2449550
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 375622
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7604000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 145 | 3481000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 159840
| Sylhet Area Total |  |  |  | 1949 | 1106 | 27643649
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 556 | 8608000
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1221120
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 4480 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 6814944 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 15 | 33840 | Low demand
| Khulna Area Total |  |  |  | 2314 | 951 | 16682384
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 65 | 257184 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 343700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 189 | 4705873
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1476383
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 371 | 6783140
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 52622
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 449140 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 130 | 3866227 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 3802255 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 255 | 8251145 | Gas shortage.
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 309600
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 114480 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249480
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 102 | 244660
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 46 | 93120 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1626144
| Rajshahi Area Total |  |  |  | 2183 | 875 | 19058873
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 122 | 2880436
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6748600
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 112 | 379200
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22728
| Rangpur Area Total |  |  |  | 605 | 514 | 10030964
| Total |  |  |  | 19107 | 9126 | 174113282
| Eastern Grid Total |  |  |  | 13543 | 6415 | 121557921
| Western Grid Total |  |  |  | 5564 | 2711 | 52555361
| National Grid Total |  |  |  | 19107 | 9126 | 174113282
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-04
(a) ENTIRE EASTERN GRID : |  | 5713 | MW | (b) ENTIRE WESTERN GRID : |  | 2950 | MW
i) Dhaka area |  | 3015 | MW | i) Khulna area |  | 1053 | MW
ii) Chittagong area |  | 869 | MW | ii) Rajshahi area |  | 986 | MW
iii) Comilla area |  | 744 | MW | iii) Barisal area |  | 227 | MW
iv) Mymensingh area |  | 771 | MW | iv) Rangpur area |  | 684 | MW
v) Sylhet area |  | 314 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8663 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 12:00 | Srimongal | 24 | 18:30 | Jhenida | 81 | 19:00
Munsiganj | 80 | 21:00 | Shahjibazar | 80 | 19:30 | Bottail | 96 | 18:30
Sonargaon | 68 | 7:00 | Fenchuganj | 26 | 18:30 | G.K Project | 38 | 18:30
Shyampur | 176 | 0:00 | Kulawara | 26 | 18:00 | Faridpur | 130 | 19:30
Bhulta | 157 | 12:00 | Sylhet | 93 | 18:30 | Madaripur | 57 | 20:00
Madanganj | 53 | 18:00 | Chatak | 18 | 18:00 | Sariatpur | 38 | 19:30
Shitalakhya | 94 | 18:30 | Sunamganj | 28 | 19:30 | Gopalganj | 67 | 19:00
Rahim steel | 13 | 18:00 | Biani Bazar | 32 | 19:00 | Bagerhat | 65 | 18:00
Matuail | 80 | 12:00 | Comilla (S) | 112 | 18:00 | Mongla | 36 | 9:00
Ghorasal | 61 | 18:30 | Comilla(N) | 77 | 19:00 | Satkhira | 69 | 18:30
Narsingdi | 117 | 19:30 | Chandpur | 56 | 20:00 | Gallamari | 39 | 13:00
Haripur (SBU) | 84 | 19:30 | Feni | 89 | 18:30 | Magura | 34 | 18:30
Ullon | 42 | 18:00 | Chowmuhani | 114 | 19:30 | Norail | 27 | 18:30
Hasnabad | 135 | 20:00 | Ashuganj | 35 | 21:00 | Chuadanga | 62 | 18:30
Magbazar | 72 | 13:00 | Daudkandi | 104 | 20:00 | Barisal(N) | 31 | 19:00
Maniknagar | 70 | 12:00 | B.Baria | 94 | 19:00 | Barisal (S) | 66 | 18:30
Bangabhaban | 20 | 13:00 | Ramganj | 58 | 19:00 | Patuakhali | 72 | 20:00
Narinda | 76 | 16:00 | Chaddagram | 16 | 18:00 | Bhandaria | 40 | 20:00
Dhanmondi | 78 | 13:00 | PHP | 5 | 24:00 | Borhan Uddin | 29 | 21:00
Lalbag | 64 | 18:30 | Madunaghat | 39 | 18:30 | Ishurdi | 45 | 18:30
Madartek | 43 | 19:00 | Hathazari | 66 | 18:30 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 142 | 11:00 | Natore | 92 | 19:30
Mirpur | 71 | 18:30 | Halishahar | 86 | 18:30 | Bogra | 133 | 19:00
Kalyanpur | 69 | 18:00 | Baraulia | 149 | 8:00 | Noagaon | 90 | 18:30
Gulshan | 92 | 18:00 | Sikalbaha | 20 | 18:00 | Rajshahi | 92 | 20:00
Uttara | 42 | 18:30 | Dohazari | 72 | 18:30 | Rajshahi New | 12 | 19:30
Uttara New | 32 | 18:30 | Cox'sbazar | 74 | 19:30 | C.Nawabganj | 66 | 18:30
Kamrangirchar | 71 | 13:00 | Chandraghona | 22 | 8:00 | Amnura | 34 | 18:30
Savar | 92 | 19:00 | Kaptai | 3.8 | 18:30 | Pabna | 73 | 18:30
Bhasantec | 93 | 19:00 | A. Khaer Stl. | 6 | 2:00 | Shahjadpur | 83 | 19:30
Agargaon | 37 | 19:00 | Bakulia | 70 | 18:30 | Serajganj | 70 | 8:00
Satmosjid | 61 | 18:30 | Julda | 20 | 9:00 | Niyamatpur | 89 | 19:30
Tongi | 93 | 18:00 | TK chemical | 10 | 18:00 | Joypurhat | 54 | 19:00
Kabirpur | 154 | 18:00 | Modern Steel | 17 | 12:00 | Sherpur(Bogura) | 39 | 8:00
Basundhara | 82 | 18:00 | Shahmirpur | 23 | 19:00 | Mohastangor | 34 | 18:30
Manikganj | 58 | 19:30 | Khagrachhari | 18 | 19:00 | Rangpur | 119 | 18:30
Joydevpur | 161 | 18:00 | Matarbari | 22.5 | 19:00 | Lalmonirhat | 49 | 19:00
New Tongi | 77 | 18:30 | Baroiar Hat | 16 | 18:30 | Saidpur | 98 | 18:30
Korda | 186 | 18:30 | Rangamati | 8 | 18:00 | Purbasadipur | 101 | 18:30
Dhamrai | 44 | 19:30 | Abul Khair 230 | 86 | 0:00 | Thakurgaon | 60 | 19:00
Valuka | 80 | 18:00 | BSRM | 109 | 5:00 | Palashbari | 102 | 18:00
Tangail | 130 | 18:00 | GPH Ispat | 42 | 10:00 | Barapukuria | 52 | 19:00
Mymensing | 185 | 18:30 | Goalpara | 18 | 18:30 | Panchagar | 43 | 19:00
Kishorganj | 89 | 21:00 | Central s/s | 66 | 19:00 | Joldhaka | 24 | 18:30
Netrokona | 102 | 19:30 | Noapara | 47 | 18:30 | Kurigram | 49 | 0.77083
Jamalpur | 104 | 20:00 | Jessore | 92 | 19:00
Sherpur | 94 | 18:30 | Benapol | 30 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-04 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 402 | 0.8125 | 384 | 0.375 | Kaliakoir | 394 | 0.041667 | 372 | 0.83333
Bheramara | 408 | 24:00 | 400 | 0.41667 | Bhulta | 408 | 0.83333 | 388 | 0.45833
Ashuganj(N) | 398 | 0.25 | 380 | 0.5 | Gopalganj | 399 | 0.083333 | 377 | 0.8125
Payra | 236 | 0.8125 | 226 | 0.45833
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 238 | 0.5 | Hathazari | 242 | 0.79167 | 232 | 0.45833
Ishurdi | 242 | 0.125 | 228 | 0.33333 | Megnaghat | 245 | 24:00 | 241 | 0.29167
Ashuganj | 246 | 0.79167 | 239 | 0.5 | Fenchuganj | 240 | 0.8125 | 230 | 0.5
Serajganj | 235 | 0.041667 | 230 | 0.29167 | Siddhirganj | 238 | 0.8125 | 229 | 0.45833
Baghabari | 243 | 0.041667 | 237 | 0.41667 | Maniknagar | 238 | 0.8125 | 228 | 0.5
Barapukuria | 233 | 0.125 | 228 | 0.33333 | Old Airport | 250 | 0.041667 | 238 | 0.29167
Bogra | 231 | 24:00 | 230 | 0.33333 | Barisal | 224 | 0.20833 | 219 | 0.875
Khulna South | 241 | 0.125 | 223 | 0.79167 | AKSML | 229 | 0.8125 | 222 | 0.375
Rampura | 235 | 0.8125 | 229 | 0.45833 | BSRM | 225 | 0.79167 | 220 | 0.41667
Haripur | 237 | 0.79167 | 230 | 0.29167 | Bibiyana | 239 | 0.83333 | 229 | 0.5
Hasnabad | 240 | 0.8125 | 230 | 0.41667 | Bhulta | 238 | 0.083333 | 233 | 0.83333
Shyampur | 239 | 0.83333 | 229 | 0.45833 | Ashuganj (S) | 241 | 0.79167 | 231 | 0.5
Aminbazar | 235 | 0.8125 | 227 | 0.29167 | Kaliakoir | 407 | 0.083333 | 394 | 0.77083
Tongi | 242 | 0.875 | 236 | 0.41667 | GPH | 243 | 0.041667 | 237 | 0.5
Comilla (N) | 228 | 0.8125 | 221 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 0.8125 | 133 | 0.375 | Khulshi | 133 | 0.8125 | 129 | 0.375
Munsiganj | 140 | 0.75 | 133 | 0.29167 | Halishahar | 136 | 0.8125 | 131 | 0.33333
Sonargaon | 138 | 0.91667 | 132 | 0.29167 | Baraulia | 135 | 0.125 | 130 | 0.29167
Shyampur | 139 | 0.8125 | 133 | 0.45833 | Sikalbaha | 135 | 0.8125 | 130 | 0.41667
Bhulta | 132 | 0.75 | 126 | 0.5 | Dohazari | 132 | 0.625 | 129 | 0.083333
Madanganj | 141 | 0.79167 | 130 | 0.45833 | Cox'sbazar | 129 | 0.54167 | 125 | 0.25
Shitalakhya | 143 | 0.79167 | 132 | 0.45833 | Chandraghona | 135 | 0.8125 | 132 | 0.41667
Rahim steal | 138 | 18:00 | 133 | 0.45833 | Kaptai | 136 | 0.8125 | 132 | 0.33333
Matuail | 137 | 0.77083 | 132 | 0.5 | A. Khaer Stl. | 134 | 0.125 | 130 | 0.41667
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | Bakulia | 134 | 0.79167 | 129 | 0.41667
Narsinghdi | 134 | 0.041667 | 131 | 0.25 | Julda | 134 | 0.77083 | 130 | 0.41667
Haripur (SBU) | 138 | 0.79167 | 133 | 0.45833 | TK Chemical | 135 | 0.8125 | 130 | 0.45833
Ullon | 132 | 1904-01-02 | 126 | 0.5 | Modern Steel | 134 | 0.79167 | 130 | 0.083333
Hasnabad | 139 | 0.8125 | 131 | 0.5 | Shahmirpur | 134 | 0.8125 | 130 | 0.41667
Magbazar | 132 | 0.95833 | 126 | 0.5 | Khagrachhari | 134 | 0.875 | 130 | 0.54167
Maniknagar | 139 | 0.875 | 135 | 0.5 | Matarbari | 130 | 0.041667 | 125 | 0.77083
Bangabhaban | 139 | 0.875 | 135 | 0.5 | Baroiar Hat | 136 | 0.95833 | 134 | 0.29167
Narinda | 139 | 0.875 | 135 | 0.5 | Rangamati | 134 | 0.16667 | 131 | 10:00
Dhanmondi | 132 | 1904-01-02 | 126 | 0.5 | Goalpara | 139 | 0.20833 | 130 | 19:00
Lalbag | 138 | 0.8125 | 130 | 0.5 | Central s/s | 135 | 0.083333 | 130 | 0.79167
Madartek | 131 | 0.83333 | 126 | 0.5 | Noapara | 138 | 0.041667 | 127 | 0.77083
Dhaka University |  |  |  |  | Jessore | 133 | 0.125 | 124 | 0.77083
Mirpur | 136 | 0.25 | 131 | 0.5 | Benapol | 136 | 0.041667 | 124 | 0.33333
Kalyanpur | 140 | 0.20833 | 134 | 0.5 | Jhenida | 136 | 0.16667 | 122 | 0.33333
Gulshan | 131 | 0.083333 | 127 | 0.54167 | Bottail | 138 | 0.041667 | 129 | 0.77083
Uttara | 137 | 0.20833 | 125 | 0.5 | G.K Project | 141 | 0.083333 | 136 | 0.77083
Uttara New | 137 | 0.20833 | 131 | 0.5 | Faridpur | 140 | 0.041667 | 132 | 0.77083
Kamrangirchar | 135 | 0.16667 | 129 | 0.5 | Madaripur | 139 | 0.083333 | 132 | 0.77083
Savar | 136 | 0.25 | 130 | 0.5 | Sariatpur | 142 | 0.041667 | 134 | 0.77083
Bhasantec | 137 | 0.20833 | 131 | 0.5 | Gopalganj | 144 | 0.125 | 135 | 0.8125
Agargaon | 138 | 0.20833 | 132 | 0.5 | Bagerhat | 135 | 0.083333 | 124 | 0.29167
Satmosjid | 137 | 0.20833 | 132 | 0.5 | Mongla | 133 | 0.083333 | 125 | 0.29167
Tongi | 142 | 0.8125 | 136 | 0.45833 | Satkhira | 136 | 0.16667 | 125 | 0.33333
Kabirpur | 140 | 20:00 | 128 | 0.5 | Gallamari | 137 | 0.125 | 129 | 0.77083
Basundhara | 132 | 19:00 | 126 | 0.45833 | Magura | 136 | 0.20833 | 121 | 0.29167
Manikganj | 138 | 0.8125 | 132 | 0.66667 | Norail | 134 | 0.083333 | 121 | 0.77083
Joydevpur | 143 | 0.875 | 138 | 0.5 | Chuadanga | 130 | 0.041667 | 118 | 0.77083
New Tongi | 141 | 0.83333 | 133 | 0.33333 | Barisal(N) | 141 | 0.041667 | 135 | 0.29167
Kodda | 141 | 0.79167 | 126 | 0.16667 | Barisal (S) | 141 | 0.041667 | 134 | 0.29167
Dhamrai | 136 | 1904-01-02 | 129 | 0.5 | Patuakhali | 138 | 0.625 | 133 | 0.33333
Valuka | 130 | 0.041667 | 114 | 0.33333 | Bhandaria | 135 | 0.041667 | 130 | 0.29167
Tangail | 134 | 0.20833 | 125 | 0.41667 | Ishurdi | 138 | 0.125 | 130 | 0.33333
Mymensing | 130 | 1 :00 | 113 | 0.29167 | Ruppur Paromanobik | 137 | 0.20833 | 132 | 0.29167
Kishorganj | 132 | 0.041667 | 123 | 0.29167 | Natore | 134 | 0.041667 | 125 | 0.33333
Netrokona | 128 | 0.041667 | 111 | 0.29167 | Bogra | 136 | 0.125 | 125 | 0.29167
Jamalpur | 135 | 0.041667 | 118 | 0.16667 | Noagaon | 132 | 0.16667 | 117 | 0.33333
Sherpur | 136 | 0.041667 | 110 | 0.29167 | Rajshahi | 131 | 0.75 | 125 | 0.29167
Srimongal | 140 | 0.70833 | 137 | 0.77083 | Rajshahi New | 131 | 0.8125 | 119 | 0.33333
Shahjibazar | 138 | 1904-01-02 | 134 | 0.29167 | C.Nawabganj | 130 | 0.75 | 118 | 0.29167
Fenchuganj | 139 | 0.041667 | 137 | 11:00 | Amnura | 132 | 0.79167 | 114 | 0.29167
Khulawara | 139 | 0.20833 | 136 | 0.75 | Pabna | 137 | 0.16667 | 131 | 0.375
Sylhet | 137 | 0.041667 | 134 | 0.79167 | Shahjadpur | 140 | 0.58333 | 135 | 0.45833
Chatak | 137 | 0.083333 | 132 | 0.77083 | Serajganj | 137 | 0.16667 | 130 | 0.33333
Sunamganj | 137 | 0.083333 | 132 | 0.77083 | Niyamatpur | 130 | 0.083333 | 116 | 0.33333
Biani Bazar | 138 | 0.041667 | 133 | 0.83333 | Joypurhat | 133 | 0.083333 | 117 | 0.33333
Comilla(s) | 135 | 0.20833 | 126 | 0.375 | Sherpur(Bogura) | 137 | 0.125 | 129 | 0.29167
Comilla(n) | 143 | 20:00 | 138 | 0.5 | Mohastangor | 134 | 0.083333 | 124 | 0.33333
Chandpur | 138 | 0.29167 | 137 | 0.95833 | Rangpur | 131 | 0.16667 | 120 | 0.33333
Feni | 136 | 0.95833 | 134 | 0.54167 | Lalmonirhat | 125 | 0.083333 | 115 | 0.33333
Chowmuhani | 134 | 0.29167 | 132 | 0.66667 | Saidpur | 131 | 0.083333 | 121 | 0.33333
Ashuganj | 139 | 0.041667 | 135 | 0.041667 | Purbasadipur | 128 | 0.16667 | 115 | 0.33333
Daudkandi | 138 | 0.8125 | 133 | 0.45833 | Thakurgaon | 128 | 0.20833 | 114 | 0.77083
B.Baria | 136 | 1904-01-02 | 132 | 0.29167 | Palashbari | 127 | 0.125 | 116 | 0.33333
Ramganj | 133 | 0.58333 | 129 | 0.875 | Barapukuria | 133 | 0.125 | 128 | 0.33333
Chaddagram | 139 | 0.125 | 135 | 0.41667 | Panchagar | 124 | 0.125 | 112 | 0.33333
PHP | 134 | 0.91667 | 132 | 0.41667 | Joldhaka | 130 | 0.083333 | 117 | 0.33333
Madanhat | 135 | 0.041667 | 132 | 0.29167 | Kurigram | 131 | 0.16667 | 117 | 0.33333
Hathazari | 136 | 0.875 | 132 | 0.5

## L-Curve
Date | 2020-02-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 198 | 4857 | 1961 | 6818 |  |  |  | QF-LDC-12
0:30 | 147.5 | 4624 | 1936 | 6560 | Date: | 2020-02-04
1:00 | 97 | 4391 | 1911 | 6302
1:30 | 84 | 4201.5 | 1879 | 6080.5
2:00 | 71 | 4012 | 1847 | 5859
2:30 | 74.5 | 4002.5 | 1798.5 | 5801 | [5 empty] | Gen. at Eve. Peak | 9126 | 9126 MW (19:00 )
3:00 | 78 | 3993 | 1750 | 5743 | [6 empty] | 19:00
3:30 | 82.5 | 3912.5 | 1727.5 | 5640 | [5 empty] | Gen. at Day Peak | 7643.3 | 7643.3 MW (12:00 )
4:00 | 87 | 3832 | 1705 | 5537 | [6 empty] | 12:00
4:30 | 88.5 | 3827.5 | 1690 | 5517.5 | [5 empty] | Highest Generation | 9126
5:00 | 90 | 3823 | 1675 | 5498 | [6 empty] | 19:00
5:30 | 84.5 | 3931.5 | 1728 | 5659.5
6:00 | 79 | 4040 | 1781 | 5821
6:30 | 62 | 4152.65 | 2002.05 | 6154.7
7:00 | 45 | 4265.3 | 2223.1 | 6488.4
7:30 | 52.5 | 4486.95 | 2282.45 | 6769.4
8:00 | 60 | 4708.6 | 2341.8 | 7050.4
8:30 | 33 | 4834.85 | 2368 | 7202.85
9:00 | 6 | 4961.1 | 2394.2 | 7355.3
9:30 | 25 | 5027.95 | 2363.5 | 7391.45
10:00 | 44 | 5094.8 | 2332.8 | 7427.6
10:30 | 57.5 | 5149.9 | 2262.05 | 7411.95
11:00 | 71 | 5205 | 2191.3 | 7396.3
11:30 | 126 | 5336.25 | 2183.55 | 7519.8
12:00 | 181 | 5467.5 | 2175.8 | 7643.3
12:30 | 218 | 5502.95 | 2177.75 | 7680.7
13:00 | 255 | 5538.4 | 2179.7 | 7718.1
13:30 | 185.5 | 5338.795 | 2128.05 | 7466.845
14:00 | 116 | 5139.19 | 2076.4 | 7215.59
14:30 | 69 | 5120.405 | 2016.3 | 7136.705
15:00 | 22 | 5101.62 | 1956.2 | 7057.82
15:30 | 19 | 5007.075 | 1953.3 | 6960.375
16:00 | 16 | 4912.53 | 1950.4 | 6862.93
16:30 | 25 | 4942.74 | 1958.7 | 6901.44
17:00 | 34 | 4972.95 | 1967 | 6939.95
17:30 | 106.5 | 5330.475 | 2211.5 | 7541.975
18:00 | 179 | 5688 | 2456 | 8144
18:30 | 302 | 6051.5 | 2583.5 | 8635
19:00 | 425 | 6415 | 2711 | 9126
19:30 | 420 | 6331 | 2696 | 9027
20:00 | 450 | 6281 | 2623 | 8904 |  |  |  | Executive Engineer
20:30 | 427 | 6252 | 2567.5 | 8819.5 |  |  |  | Network Operation Division
21:00 | 404 | 6223 | 2512 | 8735
21:30 | 343 | 5981.5 | 2423.5 | 8405
22:00 | 282 | 5740 | 2335 | 8075 |  |  |  |  | Page 6 of 7
22:30 | 216 | 5503.5 | 2274 | 7777.5
23:00 | 150 | 5267 | 2213 | 7480
23:30 | 174 | 5062 | 2087 | 7149
24:00 | 198 | 4857 | 1961 | 6818
9126 MW (19:00 )
7643.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-04 |  | Energy | 174113282
[10 empty] | 2020-02-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3926 | 295 | 1417 | 978 | 401 | 70 | 0 | 0 | 82
0:30 | 3993.5 | 215.5 | 1342.5 | 626.5 | 401.5 | 75 | 0 | 0 | 81 | Date: | 2020-02-04
1:00 | 4061 | 136 | 1268 | 275 | 402 | 80 | 0 | 0 | 80
1:30 | 3888.5 | 136 | 1274 | 221.5 | 401.5 | 80 | 0 | 0 | 79 | [7 empty] | Total Energy | 174.1133 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3716 | 136 | 1280 | 168 | 401 | 80 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3712 | 136 | 1247 | 148 | 401 | 80 | 0 | 0 | 77 | [7 empty] | Energy Requirement | 174.1133
3:00 | 3708 | 136 | 1214 | 128 | 401 | 80 | 0 | 0 | 76
3:30 | 3627 | 136 | 1196.5 | 124 | 400.5 | 80 | 0 | 0 | 76 | [6 empty] | Shortage
4:00 | 3546 | 136 | 1179 | 120 | 400 | 80 | 0 | 0 | 76
4:30 | 3532 | 135.5 | 1176 | 120 | 399 | 80 | 0 | 0 | 75
5:00 | 3518 | 135 | 1173 | 120 | 398 | 80 | 0 | 0 | 74
5:30 | 3654 | 135.5 | 1182 | 135 | 398 | 80 | 0 | 0 | 75
6:00 | 3790 | 136 | 1191 | 150 | 398 | 80 | 0 | 0 | 76
6:30 | 3976.5 | 262.5 | 1198.5 | 162 | 398.5 | 80 | 0 | 0 | 76 |  |  |  |  | Coal
7:00 | 4163 | 389 | 1206 | 174 | 399 | 80 | 0 | 0 | 76
7:30 | 4203.5 | 389.5 | 1314 | 300 | 399.5 | 80 | 0 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 4244 | 390 | 1422 | 426 | 400 | 80 | 0 | 0 | 80
8:30 | 4202.5 | 390 | 1414 | 610.5 | 400.5 | 80 | 10 | 0 | 82.5
9:00 | 4161 | 390 | 1406 | 795 | 401 | 80 | 20 | 0 | 85
9:30 | 4108.5 | 390 | 1419.5 | 862.5 | 400.5 | 75 | 26 | 0 | 87.5
10:00 | 4056 | 390 | 1433 | 930 | 400 | 70 | 32 | 0 | 90
10:30 | 4020.5 | 390 | 1421.5 | 963 | 402 | 70 | 24 | 0 | 92.5
11:00 | 3985 | 390 | 1410 | 996 | 404 | 70 | 16 | 0 | 95
11:30 | 3995.5 | 390 | 1431 | 1086.5 | 402.5 | 70 | 16 | 0 | 97.5
12:00 | 4006 | 390 | 1452 | 1177 | 401 | 70 | 16 | 0 | 100
12:30 | 3949 | 390 | 1428 | 1287 | 401.5 | 70 | 24 | 0 | 100
13:00 | 3892 | 390 | 1404 | 1397 | 402 | 70 | 32 | 0 | 100
13:30 | 3892 | 390 | 1404 | 1397 | 402 | 70 | 32 | 0 | 100
14:00 | 3892 | 390 | 1404 | 1397 | 402 | 70 | 32 | 0 | 100
14:30 | 3772.5 | 389 | 1264.5 | 1342.5 | 401 | 70 | 24 | 0 | 98.5
15:00 | 3653 | 388 | 1125 | 1288 | 400 | 70 | 16 | 0 | 97
15:30 | 3677 | 388 | 1159 | 1140.5 | 400.5 | 70 | 16 | 0 | 93
16:00 | 3701 | 388 | 1193 | 993 | 401 | 70 | 16 | 0 | 89
16:30 | 3692 | 387 | 1231.5 | 1003.5 | 401.5 | 70 | 16 | 0 | 92.5
17:00 | 3683 | 386 | 1270 | 1014 | 402 | 70 | 16 | 0 | 96
17:30 | 3794.5 | 470.5 | 1268.5 | 1387.5 | 401 | 70.5 | 44 | 0 | 104
18:00 | 3906 | 555 | 1267 | 1761 | 400 | 71 | 72 | 0 | 112
18:30 | 3986.5 | 555.5 | 1296.5 | 2115 | 401 | 71 | 99.5 | 0 | 110
19:00 | 4067 | 556 | 1326 | 2469 | 402 | 71 | 127 | 0 | 108
19:30 | 4070 | 556 | 1320 | 2373 | 402 | 71 | 127 | 0 | 108
20:00 | 4139 | 555 | 1313 | 2227 | 402 | 71 | 85 | 0 | 112
20:30 | 4172.5 | 555.5 | 1327.5 | 2126 | 402 | 70.5 | 55.5 | 0 | 110
21:00 | 4206 | 556 | 1342 | 2025 | 402 | 70 | 26 | 0 | 108
21:30 | 4175.5 | 558.5 | 1349.5 | 1733.5 | 402 | 70 | 13 | 0 | 103
22:00 | 4145 | 561 | 1357 | 1442 | 402 | 70 | 0 | 0 | 98
22:30 | 4088.5 | 549.5 | 1365 | 1210 | 400.5 | 70 | 0 | 0 | 94
23:00 | 4032 | 538 | 1373 | 978 | 399 | 70 | 0 | 0 | 90
23:30 | 3979 | 416.5 | 1395 | 978 | 400 | 70 | 0 | 0 | 86 | Max Temp. in Dhaka |  | 25.7° C
24:00 | 3926 | 295 | 1417 | 978 | 401 | 70 | 0 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2020-02-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 |  | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 607440
2 | Karnaphuli Hydro PP Unit-4 & 5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1068000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.1 | 6.2 | 12.2 | 17.4 | 19.5 | 19.6 | 19.7 | 17.39 | 13.62 | 8.13 | 2.41 | [9 empty] | 137298
6 | Sikalbaha 225MW CCPP (Gas) | 216 | 201 | 206 | 202 | 201 | 215 | 215 | 214 | 202 | 201 | 202 | 202 | 202 | 202 | 203 | 213 | 216 | 205 |  | 203 | 202 | 202 | 210 | 215 | 202 | 202 | 4888927
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 145 | 145 | 145 | 145 | 145 | 151 | 151 | 140 | 139 | 139 | 139 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 125 | 124 | 124 | 134 | 124 | 3084664
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 1 | 20 |  | 31 | 34 | 34 | 34 | 17 |  |  | 152218
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 60 | 67 | 67 | 67 | 67 | 67 | 100 | 100 | 92 | 32 | 37 | 62 | 34 | 32 | 32 | 41 | 67 | 67 |  | 65 | 63 | 65 | 67 | 42 | 42 | 37 | 1573000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 15 |  | 75 | 30 | 0 |  |  |  |  | 150545
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1640000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 201 | 200 | 200 | 130 | 130 | 130 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 101 | 100 | 100 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3789000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 360 | 300 | 300 | 300 | 300 | 330 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 385 | 380 | 380 | 320 |  | 350 | 350 | 350 | 380 | 380 | 380 | 380 | 8430873
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 80 | 80 | 80 | 80 | 84 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404320
32 | Ashuganj 50 MW PP | 43 | 43 | 40 | 40 | 40 | 36 | 43 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 20 | 20 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 851832
33 | Ashuganj 225 MW CCPP | 0 |  |  | 0 | 27 | 49 | 61 | 63 | 136 | 211 | 190 | 185 | 183 | 165 | 166 | 186 | 174 | 202 |  | 194 | 228 | 228 | 228 | 196 | 189 | 180 | 3198000
34 | Ashuganj 450 MW CCPP(South) | 305 | 275 | 300 | 275 | 270 | 345 | 345 | 330 | 310 | 310 | 310 | 305 | 260 | 260 | 260 | 290 | 270 | 290 |  | 295 | 295 | 295 | 310 | 320 | 275 | 270 | 7303000
| Ashuganj 450 MW CCPP(North) | 190 | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 17 | 17 | 24 | 75 | 95 | 118 | 135 | 240 |  | 310 | 345 | 360 | 360 | 340 | 330 | 285 | 3350900
35 | Ashuganj 55 MW PP (Precision) | 5 | 52 | 56 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 646080
36 | Chandpur 150 MW CCPP | 89 | 88 | 89 | 89 | 89 | 90 | 89 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 89 | 50 | 0 | 2022130
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 352 | 362 | 353 | 339 | 356 | 380 | 375 | 364 | 335 | 338 | 342 | 347 | 338 | 275 | 315 | 358 | 351 |  | 365 | 342 | 337 | 350 | 361 | 343 | 359 | 8464390
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5186750
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 130 | 148 | 149 | 151 | 151 | 162 | 163 | 151 | 130 | 131 | 129 | 127 | 124 | 105 | 105 | 105 | 104 | 126 |  | 126 | 108 | 107 | 101 | 103 | 103 | 104 | 2973960
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 |  | 59 | 60 | 60 | 59 | 60 | 60 | 60 | 1411000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1024440
46 | Shajibazar 330 MW CCPP | 148 | 166 | 149 | 162 | 150 | 159 | 163 | 156 | 148 | 148 | 152 | 153 | 148 | 149 | 150 | 160 | 150 | 163 |  | 148 | 145 | 150 | 157 | 153 | 162 | 148 | 3563000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 68 | 69 | 67 | 65 | 65 | 64 | 45 | 45 | 45 | 45 | 67 |  | 67 | 68 | 67 | 67 | 67 | 67 | 67 | 1353312
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 61 | 61 | 76 | 56 | 56 | 59 | 20 | 50 | 59 | 59 | 59 |  | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 998400
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 153 | 152 | 153 | 153 | 153 | 153 | 155 | 153 | 132 | 130 | 147 | 146 | 152 | 152 | 150 | 66 | 0 | [9 empty] | 2449550
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 159840
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 155184
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 48 | 45 | 45 | 47 | 53 | 53 | 11 | 51 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 872400
56 | Shahjahanulla 25 MW PP | 16 | [7 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 375622
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 270 | 320 | 310 | 305 | 315 | 325 | 325 | 310 | 300 | 300 | 305 | 295 | 285 | 295 | 285 | 325 | 310 |  | 315 | 300 | 290 | 310 | 320 | 300 | 305 | 7604000
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 442704
61 | Narshingdi 22 MW PP (Doreen) | 22 | [6 empty] | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 339264
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 397512
63 | Impoprt (Tripura) | 80 | 78 | 76 | 76 | 74 | 76 | 76 | 80 | 85 | 90 | 95 | 100 | 100 | 99 | 97 | 89 | 96 | 112 |  | 108 | 108 | 112 | 108 | 98 | 90 | 82 | 2169600
64 | Malancha, Ctg. EPZ (United) | 33 | 32 | 36 | 36 | 42 | 42 | 39 | 12 | 4 | 2 | 2 | 5 | 10 | 7 | 4 | 4 | 6 | 12 |  | 25 | 28 | 30 | 36 | 41 | 42 | 42 | 548640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | [7 empty] | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 339084
66 | Feni 11 MW PP (Doreen) | [7 empty] | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 158940
67 | Jangalia 33MW PP (Summit) | 20 | [6 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 580900
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476380
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 |  | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 18 | 18 | 33 | 34 | 34 | 34 | 27 | 26 | 32 | 31 | 14 |  | 24 | 31 | 32 | 32 | 32 | 32 | 32 | 687420
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 20 | 20 | 20 | 661600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 721800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 5 | 55 | 88 | 93 | 100 | 100 | 100 | 100 | 72 | 60 | 75 |  | 100 | 100 | 100 | 100 | 100 | 90 | 50 | 1435200
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [8 empty] | 20 | 32 | 16 | 16 | 32 | 16 | 16 | 16 | 16 | 16 | [8 empty] | 224640
80 | Jamalpur 95 MW PP(Powerpac) | 90 | 48 | 8 |  |  |  | 6 | 73 | 95 | 92 | 92 | 92 | 92 | 92 | 95 | 95 | 92 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1798080
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.2 | 0.9 | 2.8 | 3.9 | 4.6 | 4.8 | 4.7 | 4.1 | 2.9 | 1.7 | 0.34 | [9 empty] | 31200
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [16 empty] | 1 | 22 |  | 60 | 80 | 85 | 82 | 0 |  |  | 286536
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 0 | 22 |  | 83 | 30 | [5 empty] | 153931
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 160 | 160 | 210 | 300 | 260 | 260 | 245 | 250 | 260 |  | 270 | 255 | 250 | 253 | 254 | 245 | 232 | 4771287
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 17 | 40 | 40 | 55 | 53 | 93 | 100 | 65 | 55 | 75 |  | 100 | 100 | 100 | 100 | 100 | 55 | 50 | 1158720
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 47 | 47 | 5 | 5 | 5 | 5 | 10 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 41 | 44 | 44 | 50 | 50 | 50 | 50 | 961056
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 992688
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 7 | 24 | 24 | 48 | 72 | 102 | 102 | 48 | 48 | 72 |  | 102 | 102 | 102 | 102 | 102 | 48 | 7 | 1100304
95 | Patenga 50MW PP (Baraka) | [12 empty] | 7 | 19 | 19 | 19 | 19 | 26 |  | 50 | 50 | 50 | 50 | 45 |  |  | 324960
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 32 |  | 85 | 87 | 89 | 65 | 18 | 11 | 12 | 338880
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 12 |  | 47 | 24 | 24 | 24 |  |  |  | 146688
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 1 | 18 |  | 43 | 30 | 30 | 30 | 0 |  |  | 150818
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 55 |  | 55 | 55 | 55 | 55 | 18 |  |  | 225286
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 163 | 100 | 100 | 100 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 3234845
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.5 | 0.1 | 1.5 | 1.9 | 2.1 | 2 | 1.7 | 1.1 | 0.7 | 0.2 | [9 empty] | 12350
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 868320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 3 | 7 | 7 | 7 | 7 | 7 | 7 |  |  |  | 0 | 21 |  | 40 | 40 | 40 |  |  |  |  | 211200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 0 | 12 | 31 | 71 | 103 | 100 | 120 | 135 | 85 | 85 | 85 | 95 |  | 142 | 149 | 149 | 111 | 85 | 35 | 0 | 1464480
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 20 | 80 |  | 90 | 90 | 90 | 90 | 10 |  |  | 358080
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 3 | 40 |  | 130 | 150 | 100 | 50 |  |  |  | 429890
118 | Bibiyana-III 400 MW CCPP | 145 | 146 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 144 | 145 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 144 | 145 | 3481000
| Jamalpur 115 MW PP (United) | 32 | [5 empty] | 3 | 55 | 92 | 105 | 105 | 105 | 115 | 55 | 55 | 55 | 55 | 80 |  | 99 | 115 | 115 | 115 | 90 | 50 | 24 | 1585200
| Anwara 300 MW PP (United) | 33 | [6 empty] | 16 | 100 | 100 | 121 | 209 | 214 | 215 | 216 | 125 | 126 | 213 |  | 217 | 217 | 217 | 217 | 217 | 162 | 52 | 2797636
120 | Eastern Zone Total | 4391 | 4012 | 3993 | 3832 | 3823 | 4040 | 4265.3 | 4708.6 | 4961.1 | 5094.8 | 5205 | 5467.5 | 5538.4 | 5139.19 | 5101.62 | 4912.53 | 4972.95 | 5688 |  | 6415 | 6331 | 6281 | 6223 | 5740 | 5267 | 4857 | 121557921
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 32 | 66 | 49 | 49 | 49 | 115 | 83 | 83 | 49 | 49 | 115 |  | 115 | 115 | 115 | 115 | 105 | 64 | 0 | 1221120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 27 |  | 65 | 80 | 80 | 80 | 0 |  |  | 257184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 80 | 0 |  |  |  |  | 23 | 70 | 73 | 90 | 96 | 96 | 57 | 52 | 53 | 54 | 54 |  | 97 | 98 | 98 | 97 | 98 | 96 | 96 | 1476383
| Bhola 225 MW CCPP | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 188 | 189 | 189 | 177 | 190 | 189 | 189 | 189 | 189 |  | 189 | 186 | 188 | 188 | 188 | 189 | 188 | 4705873
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 14 | 14 | 13 | 15 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 12 | 18 |  | 20 | 20 | 20 | 20 | 20 | 19 | 17 | 343700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 6 |  | 0 | [6 empty] | 4480
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [16 empty] | 0 | 15 |  | 15 | [6 empty] | 33840
146 | Bheramara HVDC | 136 | 136 | 136 | 136 | 135 | 136 | 389 | 390 | 390 | 390 | 390 | 390 | 390 | 388 | 388 | 388 | 386 | 555 |  | 556 | 556 | 555 | 556 | 561 | 538 | 295 | 8608000
147 | Bheramara 410 MW CCPP | 300 | 250 | 250 | 250 | 230 | 300 | 375 | 365 | 310 | 285 | 260 | 245 | 240 | 235 | 225 | 225 | 225 | 250 |  | 265 | 265 | 270 | 270 | 275 | 275 | 290 | 6814944
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 122 | 121 | 121 | 120 | 118 | 118 | 119 | 120 | 122 | 120 | 124 | 121 | 122 | 122 | 120 | 121 | 122 | 120 |  | 122 | 122 | 122 | 122 | 122 | 119 | 121 | 2880436
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 279 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6748600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 0 |  | 25 | 25 | 25 |  |  |  |  | 52622
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 145 | 130 | 130 | 130 | 145 | 190 | 220 | 214 | 190 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3866227
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 175 | 175 | 130 | 130 | 142 | 192 | 206 | 192 | 168 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3802255
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 386 | 431 | 430 | 431 | 425 | 431 | 435 | 432 | 387 | 402 | 346 | 342 | 297 | 288 | 189 | 257 | 256 | 256 |  | 255 | 257 | 258 | 256 | 256 | 266 | 307 | 8251145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | [6 empty] | 3 | 11 | 18 | 22 | 22 | 21 | 21 | 20 | 18 | 22 | 22 |  | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 309600
163 | Bogura 20 MW PP (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 114480
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249480
165 | Amnura 50 MW PP(Sinha) | 0 | [5 empty] | 12 | 24 | 40 | 32 | 40 | 40 | 40 | 12 | 12 | 12 | 12 | 40 |  | 40 | 40 | 40 | 24 | 24 | 0 |  | 449140
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 50 |  | 102 | 102 | 60 | 26 | 0 |  |  | 244660
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 4 |  | 46 | 30 | [5 empty] | 93120
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 17 | 82 | 109 | 109 | 109 | 109 | 109 | 108 | 70 | 70 | 109 |  | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 1626144
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 14 | 70 |  | 112 | 113 | 105 | 71 | 0 |  |  | 379200
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.8 | 2.2 | 3.8 | 4.3 | 4.8 | 4.7 | 4.4 | 3.2 | 1.4 | [10 empty] | 22728
178
178