## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-06 | Thursday
|  | Date (day): | 2020-02-06 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11679.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14545 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-05 | 2020-02-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 150 | 150 | 150
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 320 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 337 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint |  | 2020-10-02
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-2 Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 29 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 224 | 285 | 280 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 60 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 227 | 200 | 240 | 240 |  | 118 | ST Under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 53 | 56 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 91 | 149 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 8 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1874 | 2530 | 3329 | 4006 | 401 | 1278
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.46 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 16 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 72 | 72 | 72 | 158 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 202 | 210 | 220
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 104 | 104 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 34 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 93 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 178 | 215 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 728.06 | 1025 | 1487 | 1642 | 398 | 108
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 175 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 280 | 320 | 360
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 295 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 42 | 42 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 24 | 24 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 50 | 0 | 0 |  | 163 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 112 | 100 | 108
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1258 | 1380 | 1557 | 2269 | 454 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 104 | 110 | 120 | 82 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 95 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 110 | 115 | 80 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 326 | 381 | 408.6 | 552 | 82 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 55 | 55 | 55
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 150 | 160 | 160 |  | 170 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 62 | 62 | 62 |  | 24 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 150 | 150 |  |  | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 145 | 145 | 230 | 230 |  | 170 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1082 | 1097 | 1427 | 1427 | 0 | 384
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 396 | 565 | 400 | 745
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 5 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 355 | 350 | 350 | 60 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 712 | 1040 | 1108 | 1924 | 60 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 180 | 194 | 194
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 297 | 377 | 379 | 449 | 0 | 13
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 130 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 0 | 225 | 225 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 276 | 326 | 410 | 410 | ` |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 68 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 722 | 756 | 1458 | 1724 | 391 | 15
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 121 | 120 | 120 | 120
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 279 | 280 | 285 | 285
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 405.2 | 513 | 526 | 552 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7404.26 | 9099 | 11679.6 | 14545 | 1786 | 2053
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7012.849 | 8618 | 11062.1819 | 13776.1084
A. |  | 2020-02-05 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9099 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5624 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9099 | MW
3 | Day peak Generation : |  |  | 7404.26 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8618 | MW
4 | Evening peak Generation : |  |  | 9099 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 177.0536 | MKWHr | By Solar | 0.16887 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.0826 | MKWHr |  | By Oil: | 23.8477 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 9.6132 | MKWHr |  | By Hydro: | 1.6274 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1786 | MW | Dhaka | 3018 | 3018 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2053 | MW | Chittagong | 880 | 880 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3839 | MW | Khulna | 1062 | 1062 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1082.76 | MMCFD |  |  | Rajshahi | 953 | 953 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 123658121.36 | ii) Oil : | Taka | 164528476.92 | Comilla | 752 | 752 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 45770778.98 | Total | Taka | 333957377.26 | Mymensingh | 732 | 732 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.9525 | MKWHr. | Sylhet | 326 | 326 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -390 | MW (E to W) at | 19:00 | hrs | Barisal | 222 | 222 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -393 | MW at | 18:30 | hrs | Rangpur | 673 | 673 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26° C |  |  | Total | 8618 | 8618 |  | 0
B. |  | 2020-02-06 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 26.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14545 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7900 | MW
4 | Reserve(Generation end) |  |  |  | 5245 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 180.9648 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5573 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.7622 | MKWHr. | ii) HVDC Flow at Peak Time |  | 565 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9517 | MKWHr. | iii) Maximum HVDC Flow : |  | 737 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.59 |  | (b) Today: | 93.47 |  | (c) Rule Curve: |  | 96.3
.

## YesterdayGen
2020-02-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 354 | 0 |  | 0 | 225 | 260 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 20 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 19 | 42 | 0 | 0 | 100 | 290 | 275 | 181 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 76 | 104 | 72 | 17 | 0 | 60 | 44 | 53 | 50 | 163 | 152 | 67 | 59 | 0 | 0 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 8 | 122 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4610 | 1730 | 6340 | 3901 | 136 | 1411 | 344 | 402 | 70 | 0 | 76 | 0 | 0 | 93.64
2:00 | 72 | 0 | 150 | 0 | 380 | 0 | 0 | 339 | 0 |  | 0 | 225 | 257 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 100 | 275 | 270 | 186 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 17 | 74 | 104 | 24 | 17 | 0 | 60 | 44 | 5 | 5 | 163 | 153 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 63 | 0 | 130 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4279 | 1726 | 6005 | 3792 | 136 | 1251 | 281 | 401 | 70 | 0 | 74 | 0 | 0 | 93.63
3:00 | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 338 | 0 |  | 0 | 225 | 260 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 184 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 0 | 80 | 290 | 280 | 176 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 70 | 104 | 8 | 17 | 0 | 60 | 44 | 5 | 5 | 130 | 152 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 33 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4140 | 1647 | 5787 | 3747 | 137 | 1094 | 268 | 401 | 70 | 0 | 70 | 0 | 0 | 93.62
4:00 | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 342 | 0 |  | 0 | 225 | 255 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 0 | 80 | 275 | 270 | 164 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 104 | 8 | 17 | 0 | 60 | 44 | 5 | 5 | 130 | 153 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4038 | 1597 | 5635 | 3642 | 137 | 1054 | 263 | 401 | 70 | 0 | 68 | 0 | 0 | 93.61
5:00 | 72 | 0 | 101 | 0 | 300 | 0 | 0 | 300 | 0 |  | 0 | 225 | 262 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 0 | 80 | 290 | 285 | 177 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 72 | 104 | 8 | 17 | 0 | 60 | 44 | 5 | 5 | 100 | 154 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4028 | 1596 | 5624 | 3641 | 136 | 1034 | 270 | 401 | 70 | 0 | 72 | 0 | 0 | 93.6
6:00 | 72 | 0 | 0 | 0 | 378 | 0 | 0 | 329 | 0 |  | 0 | 225 | 263 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 0 | 80 | 340 | 315 | 178 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 76 | 104 | 11 | 17 | 0 | 60 | 44 | 5 | 5 | 100 | 154 | 56 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 158 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4215 | 1817 | 6032 | 3938 | 136 | 1137 | 274 | 401 | 70 | 0 | 76 | 0 | 0 | 93.59
7:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 366 | 0 |  | 0 | 225 | 278 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 18 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 214 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 80 | 360 | 350 | 202 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 78 | 105 | 60 | 17 | 0 | 60 | 44 | 5 | 5 | 100 | 162 | 56 | 5 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 144 | 2 | 0 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 |  | 397 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 177 | 0 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4448.11 | 2160.1 | 6608.21 | 4131 | 397 | 1191 | 340 | 400 | 70 | 0 | 78 | 1.21 | 0 | 93.58
8:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 377 | 0 |  | 0 | 225 | 230 | 3 | 0 | 0 | 238 | 0 | 0 | 0 | 20 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 28 | 0 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 0 | 0 | 100 | 320 | 315 | 180 | 55 | 0 | 32 | 5 | 0 | 32 | 0 | 0 | 0 | 22 | 11 | 25 | 17 | 78 | 105 | 95 | 17 | 0.4 | 60 | 44 | 51 | 38 | 130 | 147 | 69 | 59 | 0 | 0 | 0 | 0 | 10 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5.92 | 0 | 0 | 0 | 145 | 70 | 0 | 0 | 1.4 | 66 | 0 | 0 | 0 | 0 |  | 396 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 5 | 0 | 120 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 82 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 17 | 0 |  | 4912.72 | 2205.8 | 7118.52 | 4083 | 396 | 1445 | 638 | 400 | 70 | 0 | 78 | 8.52 | 0 | 93.58
9:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 338 | 0 |  | 0 | 225 | 230 | 28 | 0 | 0 | 233 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 0 | 25 | 22 | 25 | 33 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 202 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 100 | 320 | 295 | 181 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 66 | 105 | 95 | 17 | 0 | 58 | 44 | 51 | 50 | 130 | 149 | 67 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 10.93 | 0 | 0 | 0 | 145 | 101 | 0 | 0 | 2.8 | 100 | 0 | 0 | 0 | 0 |  | 396 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 96 | 0 | 160 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 109 | 0 |  | 5066.73 | 2290.4 | 7357.13 | 4056 | 396 | 1389 | 962 | 402 | 70 | 0 | 66 | 16.13 | 0 | 93.57
10:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 336 | 0 |  | 0 | 225 | 220 | 45 | 0 | 0 | 231 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 0 | 25 | 22 | 30 | 25 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 232 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 320 | 275 | 166 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 71 | 103 | 95 | 17 | 1.5 | 60 | 44 | 51 | 50 | 130 | 151 | 65 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 15.6 | 0 | 0 | 0 | 145 | 102 | 0 | 0 | 3.7 | 105 | 0 | 0 | 0 | 0 |  | 396 | 0 | 280 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 122 | 0 | 279 | 0 | 0 | 140 | 0 | 0 | 0 | 96 | 0 | 156 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 109 | 0 |  | 5056.8 | 2229.7 | 7286.5 | 3968 | 396 | 1370 | 986 | 401 | 70 | 0 | 71 | 24.5 | 0 | 93.57
11:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 348 | 0 |  | 0 | 225 | 225 | 24 | 0 | 0 | 228 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 2 | 0 | 0 | 100 | 320 | 335 | 167 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 72 | 102 | 90 | 17 | 2.1 | 60 | 44 | 49 | 50 | 130 | 148 | 64 | 0 | 0 | 0 | 0 | 0 | 9 | 325 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17.08 | 0 | 0 | 0 | 145 | 109 | 0 | 0 | 4.4 | 160 | 0 | 0 | 0 | 0 |  | 395 | 0 | 250 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 279 | 0 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 130 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 109 | 0 |  | 5138.58 | 2139.7 | 7278.28 | 3929 | 395 | 1353 | 1031 | 400 | 70 | 0 | 72 | 28.28 | 0 | 93.56
12:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 348 | 0 |  | 0 | 225 | 224 | 29 | 0 | 0 | 227 | 0 | 0 | 0 | 24 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 21 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 3 | 0 | 0 | 100 | 330 | 325 | 175 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 82 | 102 | 95 | 17 | 2 | 60 | 42 | 53 | 50 | 163 | 154 | 63 | 0 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18.46 | 0 | 0 | 0 | 145 | 110 | 8 | 0 | 4.6 | 178 | 0 | 0 | 0 | 0 |  | 396 | 0 | 250 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 279 | 0 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 130 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 109 | 0 |  | 5268.06 | 2136.2 | 7404.26 | 3962 | 396 | 1354 | 1110 | 400 | 70 | 0 | 82 | 30.26 | 0 | 93.56
13:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 357 | 0 |  | 0 | 225 | 220 | 70 | 0 | 0 | 227 | 0 | 0 | 0 | 70 | 60 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 21 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 10 | 0 | 0 | 100 | 320 | 315 | 165 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 82 | 102 | 89 | 17 | 1.8 | 60 | 42 | 53 | 50 | 163 | 148 | 63 | 0 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 15 | 0 | 0 | 0 | 145 | 115 | 34 | 0 | 4.2 | 215 | 0 | 0 | 0 | 0 |  | 396 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 130 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 109 | 0 |  | 5434 | 2145.2 | 7579.2 | 3933 | 396 | 1352 | 1319 | 401 | 70 | 0 | 82 | 26.2 | 0 | 93.55
14:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 338 | 0 |  | 0 | 225 | 220 | 55 | 0 | 0 | 180 | 0 | 0 | 0 | 85 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 21 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 2 | 0 | 0 | 100 | 325 | 275 | 174 | 55 | 0 | 39 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 82 | 101 | 95 | 17 | 0.7 | 60 | 42 | 53 | 50 | 100 | 157 | 63 | 0 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 6.7 | 0 | 0 | 0 | 145 | 115 | 17 | 0 | 3.6 | 123 | 0 | 0 | 0 | 0 |  | 396 | 0 | 245 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 100 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 70 | 0 |  | 5098 | 2032.1 | 7130.1 | 3824 | 396 | 1243 | 1099 | 401 | 70 | 0 | 82 | 15.1 | 0 | 93.55
15:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 353 | 0 |  | 0 | 225 | 230 | 50 | 0 | 0 | 180 | 0 | 0 | 0 | 70 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 21 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 2 | 0 | 0 | 100 | 320 | 275 | 171 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 84 | 101 | 95 | 17 | 0.8 | 60 | 54 | 53 | 50 | 100 | 153 | 63 | 0 | 0 | 0 | 0 | 0 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 8.6 | 0 | 0 | 0 | 145 | 80 | 35 | 0 | 2.7 | 123 | 0 | 0 | 0 | 0 |  | 396 | 0 | 240 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 118 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 70 | 0 |  | 5129.1 | 1938 | 7067.1 | 3736 | 396 | 1300 | 1068 | 398 | 70 | 0 | 84 | 15.1 | 0 | 93.54
16:00 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 339 | 0 |  | 0 | 225 | 235 | 24 | 0 | 0 | 180 | 0 | 0 | 0 | 63 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 23 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 2 | 0 | 0 | 100 | 310 | 270 | 165 | 55 | 50 | 39 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 79 | 101 | 86 | 17 | 0.4 | 60 | 55 | 53 | 50 | 100 | 147 | 64 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 6.8 | 0 | 0 | 0 | 145 | 80 | 35 | 0 | 1.4 | 123 | 0 | 0 | 0 | 0 |  | 396 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 70 | 0 |  | 5087.6 | 1925.3 | 7012.9 | 3768 | 396 | 1280 | 1010 | 400 | 70 | 0 | 79 | 9.9 | 0 | 93.54
17:00 | 72 | 0 | 100 | 0 | 380 | 0 | 0 | 338 | 0 |  | 0 | 225 | 245 | 22 | 0 | 0 | 180 | 0 | 0 | 0 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 22 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 1 | 19 | 19 | 9 | 0 | 0 | 100 | 280 | 270 | 165 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 82 | 102 | 95 | 17 | 0.2 | 60 | 55 | 53 | 50 | 100 | 146 | 64 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 3 | 0 | 149 | 1.8 | 10 | 0 | 2 | 145 | 80 | 35 | 2 | 0.3 | 88 | 0 | 0 | 0 | 0 |  | 396 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 117 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 0 | 32 | 0 | 0.4 | 70 | 0 |  | 5095.3 | 1989.4 | 7084.7 | 3819 | 396 | 1290 | 1028 | 397 | 70 | 0 | 82 | 2.7 | 0 | 93.53
18:00 | 72 | 0 | 100 | 0 | 320 | 0 | 0 | 338 | 0 |  | 0 | 225 | 220 | 36 | 17 | 12 | 180 | 0 | 0 | 0 | 50 | 50 | 0 | 12 | 0 | 0 | 9 | 53 | 55 | 0 | 22 | 25 | 6 | 25 | 25 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 22 | 22 | 19 | 15 | 0 | 0 | 100 | 280 | 270 | 164 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 102 | 89 | 17 | 0 | 60 | 55 | 53 | 50 | 100 | 148 | 67 | 50 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 10 | 0 | 0 | 22 | 0 | 151 | 0 | 48 | 0 | 35 | 145 | 95 | 35 | 22 | 0 | 213 | 0 | 0 | 0 | 0 |  | 514 | 0 | 340 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 53 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 282 | 0 | 0 | 35 | 0 | 98 | 0 | 0 | 109 | 0 |  | 5496 | 2474 | 7970 | 3777 | 514 | 1336 | 1704 | 401 | 71 | 53 | 114 | 0 | 0 | 93.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 150 | 0 | 320 | 0 | 0 | 337 | 0 |  | 0 | 225 | 285 | 100 | 60 | 55 | 200 | 0 | 0 | 0 | 100 | 102 | 0 | 50 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 32 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 93 | 50 | 19 | 26 | 0 | 0 | 100 | 280 | 295 | 184 | 55 | 50 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 104 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 150 | 67 | 62 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 50 | 0 | 149 | 0 | 90 | 0 | 100 | 145 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 565 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 5 | 0 | 180 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 0 |  | 6413 | 2686 | 9099 | 3996 | 565 | 1436 | 2445 | 400 | 72 | 73 | 112 | 0 | 0 | 93.52
19:30 | 72 | 0 | 150 | 0 | 320 | 0 | 0 | 350 | 0 |  | 0 | 225 | 275 | 100 | 70 | 55 | 200 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 98 | 50 | 19 | 28 | 0 | 0 | 100 | 315 | 315 | 197 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 103 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 154 | 67 | 62 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 149 | 0 | 90 | 0 | 100 | 145 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 556 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 0 |  | 6359 | 2684 | 9043 | 4048 | 556 | 1462 | 2328 | 400 | 71 | 68 | 110 | 0 | 0 | 0
20:00 | 72 | 0 | 150 | 0 | 320 | 0 | 0 | 340 | 0 |  | 0 | 225 | 275 | 100 | 90 | 55 | 200 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 29 | 25 | 25 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 98 | 50 | 19 | 28 | 0 | 0 | 100 | 295 | 295 | 184 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 104 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 148 | 67 | 62 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 149 | 0 | 90 | 0 | 100 | 145 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 566 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 19 | 80 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 0 | 110 | 0 | 0 | 109 | 0 |  | 6303 | 2696 | 8999 | 3982 | 566 | 1456 | 2345 | 401 | 71 | 68 | 110 | 0 | 0 | 93.52
21:00 | 72 | 0 | 151 | 0 | 350 | 0 | 0 | 338 | 0 |  | 0 | 225 | 255 | 100 | 15 | 30 | 203 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 98 | 50 | 19 | 35 | 0 | 0 | 100 | 295 | 290 | 185 | 55 | 0 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 104 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 151 | 67 | 62 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 144 | 0 | 90 | 0 | 50 | 144 | 115 | 0 | 34 | 0 | 217 | 0 | 0 | 0 | 0 |  | 566 | 0 | 385 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 109 | 0 |  | 6147 | 2637 | 8784 | 4024 | 566 | 1483 | 2113 | 401 | 71 | 18 | 108 | 0 | 0 | 93.51
22:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 337 | 0 |  | 0 | 225 | 250 | 75 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 100 | 295 | 295 | 185 | 55 | 40 | 41 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 104 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 150 | 62 | 62 | 0 | 44 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 144 | 80 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 737 | 0 | 390 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 116 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5521 | 2533 | 8054 | 4147 | 737 | 1477 | 1124 | 396 | 71 | 0 | 102 | 0 | 0 | 93.51
23:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 345 | 0 |  | 0 | 225 | 245 | 50 | 0 | 0 | 200 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 31 | 40 | 120 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 100 | 300 | 295 | 189 | 55 | 0 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 106 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 153 | 67 | 62 | 0 | 68 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 50 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 542 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 119 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 5192 | 2182 | 7374 | 4165 | 542 | 1468 | 639 | 399 | 71 | 0 | 90 | 0 | 0 | 93.5
24:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 347 | 0 |  | 0 | 225 | 260 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 30 | 40 | 120 | 0 | 0 | 201 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 100 | 295 | 295 | 180 | 55 | 0 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 84 | 108 | 50 | 17 | 0 | 60 | 55 | 53 | 50 | 100 | 147 | 69 | 62 | 0 | 70 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4938 | 1901 | 6839 | 4144 | 301 | 1418 | 421 | 401 | 70 | 0 | 84 | 0 | 0 | 93.5
KWH | 1648000 | 0 | 1758000 | 0 | 8560255 | 0 | 0 | 8356860 | 0 |  | 0 | 5125000 | 5948887 | 878400 | 260544 | 164918 | 4685729 | 0 | 40000 | 0 | 1099200 | 824688 | 0 | 81993 | 0 | 0 | 116688 | 814320 | 509915 | 0 | 298656 | 600000 | 621900 | 671500 | 710300 | 0 | 0 | 663360 | 964000 | 2700000 | 0 | 0 | 4863700 | 0 | 2721784 | 0 |  | 0 | 0 | 0 | 0 | 362880 | 324480 | 427920 | 523200 | 0 | 0 | 2304140 | 7711100 | 7185500 | 4387000 | 970181 | 132720 | 751536 | 421440 | 0 | 1043968 | 0 | 0 | 0 | 398340 | 201780 | 597400 | 492580 | 1951680 | 2432040 | 1841280 | 392868 | 0 | 1414000 | 1149000 | 974400 | 981288 | 3208500 | 3414000 | 1488864 | 563520 | 0 | 3714204 | 0 | 0 | 179280 | 7526300 | 376255 | 238512 | 0 | 75272 | 0 | 0 | 192000 | 0 | 1579680 | 108000 | 32448 | 0 | 306109 | 3486000 | 1712400 | 179520 | 150545 | 28560 | 2361055 | 0 | 0 | 0 | 0 |  | 8762182 | 0 | 7675776 | 0 | 891840 | 0 | 0 | 0 | 0 | 1536 | 0 | 4572095 | 348600 | 285696 | 0 | 0 | 0 | 0 | 0 | 177784 | 614240 | 0 | 0 | 0 | 0 | 378240 | 114912 | 245700 | 2830254 | 0 | 6782900 | 0 | 0 | 3525409 | 0 | 0 | 0 | 1827255 | 0 | 2141845 | 0 | 7803272 | 0 | 0 | 118080 | 0 | 432960 | 0 | 32313 | 1508352 | 0 |  | 125982342 | 51071241 | 177053583 | 99093268 | 8762182 | 31989356 | 23668390 | 9613154 | 1627360 | 179320 | 1951680 | 168873 | 0
Fuel Cost | 1845760 | 0 | 1881060 | 0 | 6334588.7 | 0 | 0 | 6016939.2 | 0 |  | 0 | 4100000 | 5353998.3 | 8959680 | 2821691.52 | 1692058.68 | 5810303.96 | 0 | 50000 | 0 | 12201120 | 8378830.08 | 0 | 859286.64 | 0 | 0 | 1092199.68 | 7809328.8 | 4864589.1 | 0 | 223992 | 450000 | 0 | 0 | 0 | 0 | 0 | 172473.6 | 250640 | 4131000 | 0 | 0 | 5106885 | 0 | 3456665.68 | 0 |  | 0 | 0 | 0 | 0 | 3450988.8 | 3037132.8 | 393686.4 | 1454496 | 0 | 0 | 2419347 | 5706214 | 6035820 | 4036040 | 950777.38 | 176517.6 | 616259.52 | 434083.2 | 0 | 1492874.24 | 0 | 0 | 0 | 406306.8 | 151335 | 1129086 | 369435 | 13466592 | 1994272.8 | 17510572.8 | 400725.36 | 0 | 1923040 | 1562640 | 1325184 | 1226610 | 3978540 | 3140880 | 2218407.36 | 991795.2 | 0 | 5645590.08 | 0 | 0 | 421308 | 5343673 | 282191.25 | 181269.12 | 0 | 788097.84 | 0 | 0 | 1847040 | 0 | 15938971.2 | 1246320 | 302415.36 | 0 | 2868241.33 | 3276840 | 15017748 | 1599523.2 | 1422650.25 | 0 | 21768927.1 | 0 | 0 | 0 | 0 |  | 23657891.4 | 0 | 5987105.28 | 0 | 8597337.6 | 0 | 0 | 0 | 0 | 20121.6 | 0 | 3657676 | 540330 | 3068375.04 | 0 | 0 | 0 | 0 | 0 | 1760061.6 | 6369668.8 | 0 | 0 | 0 | 0 | 416064 | 189604.8 | 185994.9 | 18028717.98 | 0 | 27742061 | 0 | 0 | 3102359.92 | 0 | 0 | 0 | 2905335.45 | 0 | 1884823.6 | 0 | 5696388.56 | 0 | 0 | 1083974.4 | 0 | 4043846.4 | 0 | 0 | 0 | 0 |  | 253813555.93 | 118937738.33 | 372751294.26 | 92191057.53 | 23657891.4 | 31467063.83 | 162748293.72 | 45770778.98 | 423113.6 | 1780183.2 | 13466592 | 1246320 | 0
Yesterday Day Peak | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 348 | 0 |  | 0 | 225 | 224 | 29 | 0 | 0 | 227 | 0 | 0 | 0 | 24 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 21 | 33 | 25 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 3 | 0 | 0 | 100 | 330 | 325 | 175 | 55 | 0 | 36 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 14 | 82 | 102 | 95 | 17 | 2 | 60 | 42 | 53 | 50 | 163 | 154 | 63 | 0 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 18.46 | 0 | 0 | 0 | 145 | 110 | 8 | 0 | 4.6 | 178 | 0 | 0 | 0 | 0 |  | 396 | 0 | 250 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 5 | 11 | 121 | 0 | 279 | 0 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 130 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 109 | 0 |  | 7404.26 | DayPeak
Yesterday Evening Peak | 72 | 0 | 150 | 0 | 320 | 0 | 0 | 337 | 0 | 0 | 0 | 225 | 285 | 100 | 60 | 55 | 200 | 0 | 0 | 0 | 100 | 102 | 0 | 50 | 0 | 0 | 47 | 53 | 55 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 32 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 50 | 19 | 26 | 0 | 0 | 100 | 280 | 295 | 184 | 55 | 50 | 42 | 24 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 104 | 95 | 17 | 0 | 60 | 55 | 53 | 50 | 130 | 150 | 67 | 62 | 0 | 0 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 50 | 0 | 149 | 0 | 90 | 0 | 100 | 145 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 565 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 5 | 0 | 180 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 120 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 0 |  | 9099 | EvPeak
Forecast for Evening | 72 | 0 | 150 | 0 | 365 | 0 | 0 | 412 | 0 | 0 | 0 | 225 | 305 | 100 | 100 | 55 | 240 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 32 | 40 | 120 | 0 | 25 | 220 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 0 | 100 | 360 | 360 | 225 | 55 | 0 | 42 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 108 | 120 | 95 | 22 | 0 | 60 | 55 | 51 | 44 | 163 | 160 | 66 | 62 | 0 | 150 | 0 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 230 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 745 | 40 | 350 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 194 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 5 | 11 | 120 | 0 | 285 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113
Forecast for Day | 72 | 0 | 150 | 0 | 365 | 0 | 0 | 412 | 0 | 0 | 0 | 225 | 280 | 100 | 100 | 55 | 240 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 52 | 0 | 32 | 40 | 120 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 320 | 360 | 225 | 55 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 100 | 110 | 95 | 22 | 1.6 | 60 | 55 | 51 | 44 | 163 | 160 | 66 | 62 | 0 | 150 | 0 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 90 | 0 | 100 | 230 | 80 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 400 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 194 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 5 | 11 | 120 | 0 | 285 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 225 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113
Generation at 08:00(Today) | 72 | 0 | 150 | 0 | 340 | 0 | 0 | 378 | 0 | 0 | 0 | 225 | 280 | 1 | 0 | 0 | 235 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 18 | 25 | 0 | 0 | 30 | 40 | 100 | 0 | 0 | 213 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 0 | 100 | 340 | 330 | 202 | 26 | 0 | 35 | 5 | 0 | 38 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 78 | 106 | 92 | 17 | 0.5 | 60 | 54 | 44 | 29 | 130 | 152 | 69 | 62 | 0 | 153 | 0 | 0 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 0 | 0 | 0 | 145 | 91 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 445 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 5 | 11 | 121 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 94 | 0 | 0.8 | 5 | 0 | 0
199
| Minimum Generation |  | 5624 | 5:00
| Highest Generation |  | 9099 | 19:00
| Day Peak Generation |  | 7404.26 | 12:00
| Evening Peak Generation |  | 9099 | 19:00
| HVDC Max Flow |  | 737 | 22:00
| HVDC EvPeak Flow |  | 565 | 19:00
| Load factor L.F |  | 81.08%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7404.26 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5573 | MW
Evening Peak Generation : |  | 9099 | MW Hour : | 19:00 | Available Max Generation : |  | 14545 | MW
E.P. Demand (at gen end) : |  | 9099 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 9099 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5245 | MW
Total Gen. (MKWH) : |  | 177.0536 | System Load Factor : | 81.08% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -393 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-06
Actual : | 93.47 | Ft.(MSL) , | Rule curve : | 96.3 | Ft.( MSL )
Gas Consumed : | Total = | 1082.76 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 123658121.36
: |  | Coal : | 45770778.98 | Oil : | 164528476.92 | Total : | 333957377.26
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3289.2023 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1113.7349 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 997.0186 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 900.5882 |  |  | 0 | 0%
) | 0 | 0:00 | 814.0152 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 656.8694 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 373.4349 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.2889 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 506.5809 |  |  | 0 | 0%
Total | 0 |  | 8820.7331 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Haripur 360 MW CCPP
3) Ghorasal Unit-3,5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,4
6) Sirajganj unit-2,3
7)Shajibazar 330 MW GT-1
8) Chandpur 150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Naogaon 132/33 kV T-1 & T-2 transformers tripped at 11:58 from 33 kV showing O/C relay and |  |  |  |  | About 50 MW power interruption occurred under Naogaon S/S area
were switched on at 12:13. |  |  |  |  | from 11:58 to 12:13.
b) Rangamati 132 kV main Bus was under shut down from 09:37 to 17:26 for A/M.
c) Savar-Aminbazar 132 kV Ckt-2 was under shut down from 09:53 to 17:11 for A/M.
d) Mirpur 132/33kV T-1 transformer was shut down at 09:10 for A/M.
e) Cumilla(S)-Tripura 132 kV Ckt-1 was under shut down from 08:45 to 16:58 for A/M.
f) Mymensing 132/33 kV T-3 transformer was under shut down from 09:27 to 13:57 for A/M.
g) Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-1 was under shut down from 10: to 10:56 for A/M.
h) Haripur 132 kV reserve Bus was under shut down from 10:14 to 17:13:43 for C/M.
i) Shahjibazar S/S-Shahjibazar-86 P/S 132 kV Ckt was under shut down from 08:37 to 16:54 for A/M.
j) B.Baria 132/33 kV T-1 transformer was under shut down from 09:42 to 14:40 for C/M.
k) Tongi-Kabirpur 132 kV Ckt-1 was under shut down from 11:58 to 18:35 for A/M.
l) Rampura-Mogbazar 132 kV Ckt-1 was under shut down from 09:09 to 13:47 for A/M.
m) Rajshahi-Rajshahi(N) 132 kV Ckt-1 was under shut down from 09:39 to 13:59 for D/W.
n) Bheramara HVDC-Ishurdi 230 kV Ckt-3 was under shut down from 10:11 to 16:56 for C/M.
o) Chandraghona-Rangamati 132 kV Ckt-2 was under shut down from 10:12 to 17:20 for A/M.
p) Fenchuganj S/S-Fenchuganj P/P 132 kV Ckt-2 was under shut down from 10:57 to 11:25 for breaker
gas leakage maintenance.
q) Rampura-Mogbazar 132 kV Ckt-2 was under shut down from 13:52 to 14:45 for A/M.
r) Chandpur-150 MW CCPP GT was synchronized at 15:37 and shut down at 16:30 due to GBC problem.
s) After maintenance Ghorasal #4 was synchronized at 16:00.
t) After maintenance Sylhet-150 MW GT was synchronized at 21:32.
u) Sirajganj #3 was shut down at 14:14 due to gas shortage.
v) Fenchuganj #2 CCPP ST was synchronized at 14:42.
w) Kabirpur 132/33 kV T-3 transformer was shut down at 17:13 due to R-phase DS finger problem and
was switched on at 20:21.
x) Saidpur-Purbasadipur 132 kV Ckt-1 & 2 were under shut down from 15:20 to 16:25 due to D/W.
y) Bogura(N)-Bogura(O) 132 kV Ckt-1 was under shut down from 07:31 to 08:57 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 72 | 1648000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 1758000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 8560255
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 337 | 8356860 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5125000 | GT-2 Under maint
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 878400
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 5948887 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 60 | 260544 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 164918
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 81993 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 298656
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 40000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1099200
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 200 | 4685729 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 824688
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 116688
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 814320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 509915
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1221900 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 671500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 710300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 75272 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1579680
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 179520 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2530 | 45610225
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2700000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 108000
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 324480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 72 | 1627360 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4863700
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2721784 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 150545 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 32448 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 427920
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 523200
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 362880 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28560
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 215 | 2361055 | Transformer overload.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1025 | 16231932
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2304140 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4387000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7711100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7185500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 751536
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 24 | 421440 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 970181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1043968
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 306109 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 132720 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 398340
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 201780
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 1951680
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 597400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 492580
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1380 | 28855474
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2432040 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 392868 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1841280
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 0
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 192000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1712400
| Mymensingh Area Total |  |  |  | 637 | 381 | 6570588
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1414000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 55 | 1149000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3208500
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 150 | 3414000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 974400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 981288
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 238512
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1488864 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 62 | 563520 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 3714204
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 376255
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7526300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 145 | 3486000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 179280
| Sylhet Area Total |  |  |  | 1949 | 1097 | 28714123
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 565 | 8762182
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 891840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 1536
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 7675776 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1040 | 17331334
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 285696 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 348600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 180 | 4572095
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1827255
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 377 | 7033646
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 614240
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 130 | 3525409 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 2141845 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 326 | 7803272 | Gas shortage.
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 378240
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 5 | 114912 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245700
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 68 | 177784
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 118080 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1508352
| Rajshahi Area Total |  |  |  | 2183 | 756 | 16627834
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 120 | 2830254
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6782900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 432960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 32313
| Rangpur Area Total |  |  |  | 605 | 513 | 10078427
| Total |  |  |  | 19107 | 9099 | 177053583
| Eastern Grid Total |  |  |  | 13543 | 6413 | 125982342
| Western Grid Total |  |  |  | 5564 | 2686 | 51071241
| National Grid Total |  |  |  | 19107 | 9099 | 177053583
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-05
(a) ENTIRE EASTERN GRID : |  | 5708 | MW | (b) ENTIRE WESTERN GRID : |  | 2910 | MW
i) Dhaka area |  | 3018 | MW | i) Khulna area |  | 1062 | MW
ii) Chittagong area |  | 880 | MW | ii) Rajshahi area |  | 953 | MW
iii) Comilla area |  | 752 | MW | iii) Barisal area |  | 222 | MW
iv) Mymensingh area |  | 732 | MW | iv) Rangpur area |  | 673 | MW
v) Sylhet area |  | 326 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8618 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 12:00 | Srimongal | 25 | 19:00 | Jhenida | 85 | 18:30
Munsiganj | 90 | 19:30 | Shahjibazar | 79 | 18:30 | Bottail | 92 | 18:30
Sonargaon | 64 | 21:00 | Fenchuganj | 25 | 19:30 | G.K Project | 37 | 18:30
Shyampur | 180 | 9:00 | Kulawara | 27 | 19:30 | Faridpur | 132 | 19:00
Bhulta | 145 | 1:00 | Sylhet | 96 | 19:00 | Madaripur | 58 | 20:00
Madanganj | 51 | 13:00 | Chatak | 20 | 20:00 | Sariatpur | 38 | 20:00
Shitalakhya | 97 | 15:00 | Sunamganj | 28 | 19:00 | Gopalganj | 64 | 19:00
Rahim steel | 11 | 14:00 | Biani Bazar | 32 | 19:00 | Bagerhat | 67 | 18:30
Matuail | 79 | 12:00 | Comilla (S) | 114 | 18:00 | Mongla | 36 | 7:00
Ghorasal | 56 | 19:00 | Comilla(N) | 77 | 19:00 | Satkhira | 68 | 18:30
Narsingdi | 116 | 19:00 | Chandpur | 58 | 19:00 | Gallamari | 38 | 13:00
Haripur (SBU) | 89 | 19:00 | Feni | 89 | 20:00 | Magura | 38 | 18:30
Ullon | 48 | 18:00 | Chowmuhani | 110 | 18:30 | Norail | 27 | 19:00
Hasnabad | 126 | 19:00 | Ashuganj | 37 | 19:30 | Chuadanga | 61 | 19:00
Magbazar | 71 | 19:00 | Daudkandi | 108 | 19:00 | Barisal(N) | 30 | 19:00
Maniknagar | 72 | 17:00 | B.Baria | 96 | 18:00 | Barisal (S) | 66 | 18:30
Bangabhaban | 22 | 13:00 | Ramganj | 58 | 19:00 | Patuakhali | 72 | 21:00
Narinda | 74 | 12:00 | Chaddagram | 24 | 14:00 | Bhandaria | 40 | 19:30
Dhanmondi | 86 | 13:00 | PHP | 4 | 10:00 | Borhan Uddin | 25 | 21:00
Lalbag | 62 | 18:30 | Madunaghat | 39 | 18:30 | Ishurdi | 43 | 19:30
Madartek | 42 | 18:00 | Hathazari | 70 | 18:30 | Ruppur Paromanobik | 1 | 20:00
Dhaka University |  |  | Khulshi | 150 | 12:00 | Natore | 91 | 18:30
Mirpur | 69 | 6:00 | Halishahar | 93 | 18:00 | Bogra | 132 | 18:30
Kalyanpur | 72 | 6:00 | Baraulia | 147 | 12:00 | Noagaon | 88 | 19:00
Gulshan | 96 | 6:00 | Sikalbaha | 28 | 18:00 | Rajshahi | 93 | 20:00
Uttara | 36 | 6:00 | Dohazari | 64 | 19:00 | Rajshahi New | 12 | 20:00
Uttara New | 34 | 6:00 | Cox'sbazar | 74 | 20:00 | C.Nawabganj | 65 | 19:00
Kamrangirchar | 74 | 19:00 | Chandraghona | 32 | 18:30 | Amnura | 32 | 19:00
Savar | 102 | 10:00 | Kaptai | 3.7 | 18:30 | Pabna | 72 | 19:00
Bhasantec | 89 | 6:00 | A. Khaer Stl. | 8 | 12:00 | Shahjadpur | 82 | 20:00
Agargaon | 37 | 6:00 | Bakulia | 76 | 18:30 | Serajganj | 70 | 19:30
Satmosjid | 62 | 6:00 | Julda | 20 | 7:00 | Niyamatpur | 91 | 13:00
Tongi | 97 | 11:00 | TK chemical | 10.3 | 19:00 | Joypurhat | 53 | 20:00
Kabirpur | 137 | 18:30 | Modern Steel | 16 | 4:00 | Sherpur(Bogura) | 42 | 18:30
Basundhara | 76 | 18:00 | Shahmirpur | 22.5 | 18:30 | Mohastangor | 31 | 18:30
Manikganj | 58 | 19:30 | Khagrachhari | 18 | 18:30 | Rangpur | 116 | 19:30
Joydevpur | 157 | 19:00 | Matarbari | 23.5 | 18:30 | Lalmonirhat | 50 | 18:30
New Tongi | 79 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 96 | 18:30
Korda | 187 | 18:30 | Rangamati | 8 | 19:30 | Purbasadipur | 98 | 18:30
Dhamrai | 44 | 18:30 | Abul Khair 230 | 4 | 20:00 | Thakurgaon | 60 | 20:00
Valuka | 82 | 18:00 | BSRM | 102 | 11:00 | Palashbari | 97 | 19:00
Tangail | 136 | 18:00 | GPH Ispat | 25 | 14:00 | Barapukuria | 48 | 20:00
Mymensing | 170 | 18:30 | Goalpara | 19 | 13:00 | Panchagar | 41 | 19:00
Kishorganj | 82 | 22:00 | Central s/s | 66 | 18:30 | Joldhaka | 25 | 19:00
Netrokona | 106 | 19:30 | Noapara | 52 | 19:00 | Kurigram | 49 | 0.79167
Jamalpur | 105 | 18:30 | Jessore | 88 | 18:30
Sherpur | 90 | 19:00 | Benapol | 32 | 9:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-05 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.75 | 392 | 0.5 | Kaliakoir | 393 | 0.125 | 371 | 0.8125
Bheramara | 408 | 0.083333 | 402 | 0.41667 | Bhulta | 407 | 0.75 | 397 | 0.45833
Ashuganj(N) | 396 | 0.083333 | 384 | 0.45833 | Gopalganj | 397 | 0.16667 | 375 | 0.8125
Payra | 237 | 0.16667 | 230 | 0.41667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 240 | 0.041667 | Hathazari | 242 | 0.75 | 238 | 0.16667
Ishurdi | 242 | 0.20833 | 227 | 0.33333 | Megnaghat | 246 | 24:00 | 241 | 0.29167
Ashuganj | 247 | 0.75 | 240 | 0.45833 | Fenchuganj | 241 | 0.16667 | 230 | 0.5
Serajganj | 235 | 0.16667 | 230 | 0.33333 | Siddhirganj | 238 | 0.041667 | 231 | 0.5
Baghabari | 245 | 0.041667 | 236 | 0.29167 | Maniknagar | 239 | 0.16667 | 231 | 0.45833
Barapukuria | 233 | 0.041667 | 228 | 0.375 | Old Airport | 246 | 0.041667 | 236 | 0.29167
Bogra | 231 | 0.16667 | 230 | 0.29167 | Barisal | 227 | 0.75 | 220 | 0.45833
Khulna South | 239 | 0.16667 | 220 | 0.33333 | AKSML | 229 | 0.75 | 223 | 0.45833
Rampura | 235 | 0.041667 | 230 | 0.5 | BSRM | 225 | 0.75 | 220 | 0.45833
Haripur | 238 | 0.79167 | 232 | 0.41667 | Bibiyana | 240 | 0.16667 | 233 | 0.45833
Hasnabad | 237 | 0.77083 | 232 | 0.375 | Bhulta | 237 | 0.79167 | 228 | 0.041667
Shyampur | 240 | 0.125 | 232 | 0.5 | Ashuganj (S) | 240 | 0.20833 | 233 | 0.58333
Aminbazar | 235 | 0.75 | 229 | 0.41667 | Kaliakoir | 407 | 0.083333 | 394 | 0.77083
Tongi | 243 | 0.125 | 238 | 0.45833 | GPH | 244 | 0.54167 | 239 | 0.25
Comilla (N) | 229 | 0.77083 | 223 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 0.75 | 133 | 0.41667 | Khulshi | 133 | 0.83333 | 129 | 0.41667
Munsiganj | 142 | 0.79167 | 134 | 0.25 | Halishahar | 135 | 0.8125 | 129 | 0.45833
Sonargaon | 138 | 0.83333 | 133 | 0.41667 | Baraulia | 135 | 0.79167 | 130 | 0.375
Shyampur | 140 | 0.875 | 133 | 0.5 | Sikalbaha | 135 | 0.77083 | 130 | 0.41667
Bhulta | 132 | 0.75 | 127 | 0.5 | Dohazari | 133 | 0.8125 | 130 | 0.41667
Madanganj | 140 | 0.77083 | 131 | 0.41667 | Cox'sbazar | 128 | 0.54167 | 125 | 0.45833
Shitalakhya | 143 | 0.77083 | 134 | 0.41667 | Chandraghona | 135 | 0.77083 | 132 | 0.375
Rahim steal | 138 | 18:00 | 134 | 0.29167 | Kaptai | 135 | 0.041667 | 132 | 0.41667
Matuail | 138 | 0.8125 | 132 | 0.41667 | A. Khaer Stl. | 133 | 0.041667 | 130 | 0.29167
Ghorasal | 142 | 0.041667 | 140 | 0.29167 | Bakulia | 134 | 0.77083 | 129 | 0.41667
Narsinghdi | 136 | 0.58333 | 130 | 0.41667 | Julda | 134 | 0.77083 | 130 | 0.29167
Haripur (SBU) | 139 | 0.75 | 134 | 0.41667 | TK Chemical | 135 | 0.77083 | 131 | 0.25
Ullon | 133 | 0.20833 | 127 | 0.54167 | Modern Steel | 134 | 0.77083 | 130 | 0.41667
Hasnabad | 136 | 0.25 | 132 | 0.25 | Shahmirpur | 134 | 0.79167 | 130 | 0.41667
Magbazar | 134 | 0.25 | 125 | 0.5 | Khagrachhari | 133 | 0.041667 | 130 | 0.45833
Maniknagar | 139 | 0.25 | 135 | 0.5 | Matarbari | 130 | 0.041667 | 128 | 0.29167
Bangabhaban | 139 | 0.25 | 135 | 0.5 | Baroiar Hat | 135 | 0.041667 | 133 | 0.41667
Narinda | 139 | 0.25 | 135 | 0.5 | Rangamati | 134 | 0.75 | 131 | 11:00
Dhanmondi | 133 | 0.20833 | 127 | 0.54167 | Goalpara | 134 | 0.041667 | 125 | 8:00
Lalbag | 138 | 0.25 | 132 | 0.5 | Central s/s | 135 | 0.16667 | 124 | 0.33333
Madartek | 133 | 0.20833 | 126 | 0.5 | Noapara | 134 | 0.083333 | 127 | 0.29167
Dhaka University |  |  |  |  | Jessore | 132 | 0.75 | 120 | 0.33333
Mirpur | 137 | 0.25 | 135 | 0.5 | Benapol | 133 | 0.16667 | 120 | 0.29167
Kalyanpur | 140 | 0.25 | 135 | 0.5 | Jhenida | 133 | 0.20833 | 122 | 0.33333
Gulshan | 131 | 0.25 | 125 | 0.5 | Bottail | 135 | 0.083333 | 128 | 0.77083
Uttara | 138 | 0.25 | 132 | 0.5 | G.K Project | 141 | 0.125 | 134 | 0.33333
Uttara New | 133 | 0.25 | 132 | 0.5 | Faridpur | 140 | 0.16667 | 132 | 0.79167
Kamrangirchar | 137 | 0.25 | 131 | 0.5 | Madaripur | 139 | 0.16667 | 132 | 0.79167
Savar | 135 | 0.25 | 130 | 0.5 | Sariatpur | 141 | 0.20833 | 133 | 0.8125
Bhasantec | 138 | 0.25 | 133 | 0.5 | Gopalganj | 144 | 0.125 | 135 | 0.29167
Agargaon | 138 | 0.25 | 134 | 0.5 | Bagerhat | 133 | 0.083333 | 126 | 0.77083
Satmosjid | 138 | 0.25 | 132 | 0.5 | Mongla | 131 | 0.083333 | 123 | 0.33333
Tongi | 142 | 0.875 | 136 | 0.41667 | Satkhira | 134 | 0.20833 | 123 | 0.33333
Kabirpur | 136 | 24:00 | 131 | 0.5 | Gallamari | 135 | 0.16667 | 124 | 0.29167
Basundhara | 133 | 4:00 | 126 | 0.45833 | Magura | 135 | 0.083333 | 120 | 0.33333
Manikganj | 142 | 0.75 | 134 | 0.375 | Norail | 133 | 0.125 | 121 | 0.33333
Joydevpur | 143 | 1904-01-02 | 139 | 0.45833 | Chuadanga | 132 | 0.125 | 117 | 0.29167
New Tongi | 142 | 0.75 | 136 | 0.375 | Barisal(N) | 141 | 0.70833 | 134 | 0.29167
Kodda | 142 | 0.875 | 130 | 0.91667 | Barisal (S) | 140 | 0.75 | 130 | 0.25
Dhamrai | 137 | 0.16667 | 131 | 0.45833 | Patuakhali | 138 | 0.083333 | 131 | 0.29167
Valuka | 127 | 0.58333 | 113 | 0.33333 | Bhandaria | 136 | 0.083333 | 129 | 0.29167
Tangail | 133 | 0 | 124 | 0.54167 | Ishurdi | 138 | 0.20833 | 131 | 0.33333
Mymensing | 129 | 0.58333 | 115 | 0.33333 | Ruppur Paromanobik | 137 | 0.16667 | 130 | 0.29167
Kishorganj | 132 | 0.16667 | 122 | 0.33333 | Natore | 135 | 0.75 | 125 | 0.33333
Netrokona | 126 | 0.58333 | 116 | 0.29167 | Bogra | 136 | 0.20833 | 127 | 0.33333
Jamalpur | 134 | 0.75 | 118 | 0.16667 | Noagaon | 132 | 0.20833 | 120 | 0.33333
Sherpur | 134 | 0.58333 | 115 | 0.125 | Rajshahi | 133 | 0.625 | 123 | 0.29167
Srimongal | 140 | 0.041667 | 137 | 0.5 | Rajshahi New | 133 | 0.75 | 119 | 0.29167
Shahjibazar | 138 | 0.041667 | 135 | 0.41667 | C.Nawabganj | 130 | 0.75 | 119 | 0.33333
Fenchuganj | 139 | 0.041667 | 137 | 7:00 | Amnura | 132 | 0.77083 | 118 | 0.29167
Khulawara | 138 | 0.041667 | 137 | 0.45833 | Pabna | 137 | 0.20833 | 130 | 0.29167
Sylhet | 137 | 0.91667 | 134 | 0.5 | Shahjadpur | 144 | 0.16667 | 135 | 0.83333
Chatak | 136 | 0.041667 | 133 | 0.45833 | Serajganj | 136 | 0.16667 | 130 | 0.33333
Sunamganj | 136 | 0.041667 | 132 | 0.79167 | Niyamatpur | 128 | 0.20833 | 114 | 0.33333
Biani Bazar | 137 | 0.041667 | 134 | 0.75 | Joypurhat | 131 | 0.16667 | 118 | 0.33333
Comilla(s) | 133 | 0.95833 | 126 | 0.375 | Sherpur(Bogura) | 137 | 0.16667 | 131 | 0.54167
Comilla(n) | 142 | 22:00 | 140 | 0.54167 | Mohastangor | 135 | 0.16667 | 126 | 0.29167
Chandpur | 138 | 0.33333 | 135 | 0.83333 | Rangpur | 130 | 0.75 | 126 | 0.29167
Feni | 136 | 0.29167 | 133 | 0.54167 | Lalmonirhat | 127 | 0.20833 | 116 | 0.33333
Chowmuhani | 131 | 0.29167 | 129 | 0.77083 | Saidpur | 132 | 0.20833 | 120 | 0.33333
Ashuganj | 139 | 0.8125 | 136 | 0.29167 | Purbasadipur | 127 | 0.16667 | 113 | 0.33333
Daudkandi | 137 | 0.29167 | 134 | 0.45833 | Thakurgaon | 124 | 0.16667 | 112 | 0.33333
B.Baria | 135 | 0.91667 | 133 | 0.29167 | Palashbari | 126 | 0.70833 | 119 | 0.33333
Ramganj | 132 | 0.33333 | 127 | 0.75 | Barapukuria | 133 | 0.25 | 128 | 0.33333
Chaddagram | 138 | 0.041667 | 135 | 0.41667 | Panchagar | 124 | 0.25 | 110 | 0.33333
PHP | 134 | 0.33333 | 130 | 0.79167 | Joldhaka | 129 | 0.20833 | 118 | 0.77083
Madanhat | 137 | 0.77083 | 133 | 0.375 | Kurigram | 130 | 0.20833 | 117 | 0.33333
Hathazari | 136 | 0.041667 | 133 | 0.375

## L-Curve
Date | 2020-02-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 254 | 4938 | 1901 | 6839 |  |  |  | QF-LDC-12
0:30 | 257 | 4774 | 1815.5 | 6589.5 | Date: | 2020-02-05
1:00 | 260 | 4610 | 1730 | 6340
1:30 | 224.5 | 4444.5 | 1728 | 6172.5
2:00 | 189 | 4279 | 1726 | 6005
2:30 | 185.5 | 4209.5 | 1686.5 | 5896 | [5 empty] | Gen. at Eve. Peak | 9099 | 9099 MW (19:00 )
3:00 | 182 | 4140 | 1647 | 5787 | [6 empty] | 19:00
3:30 | 171 | 4089 | 1622 | 5711 | [5 empty] | Gen. at Day Peak | 7404.26 | 7404.26 MW (12:00 )
4:00 | 160 | 4038 | 1597 | 5635 | [6 empty] | 12:00
4:30 | 155 | 4033 | 1596.5 | 5629.5 | [5 empty] | Highest Generation | 9099
5:00 | 150 | 4028 | 1596 | 5624 | [6 empty] | 19:00
5:30 | 144 | 4121.5 | 1706.5 | 5828
6:00 | 138 | 4215 | 1817 | 6032
6:30 | 129 | 4331.555 | 1988.55 | 6320.105
7:00 | 120 | 4448.11 | 2160.1 | 6608.21
7:30 | 176.5 | 4680.415 | 2182.95 | 6863.365
8:00 | 233 | 4912.72 | 2205.8 | 7118.52
8:30 | 158.5 | 4989.725 | 2248.1 | 7237.825
9:00 | 84 | 5066.73 | 2290.4 | 7357.13
9:30 | 48.5 | 5061.765 | 2260.05 | 7321.815
10:00 | 13 | 5056.8 | 2229.7 | 7286.5
10:30 | 33 | 5097.69 | 2184.7 | 7282.39
11:00 | 53 | 5138.58 | 2139.7 | 7278.28
11:30 | 76.5 | 5203.32 | 2137.95 | 7341.27
12:00 | 100 | 5268.06 | 2136.2 | 7404.26
12:30 | 151.5 | 5351.03 | 2140.7 | 7491.73
13:00 | 203 | 5434 | 2145.2 | 7579.2
13:30 | 165.5 | 5266 | 2088.65 | 7354.65
14:00 | 128 | 5098 | 2032.1 | 7130.1
14:30 | 113 | 5113.55 | 1985.05 | 7098.6
15:00 | 98 | 5129.1 | 1938 | 7067.1
15:30 | 69 | 5108.35 | 1931.65 | 7040
16:00 | 40 | 5087.6 | 1925.3 | 7012.9
16:30 | 35 | 5091.45 | 1957.35 | 7048.8
17:00 | 30 | 5095.3 | 1989.4 | 7084.7
17:30 | 99 | 5295.65 | 2231.7 | 7527.35
18:00 | 168 | 5496 | 2474 | 7970
18:30 | 279 | 5954.5 | 2580 | 8534.5
19:00 | 390 | 6413 | 2686 | 9099
19:30 | 360 | 6359 | 2684 | 9043
20:00 | 365 | 6303 | 2696 | 8999 |  |  |  | Executive Engineer
20:30 | 324 | 6225 | 2666.5 | 8891.5 |  |  |  | Network Operation Division
21:00 | 283 | 6147 | 2637 | 8784
21:30 | 188.5 | 5834 | 2585 | 8419
22:00 | 94 | 5521 | 2533 | 8054 |  |  |  |  | Page 6 of 7
22:30 | 142 | 5356.5 | 2357.5 | 7714
23:00 | 190 | 5192 | 2182 | 7374
23:30 | 222 | 5065 | 2041.5 | 7106.5
24:00 | 254 | 4938 | 1901 | 6839
9099 MW (19:00 )
7404.26 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-05 |  | Energy | 177053583
[10 empty] | 2020-02-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4144 | 301 | 1418 | 639 | 401 | 70 | 0 | 0 | 84
0:30 | 4022.5 | 218.5 | 1414.5 | 491.5 | 401.5 | 70 | 0 | 0 | 80 | Date: | 2020-02-05
1:00 | 3901 | 136 | 1411 | 344 | 402 | 70 | 0 | 0 | 76
1:30 | 3846.5 | 136 | 1331 | 312.5 | 401.5 | 70 | 0 | 0 | 75 | [7 empty] | Total Energy | 177.0536 | Total Energy Gen 177.054 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.054 MKWHr
2:00 | 3792 | 136 | 1251 | 281 | 401 | 70 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3769.5 | 136.5 | 1172.5 | 274.5 | 401 | 70 | 0 | 0 | 72 | [7 empty] | Energy Requirement | 177.0536
3:00 | 3747 | 137 | 1094 | 268 | 401 | 70 | 0 | 0 | 70
3:30 | 3694.5 | 137 | 1074 | 265.5 | 401 | 70 | 0 | 0 | 69 | [6 empty] | Shortage
4:00 | 3642 | 137 | 1054 | 263 | 401 | 70 | 0 | 0 | 68
4:30 | 3641.5 | 136.5 | 1044 | 266.5 | 401 | 70 | 0 | 0 | 70
5:00 | 3641 | 136 | 1034 | 270 | 401 | 70 | 0 | 0 | 72
5:30 | 3789.5 | 136 | 1085.5 | 272 | 401 | 70 | 0 | 0 | 74
6:00 | 3938 | 136 | 1137 | 274 | 401 | 70 | 0 | 0 | 76
6:30 | 4034.5 | 266.5 | 1164 | 307 | 400.5 | 70 | 0 | 0 | 77 |  |  |  |  | Coal
7:00 | 4131 | 397 | 1191 | 340 | 400 | 70 | 0 | 0 | 78
7:30 | 4107 | 396.5 | 1318 | 489 | 400 | 70 | 0 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 4083 | 396 | 1445 | 638 | 400 | 70 | 0 | 0 | 78
8:30 | 4069.5 | 396 | 1417 | 800 | 401 | 70 | 0 | 0 | 72
9:00 | 4056 | 396 | 1389 | 962 | 402 | 70 | 0 | 0 | 66
9:30 | 4012 | 396 | 1379.5 | 974 | 401.5 | 70 | 0 | 0 | 68.5
10:00 | 3968 | 396 | 1370 | 986 | 401 | 70 | 0 | 0 | 71
10:30 | 3948.5 | 395.5 | 1361.5 | 1008.5 | 400.5 | 70 | 0 | 0 | 71.5
11:00 | 3929 | 395 | 1353 | 1031 | 400 | 70 | 0 | 0 | 72
11:30 | 3945.5 | 395.5 | 1353.5 | 1070.5 | 400 | 70 | 0 | 0 | 77
12:00 | 3962 | 396 | 1354 | 1110 | 400 | 70 | 0 | 0 | 82
12:30 | 3947.5 | 396 | 1353 | 1214.5 | 400.5 | 70 | 0 | 0 | 82
13:00 | 3933 | 396 | 1352 | 1319 | 401 | 70 | 0 | 0 | 82
13:30 | 3933 | 396 | 1352 | 1319 | 401 | 70 | 0 | 0 | 82
14:00 | 3933 | 396 | 1352 | 1319 | 401 | 70 | 0 | 0 | 82
14:30 | 3834.5 | 396 | 1326 | 1193.5 | 399.5 | 70 | 0 | 0 | 83
15:00 | 3736 | 396 | 1300 | 1068 | 398 | 70 | 0 | 0 | 84
15:30 | 3752 | 396 | 1290 | 1039 | 399 | 70 | 0 | 0 | 81.5
16:00 | 3768 | 396 | 1280 | 1010 | 400 | 70 | 0 | 0 | 79
16:30 | 3793.5 | 396 | 1285 | 1019 | 398.5 | 70 | 0 | 0 | 80.5
17:00 | 3819 | 396 | 1290 | 1028 | 397 | 70 | 0 | 0 | 82
17:30 | 3798 | 455 | 1313 | 1366 | 399 | 70.5 | 26.5 | 0 | 98
18:00 | 3777 | 514 | 1336 | 1704 | 401 | 71 | 53 | 0 | 114
18:30 | 3886.5 | 539.5 | 1386 | 2074.5 | 400.5 | 71.5 | 63 | 0 | 113
19:00 | 3996 | 565 | 1436 | 2445 | 400 | 72 | 73 | 0 | 112
19:30 | 4048 | 556 | 1462 | 2328 | 400 | 71 | 68 | 0 | 110
20:00 | 3982 | 566 | 1456 | 2345 | 401 | 71 | 68 | 0 | 110
20:30 | 4003 | 566 | 1469.5 | 2229 | 401 | 71 | 43 | 0 | 109
21:00 | 4024 | 566 | 1483 | 2113 | 401 | 71 | 18 | 0 | 108
21:30 | 4085.5 | 651.5 | 1480 | 1618.5 | 398.5 | 71 | 9 | 0 | 105
22:00 | 4147 | 737 | 1477 | 1124 | 396 | 71 | 0 | 0 | 102
22:30 | 4156 | 639.5 | 1472.5 | 881.5 | 397.5 | 71 | 0 | 0 | 96
23:00 | 4165 | 542 | 1468 | 639 | 399 | 71 | 0 | 0 | 90
23:30 | 4154.5 | 421.5 | 1443 | 639 | 400 | 70.5 | 0 | 0 | 87 | Max Temp. in Dhaka |  | 26° C
24:00 | 4144 | 301 | 1418 | 639 | 401 | 70 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 177.054 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.054 MKWHr
Note on W13: Author:

## Generation
2020-02-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 |  | 32 | 31 | 31 | 31 | 31 | 31 | 30 | 663360
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5.92 | 10.93 | 15.6 | 17.08 | 18.46 | 15 | 6.7 | 8.6 | 6.8 | 1.8 | [9 empty] | 108000
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 184 | 182 | 182 | 206 | 214 | 202 | 202 | 232 | 203 | 205 | 203 | 203 | 203 | 202 | 202 | 202 |  | 202 | 202 | 203 | 202 | 202 | 204 | 201 | 4863700
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 124 | 124 | 104 | 104 | 104 | 104 | 116 | 130 | 135 | 103 | 105 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 140 | 140 | 140 | 2721784
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 2 | 22 |  | 34 | 34 | 34 | 34 |  |  | 0 | 150545
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 0 | [25 empty] | 40000
17 | Siddhirganj 335 MW CCPP | 6 | 31 | 229 | 188 | 188 | 235 | 232 | 238 | 233 | 231 | 228 | 227 | 227 | 180 | 180 | 180 | 180 | 180 |  | 200 | 200 | 200 | 203 | 200 | 200 | 200 | 4685729
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 0 | 10 |  | 45 | 0 | 0 |  |  |  |  | 75272
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 970181
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1648000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 100 | 100 | 101 | [11 empty] | 100 | 100 |  | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 1758000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 380 | 300 | 300 | 300 | 378 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 320 |  | 320 | 320 | 320 | 350 | 350 | 350 | 350 | 8560255
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2304140
32 | Ashuganj 50 MW PP | 40 | 40 | 5 | 5 | 5 | 5 | 5 | 32 | 36 | 36 | 36 | 36 | 36 | 39 | 42 | 39 | 42 | 42 |  | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 751536
33 | Ashuganj 225 MW CCPP | 181 | 186 | 176 | 164 | 177 | 178 | 202 | 180 | 181 | 166 | 167 | 175 | 165 | 174 | 171 | 165 | 165 | 164 |  | 184 | 197 | 184 | 185 | 185 | 189 | 180 | 4387000
34 | Ashuganj 450 MW CCPP(South) | 275 | 270 | 280 | 270 | 285 | 315 | 350 | 315 | 295 | 275 | 335 | 325 | 315 | 275 | 275 | 270 | 270 | 270 |  | 295 | 315 | 295 | 290 | 295 | 295 | 295 | 7185500
| Ashuganj 450 MW CCPP(North) | 290 | 275 | 290 | 275 | 290 | 340 | 360 | 320 | 320 | 320 | 320 | 330 | 320 | 325 | 320 | 310 | 280 | 280 |  | 280 | 315 | 295 | 295 | 295 | 300 | 295 | 7711100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 5 | 5 | 421440
36 | Chandpur 150 MW CCPP | [15 empty] | 50 | 0 | 0 |  | 50 | 0 | 0 |  | 40 | 0 | 0 | 132720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 354 | 339 | 338 | 342 | 300 | 329 | 366 | 377 | 338 | 336 | 348 | 348 | 357 | 338 | 353 | 339 | 338 | 338 |  | 337 | 350 | 340 | 338 | 337 | 345 | 347 | 8356860
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5125000
41 | Haripur 360MW CCPP(HPL)
42 | RPCL 210MW CCPP | 104 | 104 | 104 | 104 | 104 | 104 | 105 | 105 | 105 | 103 | 102 | 102 | 102 | 101 | 101 | 101 | 102 | 102 |  | 104 | 103 | 104 | 104 | 104 | 106 | 108 | 2432040
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1414000
45 | Fenchugonj CCPP Phase-2 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 42 | 42 | 54 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1149000
46 | Shajibazar 330 MW CCPP | 152 | 153 | 152 | 153 | 154 | 154 | 162 | 147 | 149 | 151 | 148 | 154 | 148 | 157 | 153 | 147 | 146 | 148 |  | 150 | 154 | 148 | 151 | 150 | 153 | 147 | 3414000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 45 | 45 | 45 | 45 | 56 | 56 | 69 | 67 | 65 | 64 | 63 | 63 | 63 | 63 | 64 | 64 | 67 |  | 67 | 67 | 67 | 67 | 62 | 67 | 69 | 1488864
48 | Shahjibazar 86MW PP (Shahjibazar) | 59 | 5 | 5 | 5 | 5 | 5 | 5 | 59 | [9 empty] | 50 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 563520
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | [23 empty] | 44 | 68 | 70 | 3714204
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [6 empty] | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 179280
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 238512
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 | 49 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 974400
56 | Shahjahanulla 25 MW PP | 23 | [7 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 376255
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 310 | 290 | 300 | 310 | 325 | 310 | 300 | 300 | 325 | 310 | 310 | 280 | 320 | 300 | 300 | 280 |  | 280 | 310 | 300 | 300 | 290 | 300 | 280 | 7526300
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 427920
61 | Narshingdi 22 MW PP (Doreen) | 22 | [10 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 298656
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 392868
63 | Impoprt (Tripura) | 76 | 74 | 70 | 68 | 72 | 76 | 78 | 78 | 66 | 71 | 72 | 82 | 82 | 82 | 84 | 79 | 82 | 114 |  | 112 | 110 | 110 | 108 | 102 | 90 | 84 | 1951680
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 34 | 34 | 34 | 34 | 32 | 18 | 4 | 2 | 2 | 3 | 10 | 2 | 2 | 2 | 9 | 15 |  | 26 | 28 | 28 | 35 | 38 | 40 | 40 | 523200
65 | Feni 22MW PP (Doreen) | 22 | 22 |  |  |  |  | 8 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 398340
66 | Feni 11 MW PP (Doreen) | 11 | 11 | [5 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201780
67 | Jangalia 33MW PP (Summit) | 33 | [6 empty] | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 597400
68 | Cumilla 25 MW PP (Summit) | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 492580
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 23 | 22 | 6 |  | 28 | 28 | 29 | 32 | 32 | 32 | 32 | 621900
71 | Maona 33 MW PP(Summit) | 20 | 18 | 18 | 18 | 18 | 18 | 18 |  | 25 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 671500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 710300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 20 | 60 | 60 | 24 | 24 | 70 | 85 | 70 | 63 | 40 | 50 |  | 100 | 100 | 100 | 100 | 100 | 60 | 8 | 1099200
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 72 | 24 | 8 | 8 | 8 | 11 | 60 | 95 | 95 | 95 | 90 | 95 | 89 | 95 | 95 | 86 | 95 | 89 |  | 95 | 95 | 95 | 95 | 95 | 95 | 50 | 1841280
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [11 empty] | 8 | 34 | 17 | 35 | 35 | 35 | 35 | [7 empty] | 0 | 179520
| Kaptai 7 MW Solar PP | [6 empty] | 0.11 | 1.4 | 2.8 | 3.7 | 4.4 | 4.6 | 4.2 | 3.6 | 2.7 | 1.4 | 0.3 | 0 | [8 empty] | 28560
| Jodiac Power | [25 empty] | 0 | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [16 empty] | 0 | 17 |  | 60 | 70 | 90 | 15 | 0 | 0 |  | 260544
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 12 |  | 50 | [5 empty] | 0 | 81993
86 | Meghnaghat CCPP(Summit) | 260 | 257 | 260 | 255 | 262 | 263 | 278 | 230 | 230 | 220 | 225 | 224 | 220 | 220 | 230 | 235 | 245 | 220 |  | 285 | 275 | 275 | 255 | 250 | 245 | 260 | 5948887
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 3 | 28 | 45 | 24 | 29 | 70 | 55 | 50 | 24 | 22 | 36 |  | 100 | 100 | 100 | 100 | 75 | 50 |  | 878400
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 981288
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 32 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1043968
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 24 | 24 | 24 | 32 | 50 | 60 | 40 | 40 | 24 | 24 | 50 |  | 102 | 102 | 102 | 102 | 48 |  | 0 | 824688
95 | Patenga 50MW PP (Baraka) | [10 empty] | 1 | 16 | 18 | 19 | 19 | 19 | 19 | 22 |  | 50 | 50 | 50 | 50 |  |  | 0 | 324480
96 | Chattogram 108 MW PP (ECPV) | 12 | [15 empty] | 1 | 22 |  | 93 | 98 | 98 | 98 |  |  | 0 | 362880
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 9 |  | 47 | 18 | 18 | 18 |  |  | 0 | 116688
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [16 empty] | 0 | 12 |  | 55 | 55 | 55 | 30 | 0 |  |  | 164918
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 55 | 55 | 55 |  |  | 0 | 509915
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 3208500
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.4 | 0 | 1.5 | 2.1 | 2 | 1.8 | 0.7 | 0.8 | 0.4 | 0.2 | 0 | [8 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 35 | 35 | 35 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 814320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 3 | 22 |  | 50 | 50 | 50 | 32 |  |  | 0 | 192000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 2 | 35 | 46 | 60 | 91 | 144 | 115 | 112 | 143 | 149 | 151 |  | 149 | 149 | 149 | 144 | 65 | 0 | 0 | 1579680
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 10 | 48 |  | 90 | 90 | 90 | 90 | 0 |  |  | 32448
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 35 |  | 100 | 100 | 100 | 50 |  |  | 0 | 306109
118 | Bibiyana-III 400 MW CCPP | 144 | 145 | 145 | 145 | 145 | 145 | 144 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 144 | 144 | 144 | 145 | 3486000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 70 | 101 | 102 | 109 | 110 | 115 | 115 | 80 | 80 | 80 | 95 |  | 115 | 115 | 115 | 115 | 80 | 50 | 50 | 1712400
| Anwara 300 MW PP (United) | [7 empty] | 66 | 100 | 105 | 160 | 178 | 215 | 123 | 123 | 123 | 88 | 213 |  | 215 | 217 | 217 | 217 | 161 | 51 | 0 | 2361055
120 | Eastern Zone Total | 4610 | 4279 | 4140 | 4038 | 4028 | 4215 | 4448.11 | 4912.72 | 5066.73 | 5056.8 | 5138.58 | 5268.06 | 5434 | 5098 | 5129.1 | 5087.6 | 5095.3 | 5496 |  | 6413 | 6359 | 6303 | 6147 | 5521 | 5192 | 4938 | 125993542
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 16 | 32 | 32 | 49 | 66 | 83 | 53 | 52 | 16 | 16 | 86 |  | 115 | 115 | 115 | 115 | 64 | 0 |  | 891840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 48 |  | 80 | 80 | 80 | 80 | 0 |  |  | 285696
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 63 | 33 | 13 | 13 | 13 | 13 | 82 | 96 | 96 | 95 | 95 | 95 | 97 | 95 | 96 | 96 | 97 |  | 97 | 97 | 96 | 96 | 97 | 97 | 97 | 1827255
| Bhola 225 MW CCPP | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 188 | 189 | 189 | 189 | 188 | 171 | 171 | 176 |  | 180 | 178 | 178 | 178 | 183 | 188 | 181 | 4572095
140 | Bhola 33 MW PP (Venture) | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 13 | 12 | 12 | 11 | 13 | 13 | 13 | 12 | 11 | 11 | 17 |  | 20 | 20 | 19 | 20 | 20 | 18 | 17 | 348600
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 5 | 0 | [5 empty] | 1536
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 136 | 136 | 137 | 137 | 136 | 136 | 397 | 396 | 396 | 396 | 395 | 396 | 396 | 396 | 396 | 396 | 396 | 514 |  | 565 | 556 | 566 | 566 | 737 | 542 | 301 | 8762182
147 | Bheramara 410 MW CCPP | 290 | 290 | 290 | 260 | 260 | 360 | 380 | 340 | 310 | 280 | 250 | 250 | 250 | 245 | 240 | 280 | 310 | 340 |  | 355 | 375 | 375 | 385 | 390 | 390 | 390 | 7675776
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 122 | 121 | 121 | 121 | 121 | 121 | 120 | 120 | 122 | 122 | 121 | 121 | 121 | 121 | 118 | 120 | 117 | 121 |  | 120 | 120 | 121 | 121 | 116 | 119 | 121 | 2830254
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 279 | 279 | 279 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6782900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 150 | 140 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3525409
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 158 | 177 | 160 | 160 | 156 | 130 | 130 | 130 | 100 | 0 | [11 empty] | 2141845
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 306 | 356 | 306 | 306 | 307 | 399 | 441 | 390 | 354 | 337 | 301 | 276 | 270 | 260 | 280 | 280 | 280 | 282 |  | 326 | 320 | 326 | 345 | 345 | 345 | 346 | 7803272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 21 | 21 | 18 | 18 | 18 | 18 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 378240
163 | Bogura 20 MW PP (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 114912
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 245700
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 |  | 50 | 50 | 50 | 50 | 24 |  |  | 614240
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 53 |  | 68 | 68 | 68 | 18 |  |  |  | 177784
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 3 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 118080
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 17 | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 70 | 70 | 109 |  | 109 | 109 | 109 | 109 | 109 | 35 |  | 1508352
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 32 | 98 |  | 113 | 113 | 110 | 106 |  |  |  | 432960
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.8 | 2.4 | 3.7 | 4.7 | 5.2 | 5.2 | 4.1 | 3 | 1.3 | 0.4 | 0 | [8 empty] | 32313
178
178