## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-12 | Wednesday
|  | Date (day): | 2020-02-12 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12109.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14885 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-11 | 2020-02-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 355 | 313 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 65 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 342 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 367 | 330 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 92 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 30 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 53 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 105 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2067 | 2415 | 3514 | 4146 | 883 | 755
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.17 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 69 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 203 | 220 | 220
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 146 | 139 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 26 | 60 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.9 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 200 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 672.07 | 967 | 1495 | 1630 | 400 | 108
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 |  |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 183 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 355 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 39 | 40 | 40
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 38 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 91 | 90 | 90
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 20 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 110 | 101 | 111
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1368 | 1329 | 1679 | 2353 | 454 | 8
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 126 | 100 | 120 | 82 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 60 | 32 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 391.2 | 390 | 433.6 | 552 | 82 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 88 | 85 | 85 | 85
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 54 | 66 | 66 | 66
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 149 | 149 | 150 | 150 |  | 180 | GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 82 | 82
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 27 | 116 | 120 | 120 |  | 122 | Combined cycle testing
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 145 | 145 | 145 | 145 |  | 255 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1181 | 1323 | 1375 | 1375 | 0 | 557
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 492 | 771 | 501 | 797
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 215 | 300 | 300 | 110 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 858 | 1101 | 1159 | 1926 | 110 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 6 | 21 | 20 | 21 |  | 12 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 110 | 138 | 110 | 194
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 302 | 301 | 300 | 300 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 418 | 460 | 595 | 750 | 0 | 12
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 190 | 130 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 6 | 130 | 225 | 225
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 305 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 3 | 3 | 5 | 5 |  | 5 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 51 | 80 | 102
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 755 | 851 | 1458 | 1726 | 391 | 15
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 90 | 90 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 190 | 189 | 190 | 190 |  |  | Engine problem
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 109 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 320.3 | 388 | 401 | 427 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 8030.57 | 9224 | 12109.6 | 14885 | 2320 | 1547
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7523.871 | 8642 | 11345.5294 | 13945.812
A. |  | 2020-02-11 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9224 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5670 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9224 | MW
3 | Day peak Generation : |  |  | 8030.57 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8642 | MW
4 | Evening peak Generation : |  |  | 9224 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 179.8252 | MKWHr | By Solar | 0.1753 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.5718 | MKWHr |  | By Oil: | 18.5939 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.3305 | MKWHr |  | By Hydro: | 1.5918 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2320 | MW | Dhaka | 3014 | 3014 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1547 | MW | Chittagong | 898 | 898 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3867 | MW | Khulna | 1061 | 1061 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1097.37 | MMCFD |  |  | Rajshahi | 963 | 963 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 120865631.532 | ii) Oil : | Taka | 134624880.12 | Comilla | 750 | 750 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 32734194.3 | Total | Taka | 288224705.952 | Mymensingh | 753 | 753 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.929 | MKWHr. | Sylhet | 319 | 319 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -335 | MW (E to W) at | 19:30 | hrs | Barisal | 217 | 217 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -469 | MW at | 7:00 | hrs | Rangpur | 667 | 667 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27° C |  |  | Total | 8642 | 8642 |  | 0
B. |  | 2020-02-12 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 26.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14885 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
4 | Reserve(Generation end) |  |  |  | 5485 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 183.2564 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5734 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.4931 | MKWHr. | ii) HVDC Flow at Peak Time |  | 771 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0688 | MKWHr. | iii) Maximum HVDC Flow : |  | 772 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 92.72 |  | (b) Today: | 92.57 |  | (c) Rule Curve: |  | 95.46
.

## YesterdayGen
2020-02-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 100 | 0 | 325 | 0 | 0 | 337 | 363 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 80 | 265 | 270 | 171 | 8 | 90 | 46 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 82 | 107 | 50 | 20 | 0 | 87 | 76 | 5 | 5 | 163 | 143 | 45 | 5 | 0 | 9 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 139 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 90 | 0 | 189 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 |  | 4577 | 1773 | 6350 | 3544 | 139 | 1684 | 224 | 607 | 70 | 0 | 82 | 0 | 0 | 92.74
2:00 | 72 | 0 | 101 | 0 | 287 | 0 | 0 | 326 | 363 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 192 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 80 | 280 | 280 | 179 | 8 | 90 | 20 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 78 | 106 | 16 | 22 | 0 | 87 | 50 | 5 | 5 | 130 | 142 | 45 | 5 | 0 | 9 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 91 | 0 | 190 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 |  | 4404 | 1712 | 6116 | 3407 | 137 | 1627 | 190 | 608 | 69 | 0 | 78 | 0 | 0 | 92.74
3:00 | 72 | 0 | 100 | 0 | 278 | 0 | 0 | 296 | 300 |  | 0 | 320 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 194 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 80 | 270 | 275 | 175 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 106 | 0 | 22 | 0 | 87 | 50 | 5 | 5 | 130 | 142 | 45 | 5 | 0 | 9 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 138 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 91 | 0 | 190 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 |  | 4222 | 1626 | 5848 | 3280 | 138 | 1530 | 174 | 583 | 69 | 0 | 74 | 0 | 0 | 92.73
4:00 | 72 | 0 | 101 | 0 | 275 | 0 | 0 | 326 | 260 |  | 0 | 320 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 80 | 260 | 260 | 173 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 74 | 106 | 0 | 22 | 0 | 87 | 50 | 5 | 5 | 100 | 141 | 45 | 5 | 0 | 9 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 91 | 0 | 191 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 |  | 4125 | 1545 | 5670 | 3243 | 137 | 1389 | 174 | 585 | 68 | 0 | 74 | 0 | 0 | 92.73
5:00 | 72 | 0 | 101 | 0 | 275 | 0 | 0 | 340 | 260 |  | 0 | 320 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 182 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 80 | 265 | 265 | 166 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 70 | 107 | 0 | 22 | 0 | 87 | 50 | 5 | 5 | 100 | 142 | 45 | 5 | 0 | 10 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 137 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 |  | 4140 | 1541 | 5681 | 3262 | 137 | 1388 | 174 | 582 | 68 | 0 | 70 | 0 | 0 | 92.72
6:00 | 72 | 0 | 102 | 0 | 310 | 0 | 0 | 361 | 310 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 193 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 80 | 335 | 330 | 184 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 72 | 107 | 14 | 22 | 0 | 60 | 50 | 5 | 5 | 130 | 142 | 45 | 5 | 0 | 10 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 8 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 |  | 4491 | 1593 | 6084 | 3516 | 136 | 1522 | 188 | 582 | 68 | 0 | 72 | 0 | 0 | 92.72
7:00 | 72 | 0 | 150 | 0 | 350 | 0 | 0 | 371 | 310 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 214 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 0 | 80 | 335 | 340 | 185 | 8 | 90 | 35 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 0 | 14 | 82 | 107 | 74 | 22 | 0.1 | 60 | 50 | 5 | 10 | 130 | 142 | 45 | 5 | 0 | 15 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10 | 1.4 | 0 | 0 | 0 | 145 | 6 | 0 | 0 | 0.23 | 0 | 0 | 0 | 0 | 0 |  | 367 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 91 | 0 | 190 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 300 |  | 4868.73 | 1884.1 | 6752.83 | 3810 | 367 | 1579 | 264 | 581 | 68 | 0 | 82 | 1.83 | 0 | 92.71
8:00 | 72 | 0 | 150 | 0 | 342 | 0 | 0 | 371 | 330 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 10 | 25 | 30 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 214 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 0 | 80 | 330 | 335 | 202 | 8 | 91 | 35 | 5 | 0 | 40 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 72 | 106 | 95 | 22 | 0.5 | 61 | 50 | 51 | 50 | 130 | 142 | 69 | 78 | 0 | 20 | 0 | 0 | 10 | 325 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 32 | 6.7 | 0 | 0 | 0 | 145 | 90 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 |  | 494 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 22 | 3 | 0 | 91 | 0 | 190 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 12 | 0 | 1.2 | 25 | 300 |  | 5329.3 | 2125.2 | 7454.5 | 3903 | 494 | 1789 | 537 | 581 | 69 | 0 | 72 | 9.5 | 0 | 92.71
9:00 | 72 | 0 | 0 | 0 | 314 | 0 | 0 | 364 | 363 |  | 0 | 400 | 150 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 202 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 7 | 19 | 2 | 0 | 0 | 100 | 295 | 305 | 187 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 72 | 105 | 50 | 22 | 1 | 59 | 51 | 51 | 48 | 130 | 142 | 67 | 78 | 0 | 20 | 0 | 0 | 9 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 77 | 11.9 | 0 | 0 | 0 | 145 | 115 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 493 | 0 | 300 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 35 | 0 | 2.8 | 100 | 306 |  | 5245.9 | 2359.8 | 7605.7 | 3665 | 493 | 1909 | 793 | 586 | 70 | 0 | 72 | 17.7 | 0 | 92.7
10:00 | 72 | 0 | 0 | 0 | 343 | 0 | 0 | 351 | 335 |  | 0 | 360 | 150 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 232 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 2 | 0 | 0 | 100 | 325 | 235 | 188 | 26 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 74 | 103 | 50 | 22 | 1 | 60 | 54 | 51 | 48 | 130 | 142 | 65 | 81 | 0 | 20 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 16.17 | 0 | 0 | 0 | 145 | 115 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 |  | 494 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 91 | 0 | 190 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 422 | 0 | 0 | 0 | 0 | 40 | 0 | 3.8 | 70 | 303 |  | 5287.17 | 2342.8 | 7629.97 | 3634 | 494 | 1829 | 921 | 584 | 70 | 0 | 74 | 23.97 | 0 | 92.69
11:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 355 | 334 |  | 0 | 360 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 17 | 24 | 19 | 2 | 0 | 0 | 100 | 295 | 305 | 172 | 45 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 78 | 106 | 40 | 22 | 2.1 | 72 | 54 | 51 | 48 | 130 | 148 | 63 | 81 | 0 | 27 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 105 | 0 | 30 | 0 | 0 | 145 | 115 | 0 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 |  | 494 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 435 | 0 | 0 | 0 | 0 | 40 | 0 | 5.3 | 70 | 303 |  | 5401.7 | 2372.3 | 7774 | 3680 | 494 | 1885 | 972 | 583 | 70 | 0 | 78 | 12 | 0 | 92.69
12:00 | 72 | 0 | 0 | 0 | 355 | 0 | 0 | 353 | 345 |  | 0 | 360 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 209 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 26 | 26 | 19 | 2 | 0 | 0 | 100 | 360 | 355 | 186 | 45 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 78 | 142 | 50 | 22 | 2.2 | 88 | 54 | 51 | 48 | 130 | 149 | 63 | 82 | 0 | 27 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 105 | 19.17 | 30 | 0 | 0 | 145 | 115 | 0 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 |  | 492 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 404 | 0 | 0 | 0 | 0 | 35 | 0 | 5.3 | 70 | 302 |  | 5679.27 | 2351.3 | 8030.57 | 3924 | 492 | 1865 | 988 | 582 | 70 | 0 | 78 | 31.57 | 0 | 92.68
13:00 | 72 | 0 | 0 | 0 | 314 | 0 | 0 | 367 | 364 |  | 0 | 450 | 150 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 25 | 26 | 19 | 9 | 0 | 0 | 100 | 305 | 330 | 155 | 26 | 82 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 76 | 124 | 50 | 22 | 2 | 88 | 54 | 53 | 50 | 163 | 148 | 63 | 82 | 0 | 38 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 103 | 18.74 | 60 | 0 | 0 | 145 | 115 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 |  | 492 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 357 | 0 | 0 | 0 | 0 | 35 | 0 | 5.8 | 90 | 301 |  | 5707.44 | 2361.8 | 8069.24 | 3776 | 492 | 1963 | 1080 | 581 | 70 | 0 | 76 | 31.24 | 0 | 92.68
14:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 340 | 370 |  | 0 | 380 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 25 | 25 | 19 | 2 | 0 | 0 | 100 | 315 | 275 | 177 | 8 | 87 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 92 | 106 | 50 | 22 | 1.8 | 88 | 54 | 53 | 50 | 130 | 146 | 64 | 50 | 0 | 22 | 16 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 60 | 16.62 | 20 | 0 | 0 | 145 | 115 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 |  | 493 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 88 | 0 | 190 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 352 | 0 | 0 | 0 | 0 | 35 | 0 | 5.3 | 70 | 301 |  | 5279.12 | 2321.3 | 7600.42 | 3697 | 493 | 1774 | 867 | 579 | 70 | 0 | 92 | 28.42 | 0 | 92.68
15:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 339 | 314 |  | 0 | 380 | 150 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 12 | 24 | 19 | 2 | 0 | 0 | 100 | 315 | 275 | 185 | 8 | 90 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 86 | 105 | 50 | 20 | 1.3 | 88 | 54 | 53 | 47 | 130 | 149 | 63 | 50 | 0 | 14 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 69 | 12 | 10 | 0 | 0 | 145 | 115 | 0 | 0 | 2.9 | 33 | 0 | 0 | 0 | 0 |  | 492 | 0 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 90 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 375 | 0 | 0 | 0 | 0 | 20 | 0 | 4 | 50 | 303 |  | 5168.2 | 2249 | 7417.2 | 3671 | 492 | 1744 | 753 | 582 | 69 | 0 | 86 | 20.2 | 0 | 92.68
16:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 344 | 314 |  | 0 | 380 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 16 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 202 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 4 | 20 | 19 | 2 | 0 | 0 | 100 | 315 | 275 | 187 | 8 | 87 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 20 | 82 | 123 | 50 | 22 | 0.7 | 88 | 52 | 53 | 50 | 130 | 146 | 63 | 50 | 0 | 50 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 81 | 7 | 0 | 0 | 0 | 145 | 75 | 0 | 0 | 1.72 | 33 | 0 | 0 | 0 | 0 |  | 492 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 93 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 385 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 50 | 302 |  | 5115.42 | 2231 | 7346.42 | 3752 | 492 | 1765 | 592 | 584 | 68 | 0 | 82 | 11.42 | 0 | 92.67
17:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 342 | 313 |  | 0 | 380 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 34 | 25 | 16 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 2 | 0 | 0 | 100 | 315 | 275 | 184 | 8 | 80 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 25 | 20 | 82 | 123 | 50 | 22 | 0.2 | 88 | 53 | 53 | 50 | 130 | 148 | 65 | 50 | 0 | 46 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 83 | 2 | 0 | 0 | 0 | 145 | 75 | 0 | 0 | 0.36 | 33 | 0 | 0 | 0 | 0 |  | 480 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 90 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 303 |  | 5097.56 | 2162 | 7259.56 | 3770 | 480 | 1699 | 576 | 582 | 68 | 0 | 82 | 2.56 | 0 | 92.66
18:00 | 72 | 0 | 0 | 0 | 337 | 0 | 0 | 357 | 314 |  | 0 | 360 | 120 | 9 | 4 | 0 | 0 | 0 | 0 | 0 | 32 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 16 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 215 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 4 | 26 | 19 | 4 | 0 | 0 | 100 | 280 | 300 | 199 | 8 | 91 | 39 | 5 | 0 | 43 | 0 | 8 | 0 | 18 | 0 | 25 | 21 | 98 | 124 | 95 | 22 | 0 | 88 | 55 | 25 | 20 | 100 | 148 | 67 | 30 | 0 | 115 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 12 | 0 | 96 | 0 | 36 | 0 | 8 | 145 | 80 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 |  | 674 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 16 | 0 | 0 | 0 | 0 | 34 | 0 | 34 | 36 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 301 |  | 5453 | 2493 | 7946 | 3890 | 674 | 1629 | 930 | 581 | 68 | 76 | 98 | 0 | 0 | 92.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 0 | 0 | 315 | 0 | 0 | 351 | 364 |  | 0 | 400 | 150 | 70 | 28 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 46 | 48 | 19 | 14 | 0 | 0 | 100 | 320 | 325 | 193 | 8 | 91 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 110 | 125 | 95 | 22 | 0 | 88 | 54 | 53 | 45 | 163 | 148 | 67 | 82 | 0 | 115 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 145 | 0 | 90 | 0 | 32 | 145 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 |  | 771 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 331 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 303 |  | 6347 | 2866 | 9213 | 3957 | 771 | 1883 | 1740 | 583 | 68 | 101 | 110 | 0 | 0 | 92.65
19:30 | 72 | 0 | 0 | 0 | 313 | 65 | 0 | 342 | 367 |  | 0 | 400 | 150 | 92 | 30 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 60 | 50 | 19 | 17 | 0 | 0 | 100 | 315 | 320 | 183 | 8 | 91 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 110 | 126 | 95 | 22 | 0 | 85 | 66 | 53 | 50 | 163 | 149 | 67 | 82 | 0 | 116 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 149 | 0 | 90 | 0 | 38 | 145 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 |  | 771 | 0 | 215 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 21 | 0 | 0 | 0 | 0 | 40 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 305 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 301 |  | 6424 | 2800 | 9224 | 3910 | 771 | 1899 | 1794 | 580 | 69 | 91 | 110 | 0 | 0 | 0
20:00 | 72 | 0 | 0 | 0 | 320 | 82 | 0 | 340 | 365 |  | 0 | 400 | 150 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 25 | 50 | 19 | 25 | 0 | 0 | 100 | 310 | 320 | 189 | 8 | 88 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 110 | 125 | 95 | 22 | 0 | 86 | 66 | 53 | 50 | 163 | 147 | 67 | 82 | 0 | 115 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 142 | 0 | 50 | 0 | 20 | 145 | 115 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0 |  | 771 | 0 | 215 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 21 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 301 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 316 |  | 6350 | 2804 | 9154 | 3909 | 771 | 1923 | 1700 | 596 | 69 | 76 | 110 | 0 | 0 | 92.65
21:00 | 72 | 0 | 0 | 0 | 313 | 105 | 0 | 342 | 330 |  | 0 | 400 | 150 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 33 | 0 | 0 | 100 | 315 | 320 | 176 | 8 | 80 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 110 | 125 | 95 | 22 | 0 | 85 | 66 | 53 | 50 | 130 | 147 | 67 | 82 | 0 | 116 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 87 | 0 | 50 | 0 | 0 | 145 | 115 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 0 |  | 771 | 0 | 210 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 21 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 14 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 109 | 330 |  | 6195 | 2819 | 9014 | 3892 | 771 | 1909 | 1577 | 610 | 69 | 76 | 110 | 0 | 0 | 92.64
22:00 | 72 | 0 | 0 | 0 | 313 | 105 | 0 | 344 | 300 |  | 0 | 360 | 150 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 58 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 0 | 100 | 315 | 320 | 161 | 8 | 80 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 104 | 125 | 95 | 22 | 0 | 85 | 66 | 53 | 50 | 100 | 146 | 67 | 81 | 0 | 116 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 145 | 65 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 772 | 0 | 215 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 47 | 0 | 130 | 0 | 272 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 328 |  | 5689 | 2615 | 8304 | 3869 | 772 | 1819 | 1063 | 608 | 69 | 0 | 104 | 0 | 0 | 92.64
23:00 | 72 | 0 | 0 | 0 | 334 | 104 | 0 | 338 | 300 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 0 | 100 | 335 | 330 | 156 | 8 | 90 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 96 | 125 | 95 | 22 | 0 | 87 | 66 | 53 | 50 | 100 | 142 | 67 | 80 | 0 | 116 | 17 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 145 | 45 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 529 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 93 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 271 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 70 | 330 |  | 5407 | 2198 | 7605 | 3907 | 529 | 1761 | 630 | 613 | 69 | 0 | 96 | 0 | 0 | 92.63
24:00 | 72 | 0 | 0 | 0 | 313 | 107 | 0 | 351 | 360 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 33 | 20 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 200 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 315 | 305 | 157 | 8 | 84 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 88 | 126 | 95 | 22 | 0 | 87 | 66 | 51 | 50 | 130 | 142 | 68 | 80 | 0 | 116 | 17 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 145 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 288 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 80 | 0 | 190 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 130 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 |  | 5290 | 1851 | 7141 | 3816 | 288 | 1934 | 346 | 600 | 69 | 0 | 88 | 0 | 0 | 92.63
KWH | 1627000 | 0 | 1009000 | 0 | 7609791 | 440136 | 0 | 8546222 | 7791000 |  | 0 | 8951750 | 3684015 | 703680 | 69696 | 0 | 0 | 0 | 0 | 0 | 1035840 | 647280 | 0 | 0 | 0 | 0 | 0 | 868680 | 216411 | 0 | 345348 | 600000 | 698940 | 573600 | 598700 | 0 | 0 | 627840 | 964000 | 0 | 2900000 | 0 | 4804486 | 0 | 2952151 | 0 |  | 0 | 0 | 0 | 0 | 219840 | 361920 | 328464 | 394080 | 0 | 0 | 2213978 | 7625100 | 7341000 | 4374000 | 317818 | 2098460 | 802224 | 135840 | 0 | 838684 | 0 | 10224 | 0 | 338004 | 135540 | 438400 | 503260 | 2068800 | 2690360 | 1426560 | 507780 | 13400 | 1912000 | 1385640 | 901200 | 900864 | 3349636 | 3278000 | 1433088 | 1273920 | 0 | 1160670 | 230000 | 0 | 168660 | 7540750 | 322464 | 149352 | 0 | 0 | 0 | 0 | 729600 | 0 | 1454400 | 123795 | 388800 | 0 | 70254 | 3483000 | 1695600 | 0 | 0 | 31440 | 1114036 | 0 | 0 | 0 | 0 |  | 10493091 | 0 | 6744960 | 0 | 918720 | 0 | 0 | 0 | 0 | 0 | 0 | 2814000 | 329700 | 0 | 0 | 0 | 0 | 128458 | 0 | 184724 | 610550 | 0 | 0 | 0 | 0 | 383280 | 55296 | 239796 | 2177890 | 0 | 4611500 | 0 | 0 | 3930000 | 0 | 0 | 0 | 91925 | 0 | 1404800 | 0 | 8557672 | 0 | 0 | 0 | 0 | 661440 | 0 | 6668 | 1393152 | 7541100 |  | 126546471 | 53278722 | 179825193 | 90149578 | 10493091 | 42422211 | 18270474 | 14330490 | 1591840 | 323406 | 2068800 | 175303 | 0
Fuel Cost | 1822240 | 0 | 1079630 | 0 | 5631245.34 | 426931.92 | 0 | 6153279.84 | 5921160 |  | 0 | 7161400 | 3315613.5 | 7177536 | 754807.68 | 0 | 0 | 0 | 0 | 0 | 11497824 | 6576364.8 | 0 | 0 | 0 | 0 | 0 | 8330641.2 | 2064560.94 | 0 | 259011 | 450000 | 0 | 0 | 0 | 0 | 0 | 163238.4 | 250640 | 0 | 4437000 | 0 | 5044710.3 | 0 | 3749231.77 | 0 |  | 0 | 0 | 0 | 0 | 2090678.4 | 3387571.2 | 302186.88 | 1095542.4 | 0 | 0 | 2324676.9 | 5642574 | 6166440 | 4024080 | 311461.64 | 2790951.8 | 657823.68 | 139915.2 | 0 | 1199318.12 | 0 | 119825.28 | 0 | 344764.08 | 101655 | 828576 | 377445 | 14274720 | 2206095.2 | 13566585.6 | 517935.6 | 219760 | 2600320 | 1884470.4 | 1225632 | 1126080 | 4153548.64 | 3015760 | 2135301.12 | 2242099.2 | 0 | 1764218.4 | 365700 | 0 | 396351 | 5353932.5 | 241848 | 113507.52 | 0 | 0 | 0 | 0 | 7018752 | 0 | 14674896 | 1428594.3 | 3623616 | 0 | 658279.98 | 3274020 | 14870412 | 0 | 0 | 0 | 10271411.92 | 0 | 0 | 0 | 0 |  | 28331345.7 | 0 | 5261068.8 | 0 | 8856460.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2251200 | 511035 | 0 | 0 | 0 | 0 | 1431022.12 | 0 | 1828767.6 | 6331403.5 | 0 | 0 | 0 | 0 | 421608 | 91238.4 | 181525.572 | 13873159.3 | 0 | 18861035 | 0 | 0 | 3458400 | 0 | 0 | 0 | 146160.75 | 0 | 1236224 | 0 | 6247100.56 | 0 | 0 | 0 | 0 | 6177849.6 | 0 | 0 | 0 | 0 |  | 227396399.65 | 105496604.702 | 332893004.352 | 82695116.202 | 28331345.7 | 38170515.33 | 131245265.12 | 32734194.3 | 413878.4 | 3379615 | 14274720 | 1648354.3 | 0
Yesterday Day Peak | 72 | 0 | 0 | 0 | 355 | 0 | 0 | 353 | 345 |  | 0 | 360 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 25 | 25 | 25 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 209 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 26 | 26 | 19 | 2 | 0 | 0 | 100 | 360 | 355 | 186 | 45 | 91 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 25 | 20 | 78 | 142 | 50 | 22 | 2.2 | 88 | 54 | 51 | 48 | 130 | 149 | 63 | 82 | 0 | 27 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 60 | 0 | 105 | 19.17 | 30 | 0 | 0 | 145 | 115 | 0 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 |  | 492 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 21 | 3 | 11 | 90 | 0 | 190 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 404 | 0 | 0 | 0 | 0 | 35 | 0 | 5.3 | 70 | 302 |  | 8030.57 | DayPeak
Yesterday Evening Peak | 72 | 0 | 0 | 0 | 313 | 65 | 0 | 342 | 367 | 0 | 0 | 400 | 150 | 92 | 30 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 19 | 17 | 0 | 0 | 100 | 315 | 320 | 183 | 8 | 91 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 20 | 11 | 25 | 21 | 110 | 126 | 95 | 22 | 0 | 85 | 66 | 53 | 50 | 163 | 149 | 67 | 82 | 0 | 116 | 17 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 149 | 0 | 90 | 0 | 38 | 145 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 |  | 771 | 0 | 215 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 21 | 0 | 0 | 0 | 0 | 40 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 90 | 0 | 189 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 305 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 301 |  | 9224 | EvPeak
Forecast for Evening | 72 | 0 | 0 | 0 | 365 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 30 | 40 | 0 | 120 | 25 | 220 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 0 | 0 | 100 | 360 | 360 | 225 | 55 | 90 | 40 | 5 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 111 | 120 | 95 | 22 | 0 | 85 | 66 | 51 | 44 | 163 | 150 | 66 | 82 | 0 | 120 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 145 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 797 | 40 | 300 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 194 | 21 | 110 | 30 | 0 | 0 | 50 | 45 | 102 | 50 | 40 | 40 | 52 | 38 | 22 | 5 | 11 | 90 | 0 | 190 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 300
Forecast for Day | 72 | 0 | 0 | 0 | 365 | 100 | 0 | 412 | 330 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 30 | 40 | 0 | 120 | 25 | 220 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 360 | 360 | 225 | 55 | 90 | 40 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 101 | 100 | 95 | 22 | 1.6 | 85 | 66 | 51 | 44 | 163 | 150 | 66 | 82 | 0 | 120 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 90 | 0 | 100 | 145 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 501 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 110 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 5 | 11 | 90 | 0 | 190 | 0 | 0 | 210 | 0 | 0 |  | 95 | 80 | 225 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 300
Generation at 08:00(Today) | 72 | 0 | 0 | 0 | 322 | 103 | 0 | 346 | 300 | 0 | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 34 | 20 | 25 | 0 | 0 | 28 | 40 | 0 | 110 | 0 | 213 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 120 | 320 | 290 | 202 | 26 | 90 | 36 | 20 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 25 | 19 | 80 | 88 | 95 | 20 | 0.2 | 86 | 63 | 40 | 50 | 100 | 143 | 68 | 82 | 0 | 46 | 0 | 0 | 10 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 37 | 6.2 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 481 | 0 | 285 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 3 | 11 | 91 | 0 | 160 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 433 | 0 | 0 | 0 | 0 | 105 | 0 | 1.2 | 0 | 328 | 0
199
| Minimum Generation |  | 5670 | 4:00
| Highest Generation |  | 9224 | 19:30
| Day Peak Generation |  | 8030.57 | 12:00
| Evening Peak Generation |  | 9224 | 19:30
| HVDC Max Flow |  | 772 | 22:00
| HVDC EvPeak Flow |  | 771 | 19:30
| Load factor L.F |  | 81.23%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8030.57 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5734 | MW
Evening Peak Generation : |  | 9224 | MW Hour : | 19:30 | Available Max Generation : |  | 14885 | MW
E.P. Demand (at gen end) : |  | 9224 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 9224 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5485 | MW
Total Gen. (MKWH) : |  | 179.8252 | System Load Factor : | 81.23% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -469 | MW at | 7:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-12
Actual : | 92.57 | Ft.(MSL) , | Rule curve : | 95.46 | Ft.( MSL )
Gas Consumed : | Total = | 1097.37 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 120865631.532
: |  | Coal : | 32734194.3 | Oil : | 134624880.12 | Total : | 288224705.952
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3289.5986 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1113.8726 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 997.1424 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 900.7003 |  |  | 0 | 0%
) | 0 | 0:00 | 814.1164 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 656.9511 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 373.4768 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 169.3098 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 506.6439 |  |  | 0 | 0%
Total | 0 |  | 8821.8119 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2)Shajibazar 330 MW GT-1
3) Ghorasal Unit-3,4,5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,4
6) Sirajganj unit-2
7) Summit Meghnaghat GT-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar-Mirpur 132 kV Ckt-2 was under shut down from 10:03 to 17:26 for A/M.
b) Cumilla(S) 132/33 kV T-2 transformer was under shut down from 10:20 to 11:50 for A/M.
c) Cumilla(S) 132/33 kV T-3 transformer was under shut down from 10:50 to 13:14 for A/M.
d) Cumilla(S) 132/33 kV T-4 transformer was under shut down from 13:15 to 13:59 for A/M.
e) Sikalbaha 230/132 kV TR-1 transformer was under shut down from 08:31 to 13:14 for D/W.
f) Saidpur 132/33 kV T-5 transformer was under shut down from 09:05 to 17:09 for D/W.
g) Amnura 132/33 kV T-2 transformer was shut down at 09:37 for D/W.
h) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 09:00 to 17:10 for A/M.
i) Sikalbaha (O)-Sikalbaha(N) 132 kV Ckt-2 was under shut down from 09:12 to 10:27 for C/M.
j) Gallamari 132/33 kV T-2 transformer was under shut down from 10:06 to 12:50 for C/M.
k) Satkhira 132/33 kV T-2 transformer was under shut down from 08:21 to 12:15 for C/M.
l) Bibiyana 132/33 kV T-2 transformer was under shut down from 13:20 to 15:20 for C/M.
m) Tongi-Bashundhara 132 kV Ckt-1 was under shut down from 10:30 to 14:15 for D/W.
n) Tongi 230/132 kV TR-3 transformer was under shut down from 14:25 to 17:20 for D/W.
o) Palashbari 132/33 kV T-3 transformer was shut down at 13:40 for replacing Y-phase bus loop of |  |  |  |  | About 08 MW power interruption occurred under Palashbari substation
33 kV Vandabari feeder and was switched on at 15:20. |  |  |  |  | area from 13:40 to 15:20.
p) Biyanibazar 132/33 kV T-1 transformer was under shut down from 15:22 to 16:58 for C/M.
q) Madaripur 132/33 kV T-1 & T-2 transformers tripped at 15:30 showing line O/L at 132 kV end & O/C |  |  |  |  | About 32 MW power interruption occurred under Madaripur substation
relay at 33 kV end due to 33 kV Kalkini feeder fault and were switched on at 16:00 & 16:24 respectively. |  |  |  |  | area from 15:30 to 16:00.
r) Haripur-Meghnaghat 230 kV Ckt-1 tripped at 17:56 showing dist.Z1,AB at Haripur end & dist.Z2, 3-phase
at Meghnaghat end .
s) Mymensing RPCL ST was shut down at 00:46(12/2/20) due to maintenance work.
t) Barapukuria 230/132 kV T-6 transformer tripped at 02:43(12/2/20) due to 132 kV PT burst.
u) Hasnabad-Lalbagh 132 kV Ckt- tripped at 07:41(12/2/20) showing Z1,C-phase at Hasnabad end |  |  |  |  | About 38 MW power interruption occurred under Lalbagh substation
and was switched on at 08:16(12/02/20) |  |  |  |  | area from 07:41 to 08:16(12/2/20).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 72 | 1627000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 1009000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 313 | 7609791
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 65 | 440136 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8546222 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 367 | 7791000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8951750 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 92 | 703680 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3684015 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 30 | 69696 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 345348
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1035840
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 647280
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 868680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 216411
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1298940
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 573600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 598700 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1454400
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2415 | 47471489
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123795
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 361920
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 69 | 1591840 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4804486
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2952151 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 388800
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 328464
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 394080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 219840 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 200 | 1114036 | Transformer overload.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 967 | 15210852
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2213978 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4374000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7625100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7341000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 802224 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 135840 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 317818 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 838684
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 38 | 70254 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 10224 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2098460
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 338004
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 135540
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2068800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 438400 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 503260
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1329 | 29311586
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 2690360 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507780
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1426560
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 32 | 729600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1695600
| Mymensingh Area Total |  |  |  | 637 | 390 | 7063300
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 85 | 1912000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1385640
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3349636
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 149 | 3278000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 901200
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 900864
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 149352
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1433088 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1273920 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 116 | 1160670
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 230000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 322464
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7540750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 145 | 3483000 | Machine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 168660
| Sylhet Area Total |  |  |  | 1949 | 1323 | 27489244
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 771 | 10493091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 918720
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 6744960 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1101 | 18156771
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 329700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 138 | 2814000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 91925 | Reserve
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 301 | 7541100 | On test
| Barisal Area Total |  |  |  | 462 | 460 | 10776725
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 128458
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 610550
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 130 | 3930000 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 1404800 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 305 | 8557672 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 383280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 3 | 55296 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239796
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 184724 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1393152
| Rajshahi Area Total |  |  |  | 2183 | 851 | 16887728
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 90 | 2177890
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 189 | 4611500
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 109 | 661440
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 6668
| Rangpur Area Total |  |  |  | 605 | 388 | 7457498
| Total |  |  |  | 19107 | 9224 | 179825193
| Eastern Grid Total |  |  |  | 13543 | 6424 | 126546471
| Western Grid Total |  |  |  | 5564 | 2800 | 53278722
| National Grid Total |  |  |  | 19107 | 9224 | 179825193
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-11
(a) ENTIRE EASTERN GRID : |  | 5734 | MW | (b) ENTIRE WESTERN GRID : |  | 2908 | MW
i) Dhaka area |  | 3014 | MW | i) Khulna area |  | 1061 | MW
ii) Chittagong area |  | 898 | MW | ii) Rajshahi area |  | 963 | MW
iii) Comilla area |  | 750 | MW | iii) Barisal area |  | 217 | MW
iv) Mymensingh area |  | 753 | MW | iv) Rangpur area |  | 667 | MW
v) Sylhet area |  | 319 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8642 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 18:00 | Srimongal | 23 | 18:00 | Jhenida | 83 | 18:30
Munsiganj | 80 | 20:00 | Shahjibazar | 79 | 21:00 | Bottail | 96 | 18:30
Sonargaon | 58 | 18:30 | Fenchuganj | 24 | 19:30 | G.K Project | 38 | 18:30
Shyampur | 200 | 10:00 | Kulawara | 26 | 18:00 | Faridpur | 130 | 18:30
Bhulta | 150 | 12:00 | Sylhet | 97 | 20:00 | Madaripur | 59 | 21:00
Madanganj | 134 | 17:00 | Chatak | 18 | 18:30 | Sariatpur | 38 | 19:30
Shitalakhya | 102 | 12:00 | Sunamganj | 29 | 19:00 | Gopalganj | 66 | 19:00
Rahim steel | 23 | 12:00 | Biani Bazar | 33 | 19:30 | Bagerhat | 59 | 18:30
Matuail | 84 | 12:00 | Comilla (S) | 118 | 18:30 | Mongla | 36 | 10:00
Ghorasal | 62 | 19:30 | Comilla(N) | 75 | 19:00 | Satkhira | 70 | 19:00
Narsingdi | 117 | 20:00 | Chandpur | 65 | 20:00 | Gallamari | 39 | 13:00
Haripur (SBU) | 93 | 10:00 | Feni | 87 | 18:30 | Magura | 38 | 18:30
Ullon | 45 | 19:00 | Chowmuhani | 108 | 18:30 | Norail | 27 | 18:30
Hasnabad | 135 | 20:00 | Ashuganj | 36 | 21:00 | Chuadanga | 63 | 19:00
Magbazar | 72 | 16:00 | Daudkandi | 110 | 19:30 | Barisal(N) | 29 | 19:30
Maniknagar | 68 | 12:00 | B.Baria | 95 | 19:30 | Barisal (S) | 74 | 21:00
Bangabhaban | 22 | 12:00 | Ramganj | 56 | 18:30 | Patuakhali | 72 | 20:00
Narinda | 76 | 12:00 | Chaddagram | 24 | 13:00 | Bhandaria | 38 | 19:30
Dhanmondi | 94 | 13:00 | PHP | 3 | 13:00 | Borhan Uddin | 24 | 21:00
Lalbag | 45 | 12:00 | Madunaghat | 39 | 18:00 | Ishurdi | 32 | 18:30
Madartek | 43 | 19:00 | Hathazari | 64 | 19:30 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 146 | 13:00 | Natore | 93 | 19:00
Mirpur | 71 | 19:00 | Halishahar | 86 | 11:00 | Bogra | 140 | 19:00
Kalyanpur | 72 | 18:30 | Baraulia | 155 | 13:00 | Noagaon | 93 | 8:00
Gulshan | 90 | 18:00 | Sikalbaha | 24 | 18:30 | Rajshahi | 88 | 19:00
Uttara | 37 | 18:00 | Dohazari | 68 | 20:00 | Rajshahi New | 10 | 18:30
Uttara New | 31 | 18:30 | Cox'sbazar | 77 | 18:30 | C.Nawabganj | 65 | 19:00
Kamrangirchar | 75 | 13:00 | Chandraghona | 22 | 18:30 | Amnura | 32 | 18:30
Savar | 104 | 12:00 | Kaptai | 3.8 | 18:00 | Pabna | 74 | 19:00
Bhasantec | 104 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 86 | 19:30
Agargaon | 34 | 18:30 | Bakulia | 71 | 18:30 | Serajganj | 71 | 19:30
Satmosjid | 61 | 13:00 | Julda | 17 | 12:00 | Niyamatpur | 88 | 8:00
Tongi | 94 | 11:00 | TK chemical | 3 | 15:00 | Joypurhat | 51 | 19:00
Kabirpur | 159 | 19:30 | Modern Steel | 16 | 7:00 | Sherpur(Bogura) | 42 | 8:00
Basundhara | 82 | 13:00 | Shahmirpur | 21 | 15:00 | Mohastangor | 34 | 19:00
Manikganj | 68 | 18:30 | Khagrachhari | 18 | 18:30 | Rangpur | 121 | 19:00
Joydevpur | 163 | 18:30 | Matarbari | 23 | 18:30 | Lalmonirhat | 48 | 18:30
New Tongi | 75 | 18:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 96 | 19:00
Korda | 192 | 5:00 | Rangamati | 10 | 18:30 | Purbasadipur | 98 | 8:00
Dhamrai | 38 | 19:00 | Abul Khair 230 | 139 | 23:00 | Thakurgaon | 65 | 20:00
Valuka | 80 | 18:30 | BSRM | 152 | 20:00 | Palashbari | 106 | 18:30
Tangail | 133 | 19:30 | GPH Ispat | 12 | 11:00 | Barapukuria | 50 | 20:00
Mymensing | 178 | 19:00 | Goalpara | 21 | 19:00 | Panchagar | 41 | 18:30
Kishorganj | 90 | 21:00 | Central s/s | 63 | 19:00 | Joldhaka | 24 | 18:30
Netrokona | 95 | 8:00 | Noapara | 47 | 20:00 | Kurigram | 50 | 0.79167
Jamalpur | 108 | 8:00 | Jessore | 90 | 19:00
Sherpur | 88 | 19:30 | Benapol | 32 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-11 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 407 | 0.16667 | 399 | 0.66667 | Kaliakoir | 394 | 0.16667 | 382 | 0.5
Bheramara | 410 | 0.083333 | 396 | 0.79167 | Bhulta | 399 | 0.16667 | 388 | 0.66667
Ashuganj(N) | 402 | 0.16667 | 394 | 0.5 | Gopalganj | 411 | 0.041667 | 402 | 0.77083
Payra | 414 | 0.041667 | 408 | 0.83333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 238 | 0.41667 | Hathazari | 225 | 0.16667 | 221 | 0.5
Ishurdi | 240 | 0.083333 | 230 | 0.29167 | Megnaghat | 240 | 0.041667 | 234 | 0.33333
Ashuganj | 244 | 0.16667 | 240 | 0.33333 | Fenchuganj | 244 | 0.041667 | 241 | 0.66667
Serajganj | 235 | 0.083333 | 225 | 0.29167 | Siddhirganj | 237 | 0.16667 | 231 | 0.5
Baghabari | 245 | 0.083333 | 234 | 0.29167 | Maniknagar | 236 | 0.16667 | 229 | 0.5
Barapukuria | 236 | 0.16667 | 230 | 0.33333 | Old Airport | 237 | 0.125 | 228 | 0.5
Bogra | 228 | 0.041667 | 218 | 0.33333 | Barisal | 247 | 0.20833 | 236 | 0.77083
Khulna South | 240 | 0.70833 | 224 | 0.29167 | AKSML | 225 | 0.16667 | 217 | 0.66667
Rampura | 233 | 0.16667 | 230 | 0.375 | BSRM | 229 | 0.16667 | 219 | 0.5
Haripur | 235 | 0.875 | 230 | 0.375 | Bibiyana | 243 | 0.041667 | 238 | 0.66667
Hasnabad | 235 | 0.20833 | 227 | 0.625 | Bhulta | 238 | 0.20833 | 230 | 0.66667
Shyampur | 234 | 0.16667 | 227 | 0.5 | Ashuganj (S) | 236 | 0.20833 | 227 | 0.375
Aminbazar | 237 | 0.041667 | 229 | 0.5 | Kaliakoir | 240 | 0.16667 | 232 | 0.625
Tongi | 233 | 0.16667 | 227 | 0.45833 | GPH | 225 | 0.16667 | 218 | 0.5
Comilla (N) | 240 | 0.16667 | 235 | 0.66667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.16667 | 131 | 0.625 | Khulshi | 131 | 0.79167 | 126 | 0.5
Munsiganj | 136 | 0.75 | 132 | 0.5 | Halishahar | 134 | 0.875 | 128 | 0.41667
Sonargaon | 135 | 0.8125 | 131 | 0.29167 | Baraulia | 132 | 0.58333 | 128 | 0.625
Shyampur | 137 | 0.125 | 132 | 0.66667 | Sikalbaha | 134 | 0.8125 | 128 | 0.41667
Bhulta | 130 | 0.125 | 126 | 0.5 | Dohazari | 131 | 0.8125 | 127 | 0.375
Madanganj | 137 | 0.875 | 130 | 0.45833 | Cox'sbazar | 127 | 0.083333 | 121 | 0.75
Shitalakhya | 138 | 0.8125 | 131 | 0.5 | Chandraghona | 134 | 0.875 | 130 | 0.41667
Rahim steal | 136 | 4:00 | 132 | 0.5 | Kaptai | 134 | 0.8125 | 132 | 0.041667
Matuail | 135 | 0.125 | 131 | 0.5 | A. Khaer Stl. | 133 | 0.875 | 129 | 0.41667
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | Bakulia | 132 | 0.79167 | 127 | 0.41667
Narsinghdi | 135 | 0.75 | 130 | 0.41667 | Julda | 133 | 0.79167 | 127 | 0.41667
Haripur (SBU) | 136 | 0.16667 | 132 | 0.5 | TK Chemical | 133 | 0.79167 | 128 | 0.41667
Ullon | 131 | 0.16667 | 126 | 0.5 | Modern Steel | 132 | 0.79167 | 128 | 0.5
Hasnabad | 135 | 0.25 | 130 | 0.66667 | Shahmirpur | 132 | 0.79167 | 127 | 0.70833
Magbazar | 132 | 0.25 | 126 | 0.5 | Khagrachhari | 133 | 0.041667 | 129 | 0.41667
Maniknagar | 138 | 0.25 | 134 | 0.5 | Matarbari | 128 | 0.041667 | 123 | 0.77083
Bangabhaban | 138 | 0.25 | 134 | 0.5 | Baroiar Hat | 134 | 0.54167 | 131 | 0.625
Narinda | 138 | 0.25 | 134 | 0.5 | Rangamati | 133 | 0.041667 | 130 | 10:00
Dhanmondi | 131 | 0.16667 | 126 | 0.5 | Goalpara | 138 | 0.625 | 126 | 7:00
Lalbag | 138 | 0.20833 | 131 | 0.66667 | Central s/s | 138 | 0.91667 | 126 | 0.29167
Madartek | 131 | 0.20833 | 126 | 0.5 | Noapara | 135 | 0.70833 | 128 | 0.29167
Dhaka University |  |  |  |  | Jessore | 132 | 0.625 | 122 | 0.29167
Mirpur | 138 | 0.20833 | 130 | 0.5 | Benapol | 136 | 0.91667 | 125 | 0.33333
Kalyanpur | 139 | 0.20833 | 134 | 0.5 | Jhenida | 132 | 0.041667 | 122 | 0.77083
Gulshan | 131 | 0.20833 | 125 | 0.5 | Bottail | 136 | 0.125 | 129 | 0.33333
Uttara | 137 | 0.20833 | 130 | 0.5 | G.K Project | 139 | 0.041667 | 135 | 0.33333
Uttara New | 138 | 0.20833 | 129 | 0.5 | Faridpur | 138 | 0.125 | 132 | 0.77083
Kamrangirchar | 136 | 0.20833 | 128 | 0.5 | Madaripur | 140 | 0.041667 | 134 | 0.77083
Savar | 138 | 0.20833 | 130 | 0.5 | Sariatpur | 140 | 0.125 | 133 | 0.83333
Bhasantec | 137 | 0.20833 | 131 | 0.5 | Gopalganj | 142 | 0.16667 | 135 | 0.77083
Agargaon | 138 | 0.20833 | 132 | 0.5 | Bagerhat | 136 | 0.91667 | 126 | 0.77083
Satmosjid | 138 | 0.20833 | 132 | 0.5 | Mongla | 133 | 0.70833 | 125 | 0.77083
Tongi | 139 | 0.8125 | 133 | 0.625 | Satkhira | 138 | 0.91667 | 127 | 0.77083
Kabirpur | 136 | 3:00 | 130 | 0.5 | Gallamari | 138 | 0.91667 | 129 | 0.77083
Basundhara | 131 | 1:00 | 126 | 0.54167 | Magura | 135 | 0.083333 | 120 | 0.77083
Manikganj | 140 | 0.16667 | 133 | 0.625 | Norail | 134 | 0.083333 | 120 | 0.77083
Joydevpur | 143 | 0.25 | 138 | 0.79167 | Chuadanga | 131 | 0.083333 | 117 | 0.77083
New Tongi | 139 | 0.16667 | 131 | 0.66667 | Barisal(N) | 140 | 0.125 | 133 | 0.79167
Kodda | 135 | 0.8125 | 128 | 0.875 | Barisal (S) | 139 | 0.125 | 132 | 0.75
Dhamrai | 136 | 0.125 | 130 | 0.5 | Patuakhali | 137 | 0.125 | 128 | 0.77083
Valuka | 126 | 0.875 | 117 | 0.33333 | Bhandaria | 136 | 0.125 | 129 | 0.77083
Tangail | 131 | 0.125 | 124 | 0.5 | Ishurdi | 136 | 0.041667 | 131 | 0.29167
Mymensing | 128 | 0.70833 | 116 | 0.33333 | Ruppur Paromanobik | 136 | 0.041667 | 131 | 0.29167
Kishorganj | 130 | 0.083333 | 124 | 0.33333 | Natore | 133 | 0.75 | 125 | 0.29167
Netrokona | 128 | 0.75 | 113 | 0.33333 | Bogra | 133 | 15::00 | 125 | 0.29167
Jamalpur | 136 | 0.875 | 124 | 0.25 | Noagaon | 128 | 0.125 | 116 | 0.29167
Sherpur | 134 | 0.5 | 121 | 0.33333 | Rajshahi | 130 | 0.58333 | 121 | 0.29167
Srimongal | 140 | 0.041667 | 138 | 0.77083 | Rajshahi New | 130 | 0.16667 | 122 | 0.29167
Shahjibazar | 138 | 0.041667 | 135 | 0.77083 | C.Nawabganj | 128 | 14:0 | 117 | 0.29167
Fenchuganj | 139 | 0.54167 | 137 | 16:00 | Amnura | 130 | 0.75 | 116 | 0.29167
Khulawara | 138 | 0.041667 | 136 | 0.45833 | Pabna | 136 | 0.16667 | 129 | 0.375
Sylhet | 137 | 0.041667 | 135 | 0.625 | Shahjadpur | 140 | 0.041667 | 133 | 0.33333
Chatak | 137 | 1904-01-02 | 135 | 0.41667 | Serajganj | 136 | 0.083333 | 128 | 0.29167
Sunamganj | 136 | 0.041667 | 134 | 0.77083 | Niyamatpur | 127 | 0.083333 | 110 | 0.33333
Biani Bazar | 138 | 1904-01-02 | 135 | 0.75 | Joypurhat | 130 | 0.041667 | 115 | 0.33333
Comilla(s) | 133 | 0.16667 | 129 | 0.58333 | Sherpur(Bogura) | 136 | 0.16667 | 126 | 0.29167
Comilla(n) | 141 | 22:00 | 138 | 0.66667 | Mohastangor | 134 | 0.16667 | 124 | 0.29167
Chandpur | 138 | 0.41667 | 135 | 0.75 | Rangpur | 131 | 0.625 | 122 | 0.29167
Feni | 136 | 0.29167 | 131 | 0.75 | Lalmonirhat | 130 | 0.16667 | 117 | 0.33333
Chowmuhani | 134 | 0.33333 | 128 | 0.75 | Saidpur | 130 | 0.125 | 120 | 0.33333
Ashuganj | 139 | 0.041667 | 136 | 0.54167 | Purbasadipur | 127 | 0.083333 | 116 | 0.33333
Daudkandi | 136 | 0.29167 | 133 | 0.5 | Thakurgaon | 128 | 0.16667 | 119 | 0.54167
B.Baria | 135 | 1904-01-02 | 132 | 0.5 | Palashbari | 133 | 0.125 | 120 | 0.77083
Ramganj | 130 | 0.91667 | 128 | 0.79167 | Barapukuria | 136 | 0.16667 | 130 | 0.33333
Chaddagram | 137 | 0.29167 | 134 | 0.625 | Panchagar | 126 | 0.20833 | 114 | 0.54167
PHP | 133 | 0.33333 | 129 | 0.75 | Joldhaka | 131 | 0.125 | 118 | 0.33333
Madanhat | 135 | 0.8125 | 131 | 0.41667 | Kurigram | 132 | 0.083333 | 118 | 0.33333
Hathazari | 134 | 0.041667 | 131 | 0.41667

## L-Curve
Date | 2020-02-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 351 | 5290 | 1851 | 7141 |  |  |  | QF-LDC-12
0:30 | 294.5 | 4933.5 | 1812 | 6745.5 | Date: | 2020-02-11
1:00 | 238 | 4577 | 1773 | 6350
1:30 | 198.5 | 4490.5 | 1742.5 | 6233
2:00 | 159 | 4404 | 1712 | 6116
2:30 | 164.5 | 4313 | 1669 | 5982 | [5 empty] | Gen. at Eve. Peak | 9224 | 9224 MW (19:30 )
3:00 | 170 | 4222 | 1626 | 5848 | [6 empty] | 19:30
3:30 | 167.5 | 4173.5 | 1585.5 | 5759 | [5 empty] | Gen. at Day Peak | 8030.57 | 8030.57 MW (12:00 )
4:00 | 165 | 4125 | 1545 | 5670 | [6 empty] | 12:00
4:30 | 177.5 | 4132.5 | 1543 | 5675.5 | [5 empty] | Highest Generation | 9224
5:00 | 190 | 4140 | 1541 | 5681 | [6 empty] | 19:30
5:30 | 272 | 4315.5 | 1567 | 5882.5
6:00 | 354 | 4491 | 1593 | 6084
6:30 | 411.5 | 4679.865 | 1738.55 | 6418.415
7:00 | 469 | 4868.73 | 1884.1 | 6752.83
7:30 | 386.5 | 5099.015 | 2004.65 | 7103.665
8:00 | 304 | 5329.3 | 2125.2 | 7454.5
8:30 | 242 | 5287.6 | 2242.5 | 7530.1
9:00 | 180 | 5245.9 | 2359.8 | 7605.7
9:30 | 90 | 5266.535 | 2351.3 | 7617.835
10:00 | 0 | 5287.17 | 2342.8 | 7629.97
10:30 | 2 | 5344.435 | 2357.55 | 7701.985
11:00 | 4 | 5401.7 | 2372.3 | 7774
11:30 | 74.5 | 5540.485 | 2361.8 | 7902.285
12:00 | 145 | 5679.27 | 2351.3 | 8030.57
12:30 | 128 | 5693.355 | 2356.55 | 8049.905
13:00 | 111 | 5707.44 | 2361.8 | 8069.24
13:30 | 65.5 | 5493.28 | 2341.55 | 7834.83
14:00 | 20 | 5279.12 | 2321.3 | 7600.42
14:30 | 96 | 5223.66 | 2285.15 | 7508.81
15:00 | 172 | 5168.2 | 2249 | 7417.2
15:30 | 181 | 5141.81 | 2240 | 7381.81
16:00 | 190 | 5115.42 | 2231 | 7346.42
16:30 | 134 | 5106.49 | 2196.5 | 7302.99
17:00 | 78 | 5097.56 | 2162 | 7259.56
17:30 | 51.5 | 5275.28 | 2327.5 | 7602.78
18:00 | 25 | 5453 | 2493 | 7946
18:30 | 155 | 5900 | 2679.5 | 8579.5
19:00 | 285 | 6347 | 2866 | 9213
19:30 | 335 | 6424 | 2800 | 9224
20:00 | 305 | 6350 | 2804 | 9154 |  |  |  | Executive Engineer
20:30 | 212 | 6272.5 | 2811.5 | 9084 |  |  |  | Network Operation Division
21:00 | 119 | 6195 | 2819 | 9014
21:30 | 111 | 5942 | 2717 | 8659
22:00 | 103 | 5689 | 2615 | 8304 |  |  |  |  | Page 6 of 7
22:30 | 148 | 5548 | 2406.5 | 7954.5
23:00 | 193 | 5407 | 2198 | 7605
23:30 | 272 | 5348.5 | 2024.5 | 7373
24:00 | 351 | 5290 | 1851 | 7141
9224 MW (19:30 )
8030.57 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-11 |  | Energy | 179825193
[10 empty] | 2020-02-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3816 | 288 | 1934 | 630 | 600 | 69 | 0 | 0 | 88
0:30 | 3680 | 213.5 | 1809 | 427 | 603.5 | 69.5 | 0 | 0 | 85 | Date: | 2020-02-11
1:00 | 3544 | 139 | 1684 | 224 | 607 | 70 | 0 | 0 | 82
1:30 | 3475.5 | 138 | 1655.5 | 207 | 607.5 | 69.5 | 0 | 0 | 80 | [7 empty] | Total Energy | 179.8252 | Total Energy Gen 179.825 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 179.825 MKWHr
2:00 | 3407 | 137 | 1627 | 190 | 608 | 69 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3343.5 | 137.5 | 1578.5 | 182 | 595.5 | 69 | 0 | 0 | 76 | [7 empty] | Energy Requirement | 179.8252
3:00 | 3280 | 138 | 1530 | 174 | 583 | 69 | 0 | 0 | 74
3:30 | 3261.5 | 137.5 | 1459.5 | 174 | 584 | 68.5 | 0 | 0 | 74 | [6 empty] | Shortage
4:00 | 3243 | 137 | 1389 | 174 | 585 | 68 | 0 | 0 | 74
4:30 | 3252.5 | 137 | 1388.5 | 174 | 583.5 | 68 | 0 | 0 | 72
5:00 | 3262 | 137 | 1388 | 174 | 582 | 68 | 0 | 0 | 70
5:30 | 3389 | 136.5 | 1455 | 181 | 582 | 68 | 0 | 0 | 71
6:00 | 3516 | 136 | 1522 | 188 | 582 | 68 | 0 | 0 | 72
6:30 | 3663 | 251.5 | 1550.5 | 226 | 581.5 | 68 | 0 | 0 | 77 |  |  |  |  | Coal
7:00 | 3810 | 367 | 1579 | 264 | 581 | 68 | 0 | 0 | 82
7:30 | 3856.5 | 430.5 | 1684 | 400.5 | 581 | 68.5 | 0 | 0 | 77 |  |  |  | Oil |  |  |  | ,
8:00 | 3903 | 494 | 1789 | 537 | 581 | 69 | 0 | 0 | 72
8:30 | 3784 | 493.5 | 1849 | 665 | 583.5 | 69.5 | 0 | 0 | 72
9:00 | 3665 | 493 | 1909 | 793 | 586 | 70 | 0 | 0 | 72
9:30 | 3649.5 | 493.5 | 1869 | 857 | 585 | 70 | 0 | 0 | 73
10:00 | 3634 | 494 | 1829 | 921 | 584 | 70 | 0 | 0 | 74
10:30 | 3657 | 494 | 1857 | 946.5 | 583.5 | 70 | 0 | 0 | 76
11:00 | 3680 | 494 | 1885 | 972 | 583 | 70 | 0 | 0 | 78
11:30 | 3802 | 493 | 1875 | 980 | 582.5 | 70 | 0 | 0 | 78
12:00 | 3924 | 492 | 1865 | 988 | 582 | 70 | 0 | 0 | 78
12:30 | 3850 | 492 | 1914 | 1034 | 581.5 | 70 | 0 | 0 | 77
13:00 | 3776 | 492 | 1963 | 1080 | 581 | 70 | 0 | 0 | 76
13:30 | 3776 | 492 | 1963 | 1080 | 581 | 70 | 0 | 0 | 76
14:00 | 3776 | 492 | 1963 | 1080 | 581 | 70 | 0 | 0 | 76
14:30 | 3723.5 | 492 | 1853.5 | 916.5 | 581.5 | 69.5 | 0 | 0 | 81
15:00 | 3671 | 492 | 1744 | 753 | 582 | 69 | 0 | 0 | 86
15:30 | 3711.5 | 492 | 1754.5 | 672.5 | 583 | 68.5 | 0 | 0 | 84
16:00 | 3752 | 492 | 1765 | 592 | 584 | 68 | 0 | 0 | 82
16:30 | 3761 | 486 | 1732 | 584 | 583 | 68 | 0 | 0 | 82
17:00 | 3770 | 480 | 1699 | 576 | 582 | 68 | 0 | 0 | 82
17:30 | 3830 | 577 | 1664 | 753 | 581.5 | 68 | 38 | 0 | 90
18:00 | 3890 | 674 | 1629 | 930 | 581 | 68 | 76 | 0 | 98
18:30 | 3923.5 | 722.5 | 1756 | 1335 | 582 | 68 | 88.5 | 0 | 104
19:00 | 3957 | 771 | 1883 | 1740 | 583 | 68 | 101 | 0 | 110
19:30 | 3910 | 771 | 1899 | 1794 | 580 | 69 | 91 | 0 | 110
20:00 | 3909 | 771 | 1923 | 1700 | 596 | 69 | 76 | 0 | 110
20:30 | 3900.5 | 771 | 1916 | 1638.5 | 603 | 69 | 76 | 0 | 110
21:00 | 3892 | 771 | 1909 | 1577 | 610 | 69 | 76 | 0 | 110
21:30 | 3880.5 | 771.5 | 1864 | 1320 | 609 | 69 | 38 | 0 | 107
22:00 | 3869 | 772 | 1819 | 1063 | 608 | 69 | 0 | 0 | 104
22:30 | 3888 | 650.5 | 1790 | 846.5 | 610.5 | 69 | 0 | 0 | 100
23:00 | 3907 | 529 | 1761 | 630 | 613 | 69 | 0 | 0 | 96
23:30 | 3861.5 | 408.5 | 1847.5 | 630 | 606.5 | 69 | 0 | 0 | 92 | Max Temp. in Dhaka |  | 27° C
24:00 | 3816 | 288 | 1934 | 630 | 600 | 69 | 0 | 0 | 88
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 179.825 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 179.825 MKWHr
Note on W13: Author:

## Generation
2020-02-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 29 | 29 | 28 | 28 | 28 | 28 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 |  | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 627840
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.4 | 6.7 | 11.9 | 16.17 |  | 19.17 | 18.74 | 16.62 | 12 | 7 | 2 | [9 empty] | 123795
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 192 | 194 | 182 | 182 | 193 | 214 | 214 | 202 | 232 | 203 | 209 | 203 | 204 | 203 | 202 | 203 | 215 |  | 202 | 203 | 202 | 202 | 202 | 217 | 200 | 4804486
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 104 | 104 | 104 | 114 | 146 | 146 | 146 | 107 | 139 | 146 | 139 | 110 | 103 | 106 | 104 | 116 |  | 139 | 139 | 139 | 139 | 139 | 104 | 104 | 2952151
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [16 empty] | 0 | 8 | [8 empty] | 10224
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 45 | 45 | 26 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 317818
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1627000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 100 | 101 | 100 | 101 | 101 | 102 | 150 | 150 | [18 empty] | 1009000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 325 | 287 | 278 | 275 | 275 | 310 | 350 | 342 | 314 | 343 | 315 | 355 | 314 | 315 | 315 | 315 | 315 | 337 |  | 315 | 313 | 320 | 313 | 313 | 334 | 313 | 7609791
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 2213978
32 | Ashuganj 50 MW PP | 46 | 20 | 10 | 10 | 10 | 10 | 35 | 35 | 33 | 33 | 33 | 33 | 33 | 33 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 802224
33 | Ashuganj 225 MW CCPP | 171 | 179 | 175 | 173 | 166 | 184 | 185 | 202 | 187 | 188 | 172 | 186 | 155 | 177 | 185 | 187 | 184 | 199 |  | 193 | 183 | 189 | 176 | 161 | 156 | 157 | 4374000
34 | Ashuganj 450 MW CCPP(South) | 270 | 280 | 275 | 260 | 265 | 330 | 340 | 335 | 305 | 235 | 305 | 355 | 330 | 275 | 275 | 275 | 275 | 300 |  | 325 | 320 | 320 | 320 | 320 | 330 | 305 | 7341000
| Ashuganj 450 MW CCPP(North) | 265 | 280 | 270 | 260 | 265 | 335 | 335 | 330 | 295 | 325 | 295 | 360 | 305 | 315 | 315 | 315 | 315 | 280 |  | 320 | 315 | 310 | 315 | 315 | 335 | 315 | 7625100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 135840
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 90 | 91 | 91 | 82 | 87 | 90 | 87 | 80 | 91 |  | 91 | 91 | 88 | 80 | 80 | 90 | 84 | 2098460
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 326 | 296 | 326 | 340 | 361 | 371 | 371 | 364 | 351 | 355 | 353 | 367 | 340 | 339 | 344 | 342 | 357 |  | 351 | 342 | 340 | 342 | 344 | 338 | 351 | 8546222
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 380 | 320 | 320 | 320 | 360 | 380 | 380 | 400 | 360 | 360 | 360 | 450 | 380 | 380 | 380 | 380 | 360 |  | 400 | 400 | 400 | 400 | 360 | 360 | 420 | 8951750
41 | Haripur 360MW CCPP(HPL) | 363 | 363 | 300 | 260 | 260 | 310 | 310 | 330 | 363 | 335 | 334 | 345 | 364 | 370 | 314 | 314 | 313 | 314 |  | 364 | 367 | 365 | 330 | 300 | 300 | 360 | 7791000
42 | RPCL 210MW CCPP | 107 | 106 | 106 | 106 | 107 | 107 | 107 | 106 | 105 | 103 | 106 | 142 | 124 | 106 | 105 | 123 | 123 | 124 |  | 125 | 126 | 125 | 125 | 125 | 125 | 126 | 2690360
43
44 | Fenchugonj CCPP Phase-1 | 87 | 87 | 87 | 87 | 87 | 60 | 60 | 61 | 59 | 60 | 72 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 85 | 86 | 85 | 85 | 87 | 87 | 1912000
45 | Fenchugonj CCPP Phase-2 | 76 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 54 | 54 | 54 | 54 | 54 | 54 | 52 | 53 | 55 |  | 54 | 66 | 66 | 66 | 66 | 66 | 66 | 1385640
46 | Shajibazar 330 MW CCPP | 143 | 142 | 142 | 141 | 142 | 142 | 142 | 142 | 142 | 142 | 148 | 149 | 148 | 146 | 149 | 146 | 148 | 148 |  | 148 | 149 | 147 | 147 | 146 | 142 | 142 | 3278000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 69 | 67 | 65 | 63 | 63 | 63 | 64 | 63 | 63 | 65 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 68 | 1433088
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 78 | 78 | 81 | 81 | 82 | 82 | 50 | 50 | 50 | 50 | 30 |  | 82 | 82 | 82 | 82 | 81 | 80 | 80 | 1273920
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 9 | 9 | 9 | 9 | 10 | 10 | 15 | 20 | 20 | 20 | 27 | 27 | 38 | 22 | 14 | 50 | 46 | 115 |  | 115 | 116 | 115 | 116 | 116 | 116 | 116 | 1160670
51 | Sylhet 20 MW GTPP | 0 | [12 empty] | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 230000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 168660
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 5 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 149352
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 | 51 | 51 | 53 | 53 | 53 | 53 | 53 | 25 |  | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 901200
56 | Shahjahanulla 25 MW PP | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 322464
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 280 | 300 | 290 | 290 | 295 | 325 | 325 | 315 | 285 | 310 | 310 | 320 | 290 | 290 | 300 | 300 | 310 |  | 320 | 285 | 290 | 300 | 300 | 280 | 295 | 7540750
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 328464
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 345348
62 | Tangail 22 MW PP (Doreen) | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507780
63 | Impoprt (Tripura) | 82 | 78 | 74 | 74 | 70 | 72 | 82 | 72 | 72 | 74 | 78 | 78 | 76 | 92 | 86 | 82 | 82 | 98 |  | 110 | 110 | 110 | 110 | 104 | 96 | 88 | 2068800
64 | Malancha, Ctg. EPZ (United) | 26 | 22 | 30 | 31 | 31 | 37 | 36 | 10 | 2 | 2 | 2 | 2 | 9 | 2 | 2 | 2 | 2 | 4 |  | 14 | 17 | 25 | 33 | 40 | 41 | 42 | 394080
65 | Feni 22MW PP (Doreen) | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 338004
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 135540
67 | Jangalia 33MW PP (Summit) | [6 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 438400
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 33 | 28 | 28 | 28 | 28 | 30 | 33 | 33 | 33 | 25 | 25 | 25 | 32 | 32 | 34 | 16 |  | 25 | 28 | 25 | 32 | 33 | 33 | 33 | 698940
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 573600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598700
73 | Ghorashal 108MW PP (Regent) | [20 empty] | 65 | 82 | 105 | 105 | 104 | 107 | 440136
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 2 | 24 | 70 | 70 | 70 | 88 | 75 | 48 | 16 | 16 | 32 |  | 100 | 100 | 100 | 100 | 100 | 70 |  | 1035840
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 50 | 16 |  |  |  | 14 | 74 | 95 | 50 | 50 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1426560
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.23 | 1.1 | 2 | 3 | 4.6 | 4.9 | 4.7 | 4.7 | 2.9 | 1.72 | 0.36 | 0 | [8 empty] | 31440
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [17 empty] | 4 |  | 28 | 30 | 15 |  |  |  |  | 69696
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 120 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3684015
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 10 | 48 | 50 | 50 | 60 | 50 | 35 | 7 | 7 | 9 |  | 70 | 92 | 92 | 93 | 62 |  |  | 703680
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 50 | 48 | 48 | 48 | 48 | 50 | 50 | 47 | 50 | 50 | 20 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 900864
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 838684
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 2 | 24 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 102 |  | 102 | 102 | 102 | 102 | 58 |  |  | 647280
95 | Patenga 50MW PP (Baraka) | [8 empty] | 7 | 17 | 24 | 26 | 26 | 25 | 24 | 20 | 8 | 26 |  | 48 | 50 | 50 | 50 |  |  |  | 361920
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 17 | 26 | 25 | 25 | 12 | 4 |  | 4 |  | 46 | 60 | 25 |  |  |  |  | 219840
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 35 |  | 55 | 55 | 55 | 55 |  |  |  | 216411
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 130 | 100 |  | 163 | 163 | 163 | 130 | 100 | 100 | 130 | 3349636
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 1 | 1 | 2.1 | 2.2 | 2 | 1.8 | 1.3 | 0.7 | 0.2 | 0 | [8 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 868680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 43 | 60 | 60 | 60 | 60 | 24 | 7 | 7 | 7 | 12 |  | 32 | 32 | 32 | 32 |  |  |  | 729600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 10 | 32 | 77 | 100 | 105 | 105 | 103 | 60 | 69 | 81 | 83 | 96 |  | 145 | 149 | 142 | 87 | 67 | 47 | 24 | 1454400
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 30 | 30 | 60 | 20 | 10 |  |  | 36 |  | 90 | 90 | 50 | 50 |  |  |  | 388800
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 8 |  | 32 | 38 | 20 |  |  |  |  | 70254
118 | Bibiyana-III 400 MW CCPP | 145 | 145 | 145 | 145 | 144 | 144 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 |  | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 3483000
| Jamalpur 115 MW PP (United) | [6 empty] | 6 | 90 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 75 | 75 | 80 |  | 115 | 115 | 115 | 115 | 65 | 45 | 24 | 1695600
| Anwara 300 MW PP (United) | [14 empty] | 33 | 33 | 33 | 100 |  | 200 | 200 | 217 | 217 | 161 | 70 | 0 | 1114036
120 | Eastern Zone Total | 4577 | 4404 | 4222 | 4125 | 4140 | 4491 | 4868.73 | 5329.3 | 5245.9 | 5287.17 | 5401.7 | 5679.27 | 5707.44 | 5279.12 | 5168.2 | 5115.42 | 5097.56 | 5453 | 0 | 6347 | 6424 | 6350 | 6195 | 5689 | 5407 | 5290 | 126546471
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 32 | 55 | 66 | 66 | 66 | 83 | 49 | 37 | 16 | 16 | 16 |  | 115 | 115 | 115 | 115 | 83 | 16 | 0 | 918720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [22 empty] | 14 | 47 | 13 | 13 | 91925
| Bhola 225 MW CCPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 140 | 138 | 141 | 143 | 133 | 143 | 144 | 2814000
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 14 | 14 | 13 | 15 | 14 | 13 | 12 | 6 | 6 | 6 | 7 | 7 | 13 | 11 | 12 | 16 |  | 20 | 21 | 21 | 21 | 20 | 18 | 17 | 329700
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 139 | 137 | 138 | 137 | 137 | 136 | 367 | 494 | 493 | 494 | 494 | 492 | 492 | 493 | 492 | 492 | 480 | 674 |  | 771 | 771 | 771 | 771 | 772 | 529 | 288 | 10493091
147 | Bheramara 410 MW CCPP | 310 | 280 | 220 | 220 | 220 | 270 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 285 |  | 245 | 215 | 215 | 210 | 215 | 215 | 215 | 6744960
148 | Payra 1320 MW | 328 | 327 | 302 | 303 | 302 | 302 | 300 | 300 | 306 | 303 | 303 | 302 | 301 | 301 | 303 | 302 | 303 | 301 |  | 303 | 301 | 316 | 330 | 328 | 330 | 330 | 7541100
149
150 | Barapukuria TPP Unit-1 | 90 | 91 | 91 | 91 | 90 | 90 | 91 | 91 | 90 | 91 | 90 | 90 | 90 | 88 | 90 | 93 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 93 | 80 | 2177890
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 189 | 190 | 190 | 191 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 189 | 189 | 189 | 190 |  | 190 | 189 | 190 | 190 | 190 | 190 | 190 | 4611500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 34 |  | 50 | 40 | 25 | 25 | 0 |  |  | 128458
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 150 | 150 | 130 | 130 | 130 | 160 | 160 | 160 | 160 | 170 | 190 | 200 | 200 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3930000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [9 empty] | 1 | 7 | 6 | 16 | 36 | 77 | 102 | 116 | 116 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1404800
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 397 | 398 | 397 | 335 | 335 | 336 | 335 | 334 | 420 | 422 | 435 | 404 | 357 | 352 | 375 | 385 | 319 | 359 |  | 331 | 305 | 301 | 300 | 272 | 271 | 278 | 8557672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 383280
163 | Bogura 20 MW PP (Energyprima) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 55296
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239796
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 24 | 12 | 12 | 36 |  | 50 | 50 | 50 | 40 | 25 | 12 | 0 | 610550
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 34 |  | 51 | 51 | 51 | 51 | 0 |  |  | 184724
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 25 | 100 | 70 | 70 | 70 | 90 | 70 | 50 | 50 | 50 | 66 |  | 109 | 109 | 109 | 109 | 109 | 70 | 0 | 1393152
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 12 | 35 | 40 | 40 | 35 | 35 | 35 | 20 | 2 | 0 |  |  | 105 | 109 | 113 | 114 | 35 | 2 | 0 | 661440
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 1.2 | 2.8 | 3.8 | 5.3 | 5.3 | 5.8 | 5.3 | 4 | 2 | 0 | 0 |  | 0 | [6 empty] | 6668
178
178