## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-17 | Monday
|  | Date (day): | 2020-02-17 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11679.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14345 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-16 | 2020-02-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 100 | 100 | 80 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 300 | 320 | 320
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 349 | 330 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 360 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 120 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 65 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 36 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 30 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 90 | 150 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 2 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1821 | 2314 | 3258 | 3860 | 1071 | 800
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15.3 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 71 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 104 | 145 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 22 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 86 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.7 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 87 | 198 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 668 | 1030 | 1510 | 1645 | 400 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 80 | 100 | 100 | 34 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 290 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 280 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 40 | 40
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 20 | 20 | 20 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 24 | 26 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 120 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 57 | ST under shut down
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 114 | 104 | 113
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 0 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1348 | 1360 | 1650 | 2323 | 535 | 65
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 104 | 100 | 110 | 92 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.5 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 120 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 308.5 | 456 | 433.6 | 542 | 92 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 88 | 88 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 73 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 152 | 145 | 150 | 150 |  | 110 | GT-2 shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 63 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 78 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 67 | 128 | 128
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 988 | 1081 | 1246 | 1246 | 0 | 510
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 526 | 771 | 540 | 775
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 180 | 330 | 330 | 80 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 858 | 1066 | 1148 | 1934 | 80 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 9 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 85 | 84 | 85 | 84 |  | 68 | GT-1 under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 42 | 97 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 453 | 548 | 300 | 300 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 593 | 738 | 570 | 639 | 0 | 81
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 130 | 140 | 140 | 70 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 225 | 225 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 433 | 300 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 51 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 748 | 696 | 1383 | 1649 | 461 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 89 | 90 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 270 | 270
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 76 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.1 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 348.1 | 386 | 481 | 507 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7680.6 | 9127 | 11679.6 | 14345 | 2639 | 1666
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7321.2688 | 8700 | 11133.1785 | 13673.8797
A. |  | 2020-02-16 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9127 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5738 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9127 | MW
3 | Day peak Generation : |  |  | 7680.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8700 | MW
4 | Evening peak Generation : |  |  | 9127 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 177.7565 | MKWHr | By Solar | 0.18418 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 125.849 | MKWHr |  | By Oil: | 20.3573 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.6606 | MKWHr |  | By Hydro: | 1.5881 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2639 | MW | Dhaka | 3116 | 3116 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1666 | MW | Chittagong | 942 | 942 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4305 | MW | Khulna | 1034 | 1034 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1016.2 | MMCFD |  |  | Rajshahi | 940 | 940 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 115320747.796 | ii) Oil : | Taka | 153979407.86 | Comilla | 735 | 735 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 35285873.32 | Total | Taka | 304586028.976 | Mymensingh | 722 | 722 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.596 | MKWHr. | Sylhet | 333 | 333 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -236 | MW (E to W) at | 19:00 | hrs | Barisal | 216 | 216 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -242 | MW at | 8:00 | hrs | Rangpur | 662 | 662 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.7° C |  |  | Total | 8700 | 8700 |  | 0
B. |  | 2020-02-17 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 29.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14345 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 4845 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 185.021 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5693 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.0196 | MKWHr. | ii) HVDC Flow at Peak Time |  | 771 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0976 | MKWHr. | iii) Maximum HVDC Flow : |  | 772 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.89 |  | (b) Today: | 91.74 |  | (c) Rule Curve: |  | 94.76
.

## YesterdayGen
2020-02-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 0 | 0 | 0 | 300 | 0 | 0 | 337 | 367 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 216 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 315 | 315 | 185 | 8 | 90 | 42 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 18 | 80 | 72 | 50 | 22 | 0 | 88 | 73 | 5 | 5 | 130 | 147 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 135 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 8 | 90 | 0 | 220 | 0 | 0 | 220 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 |  | 4527 | 1879 | 6406 | 3447 | 135 | 1787 | 302 | 587 | 68 | 0 | 80 | 0 | 0 | 91.94
2:00 | 72 | 0 | 0 | 0 | 304 | 0 | 0 | 339 | 367 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 215 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 320 | 320 | 175 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 80 | 94 | 50 | 22 | 0 | 88 | 61 | 5 | 5 | 130 | 150 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 131 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 90 | 0 | 220 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 |  | 4393 | 1760 | 6153 | 3357 | 131 | 1735 | 220 | 562 | 68 | 0 | 80 | 0 | 0 | 91.93
3:00 | 72 | 0 | 0 | 0 | 302 | 0 | 0 | 350 | 327 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 275 | 280 | 178 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 78 | 94 | 50 | 22 | 0 | 88 | 61 | 5 | 5 | 130 | 152 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 130 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 90 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 |  | 4185 | 1721 | 5906 | 3253 | 130 | 1639 | 178 | 560 | 68 | 0 | 78 | 0 | 0 | 91.92
4:00 | 72 | 0 | 0 | 0 | 310 | 0 | 0 | 346 | 307 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 275 | 280 | 176 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 76 | 94 | 50 | 22 | 0 | 88 | 61 | 5 | 5 | 130 | 154 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 131 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 90 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 |  | 4166 | 1685 | 5851 | 3264 | 131 | 1571 | 178 | 561 | 70 | 0 | 76 | 0 | 0 | 91.91
5:00 | 72 | 0 | 0 | 0 | 300 | 0 | 0 | 340 | 277 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 265 | 265 | 166 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 76 | 94 | 50 | 22 | 0 | 88 | 61 | 5 | 5 | 130 | 157 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 132 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 90 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 |  | 4083 | 1655 | 5738 | 3191 | 132 | 1530 | 178 | 561 | 70 | 0 | 76 | 0 | 0 | 91.9
6:00 | 72 | 0 | 0 | 0 | 330 | 0 | 0 | 355 | 275 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 216 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 295 | 285 | 196 | 8 | 90 | 10 | 5 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 20 | 18 | 76 | 106 | 50 | 22 | 0 | 88 | 61 | 20 | 11 | 163 | 147 | 45 | 81 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 151 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 90 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 |  | 4347 | 1705 | 6052 | 3347 | 151 | 1646 | 184 | 578 | 70 | 0 | 76 | 0 | 0 | 91.89
7:00 | 72 | 0 | 0 | 0 | 320 | 0 | 0 | 343 | 275 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 20 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 80 | 340 | 290 | 200 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 18 | 82 | 106 | 50 | 22 | 0 | 88 | 61 | 48 | 50 | 163 | 159 | 57 | 79 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0.5 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 |  | 524 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 11 | 91 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 5 | 285 |  | 4600.63 | 2128.1 | 6728.73 | 3463 | 524 | 1726 | 267 | 596 | 70 | 0 | 82 | 0.73 | 0 | 91.88
8:00 | 72 | 0 | 0 | 0 | 324 | 0 | 0 | 363 | 357 |  | 0 | 472 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 32 | 20 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 208 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 135 | 315 | 310 | 181 | 8 | 89 | 36 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 74 | 107 | 50 | 22 | 0.2 | 88 | 73 | 48 | 50 | 163 | 151 | 67 | 79 | 0 | 0 | 0 | 0 | 8 | 320 | 23 | 8 | 0 | 0 | 0 | 0 | 14 | 0 | 52 | 2.3 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0.6 | 85 | 0 | 0 | 0 | 0 |  | 524 | 0 | 330 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 91 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 35 | 0 | 0.7 | 70 | 317 |  | 5174.1 | 2359.7 | 7533.8 | 3552 | 524 | 2008 | 676 | 628 | 68 | 0 | 74 | 3.8 | 0 | 91.88
9:00 | 72 | 0 | 0 | 0 | 325 | 0 | 0 | 335 | 300 |  | 0 | 472 | 150 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 209 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 275 | 290 | 165 | 8 | 89 | 33 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 76 | 107 | 50 | 0 | 0.7 | 85 | 73 | 48 | 50 | 163 | 149 | 66 | 40 | 0 | 0 | 0 | 0 | 8 | 280 | 23 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 96 | 7.8 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1.5 | 98 | 0 | 0 | 0 | 0 |  | 524 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 40 | 0 | 1.8 | 109 | 351 |  | 5068 | 2449.8 | 7517.8 | 3394 | 524 | 1887 | 896 | 661 | 68 | 0 | 76 | 11.8 | 0 | 91.87
10:00 | 72 | 0 | 0 | 0 | 331 | 0 | 0 | 358 | 360 |  | 0 | 225 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 209 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 0 | 100 | 320 | 320 | 184 | 24 | 90 | 36 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 72 | 105 | 40 | 0 | 1.2 | 86 | 73 | 48 | 50 | 163 | 147 | 65 | 50 | 0 | 0 | 0 | 0 | 8 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 89 | 15.1 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 3.5 | 68 | 0 | 0 | 0 | 0 |  | 524 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 90 | 0 | 221 | 0 | 0 | 185 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 36 | 0 | 3 | 50 | 403 |  | 5004.8 | 2518 | 7522.8 | 3560 | 524 | 1802 | 760 | 714 | 68 | 0 | 72 | 22.8 | 0 | 91.87
11:00 | 72 | 0 | 0 | 0 | 325 | 0 | 0 | 336 | 360 |  | 0 | 225 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 215 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 2 | 0 | 0 | 100 | 320 | 310 | 182 | 24 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 80 | 104 | 50 | 0 | 1.5 | 87 | 73 | 48 | 47 | 130 | 147 | 64 | 50 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 90 | 18.5 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 4.4 | 70 | 0 | 0 | 0 | 0 |  | 524 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 12 | 11 | 89 | 0 | 220 | 0 | 0 | 200 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 35 | 0 | 3.7 | 50 | 443 |  | 4992.4 | 2561.7 | 7554.1 | 3515 | 524 | 1774 | 811 | 752 | 70 | 0 | 80 | 28.1 | 0 | 91.86
12:00 | 72 | 0 | 0 | 0 | 350 | 0 | 0 | 349 | 320 |  | 0 | 225 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 3 | 0 | 0 | 100 | 330 | 330 | 201 | 24 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 84 | 102 | 50 | 0 | 1.5 | 89 | 73 | 45 | 47 | 130 | 152 | 63 | 50 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 90 | 15.3 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 4.7 | 87 | 0 | 0 | 0 | 0 |  | 526 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 89 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 35 | 0 | 4.1 | 60 | 453 |  | 5133.5 | 2547.1 | 7680.6 | 3601 | 526 | 1749 | 863 | 762 | 70 | 0 | 84 | 25.6 | 0 | 91.86
13:00 | 72 | 0 | 0 | 0 | 326 | 0 | 0 | 350 | 320 |  | 0 | 225 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 18 | 8 | 0 | 0 | 100 | 310 | 310 | 115 | 24 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 82 | 92 | 50 | 0 | 1.5 | 86 | 73 | 48 | 47 | 130 | 152 | 64 | 50 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 108 | 19 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 4.2 | 89 | 0 | 0 | 0 | 0 |  | 527 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 89 | 0 | 220 | 0 | 0 | 200 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 35 | 0 | 4.1 | 90 | 453 |  | 5090.7 | 2621.1 | 7711.8 | 3483 | 527 | 1764 | 994 | 762 | 71 | 0 | 82 | 28.8 | 0 | 91.85
14:00 | 72 | 0 | 0 | 0 | 299 | 0 | 0 | 368 | 300 |  | 0 | 225 | 120 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 24 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 217 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 18 | 7 | 0 | 0 | 100 | 300 | 305 | 184 | 26 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 33 | 14 | 84 | 92 | 50 | 0 | 1 | 89 | 73 | 17 | 20 | 163 | 151 | 63 | 20 | 0 | 0 | 0 | 0 | 10 | 320 | 24 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 85 | 17.61 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 3.7 | 89 | 0 | 0 | 0 | 0 |  | 526 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 70 | 454 |  | 4953.31 | 2521.6 | 7474.91 | 3465 | 526 | 1685 | 854 | 764 | 71 | 0 | 84 | 25.91 | 0 | 91.85
15:00 | 72 | 0 | 0 | 0 | 299 | 0 | 0 | 353 | 320 |  | 0 | 225 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 202 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 3 | 0 | 0 | 100 | 320 | 280 | 165 | 26 | 91 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 33 | 14 | 84 | 92 | 50 | 0 | 0.4 | 87 | 73 | 19 | 20 | 130 | 151 | 45 | 20 | 0 | 0 | 17 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 70 | 13.32 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 2.8 | 90 | 0 | 0 | 0 | 0 |  | 528 | 0 | 275 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 89 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 70 | 468 |  | 4818.52 | 2513.6 | 7332.12 | 3365 | 528 | 1653 | 835 | 777 | 71 | 0 | 84 | 19.12 | 0 | 91.84
16:00 | 72 | 0 | 0 | 0 | 300 | 0 | 0 | 300 | 290 |  | 0 | 225 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 5 | 0 | 0 | 100 | 325 | 280 | 163 | 26 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 78 | 92 | 50 | 0 | 0.3 | 86 | 73 | 20 | 30 | 130 | 145 | 45 | 30 | 0 | 0 | 17 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 55 | 0 | 100 | 7.6 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1.51 | 122 | 0 | 0 | 0 | 0 |  | 527 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 88 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 70 | 385 |  | 4841.41 | 2300.6 | 7142.01 | 3259 | 527 | 1575 | 928 | 693 | 71 | 0 | 78 | 11.01 | 0 | 91.84
17:00 | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 341 | 270 |  | 0 | 225 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 18 | 14 | 0 | 0 | 80 | 285 | 280 | 165 | 26 | 90 | 39 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 86 | 103 | 42 | 22 | 0.1 | 86 | 73 | 20 | 20 | 100 | 155 | 45 | 10 | 0 | 0 | 17 | 0 | 10 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 55 | 0 | 102 | 2.19 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0.43 | 125 | 0 | 0 | 0 | 0 |  | 528 | 0 | 200 | 0 | 69 | 0 | 0 | 0 | 0 | 4 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 89 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 70 | 444 |  | 4836.72 | 2314.6 | 7151.32 | 3332 | 528 | 1446 | 928 | 753 | 71 | 4 | 86 | 3.32 | 0 | 91.83
18:00 | 72 | 0 | 102 | 0 | 300 | 0 | 0 | 345 | 270 |  | 0 | 225 | 120 | 28 | 10 | 13 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 42 | 0 | 22 | 25 | 16 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 22 | 12 | 18 | 18 | 0 | 0 | 80 | 280 | 280 | 184 | 26 | 90 | 39 | 10 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 26 | 0 | 112 | 103 | 95 | 22 | 0 | 86 | 73 | 35 | 30 | 100 | 150 | 45 | 30 | 0 | 16 | 17 | 0 | 10 | 285 | 24 | 0 | 0 | 2 | 0 | 0 | 96 | 0 | 106 | 0 | 72 | 0 | 13 | 0 | 115 | 28 | 0 | 0 | 193 | 0 | 0 | 0 | 0 |  | 674 | 0 | 185 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 88 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 335 | 0 | 0 | 3 | 0 | 70 | 0 | 0 | 70 | 513 |  | 5433 | 2650 | 8083 | 3348 | 674 | 1468 | 1488 | 821 | 71 | 101 | 112 | 0 | 0 | 91.83
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 330 | 360 |  | 0 | 225 | 120 | 100 | 65 | 36 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 145 | 0 |  | 0 | 0 | 17 | 0 | 86 | 50 | 18 | 22 | 0 | 0 | 80 | 290 | 280 | 184 | 26 | 90 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 114 | 104 | 95 | 22 | 0 | 88 | 73 | 53 | 50 | 130 | 145 | 65 | 78 | 0 | 67 | 17 | 0 | 10 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 150 | 0 | 100 | 0 | 120 | 0 | 115 | 2 | 0 | 0 | 198 | 0 | 0 | 0 | 0 |  | 771 | 0 | 180 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 9 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 109 | 548 |  | 6241 | 2886 | 9127 | 3467 | 771 | 1723 | 2022 | 858 | 71 | 101 | 114 | 0 | 0 | 91.82
19:30 | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 338 | 363 |  | 0 | 225 | 120 | 100 | 50 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 91 | 50 | 18 | 26 | 0 | 0 | 80 | 310 | 285 | 192 | 26 | 90 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 112 | 104 | 95 | 22 | 0 | 88 | 73 | 53 | 50 | 163 | 150 | 65 | 78 | 0 | 67 | 17 | 0 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 |  | 771 | 0 | 190 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 9 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 91 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 109 | 550 |  | 6162 | 2922 | 9084 | 3506 | 771 | 1802 | 1860 | 861 | 71 | 101 | 112 | 0 | 0 | 0
20:00 | 72 | 0 | 95 | 0 | 300 | 0 | 0 | 339 | 364 |  | 0 | 225 | 120 | 100 | 50 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 91 | 50 | 18 | 30 | 0 | 0 | 80 | 320 | 305 | 184 | 26 | 92 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 116 | 107 | 95 | 22 | 0 | 85 | 73 | 53 | 50 | 163 | 144 | 66 | 78 | 0 | 68 | 17 | 0 | 10 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 772 | 0 | 210 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 91 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 549 |  | 6164 | 2951 | 9115 | 3550 | 772 | 1779 | 1866 | 860 | 71 | 101 | 116 | 0 | 0 | 0
21:00 | 72 | 0 | 99 | 0 | 330 | 0 | 0 | 347 | 364 |  | 0 | 225 | 150 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 18 | 35 | 0 | 0 | 100 | 320 | 320 | 185 | 26 | 91 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 112 | 94 | 95 | 22 | 0 | 85 | 73 | 53 | 50 | 163 | 145 | 65 | 78 | 0 | 68 | 17 | 0 | 10 | 275 | 24 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 0 | 70 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 772 | 0 | 245 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 547 |  | 5901 | 2943 | 8844 | 3641 | 772 | 1779 | 1568 | 857 | 71 | 44 | 112 | 0 | 0 | 91.81
22:00 | 72 | 0 | 101 | 0 | 302 | 0 | 0 | 339 | 365 |  | 0 | 225 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 33 | 0 | 0 | 100 | 325 | 320 | 183 | 26 | 90 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 102 | 106 | 95 | 22 | 0 | 85 | 73 | 53 | 50 | 163 | 147 | 65 | 79 | 0 | 68 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 |  | 771 | 0 | 275 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 109 | 484 |  | 5580 | 2759 | 8339 | 3664 | 771 | 1791 | 1130 | 794 | 71 | 16 | 102 | 0 | 0 | 0
23:00 | 72 | 0 | 101 | 0 | 322 | 0 | 0 | 341 | 367 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 69 | 0 | 0 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 0 | 0 | 100 | 320 | 315 | 184 | 26 | 91 | 36 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 98 | 107 | 95 | 22 | 0 | 88 | 73 | 53 | 50 | 163 | 150 | 66 | 79 | 0 | 128 | 17 | 0 | 10 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 |  | 529 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 398 |  | 5328 | 2245 | 7573 | 3722 | 529 | 1755 | 692 | 708 | 69 | 0 | 98 | 0 | 0 | 0
24:00 | 72 | 0 | 102 | 0 | 301 | 0 | 0 | 348 | 370 |  | 0 | 225 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 68 | 0 | 0 | 120 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 0 | 100 | 310 | 310 | 183 | 26 | 90 | 39 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 0 | 92 | 107 | 90 | 22 | 0 | 85 | 73 | 53 | 50 | 163 | 147 | 67 | 79 | 0 | 128 | 17 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 287 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 353 |  | 5188 | 1983 | 7171 | 3724 | 287 | 1787 | 549 | 664 | 68 | 0 | 92 | 0 | 0 | 0
KWH | 1687000 | 0 | 751000 | 0 | 7429709 | 0 | 0 | 8386560 | 7852000 |  | 0 | 6795250 | 3326051 | 535680 | 149736 | 80505 | 0 | 0 | 0 | 0 | 1286400 | 635616 | 0 | 0 | 0 | 0 | 0 | 815760 | 162872 | 0 | 326916 | 600000 | 709920 | 624400 | 622800 | 0 | 0 | 1588091 | 0 | 0 | 2900000 | 0 | 4982382 | 0 | 2443489 | 0 |  | 0 | 0 | 46370 | 0 | 234240 | 258240 | 427584 | 554880 | 0 | 0 | 2193942 | 7715900 | 7405500 | 4454000 | 485090 | 2124920 | 730584 | 453600 | 0 | 886260 | 0 | 38056 | 0 | 391860 | 147960 | 592000 | 292580 | 2097600 | 2312480 | 1492800 | 333288 | 8500 | 2073000 | 1694760 | 796800 | 875952 | 3694009 | 3443000 | 1353888 | 1164480 | 0 | 487980 | 18100 | 0 | 163980 | 7561200 | 414052 | 85232 | 0 | 20072 | 0 | 0 | 844800 | 0 | 1697760 | 123255 | 359040 | 0 | 247564 | 0 | 2221200 | 32124 | 0 | 27120 | 1987200 | 0 | 0 | 0 | 0 |  | 11019636 | 0 | 7231140 | 0 | 938880 | 0 | 0 | 0 | 0 | 3712 | 0 | 2042687 | 52871 | 0 | 0 | 0 | 0 | 66248 | 0 | 182512 | 606960 | 0 | 0 | 0 | 0 | 365040 | 222408 | 221148 | 2107636 | 0 | 5344800 | 0 | 0 | 4214927 | 0 | 0 | 0 | 1013222 | 0 | 0 | 0 | 9045272 | 0 | 0 | 36288 | 0 | 609600 | 0 | 25300 | 1441056 | 9208200 |  | 121756939 | 55999543 | 177756482 | 83866688 | 11019636 | 41982314 | 20020444 | 16660636 | 1588091 | 336898 | 2097600 | 184175 | 0
Fuel Cost | 1889440 | 0 | 803570 | 0 | 5497984.66 | 0 | 0 | 6038323.2 | 5967520 |  | 0 | 5436200 | 2993445.9 | 5463936 | 1621640.88 | 825981.3 | 0 | 0 | 0 | 0 | 14279040 | 6457858.56 | 0 | 0 | 0 | 0 | 0 | 7823138.4 | 1553798.88 | 0 | 245187 | 450000 | 0 | 0 | 0 | 0 | 0 | 412903.66 | 0 | 0 | 4437000 | 0 | 5231501.1 | 0 | 3103231.03 | 0 |  | 0 | 0 | 486421.3 | 0 | 2227622.4 | 2417126.4 | 393377.28 | 1542566.4 | 0 | 0 | 2303639.1 | 5709766 | 6220620 | 4097680 | 475388.2 | 2826143.6 | 599078.88 | 467208 | 0 | 1267351.8 | 0 | 446016.32 | 0 | 399697.2 | 110970 | 1118880 | 219435 | 14473440 | 1896233.6 | 14196528 | 339953.76 | 139400 | 2819280 | 2304873.6 | 1083648 | 1094940 | 4580571.16 | 3167560 | 2017293.12 | 2049484.8 | 0 | 741729.6 | 28779 | 0 | 385353 | 5368452 | 310539 | 64776.32 | 0 | 210153.84 | 0 | 0 | 8126976 | 0 | 17130398.4 | 1422362.7 | 3346252.8 | 0 | 2319674.68 | 0 | 19479924 | 286224.84 | 0 | 0 | 18321984 | 0 | 0 | 0 | 0 |  | 29753017.2 | 0 | 5640289.2 | 0 | 9050803.2 | 0 | 0 | 0 | 0 | 48627.2 | 0 | 1634149.6 | 81950.05 | 0 | 0 | 0 | 0 | 738002.72 | 0 | 1806868.8 | 6294175.2 | 0 | 0 | 0 | 0 | 401544 | 366973.2 | 167409.036 | 13425641.32 | 0 | 21860232 | 0 | 0 | 3709135.76 | 0 | 0 | 0 | 1611022.98 | 0 | 0 | 0 | 6603048.56 | 0 | 0 | 333123.84 | 0 | 5693664 | 0 | 0 | 0 | 0 |  | 241567474.67 | 109219677.866 | 350787152.536 | 76537525.646 | 29753017.2 | 38783222.15 | 150453471.52 | 35285873.32 | 412903.66 | 3525936.34 | 14473440 | 1561762.7 | 0
Yesterday Day Peak | 72 | 0 | 0 | 0 | 350 | 0 | 0 | 349 | 320 |  | 0 | 225 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 70 | 0 | 0 | 120 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 3 | 0 | 0 | 100 | 330 | 330 | 201 | 24 | 90 | 39 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 14 | 84 | 102 | 50 | 0 | 1.5 | 89 | 73 | 45 | 47 | 130 | 152 | 63 | 50 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 90 | 15.3 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 4.7 | 87 | 0 | 0 | 0 | 0 |  | 526 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 89 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 35 | 0 | 4.1 | 60 | 453 |  | 7680.6 | DayPeak
Yesterday Evening Peak | 72 | 0 | 100 | 0 | 300 | 0 | 0 | 330 | 360 | 0 | 0 | 225 | 120 | 100 | 65 | 36 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 71 | 0 | 0 | 120 | 0 | 203 | 0 | 145 | 0 | 0 | 0 | 0 | 17 | 0 | 86 | 50 | 18 | 22 | 0 | 0 | 80 | 290 | 280 | 184 | 26 | 90 | 39 | 20 | 0 | 43 | 0 | 8 | 0 | 22 | 11 | 33 | 0 | 114 | 104 | 95 | 22 | 0 | 88 | 73 | 53 | 50 | 130 | 145 | 65 | 78 | 0 | 67 | 17 | 0 | 10 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 150 | 0 | 100 | 0 | 120 | 0 | 115 | 2 | 0 | 0 | 198 | 0 | 0 | 0 | 0 |  | 771 | 0 | 180 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 9 | 0 | 0 | 0 | 0 | 25 | 0 | 51 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 109 | 548 |  | 9127 | EvPeak
Forecast for Evening | 72 | 0 | 100 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 25 | 52 | 0 | 70 | 0 | 0 | 120 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 90 | 40 | 20 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 113 | 110 | 95 | 22 | 0 | 88 | 73 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 128 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 775 | 40 | 330 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 84 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 40 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 90 | 0 | 270 | 17 | 17 | 140 | 0 | 0 | 0 | 95 | 100 | 225 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 300
Forecast for Day | 72 | 0 | 100 | 0 | 320 | 0 | 0 | 412 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 25 | 52 | 0 | 70 | 0 | 0 | 120 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 0 | 100 | 360 | 360 | 225 | 8 | 90 | 40 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 100 | 95 | 22 | 1.6 | 88 | 73 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 128 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 540 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 85 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 40 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 90 | 0 | 270 | 0 | 0 | 140 | 0 | 0 |  | 95 | 0 | 225 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 300
Generation at 08:00(Today) | 72 | 0 | 100 | 0 | 350 | 0 | 0 | 352 | 368 | 0 | 0 | 225 | 150 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 28 | 20 | 25 | 0 | 0 | 69 | 0 | 0 | 120 | 0 | 197 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 0 | 100 | 340 | 295 | 200 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 13 | 72 | 104 | 48 | 22 | 0.1 | 89 | 43 | 51 | 47 | 163 | 148 | 20 | 78 | 0 | 128 | 0 | 0 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 96 | 2.4 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0.67 | 109 | 0 | 0 | 0 | 0 | 0 | 534 | 0 | 350 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 18 | 9 | 11 | 92 | 0 | 179 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 8 | 0 | 0.7 | 108 | 341 | 0
199
| Minimum Generation |  | 5738 | 5:00
| Highest Generation |  | 9127 | 19:00
| Day Peak Generation |  | 7680.6 | 12:00
| Evening Peak Generation |  | 9127 | 19:00
| HVDC Max Flow |  | 772 | 20:00
| HVDC EvPeak Flow |  | 771 | 19:00
| Load factor L.F |  | 81.15%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-17
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7680.6 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 5693 | MW
Evening Peak Generation : |  | 9127 | MW Hour : | 19:00 | Available Max Generation : |  | 14345 | MW
E.P. Demand (at gen end) : |  | 9127 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9127 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4845 | MW
Total Gen. (MKWH) : |  | 177.7565 | System Load Factor : | 81.15% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -242 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-17
Actual : | 91.74 | Ft.(MSL) , | Rule curve : | 94.76 | Ft.( MSL )
Gas Consumed : | Total = | 1016.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 115320747.796
: |  | Coal : | 35285873.32 | Oil : | 153979407.86 | Total : | 304586028.976
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3379.456 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1145.0805 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1025.2198 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 926.1118 |  |  | 0 | 0%
) | 0 | 0:00 | 837.0576 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 675.4655 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 382.9909 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 174.0546 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 520.9271 |  |  | 0 | 0%
Total | 0 |  | 9066.3638 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Bhola 225 MW GT-1
|  |  |  | 2) Summit Meghnaghat GT-1 | 11) Chattrogram TPP-1
3) Ghorasal Unit-3,5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,4
6) Sirajganj unit-2
7) Siddhirganj 335 MW
8) Kaptai-2,4,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar-Savar 132 kV Ckt-1 was under shut down from 09:05 to 17:06 for A/M.
b) Daudkandi-Cumilla(N) 132 kV Ckt-2 was under shut down from 08:45 to 15:58 for A/M.
c) Ashuganj-B.Baria 132 kV Ckt-2 was under shut down from 08:48 to 14:38 for A/M.
d) Chandpur 132/33 kV T-2 transformer was under shut down from 12:45 to 14:10 for C/M.
e) Sherpur 132/33 kV T-2 transformer was under shut down from 12:01 to 12:26 for D/W.
f) Faridpur 132/33 kV T-2 transformer was under shut down from 11:06 to 13:04 for C/M.
g) Chapainawabganj 132/33 kV T-1 transformer was shut down at 09:25 for D/W.
h) Manikganj 132/33 kV GT-4 transformer was shut down at 09:52 for oil centrifuging.
i) Megnaghat-450 MW GT-2 tripped at 09:31 showing stator E/F relay.
j) After maintenance Ghorasal #4 was synchronized at 16:33.
k) Chandpur 132/33 kV T-1 transformer was under shut down from 14:55 to 15:45 for C/M.
l) Baghabari-Sirajganj 132 kV Ckt was under shut down from 16:15 to 16:26 for 132 kV breaker gas
feeling at Baghabari end.
m) After maintenance Sylhet-150 MW was synchronized at 17:49.
n) Noapara 132/33 kV T-1 & T-2 transformers tripped at 18:16 showing E/F relay due to 33 kV REB-1 |  |  |  |  | About 34 MW power interruption occurred under Noapara S/S area
& REB-5 feeders fault and were switched on at 18:19. |  |  |  |  | from 18:16 to 18:19.
o) Shahjibazar GT-8 was shut down at 05:45(17/2/20) for filter change.
p) Palashbari-Rangpur Confidence power 132 kV Ckt-2 is under shut down since 06:17(17/2/20) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 72 | 1687000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 751000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7429709 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8386560 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 360 | 7852000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 6795250 | tripped at 09:31.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 535680
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3326051 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 65 | 149736 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 36 | 80505 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 326916
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1286400
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 635616
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 815760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 162872
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1309920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 624400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 622800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 20072 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 150 | 1697760
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 2 | 32124 | Low demand
| Dhaka area Total |  |  |  | 5811 | 2314 | 44528131
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123255
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 258240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 71 | 1588091 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4982382 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 2443489 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 46370 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 359040
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 427584
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 554880
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 86 | 234240 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27120
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 198 | 1987200 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1030 | 15931891
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2193942 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4454000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7715900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7405500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 730584
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 453600 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 485090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 886260 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 120 | 247564 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 8 | 38056 | Low demand
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2124920
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 391860
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 147960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2097600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 592000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 0 | 292580 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1360 | 30257416
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2312480 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 333288
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1492800
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 844800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2221200
| Mymensingh Area Total |  |  |  | 637 | 456 | 7213068
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2073000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 73 | 1694760
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3694009 | Gas shortage.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 145 | 3443000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 796800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 875952
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 85232
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1353888 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1164480
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 67 | 487980 | Sinc at 17:31.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 18100
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 414052
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7561200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 163980
| Sylhet Area Total |  |  |  | 1949 | 1081 | 23826433
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 771 | 11019636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 938880
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 3712 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 180 | 7231140 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1066 | 19193368
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 52871 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 84 | 2042687
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1013222
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 548 | 9208200 | On test
| Barisal Area Total |  |  |  | 462 | 738 | 12316980
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 66248 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 606960
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 130 | 4214927 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 9045272 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 365040
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 222408 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 221148
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 182512 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 36288 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1441056
| Rajshahi Area Total |  |  |  | 2183 | 696 | 16401859
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 90 | 2107636
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5344800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 76 | 609600 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25300
| Rangpur Area Total |  |  |  | 605 | 386 | 8087336
| Total |  |  |  | 19107 | 9127 | 177756482
| Eastern Grid Total |  |  |  | 13543 | 6241 | 121756939
| Western Grid Total |  |  |  | 5564 | 2886 | 55999543
| National Grid Total |  |  |  | 19107 | 9127 | 177756482
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-16
(a) ENTIRE EASTERN GRID : |  | 5848 | MW | (b) ENTIRE WESTERN GRID : |  | 2852 | MW
i) Dhaka area |  | 3116 | MW | i) Khulna area |  | 1034 | MW
ii) Chittagong area |  | 942 | MW | ii) Rajshahi area |  | 940 | MW
iii) Comilla area |  | 735 | MW | iii) Barisal area |  | 216 | MW
iv) Mymensingh area |  | 722 | MW | iv) Rangpur area |  | 662 | MW
v) Sylhet area |  | 333 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8700 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 12:00 | Srimongal | 24 | 18:00 | Jhenida | 82 | 19:30
Munsiganj | 80 | 19:00 | Shahjibazar | 94 | 19:30 | Bottail | 96 | 18:30
Sonargaon | 59 | 12:00 | Fenchuganj | 26 | 19:00 | G.K Project | 39 | 18:30
Shyampur | 174 | 7:00 | Kulawara | 28 | 18:00 | Faridpur | 124 | 18:30
Bhulta | 161 | 11:00 | Sylhet | 96 | 19:30 | Madaripur | 60 | 20:00
Madanganj | 48 | 1:00 | Chatak | 17 | 18:00 | Sariatpur | 38 | 19:30
Shitalakhya | 94 | 18:30 | Sunamganj | 29 | 20:00 | Gopalganj | 66 | 19:00
Rahim steel | 20 | 11:00 | Biani Bazar | 32 | 18:30 | Bagerhat | 66 | 20:00
Matuail | 84 | 12:00 | Comilla (S) | 118 | 18:30 | Mongla | 38 | 11:00
Ghorasal | 70 | 18:30 | Comilla(N) | 99 | 20:00 | Satkhira | 71 | 19:00
Narsingdi | 107 | 19:30 | Chandpur | 71 | 21:00 | Gallamari | 41 | 13:00
Haripur (SBU) | 89 | 9:00 | Feni | 99 | 18:30 | Magura | 39 | 19:00
Ullon | 51 | 18:30 | Chowmuhani | 110 | 18:00 | Norail | 26 | 20:00
Hasnabad | 135 | 18:00 | Ashuganj | 35 | 19:30 | Chuadanga | 60 | 18:30
Magbazar | 77 | 12:00 | Daudkandi | 100 | 18:30 | Barisal(N) | 30 | 20:00
Maniknagar | 70 | 12:00 | B.Baria | 88 | 18:30 | Barisal (S) | 70 | 18:30
Bangabhaban | 20 | 12:00 | Ramganj | 58 | 19:30 | Patuakhali | 61 | 20:00
Narinda | 76 | 15:00 | Chaddagram | 16 | 13:00 | Bhandaria | 40 | 20:00
Dhanmondi | 110 | 13:00 | PHP | 2 | 10:00 | Borhan Uddin | 41 | 22:00
Lalbag | 48 | 13:00 | Madunaghat | 42 | 19:00 | Ishurdi | 34 | 18:30
Madartek | 46 | 18:30 | Hathazari | 67 | 18:00 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 138 | 11:00 | Natore | 90 | 20:00
Mirpur | 71 | 18:30 | Halishahar | 95 | 18:00 | Bogra | 134 | 20:00
Kalyanpur | 66 | 18:30 | Baraulia | 144 | 6:00 | Noagaon | 85 | 8:00
Gulshan | 90 | 13:00 | Sikalbaha | 18 | 19:30 | Rajshahi | 86 | 20:00
Uttara | 42 | 18:00 | Dohazari | 78 | 20:00 | Rajshahi New | 10 | 20:00
Uttara New | 32 | 18:30 | Cox'sbazar | 68 | 19:00 | C.Nawabganj | 68 | 12:00
Kamrangirchar | 76 | 19:00 | Chandraghona | 22 | 18:30 | Amnura | 29 | 18:30
Savar | 106 | 18:30 | Kaptai | 3.2 | 18:30 | Pabna | 74 | 19:00
Bhasantec | 103 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 74 | 19:30
Agargaon | 35 | 13:00 | Bakulia | 77 | 18:30 | Serajganj | 79 | 19:00
Satmosjid | 75 | 13:00 | Julda | 20 | 7:00 | Niyamatpur | 83 | 8:00
Tongi | 114 | 11:00 | TK chemical | 12 | 18:00 | Joypurhat | 54 | 9:00
Kabirpur | 175 | 18:30 | Modern Steel | 14 | 2:00 | Sherpur(Bogura) | 42 | 18:30
Basundhara | 76 | 19:00 | Shahmirpur | 23 | 18:30 | Mohastangor | 34 | 19:00
Manikganj | 70 | 19:00 | Khagrachhari | 18 | 18:00 | Rangpur | 113 | 18:30
Joydevpur | 167 | 18:30 | Matarbari | 31 | 19:00 | Lalmonirhat | 45 | 8:00
New Tongi | 79 | 11:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 101 | 8:00
Korda | 194 | 18:30 | Rangamati | 10 | 18:30 | Purbasadipur | 103 | 9:00
Dhamrai | 38 | 18:30 | Abul Khair 230 | 162 | 23:00 | Thakurgaon | 70 | 19:00
Valuka | 76 | 8:00 | BSRM | 117 | 7:00 | Palashbari | 96 | 19:00
Tangail | 148 | 18:30 | GPH Ispat | 51 | 11:00 | Barapukuria | 46 | 19:00
Mymensing | 165 | 18:30 | Goalpara | 18 | 18:30 | Panchagar | 36 | 19:00
Kishorganj | 89 | 19:30 | Central s/s | 60 | 18:30 | Joldhaka | 24 | 20:00
Netrokona | 99 | 18:30 | Noapara | 40 | 20:00 | Kurigram | 45 | 0.79167
Jamalpur | 103 | 20:00 | Jessore | 98 | 19:00
Sherpur | 80 | 19:00 | Benapol | 32 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-16 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 407 | 0.16667 | 397 | 0.54167 | Kaliakoir | 395 | 0.20833 | 377 | 0.625
Bheramara | 409 | 0.083333 | 398 | 0.54167 | Bhulta | 398 | 0.083333 | 384 | 0.5
Ashuganj(N) | 403 | 0.20833 | 390 | 0.5 | Gopalganj | 414 | 0.041667 | 387 | 0.77083
Payra | 414 | 0.041667 | 401 | 0.77083
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 240 | 0.041667 | Hathazari | 228 | 0.125 | 221 | 0.625
Ishurdi | 242 | 0.125 | 227 | 0.79167 | Megnaghat | 240 | 0.041667 | 231 | 0.625
Ashuganj | 244 | 0.16667 | 235 | 0.45833 | Fenchuganj | 245 | 0.25 | 240 | 0.45833
Serajganj | 234 | 0.041667 | 228 | 0.41667 | Siddhirganj | 238 | 0.16667 | 228 | 0.5
Baghabari | 242 | 0.16667 | 230 | 0.54167 | Maniknagar | 237 | 0.20833 | 227 | 0.5
Barapukuria | 239 | 0.20833 | 230 | 0.33333 | Old Airport | 237 | 0.20833 | 225 | 0.5
Bogra | 230 | 0.041667 | 218 | 0.33333 | Barisal | 249 | 0.375 | 236 | 0.77083
Khulna South | 243 | 0.083333 | 220 | 0.29167 | AKSML | 226 | 0.83333 | 219 | 0.5
Rampura | 232 | 0.041667 | 228 | 0.45833 | BSRM | 229 | 0.25 | 223 | 0.5
Haripur | 235 | 0.29167 | 228 | 0.5 | Bibiyana | 244 | 0.20833 | 232 | 0.95833
Hasnabad | 236 | 0.20833 | 228 | 0.625 | Bhulta | 238 | 0.20833 | 227 | 0.45833
Shyampur | 234 | 0.16667 | 224 | 0.5 | Ashuganj (S) | 235 | 0.125 | 229 | 0.625
Aminbazar | 237 | 0.125 | 226 | 0.54167 | Kaliakoir | 238 | 0.16667 | 228 | 0.5
Tongi | 233 | 0.16667 | 224 | 0.45833 | GPH | 225 | 0.083333 | 220 | 0.54167
Comilla (N) | 242 | 0.16667 | 234 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.25 | 130 | 0.41667 | Khulshi | 132 | 0.16667 | 128 | 0.41667
Munsiganj | 137 | 0.77083 | 129 | 0.5 | Halishahar | 133 | 0.25 | 121 | 0.29167
Sonargaon | 134 | 0.125 | 130 | 0.375 | Baraulia | 134 | 0.83333 | 130 | 0.58333
Shyampur | 137 | 0.20833 | 131 | 0.5 | Sikalbaha | 135 | 0.8125 | 130 | 0.375
Bhulta | 130 | 0.041667 | 123 | 0.5 | Dohazari | 132 | 0.33333 | 129 | 0.95833
Madanganj | 137 | 0.75 | 130 | 0.29167 | Cox'sbazar | 129 | 0.375 | 124 | 0.29167
Shitalakhya | 139 | 0.77083 | 130 | 0.625 | Chandraghona | 135 | 0.20833 | 131 | 0.5
Rahim steal | 136 | 4:00 | 130 | 0.5 | Kaptai | 135 | 0.8125 | 132 | 0.41667
Matuail | 135 | 0.20833 | 128 | 0.5 | A. Khaer Stl. | 132 | 0.041667 | 130 | 0.41667
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | Bakulia | 134 | 0.83333 | 128 | 0.58333
Narsinghdi | 134 | 0.75 | 130 | 0.8125 | Julda | 134 | 0.77083 | 129 | 0.58333
Haripur (SBU) | 136 | 0.16667 | 130 | 0.5 | TK Chemical | 135 | 0.83333 | 130 | 0.41667
Ullon | 132 | 0.20833 | 124 | 0.5 | Modern Steel | 134 | 0.79167 | 129 | 0.5
Hasnabad | 136 | 0.25 | 130 | 0.66667 | Shahmirpur | 133 | 0.77083 | 130 | 0.041667
Magbazar | 133 | 0.25 | 125 | 0.5 | Khagrachhari | 134 | 0.125 | 130 | 0.5
Maniknagar | 138 | 0.25 | 1323 | 0.5 | Matarbari | 130 | 0.125 | 126 | 0.79167
Bangabhaban | 138 | 0.25 | 1323 | 0.5 | Baroiar Hat | 134 | 0.041667 | 132 | 0.5
Narinda | 138 | 0.25 | 1323 | 0.5 | Rangamati | 134 | 0.25 | 131 | 10:00
Dhanmondi | 132 | 0.20833 | 124 | 0.5 | Goalpara | 138 | 0.083333 | 124 | 7:00
Lalbag | 137 | 0.20833 | 129 | 0.5 | Central s/s | 136 | 0.66667 | 122 | 0.29167
Madartek | 132 | 0.25 | 124 | 0.5 | Noapara | 135 | 0.66667 | 124 | 0.29167
Dhaka University |  |  |  |  | Jessore | 133 | 0.66667 | 119 | 0.29167
Mirpur | 136 | 0.16667 | 127 | 0.625 | Benapol | 135 | 0.083333 | 120 | 0.29167
Kalyanpur | 140 | 0.125 | 131 | 0.5 | Jhenida | 132 | 0.041667 | 120 | 0.79167
Gulshan | 130 | 0.083333 | 124 | 0.45833 | Bottail | 135 | 0.041667 | 126 | 0.79167
Uttara | 136 | 0.083333 | 127 | 0.625 | G.K Project | 141 | 0.20833 | 133 | 0.79167
Uttara New | 136 | 0.041667 | 127 | 0.58333 | Faridpur | 138 | 0.125 | 127 | 0.79167
Kamrangirchar | 136 | 0.125 | 128 | 0.5 | Madaripur | 140 | 0.041667 | 133 | 0.77083
Savar | 136 | 0.125 | 127 | 0.5 | Sariatpur | 140 | 0.041667 | 131 | 0.83333
Bhasantec | 137 | 0.20833 | 128 | 0.5 | Gopalganj | 143 | 0.16667 | 130 | 0.77083
Agargaon | 138 | 0.20833 | 130 | 0.5 | Bagerhat | 135 | 0.66667 | 121 | 0.29167
Satmosjid | 137 | 0.20833 | 129 | 0.5 | Mongla | 132 | 0.041667 | 121 | 0.5
Tongi | 140 | 0.16667 | 132 | 0.5 | Satkhira | 135 | 0.083333 | 125 | 0.8125
Kabirpur | 135 | 7:00 | 129 | 0.625 | Gallamari | 137 | 0.66667 | 122 | 0.29167
Basundhara | 131 | 8:00 | 125 | 0.54167 | Magura | 133 | 0.20833 | 119 | 0.79167
Manikganj | 139 | 0.875 | 132 | 0.625 | Norail | 132 | 0.083333 | 119 | 0.79167
Joydevpur | 142 | 0.125 | 137 | 0.70833 | Chuadanga | 130 | 0.041667 | 115 | 0.79167
New Tongi | 139 | 0.125 | 131 | 0.5 | Barisal(N) | 141 | 0.041667 | 133 | 0.77083
Kodda | 137 | 0.041667 | 125 | 0.70833 | Barisal (S) | 140 | 0.625 | 132 | 0.77083
Dhamrai | 137 | 0.16667 | 128 | 0.625 | Patuakhali | 139 | 0.375 | 130 | 0.77083
Valuka | 125 | 0.041667 | 116 | 0.33333 | Bhandaria | 139 | 0.041667 | 130 | 0.77083
Tangail | 134 | 0.083333 | 120 | 0.54167 | Ishurdi | 138 | 0.16667 | 130 | 0.79167
Mymensing | 127 | 0.625 | 116 | 0.91667 | Ruppur Paromanobik | 136 | 0.16667 | 129 | 0.79167
Kishorganj | 130 | 0.625 | 124 | 0.91667 | Natore | 133 | 0.75 | 126 | 0.79167
Netrokona | 124 | 0.041667 | 115 | 0.83333 | Bogra | 135 | 0.20833 | 127 | 0.33333
Jamalpur | 137 | 0.75 | 121 | 0.20833 | Noagaon | 129 | 0.16667 | 118 | 0.33333
Sherpur | 135 | 0.75 | 120 | 0.20833 | Rajshahi | 131 | 0.16667 | 122 | 0.5
Srimongal | 140 | 0.16667 | 137 | 0.875 | Rajshahi New | 131 | 0.75 | 120 | 0.5
Shahjibazar | 138 | 0.16667 | 134 | 0.54167 | C.Nawabganj | 130 | 0.16667 | 118 | 0.29167
Fenchuganj | 139 | 0.041667 | 135 | 13:00 | Amnura | 132 | 0.75 | 117 | 0.29167
Khulawara | 139 | 0.33333 | 135 | 0.54167 | Pabna | 136 | 0.16667 | 127 | 0.79167
Sylhet | 137 | 0.33333 | 133 | 0.625 | Shahjadpur | 141 | 0.75 | 135 | 0.29167
Chatak | 136 | 0.16667 | 132 | 0.58333 | Serajganj | 136 | 0.041667 | 127 | 0.5
Sunamganj | 136 | 0.20833 | 132 | 0.5 | Niyamatpur | 128 | 0.041667 | 115 | 0.33333
Biani Bazar | 137 | 0.25 | 133 | 0.5 | Joypurhat | 130 | 0.20833 | 116 | 0.33333
Comilla(s) | 133 | 0.95833 | 127 | 0.54167 | Sherpur(Bogura) | 136 | 0.041667 | 127 | 0.33333
Comilla(n) | 141 | 7:00 | 138 | 0.54167 | Mohastangor | 134 | 0.20833 | 124 | 0.33333
Chandpur | 138 | 0.33333 | 135 | 0.95833 | Rangpur | 132 | 0.20833 | 122 | 0.33333
Feni | 135 | 0.29167 | 131 | 0.8125 | Lalmonirhat | 128 | 0.20833 | 116 | 0.33333
Chowmuhani | 135 | 0.29167 | 127 | 0.83333 | Saidpur | 132 | 0.20833 | 119 | 0.33333
Ashuganj | 138 | 0.25 | 135 | 0.875 | Purbasadipur | 130 | 0.125 | 116 | 0.33333
Daudkandi | 135 | 0.79167 | 131 | 0.41667 | Thakurgaon | 129 | 0.25 | 114 | 0.33333
B.Baria | 135 | 0.25 | 132 | 0.5 | Palashbari | 129 | 0.16667 | 120 | 0.29167
Ramganj | 133 | 0.45833 | 127 | 0.83333 | Barapukuria | 139 | 0.20833 | 130 | 0.33333
Chaddagram | 137 | 0.20833 | 134 | 0.45833 | Panchagar | 126 | 0.25 | 110 | 0.33333
PHP | 134 | 0.41667 | 130 | 0.54167 | Joldhaka | 131 | 0.25 | 118 | 0.33333
Madanhat | 136 | 0.16667 | 132 | 0.91667 | Kurigram | 132 | 0.16667 | 119 | 0.33333
Hathazari | 135 | 0.16667 | 132 | 0.29167

## L-Curve
Date | 2020-02-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 221 | 5188 | 1983 | 7171 |  |  |  | QF-LDC-12
0:30 | 199.5 | 4857.5 | 1931 | 6788.5 | Date: | 2020-02-16
1:00 | 178 | 4527 | 1879 | 6406
1:30 | 184 | 4460 | 1819.5 | 6279.5
2:00 | 190 | 4393 | 1760 | 6153
2:30 | 152.5 | 4289 | 1740.5 | 6029.5 | [5 empty] | Gen. at Eve. Peak | 9127 | 9127 MW (19:00 )
3:00 | 115 | 4185 | 1721 | 5906 | [6 empty] | 19:00
3:30 | 112 | 4175.5 | 1703 | 5878.5 | [5 empty] | Gen. at Day Peak | 7680.6 | 7680.6 MW (12:00 )
4:00 | 109 | 4166 | 1685 | 5851 | [6 empty] | 12:00
4:30 | 115 | 4124.5 | 1670 | 5794.5 | [5 empty] | Highest Generation | 9127
5:00 | 121 | 4083 | 1655 | 5738 | [6 empty] | 19:00
5:30 | 158.5 | 4215 | 1680 | 5895
6:00 | 196 | 4347 | 1705 | 6052
6:30 | 181.5 | 4473.815 | 1916.55 | 6390.365
7:00 | 167 | 4600.63 | 2128.1 | 6728.73
7:30 | 204.5 | 4887.365 | 2243.9 | 7131.265
8:00 | 242 | 5174.1 | 2359.7 | 7533.8
8:30 | 142 | 5121.05 | 2404.75 | 7525.8
9:00 | 42 | 5068 | 2449.8 | 7517.8
9:30 | 105.5 | 5036.4 | 2483.9 | 7520.3
10:00 | 169 | 5004.8 | 2518 | 7522.8
10:30 | 203 | 4998.6 | 2539.85 | 7538.45
11:00 | 237 | 4992.4 | 2561.7 | 7554.1
11:30 | 172 | 5062.95 | 2554.4 | 7617.35
12:00 | 107 | 5133.5 | 2547.1 | 7680.6
12:30 | 157.5 | 5112.1 | 2584.1 | 7696.2
13:00 | 208 | 5090.7 | 2621.1 | 7711.8
13:30 | 270.5 | 5022.005 | 2571.35 | 7593.355
14:00 | 333 | 4953.31 | 2521.6 | 7474.91
14:30 | 352.5 | 4885.915 | 2517.6 | 7403.515
15:00 | 372 | 4818.52 | 2513.6 | 7332.12
15:30 | 301 | 4829.965 | 2407.1 | 7237.065
16:00 | 230 | 4841.41 | 2300.6 | 7142.01
16:30 | 215.5 | 4839.065 | 2307.6 | 7146.665
17:00 | 201 | 4836.72 | 2314.6 | 7151.32
17:30 | 150.5 | 5134.86 | 2482.3 | 7617.16
18:00 | 100 | 5433 | 2650 | 8083
18:30 | 168 | 5837 | 2768 | 8605
19:00 | 236 | 6241 | 2886 | 9127
19:30 | 175 | 6162 | 2922 | 9084
20:00 | 172 | 6164 | 2951 | 9115 |  |  |  | Executive Engineer
20:30 | 136 | 6032.5 | 2947 | 8979.5 |  |  |  | Network Operation Division
21:00 | 100 | 5901 | 2943 | 8844
21:30 | 72.5 | 5740.5 | 2851 | 8591.5
22:00 | 45 | 5580 | 2759 | 8339 |  |  |  |  | Page 6 of 7
22:30 | 121 | 5454 | 2502 | 7956
23:00 | 197 | 5328 | 2245 | 7573
23:30 | 209 | 5258 | 2114 | 7372
24:00 | 221 | 5188 | 1983 | 7171
9127 MW (19:00 )
7680.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-16 |  | Energy | 177756482
[10 empty] | 2020-02-16 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3724 | 287 | 1787 | 692 | 664 | 68 | 0 | 0 | 92
0:30 | 3585.5 | 211 | 1787 | 497 | 625.5 | 68 | 0 | 0 | 86 | Date: | 2020-02-16
1:00 | 3447 | 135 | 1787 | 302 | 587 | 68 | 0 | 0 | 80
1:30 | 3402 | 133 | 1761 | 261 | 574.5 | 68 | 0 | 0 | 80 | [7 empty] | Total Energy | 177.7565 | Total Energy Gen 177.756 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.756 MKWHr
2:00 | 3357 | 131 | 1735 | 220 | 562 | 68 | 0 | 0 | 80 | [7 empty] | Energy not Served | 0
2:30 | 3305 | 130.5 | 1687 | 199 | 561 | 68 | 0 | 0 | 79 | [7 empty] | Energy Requirement | 177.7565
3:00 | 3253 | 130 | 1639 | 178 | 560 | 68 | 0 | 0 | 78
3:30 | 3258.5 | 130.5 | 1605 | 178 | 560.5 | 69 | 0 | 0 | 77 | [6 empty] | Shortage
4:00 | 3264 | 131 | 1571 | 178 | 561 | 70 | 0 | 0 | 76
4:30 | 3227.5 | 131.5 | 1550.5 | 178 | 561 | 70 | 0 | 0 | 76
5:00 | 3191 | 132 | 1530 | 178 | 561 | 70 | 0 | 0 | 76
5:30 | 3269 | 141.5 | 1588 | 181 | 569.5 | 70 | 0 | 0 | 76
6:00 | 3347 | 151 | 1646 | 184 | 578 | 70 | 0 | 0 | 76
6:30 | 3405 | 337.5 | 1686 | 225.5 | 587 | 70 | 0 | 0 | 79 |  |  |  |  | Coal
7:00 | 3463 | 524 | 1726 | 267 | 596 | 70 | 0 | 0 | 82
7:30 | 3507.5 | 524 | 1867 | 471.5 | 612 | 69 | 0 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 3552 | 524 | 2008 | 676 | 628 | 68 | 0 | 0 | 74
8:30 | 3473 | 524 | 1947.5 | 786 | 644.5 | 68 | 0 | 0 | 75
9:00 | 3394 | 524 | 1887 | 896 | 661 | 68 | 0 | 0 | 76
9:30 | 3477 | 524 | 1844.5 | 828 | 687.5 | 68 | 0 | 0 | 74
10:00 | 3560 | 524 | 1802 | 760 | 714 | 68 | 0 | 0 | 72
10:30 | 3537.5 | 524 | 1788 | 785.5 | 733 | 69 | 0 | 0 | 76
11:00 | 3515 | 524 | 1774 | 811 | 752 | 70 | 0 | 0 | 80
11:30 | 3558 | 525 | 1761.5 | 837 | 757 | 70 | 0 | 0 | 82
12:00 | 3601 | 526 | 1749 | 863 | 762 | 70 | 0 | 0 | 84
12:30 | 3542 | 526.5 | 1756.5 | 928.5 | 762 | 70.5 | 0 | 0 | 83
13:00 | 3483 | 527 | 1764 | 994 | 762 | 71 | 0 | 0 | 82
13:30 | 3483 | 527 | 1764 | 994 | 762 | 71 | 0 | 0 | 82
14:00 | 3483 | 527 | 1764 | 994 | 762 | 71 | 0 | 0 | 82
14:30 | 3424 | 527.5 | 1708.5 | 914.5 | 769.5 | 71 | 0 | 0 | 83
15:00 | 3365 | 528 | 1653 | 835 | 777 | 71 | 0 | 0 | 84
15:30 | 3312 | 527.5 | 1614 | 881.5 | 735 | 71 | 0 | 0 | 81
16:00 | 3259 | 527 | 1575 | 928 | 693 | 71 | 0 | 0 | 78
16:30 | 3295.5 | 527.5 | 1510.5 | 928 | 723 | 71 | 2 | 0 | 82
17:00 | 3332 | 528 | 1446 | 928 | 753 | 71 | 4 | 0 | 86
17:30 | 3340 | 601 | 1457 | 1208 | 787 | 71 | 52.5 | 0 | 99
18:00 | 3348 | 674 | 1468 | 1488 | 821 | 71 | 101 | 0 | 112
18:30 | 3407.5 | 722.5 | 1595.5 | 1755 | 839.5 | 71 | 101 | 0 | 113
19:00 | 3467 | 771 | 1723 | 2022 | 858 | 71 | 101 | 0 | 114
19:30 | 3506 | 771 | 1802 | 1860 | 861 | 71 | 101 | 0 | 112
20:00 | 3550 | 772 | 1779 | 1866 | 860 | 71 | 101 | 0 | 116
20:30 | 3595.5 | 772 | 1779 | 1717 | 858.5 | 71 | 72.5 | 0 | 114
21:00 | 3641 | 772 | 1779 | 1568 | 857 | 71 | 44 | 0 | 112
21:30 | 3652.5 | 771.5 | 1785 | 1349 | 825.5 | 71 | 30 | 0 | 107
22:00 | 3664 | 771 | 1791 | 1130 | 794 | 71 | 16 | 0 | 102
22:30 | 3693 | 650 | 1773 | 911 | 751 | 70 | 8 | 0 | 100
23:00 | 3722 | 529 | 1755 | 692 | 708 | 69 | 0 | 0 | 98
23:30 | 3723 | 408 | 1771 | 692 | 686 | 68.5 | 0 | 0 | 95 | Max Temp. in Dhaka |  | 28.7° C
24:00 | 3724 | 287 | 1787 | 692 | 664 | 68 | 0 | 0 | 92
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 177.756 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 177.756 MKWHr
Note on W13: Author:

## Generation
. | 2020-02-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 68 | 68 | 68 | 70 | 70 | 70 | 70 | 68 | 68 | 68 | 70 | 70 | 71 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 69 | 68 | 1588091
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.5 | 2.3 | 7.8 | 15.1 | 18.5 | 15.3 | 19 | 17.61 | 13.32 | 7.6 | 2.19 | [9 empty] | 123255
6 | Sikalbaha 225MW CCPP (Gas) | 216 | 215 | 216 | 216 | 216 | 216 | 210 | 208 | 209 | 209 | 215 | 217 | 203 | 217 | 202 | 203 | 203 | 203 |  | 203 | 203 | 203 | 203 | 203 | 203 | 202 | 4982382
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 104 | 104 | 104 | 104 | 70 | 70 | 70 | 70 | 50 | 50 | 104 | 139 | 100 | 80 | 100 | 100 | 100 |  | 145 | 139 | 139 | 139 | 139 | 104 | 104 | 2443489
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 17 | 17 | 0 | 0 |  |  | 46370
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 38056
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 2 |  | 15 | [6 empty] | 20072
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 485090
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1687000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | [16 empty] | 100 | 102 |  | 100 | 100 | 95 | 99 | 101 | 101 | 102 | 751000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 304 | 302 | 310 | 300 | 330 | 320 | 324 | 325 | 331 | 325 | 350 | 326 | 299 | 299 | 300 | 300 | 300 |  | 300 | 300 | 300 | 330 | 302 | 322 | 301 | 7429709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 |  | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 2193942
32 | Ashuganj 50 MW PP | 42 | 5 | 5 | 5 | 5 | 10 | 33 | 36 | 33 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 36 | 39 | 730584
33 | Ashuganj 225 MW CCPP | 185 | 175 | 178 | 176 | 166 | 196 | 200 | 181 | 165 | 184 | 182 | 201 | 115 | 184 | 165 | 163 | 165 | 184 |  | 184 | 192 | 184 | 185 | 183 | 184 | 183 | 4454000
34 | Ashuganj 450 MW CCPP(South) | 315 | 320 | 280 | 280 | 265 | 285 | 290 | 310 | 290 | 320 | 310 | 330 | 310 | 305 | 280 | 280 | 280 | 280 |  | 280 | 285 | 305 | 320 | 320 | 315 | 310 | 7405500
| Ashuganj 450 MW CCPP(North) | 315 | 320 | 275 | 275 | 265 | 295 | 340 | 315 | 275 | 320 | 320 | 330 | 310 | 300 | 320 | 325 | 285 | 280 |  | 290 | 310 | 320 | 320 | 325 | 320 | 310 | 7715900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 453600
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 89 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 90 | 90 |  | 90 | 90 | 92 | 91 | 90 | 91 | 90 | 2124920
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 339 | 350 | 346 | 340 | 355 | 343 | 363 | 335 | 358 | 336 | 349 | 350 | 368 | 353 | 300 | 341 | 345 |  | 330 | 338 | 339 | 347 | 339 | 341 | 348 | 8386560
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 340 | 340 | 340 | 340 | 340 | 472 | 472 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 6795250
41 | Haripur 360MW CCPP(HPL) | 367 | 367 | 327 | 307 | 277 | 275 | 275 | 357 | 300 | 360 | 360 | 320 | 320 | 300 | 320 | 290 | 270 | 270 |  | 360 | 363 | 364 | 364 | 365 | 367 | 370 | 7852000
42 | RPCL 210MW CCPP | 72 | 94 | 94 | 94 | 94 | 106 | 106 | 107 | 107 | 105 | 104 | 102 | 92 | 92 | 92 | 92 | 103 | 103 |  | 104 | 104 | 107 | 94 | 106 | 107 | 107 | 2312480
43
44 | Fenchugonj CCPP Phase-1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 85 | 86 | 87 | 89 | 86 | 89 | 87 | 86 | 86 | 86 |  | 88 | 88 | 85 | 85 | 85 | 88 | 85 | 2073000
45 | Fenchugonj CCPP Phase-2 | 73 | 61 | 61 | 61 | 61 | 61 | 61 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1694760
46 | Shajibazar 330 MW CCPP | 147 | 150 | 152 | 154 | 157 | 147 | 159 | 151 | 149 | 147 | 147 | 152 | 152 | 151 | 151 | 145 | 155 | 150 |  | 145 | 150 | 144 | 145 | 147 | 150 | 147 | 3443000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 57 | 67 | 66 | 65 | 64 | 63 | 64 | 63 | 45 | 45 | 45 | 45 |  | 65 | 65 | 66 | 65 | 65 | 66 | 67 | 1353888
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 81 | 79 | 79 | 40 | 50 | 50 | 50 | 50 | 20 | 20 | 30 | 10 | 30 |  | 78 | 78 | 78 | 78 | 79 | 79 | 79 | 1164480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | [17 empty] | 16 |  | 67 | 67 | 68 | 68 | 68 | 128 | 128 | 487980
51 | Sylhet 20 MW GTPP | [14 empty] | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18100
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 163980
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 8 | 8 | 8 | 5 | 5 | 5 | 0 | 0 | 5 | 5 |  |  | 11 |  | 8 |  | 11 |  | 8 | 85232
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 20 | 48 | 48 | 48 | 48 | 48 | 45 | 48 | 17 | 19 | 20 | 20 | 35 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 796800
56 | Shahjahanulla 25 MW PP | [7 empty] | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 414052
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 315 | 315 | 310 | 310 | 290 | 320 | 280 | 310 | 300 | 300 | 310 | 320 | 300 | 300 | 290 | 285 |  | 270 | 310 | 280 | 275 | 290 | 270 | 300 | 7561200
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 427584
61 | Narshingdi 22 MW PP (Doreen) | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 326916
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [8 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 333288
63 | Impoprt (Tripura) | 80 | 80 | 78 | 76 | 76 | 76 | 82 | 74 | 76 | 72 | 80 | 84 | 82 | 84 | 84 | 78 | 86 | 112 |  | 114 | 112 | 116 | 112 | 102 | 98 | 92 | 2097600
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 32 | 2 | 2 | 2 | 2 | 3 | 8 | 7 | 3 | 5 | 14 | 18 |  | 22 | 26 | 30 | 35 | 33 | 36 | 38 | 554880
65 | Feni 22MW PP (Doreen) | [6 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 391860
66 | Feni 11 MW PP (Doreen) | [7 empty] | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 147960
67 | Jangalia 33MW PP (Summit) | 8 |  |  |  |  | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 26 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 592000
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 19 | 20 | 20 | 18 | 18 | 18 | 21 | 21 | 21 | 14 | 14 | 14 | 14 | 0 | [10 empty] | 292580
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 30 | 32 | 32 | 32 | 32 | 32 | 26 | 24 | 28 | 32 | 32 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 709920
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 624400
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 622800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
Chowmuhani 113 MW
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 18 | 24 | 45 | 50 | 80 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 70 | 32 | 1286400
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 90 | 1492800
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 28 |  | 2 | [6 empty] | 32124
| Kaptai 7 MW Solar PP | [6 empty] | 0.13 | 0.6 | 1.5 | 3.5 | 4.4 | 4.7 | 4.2 | 3.7 | 2.8 | 1.51 | 0.43 | [9 empty] | 27120
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 10 |  | 65 | 50 | 50 |  |  |  |  | 149736
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 3326051
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 5 | 7 | 24 | 24 | 24 | 12 | 7 | 7 | 7 | 28 |  | 100 | 100 | 100 | 100 | 40 |  |  | 535680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 11 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 20 | 20 | 30 | 20 | 30 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 875952
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 19 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 886260
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 1 | 16 | 24 | 32 | 32 | 32 | 7 | 7 | 24 | 24 | 102 |  | 102 | 102 | 102 | 102 | 50 |  |  | 635616
95 | Patenga 50MW PP (Baraka) | [10 empty] | 11 | 18 | 19 | 9 | 6 | 6 | 6 | 12 |  | 50 | 50 | 50 | 50 | 18 |  |  | 258240
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 22 |  | 86 | 91 | 91 |  |  |  |  | 234240
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 13 |  | 36 | 15 | 15 |  |  |  |  | 80505
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 42 |  | 55 | 55 | 55 | 17 |  |  |  | 162872
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 163 | 130 | 130 | 100 | 100 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3694009
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.2 | 0.7 | 1.2 | 1.5 | 1.5 | 1.5 | 1 | 0.4 | 0.3 | 0.1 | [9 empty] | 8500
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [6 empty] | 40 | 53 | 35 | 17 | 30 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 815760
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 14 | 40 | 40 | 40 | 40 | 50 | 55 | 55 | 55 | 55 | 96 |  | 120 | 70 | 70 | 16 |  |  |  | 844800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 2 | 36 | 52 | 96 | 89 | 90 | 90 | 108 | 85 | 70 | 100 | 102 | 106 |  | 150 | 149 | 149 | 149 | 110 | 50 | 41 | 1697760
115 | Juldah 100 MW PP Unit-3 (Acorn) | [9 empty] | 10 | 10 | 10 | 10 |  |  |  |  | 72 |  | 100 | 100 | 100 | 70 |  |  |  | 359040
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 13 |  | 120 | 50 | 50 |  |  |  |  | 247564
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 50 | 8 | 8 | 8 | 12 | 56 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 80 | 80 | 80 | 2221200
| Anwara 300 MW PP (United) | [7 empty] | 85 | 98 | 68 | 70 | 87 | 89 | 89 | 90 | 122 | 125 | 193 |  | 198 | 181 | 180 | 180 | 182 | 124 | 51 | 1987200
120 | Eastern Zone Total | 4527 | 4393 | 4185 | 4166 | 4083 | 4347 | 4600.63 | 5174.1 | 5068 | 5004.8 | 4992.4 | 5133.5 | 5090.7 | 4953.31 | 4818.52 | 4841.41 | 4836.72 | 5433 |  | 6241 | 6162 | 6164 | 5901 | 5580 | 5328 | 5188 | 121756939
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 40 | 66 | 32 | 32 | 32 | 49 | 49 | 52 | 66 | 69 | 83 |  | 115 | 115 | 115 | 115 | 47 | 0 |  | 938880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 51 | 0 | [6 empty] | 40 | 42 | 42 | 42 | 73 | 75 | 74 | 32 | 12 | 13 |  | 97 | 96 | 97 | 98 | 98 | 75 | 74 | 1013222
| Bhola 225 MW CCPP | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 79 | 85 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 2042687
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 15 | 15 | 14 | 16 | 15 | 13 | 12 | 11 | 11 | 13 | 7 | 10 | 0 |  |  | 8 |  | 9 | 9 | 10 | 9 | 5 | 5 | 5 | 52871
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 4 | 0 | [8 empty] | 3712
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 135 | 131 | 130 | 131 | 132 | 151 | 524 | 524 | 524 | 524 | 524 | 526 | 527 | 526 | 528 | 527 | 528 | 674 |  | 771 | 771 | 772 | 772 | 771 | 529 | 287 | 11019636
147 | Bheramara 410 MW CCPP | 330 | 345 | 340 | 350 | 325 | 365 | 365 | 330 | 300 | 350 | 330 | 300 | 300 | 300 | 275 | 225 | 200 | 185 |  | 180 | 190 | 210 | 245 | 275 | 300 | 330 | 7231140
148 | Payra 1320 MW | 277 | 252 | 250 | 251 | 251 | 268 | 285 | 317 | 351 | 403 | 443 | 453 | 453 | 454 | 468 | 385 | 444 | 513 |  | 548 | 550 | 549 | 547 | 484 | 398 | 353 | 9208200
149
150 | Barapukuria TPP Unit-1 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 90 | 90 | 89 | 89 | 89 | 90 | 89 | 88 | 89 | 88 |  | 90 | 91 | 91 | 90 | 90 | 90 | 91 | 2107636
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5344800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 25 | 25 | 25 | 0 | 0 |  |  | 66248
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 220 | 180 | 150 | 150 | 150 | 150 | 150 | 160 | 170 | 185 | 200 | 170 | 200 | 170 | 170 | 150 | 150 | 150 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 4214927
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 432 | 434 | 434 | 386 | 381 | 348 | 345 | 406 | 357 | 402 | 419 | 433 | 405 | 385 | 399 | 374 | 366 | 335 |  | 300 | 300 | 300 | 300 | 301 | 303 | 301 | 9045272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 21 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 365040
163 | Bogura 20 MW PP (Energyprima) | 12 | 0 |  |  | 0 | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 222408
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 221148
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 24 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 606960
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 51 | 51 | 51 | 36 | 8 | 0 | 0 | 182512
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 3 | [8 empty] | 36288
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 5 | 70 | 109 | 50 | 50 | 60 | 90 | 70 | 70 | 70 | 70 | 70 |  | 109 | 109 | 109 | 109 | 109 | 70 | 70 | 1441056
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 35 | 40 | 36 | 35 | 35 | 35 | 0 |  |  |  | 70 |  | 76 | 100 | 107 | 107 | 56 | 0 | 0 | 609600
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.7 | 1.8 | 3 | 3.7 | 4.1 | 4.1 | 3.6 | 2.6 | 1.6 | 0.6 | [9 empty] | 25300
178
178