## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January' 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | January 2020 |  | December 2019 |  | January 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 9223 | 29/01/20 | 8778 | 01/12/19 | 8893 | 30/01/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 4592 | 04/01/20 | 4418 | 27/12/19 | 4350 | 01/01/19 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 9223 | 29/01/20 | 8778 | 01/12/19 | 8893 | 30/01/19 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 7826.5 | 30/01/20 | 7011.5 | 01/12/19 | 7189.5 | 27/01/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 9223 | 29/01/20 | 8778 | 01/12/19 | 8893 | 04/12/18 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8654.0323 |  | 8416.16 |  | 8425.06 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 6812.4677 |  | 6544.68 |  | 6485.91 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 744 | 26/01/2020 | 734 | 05/12/19 | 710 | 12/01/19 | 956 | 27/3/2019
|  |  | 21:00 |  | 21:30 |  | 20:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 114 | 28/01/2020 | 134 | 23/12/19 | 136 | 22/01/19 | 194 | 12/06/19
|  |  | 19:00 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3270.3498 |  | 3036.88 |  | 2531.59 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 109.7554 |  | 95.87 |  | 197.11
22 | Net Generation of BPDB (MKWH) | 3160.5944 |  | 2941.01 |  | 2334.48
23 | Net Generation of IPP & RPCL (MKWH) | 1203.4622 |  | 1215.98 |  | 1416.26
24 | Net Generation of REB (MKWH) | 122.5711 |  | 120.34 |  | 137.09
24 | Net Generation of Rental Power Plant (MKWH) | 192.4291 |  | 237.5 |  | 350.99
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4679.0569 |  | 4514.83 |  | 4238.82 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 4188.1368 |  | 4033.99 |  | 3703.98 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 18.1418 |  | 26.26 |  | 28.79 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 309.3084 |  | 350.34 |  | 547.71 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 29.2644 |  | 53.83 |  | 35.25 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 4.9089 |  | 4.86 |  | 5.45 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 239.052 |  | 141.42 |  | 114.75 |  | 243.72 | Sept-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 286.1577 |  | 270.33 |  | 423.75 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 73.9585 |  | 74.74 |  | 73.45 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:January' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 9223 | 29/01/20 | 19:00
Generation Period
| Dhaka | MW | 3046
| Chattogram | MW | 959
| Cumilla | MW | 738
| Mymensingh | MW | 745
| Sylhet | MW | 317
a) | Total supply in East zone | MW | 5805
| Khulna | MW | 1029
| Barisal | MW | 225
| Rajshahi | MW | 952
| Rangpur | MW | 636
b) | Total supply in West zone | MW | 2842
c) | Total supply in both zone ( a+b) | MW | 8647
Ref: | 27.21.0000.603.16.087.20.245 | Date: 16/02/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 595 | 28/01/20 | 8:00
| b) Ishurdi end | MW | 137 | 07/01/20 | 13:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 340 | 07/01/20 | 13:00
| b) Ishurdi end | MW | 231 | 28/01/20 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 4.422 | 24/01/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 4.0497 | 24/01/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 86.1058
| b) Ishurdi end | MKWH | 0.57876
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.5614
| b) Ishurdi end | MKWH | 83.5979
23 | Transmission loss of EWI/ NO-1 | % | 2.9126
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 570 | 31/01/20 | 19:00
| b)Serajganj end | MW | 185 | 02/01/20 | 17:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 180 | 02/01/20 | 17:00
| b)Sirajganj end | MW | 530 | 31/01/20 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.054 | 29/01/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 9.95 | 29/01/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 143.058
| b)Sirajganj end | MKWH | 3.784
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.714
| b)Sirajganj end | MKWH | 142.716
30 | Transmission loss of EWI /NO-2 | % | 0.186
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/1 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV Transformer-T2 | 2020-01-04 19:54 | 2020-01-04 20:57 | 1:03 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Tongi | 132/33 kV Transformers-T-1 & T2 & 33 kV feeder fault | 2020-01-09 06:29 | 2020-01-09 06:55 | 0:26 | T | Due to Tripping of 33 kV feeder fault | 30 | 13 | Power interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-01-16 19:47 | 2020-01-16 20:03 | 0:16 | T | Tripped showing O/C relay | 47 | 12.5333 | Power interruption
Tangail | 132/33 kV Transformer-T4 | 2020-01-18 20:08 | 2020-01-18 21:58 | 1:50 | T | Tripped showing diff. relay at 33 kV side | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2020-01-19 10:26 | 2020-01-19 12:14 | 1:48 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-01-25 06:02 | 2020-01-25 16:19 | 10:17 | T | Tripped showing PRD operated | 0 | 0 | No interruption
Savar | 132/33 kV Transformers-T1 & T2 | 2020-01-25 10:37 | 2020-01-25 10:58 | 0:21 | T | Tripped showing E/F relay at 33 kV side | 56 | 19.6 | Power interruption
|  |  | Total : | 16:01 |  | Unserved Energy: |  | 45.1333
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformers-T1 & T2 | 2020-01-07 10:56 | 2020-01-07 11:08 | 0:12 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Shyampur | 132 kV main Bus | 2020-01-10 21:20 | 2020-01-10 22:35 | 1:15 | E/O | Due to red-hot maintenance | 25 | 31.25 | Power interruption
Sonargaon | 132/33 kV Transformer-T1 | 2020-01-23 12:24 | 2020-01-23 12:40 | 0:16 | T | Tripped showing 33 kV feeder fault | 64 | 17.0667 | Power interruption
|  |  | Total : | 1:43 |  | Unserved Energy: |  | 48.3167
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T2 | 2020-01-23 13:10 | 2020-01-23 14:47 | 1:37 | E/O | Due to 33 kV side flashing | 0 | 0 | No interruption
|  |  | Total : | 1:37 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sreemongal | 132/33 kV Transformers-T1 & T3 | 2020-01-07 07:22 | 2020-01-07 08:55 | 1:33 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformers-T1 | 2020-01-08 04:02 | 2020-01-08 05:00 | 0:58 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-01-08 04:02 | 2020-01-08 04:40 | 0:38 | T | Tripped showing remote protection relay | 36 | 22.8 | Power interruption
Sreemongal | 132/33 kV Transformer-T2 & 33 kV Bus-2 | 2020-01-17 10:29 | 2020-01-17 11:28 | 0:59 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-01-26 11:09 | 2020-01-26 11:54 | 0:45 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 4:53 |  | Unserved Energy: |  | 22.8
Khulna Grid Circle :
Gopalganj GIS | 400/132 kV Transformers-T01 | 2020-01-03 09:29 | 2020-01-03 12:30 | 3:01 | T | Tripped showing protection relay | 0 | 0 | No interruption
| 400/132 kV Transformers-T02 | 2020-01-03 09:29 | 2020-01-03 12:35 | 3:06 |  |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-06 03:18 | 2020-01-06 08:37 | 5:19 | T | Tripped showing over voltage | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-06 07:06 | 2020-01-06 07:36 | 0:30 | T |  | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T4 | 2020-01-12 15:20 | 2020-01-12 17:26 | 2:06 | E/O | Due to flashing of 33 kV Y-phase isolator | 15 | 31.5 | Power interruption
Noapara | 132/33 kV Transformer-T2 | 2020-01-24 11:53 | 2020-01-24 15:16 | 3:23 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2020-01-31 09:30 | 2020-01-31 09:40 | 0:10 | T | Tripped showing no signal | 0 | 0 | No interruption
Goplaganj | 400/132 kV Transformers-T01 & T02 | 2020-01-31 09:32 | 2020-01-31 13:38 | 4:06 | T | Tripped showing differential relay | 0 | 0 | No interruption
|  |  | Total : | 21:41 |  | Unserved Energy: |  | 31.5
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformers-T01 & T02 | 2020-01-14 04:47 | 2020-01-14 07:24 | 2:37 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T01 | 2020-01-14 05:47 | 2020-01-14 07:30 | 1:43 | T | Tripped showing 51M CB61 signal | 0 | 0 | No interruption
|  |  | Total : | 4:20 |  |  |  | 0
Bogura Grid Circle:
Bogura(O) | 230/132 kV Transformers-T03 & T04 | 2020-01-03 04:20 | 2020-01-03 04:26 | 0:06 | T | Tripped showing O/C. relay | 20 | 2 | Power interruption
Rajshahi | 132/33 kV Transformer-T2 | 2020-01-03 04:58 | 2020-01-03 09:55 | 4:57 | T | Tripped showing O/C. relay at 33 kV side | 8 | 39.6 | Power interruption
Norail | 132/33 kV Transformer-T1 | 2020-01-07 12:46 | 2020-01-07 13:50 | 1:04 | E/O | Due to red hot maintenance | 6 | 6.4 | Power interruption
Joypurhat | 132/33 kV Transformer-T3 | 2020-01-24 12:25 | 2020-01-24 18:31 | 6:06 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-01-28 14:56 | 2020-01-28 15:38 | 0:42 | E/O | Due to red hot maintenance | 25 | 17.5 | Power interruption
Palashbari | 132/33 kV Transformer-T3 | 2020-01-28 14:56 | 2020-01-28 15:35 | 0:39 | E/O | Due to red hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 13:34 |  | Unserved Energy: |  | 65.5
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 63:49 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Aminbazar 230 kV line-2 | 2020-01-01 17:09 | 2020-01-01 20:41 | 3:32 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
| Kaliakoir-Aminbazar 230 kV line-1 | 2020-01-01 17:09 | 2020-01-01 17:29 | 0:20 | T |  | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 & 2 | 2020-01-14 17:40 | 2020-01-14 17:49 | 0:09 | T | Tripped showing dist. relay | 60 | 9 | Power interruption
Jodevpur | Jodevpur-Kadda 132 kV line-1 | 2020-01-20 06:53 | 2020-01-20 08:00 | 1:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Summit Gazaipur 230 kV line | 2020-01-26 09:10 | 2020-01-26 10:07 | 0:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Summit Gazipur 230 kV line-2 | 2020-01-26 09:10 | 2020-01-26 10:10 | 1:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2020-01-27 09:41 | 2020-01-27 15:39 | 5:58 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-2 | 2020-01-27 14:02 | 2020-01-27 14:17 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 13:18 |  | Unserved Energy: |  | 9
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 230 kV line-2 | 2020-01-01 10:29 | 2020-01-01 10:41 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2020-01-01 14:58 | 2020-01-01 15:37 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(N) 132 kV line-2 | 2020-01-02 08:15 | 2020-01-02 09:22 | 1:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2020-01-08 04:02 | 2020-01-08 16:55 | 12:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line | 2020-01-08 16:59 | 2020-01-10 16:28 | 47:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbgah 132 kV line | 2020-01-08 10:10 | 2020-01-08 10:29 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur(O)-Shyampur(N) 132 kV line-1 | 2020-01-15 18:37 | 2020-01-15 19:42 | 1:05 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Shyampur(O)-Shyampur(N) 132 kV line-2 | 2020-01-15 19:47 | 2020-01-15 21:34 | 1:47 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2020-01-17 11:12 | 2020-01-17 11:20 | 0:08 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj (S) 230 kV line-2 | 2020-01-18 11:00 | 2020-01-18 11:10 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ashuganj (S) 230 kV line-3 | 2020-01-18 13:45 | 2020-01-18 13:58 | 0:13 | T |  | 0 | 0 | No interruption
|  |  | Total : | 66:02 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Hathazari | Hathazari-Baroaulia 132 kV line-1 | 2020-01-03 12:55 | 2020-01-03 13:05 | 0:10 | T | Tripped showing O/C & E/F .relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha(New)-Madunaghat 132 kV line | 2020-01-26 02:59 | 2020-01-26 03:38 | 0:39 | T |  | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2020-01-26 02:59 | 2020-01-26 03:47 | 0:48 | T |  | 0 | 0 | No interruption
Khulshi | Khulshi-Modern steel 132 kV line | 2020-01-29 17:00 | 2020-01-29 19:40 | 2:40 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 4:17 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-2 | 2020-01-03 10:22 | 2020-01-03 11:24 | 1:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-01-03 09:29 | 2020-01-03 09:51 | 0:22 | T | Tripped showing dist. relay | 26 | 9.5333 | Power interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-1 | 2020-01-10 11:44 | 2020-01-10 12:05 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2020-01-13 22:19 | 2020-01-13 22:41 | 0:22 | T | Tripped showing dist. relay | 25 | 9.1667 | Power interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-01-20 20:18 | 2020-01-20 20:43 | 0:25 | T | Tripped showing dist. relay | 22 | 9.1667 | Power interruption
|  |  | Total : | 2:32 |  | Unserved Energy: |  | 27.8667
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: January 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-01-05 18:20 | 2020-01-05 18:31 | 0:11 | T | Tripped showing dist. relay | 454 | 83.2333 | Power interruption
Faridpur | Faridpur-Gopalganj (New) 132 kV line-1 | 2020-01-05 18:20 | 2020-01-05 18:22 | 0:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Gopalganj (New) 132 kV line-2 | 2020-01-05 18:20 | 2020-01-05 18:36 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line-2 | 2020-01-05 19:39 | 2020-01-06 02:54 | 7:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Madaripur-Gopalganj 132 kV line-2 | 2020-01-07 02:24 | 2020-01-07 04:00 | 1:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Faridpur 132 kV line-1 | 2020-01-16 09:26 | 2020-01-16 10:28 | 1:02 | T | Tripped showing dist. relay | 175 | 151.6667 | Power interruption 09:26 to 10:18
| Gopalganj(N)-Maripur 132 kV line-1 | 2020-01-16 09:26 | 2020-01-16 10:42 | 1:16 | T | Tripped showing gen.trip & O/V relay | 0 | 0 | No interruption
| Gopalganj(N)-Maripur 132 kV line-2 | 2020-01-16 09:26 | 2020-01-16 11:01 | 1:35 | T |  | 0 | 0 | No interruption
| Gopalganj(N)-Maridpur 132 kV line-2 | 2020-01-17 03:52 | 2020-01-17 05:51 | 1:59 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2020-01-18 07:18 | 2020-01-21 16:55 | 81:37 | E/O | Due to oil leakage | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line-2 | 2020-01-31 09:30 | 2020-01-31 09:47 | 0:17 | T |  | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV line-1 | 2020-01-31 09:30 | 2020-01-31 10:16 | 0:46 | T | Tripped showing gen.trip & O/V relay | 0 | 0 | No interruption
| Madaripur-Shariatpur 132 kV line-2 | 2020-01-31 09:30 | 2020-01-31 10:30 | 1:00 | T |  | 0 | 0 | No interruption
| Madaripur-Gopalganj 132 kV line-2 | 2020-01-31 10:16 | 2020-01-31 13:24 | 3:08 | T | Tripped showing gen.trip & O/V relay | 0 | 0 | No interruption
| Madaripur-Gopalganj 132 kV line-1 | 2020-01-31 09:32 | 2020-01-31 09:45 | 0:13 | T | Tripped showing gen.trip relay | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV line-2 | 2020-01-31 09:32 | 2020-01-31 15:01 | 5:29 | T | Tripped showing gen.trip & O/V relay | 0 | 0 | No interruption
|  |  | Total : | 107:42 |  | Unserved Energy: |  | 234.9
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 & 2 | 2020-01-05 18:20 | 2020-01-05 18:44 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-HVDC 230 kV line-1 & 2 | 2020-01-14 05:47 | 2020-01-14 08:09 | 2:22 | T | Tripped showing main protection relay | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 230 kV line-1 | 2020-01-14 05:47 | 2020-01-14 08:09 | 2:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bheramara-Ishurdi 230 kV line-2 | 2020-01-14 05:47 | 2020-01-14 08:12 | 2:25 | T |  | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-1 | 2020-01-22 15:13 | 2020-01-22 15:54 | 0:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2020-01-22 15:13 | 2020-01-22 15:30 | 0:17 | T |  | 286 | 81.0333 | Power interruption
|  |  | Total : | 8:31 |  | Unserved Energy: |  | 81.0333
Bogura Grid Circle :
Bogura(O) | Bogura(O)-Bogura(N) 132 kV line-2 | 2020-01-02 04:02 | 2020-01-02 04:44 | 0:42 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Paramount 200 MW | Paramount 200 MW-Baghabari 230 kV line | 2020-01-03 04:18 | 2020-01-03 05:05 | 0:47 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajsahi(O) 132 kV line-1 | 2020-01-19 10:59 | 2020-01-19 21:54 | 10:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2020-01-20 11:31 | 2020-01-20 11:43 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(N) 132 kV line-1 & 2 | 2020-01-21 22:50 | 2020-01-21 23:43 | 0:53 | T | Tripped showing dist.& O/C relay | 46 | 29.9 | Power interruption 22:50 to 23:29
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-01-24 11:21 | 2020-01-24 13:16 | 1:55 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
|  |  | Total : | 15:24 |  | Unserved Energy: |  | 29.9
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 226:17 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kallyanpur | 132/33 kV Transformer-T3 | 2020-01-01 09:15 | 2020-01-01 20:11 | 10:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-02 08:25 | 2020-01-02 20:12 | 11:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132 kV Bus-2 | 2020-01-03 10:48 | 2020-01-03 12:30 | 1:42 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2020-01-03 12:40 | 2020-01-03 14:58 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132 kV full Bus | 2020-01-04 07:45 | 2020-01-04 14:04 | 6:19 | S/O | Due to C/M work | 35 | 221.0833 | Power interruption
New Tongi | 132/33 kV Transformer-T1 | 2020-01-04 07:53 | 2020-01-04 16:18 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 33 kV Bus | 2020-01-04 09:40 | 2020-01-04 18:30 | 8:50 | S/O | Due to D/W work | 70 | 450.3333 | Power interruption 09:40 to 16:06
Kallyanpur | 132/33 kV Transformer-T1 | 2020-01-05 08:47 | 2020-01-05 20:07 | 11:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T01 | 2020-01-05 10:27 | 2020-01-05 17:10 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-01-05 09:33 | 2020-01-05 16:12 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-01-05 08:56 | 2020-01-05 16:37 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T3 | 2020-01-05 08:50 | 2020-01-05 13:46 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 | 2020-01-06 08:35 | 2020-01-06 20:12 | 11:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T01 | 2020-01-06 08:17 | 2020-01-06 16:53 | 8:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-01-06 08:16 | 2020-01-06 16:38 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-01-06 08:50 | 2020-01-06 16:12 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2020-01-07 12:11 | 2020-01-07 16:49 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-01-07 08:10 | 2020-01-07 16:37 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-01-07 08:55 | 2020-01-07 16:38 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2020-01-08 10:07 | 2020-01-08 17:08 | 7:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-01-08 08:45 | 2020-01-08 16:58 | 8:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T2 | 2020-01-08 08:10 | 2020-01-08 16:10 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2020-01-08 09:21 | 2020-01-08 22:02 | 12:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T02 | 2020-01-09 09:07 | 2020-01-09 11:06 | 1:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2020-01-09 08:42 | 2020-01-09 21:16 | 12:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Cantonment | 132/33 kV Transformer-T2 | 2020-01-09 08:02 | 2020-01-09 18:50 | 10:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 33 kV Bus section-4 | 2020-01-09 16:06 | 2020-01-09 16:40 | 0:34 | S/O | Due to PDB work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-01-10 07:10 | 2020-01-10 13:48 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-01-11 09:06 | 2020-01-11 15:01 | 5:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-12 08:56 | 2020-01-12 15:23 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-A | 2020-01-12 10:10 | 2020-01-29 15:40 | 413:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-01-13 08:31 | 2020-01-13 15:18 | 6:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-01-13 08:10 | 2020-01-13 10:02 | 1:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | 132 kV Bus | 2020-01-13 10:28 | 2020-01-13 14:10 | 3:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 & 33 kV Bus-A | 2020-01-14 09:21 | 2020-01-14 10:25 | 1:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 | 2020-01-15 08:47 | 2020-01-15 16:55 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T4 | 2020-01-16 08:44 | 2020-01-16 15:57 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T1 |  | 2020-01-16 14:47 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 |  | 2020-01-16 15:54 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kaliakoir | 132/33 kV Transformer-T2 | 2020-01-17 08:55 | 2020-01-17 13:02 | 4:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-01-18 08:34 | 2020-01-18 15:25 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2020-01-18 10:44 | 2020-01-18 13:01 | 2:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Valuka | 132/33 kV Transformer-T2 | 2020-01-18 10:58 | 2020-01-18 15:52 | 4:54 | S/O | Due to distribution work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2020-01-18 10:30 | 2020-01-18 16:16 | 5:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV Transformer-T2 | 2020-01-19 08:12 | 2020-01-19 15:11 | 6:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2020-01-19 08:45 | 2020-01-19 16:54 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2020-01-19 09:58 | 2020-01-19 12:29 | 2:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-01-19 09:35 | 2020-01-19 13:16 | 3:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV Bus | 2020-01-19 10:24 | 2020-01-19 11:46 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-01-19 13:22 | 2020-01-19 15:25 | 2:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-01-20 08:10 | 2020-01-20 15:35 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2020-01-20 08:53 | 2020-01-20 16:37 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T1 | 2020-01-20 08:13 | 2020-01-20 14:59 | 6:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2020-01-20 09:45 | 2020-01-20 16:40 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-20 09:49 | 2020-01-20 10:40 | 0:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-A |  | 2020-01-20 08:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 | 2020-01-21 08:32 | 2020-01-21 16:57 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2020-01-21 08:15 | 2020-01-21 15:17 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-01-21 09:20 | 2020-01-21 16:35 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2020-01-22 08:42 | 2020-01-22 13:26 | 4:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T5 | 2020-01-23 08:48 | 2020-01-23 16:34 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2020-01-23 09:15 | 2020-01-23 20:08 | 10:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 | 2020-01-23 09:14 | 2020-01-23 10:04 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T2 | 2020-01-23 08:12 | 2020-01-23 15:01 | 6:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2020-01-24 08:54 | 2020-01-24 15:10 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| 33 kV Bus-A | 2020-01-25 08:56 | 2020-01-25 14:17 | 5:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2020-01-26 09:25 | 2020-01-26 14:46 | 5:21 | S/O | Due to tan-delta test | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B & 132/33 kV Transformer T3 | 2020-01-27 09:27 | 2020-01-27 15:47 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-01-27 10:08 | 2020-01-27 15:45 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 | 2020-01-27 11:13 | 2020-01-27 16:01 | 4:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | 132/33 kV Transformer-T1 | 2020-01-28 09:51 | 2020-01-28 13:43 | 3:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-01-29 08:34 | 2020-01-29 15:55 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-2 | 2020-01-29 08:15 | 2020-01-29 12:41 | 4:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-01-29 08:08 | 2020-01-29 10:06 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-29 10:02 | 2020-01-29 13:54 | 3:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T01 | 2020-01-30 08:35 | 2020-01-30 12:40 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 850:24 |  | Unserved Energy: |  | 671.4167
Dhaka (South) Grid Circle :
Siddhirganj | 132 kV bay | 2020-01-01 10:52 | 2020-01-01 13:27 | 2:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2020-01-02 08:52 | 2020-01-02 15:30 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400 kV Bus-2 | 2020-01-02 10:11 | 2020-01-02 16:20 | 6:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 33 kV Bus | 2020-01-04 08:47 | 2020-01-04 15:41 | 6:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132 kV Bus-2 | 2020-01-06 09:10 | 2020-01-06 17:43 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2020-01-07 08:40 | 2020-01-07 16:20 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 230 kV Bus-1 | 2020-01-07 09:52 | 2020-01-07 16:37 | 6:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230 kV Bus-2 | 2020-01-10 09:24 | 2020-01-10 14:16 | 4:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T03 | 2020-01-11 09:33 | 2020-01-11 22:32 | 12:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T1 | 2020-01-11 09:22 | 2020-01-11 17:41 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230 kV Bus-1 | 2020-01-11 08:50 | 2020-01-11 14:13 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-17 07:13 | 2020-01-17 08:20 | 1:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Munshiganj | 132/33 kV Transformer-T1 | 2020-01-18 10:12 | 2020-01-18 16:44 | 6:32 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-19 09:46 | 2020-01-19 13:45 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformer-T2 | 2020-01-22 08:02 | 2020-01-22 14:18 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakyha | 132/33 kV Transformer-T3 | 2020-01-22 09:35 | 2020-01-22 16:20 | 6:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2020-01-23 10:10 | 2020-01-23 14:58 | 4:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(O) | 132/33 kV Transformer-T1 |  | 2020-01-24 12:09 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sonargaon | 132 kV Bus-1 | 2020-01-25 08:22 | 2020-01-25 10:32 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2020-01-25 10:45 | 2020-01-25 12:55 | 2:10 | S/O |  | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-GT1 | 2020-01-25 09:36 | 2020-01-25 12:47 | 3:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV Transformer-T3 | 2020-01-26 09:51 | 2020-01-26 17:15 | 7:24 | S/O | Due to temperature high at B-phase bushing | 0 | 0 | No interruption
Bhulta | 400/132 kV Transformer-ATR1 | 2020-01-26 09:03 | 2020-01-26 16:40 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Labagh | 132/33 kV Transformer-T1 | 2020-01-26 09:06 | 2020-01-26 19:38 | 10:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2020-01-26 08:20 | 2020-01-26 21:19 | 12:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2020-01-27 08:46 | 2020-01-27 21:03 | 12:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV Transformer-ATR2 | 2020-01-27 08:56 | 2020-01-27 16:14 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | 132 kV main Bus | 2020-01-27 08:49 | 2020-01-27 16:45 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2020-01-28 09:11 | 2020-01-28 20:22 | 11:11 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 190:59 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | 132/33 kV Transformer-T2 | 2020-01-02 09:04 | 2020-01-02 15:30 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-01-03 07:05 | 2020-01-03 16:19 | 9:14 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-04 10:45 | 2020-01-04 11:30 | 0:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132 kV Bus | 2020-01-04 09:30 | 2020-01-04 16:06 | 6:36 | S/O | Due to A/M work | 24 | 158.4 | Power interruption
Barulia | 132/33 kV Transformer-T1 | 2020-01-05 10:28 | 2020-01-05 15:34 | 5:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T1 | 2020-01-07 09:22 | 2020-01-07 15:58 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-08 10:10 | 2020-01-08 16:20 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2020-01-08 14:38 | 2020-01-08 15:02 | 0:24 | S/O | Due to isolator problem | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2020-01-10 08:07 | 2020-01-10 16:14 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2020-01-11 09:20 | 2020-01-11 14:57 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2020-01-11 08:05 | 2020-01-11 15:37 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | 132 kV bay | 2020-01-11 08:34 | 2020-01-11 13:33 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT4 | 2020-01-12 09:18 | 2020-01-12 16:28 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT3 | 2020-01-16 08:50 | 2020-01-16 16:11 | 7:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2020-01-17 08:51 | 2020-01-17 16:47 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-18 08:17 | 2020-01-18 13:32 | 5:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1 | 2020-01-18 08:02 | 2020-01-18 13:01 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T3 | 2020-01-19 08:44 | 2020-01-19 16:46 | 8:02 | S/O | Due to A/M work | 25 | 200.8333 | Power interruption
Bakulia | 132/33 kV Transformer-T1 | 2020-01-19 08:20 | 2020-01-19 15:23 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2020-01-21 09:28 | 2020-01-21 13:15 | 3:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV Transformer-T2 | 2020-01-21 08:12 | 2020-01-21 14:09 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-21 14:14 | 2020-01-21 16:17 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-01-24 07:12 | 2020-01-24 12:44 | 5:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV Transformer-T2 | 2020-01-24 09:19 | 2020-01-24 18:16 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT4 | 2020-01-26 09:10 | 2020-01-26 12:08 | 2:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | 132/33 kV Transformer-T1 | 2020-01-30 09:21 | 2020-01-30 17:27 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-31 10:39 | 2020-01-31 15:24 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 157:23 |  | Unserved Energy : |  | 359.2333
Page: 4/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sylhet | 132/33 kV Transformer-T1 | 2020-01-05 07:29 | 2020-01-05 14:43 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-01-11 08:30 | 2020-01-11 15:52 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T3 | 2020-01-12 08:40 | 2020-01-12 15:55 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2020-01-12 09:10 | 2020-01-16 09:13 | 96:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2020-01-12 10:28 | 2020-01-12 11:56 | 1:28 | S/O | Due to projection work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV Transformer-T4 | 2020-01-13 08:45 | 2020-01-13 15:08 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenachuganj | 132 kV Bus-1 | 2020-01-13 09:54 | 2020-01-13 17:20 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 |  | 2020-01-16 14:20 |  | S/O | After maintenance work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2020-01-20 07:32 | 2020-01-20 15:58 | 8:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2020-01-23 08:22 | 2020-01-23 17:26 | 9:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-01-26 09:30 | 2020-01-26 16:53 | 7:23 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 158:04 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Khulna(C) | 230/132 kV Transformer-T2 | 2020-01-01 12:09 | 2020-01-01 12:38 | 0:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
Barishal | 132/33 kV Transformer-T2 with 33 kV Bus | 2020-01-02 08:37 | 2020-01-02 16:47 | 8:10 | S/O | Due to Bus extension work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T3 | 2020-01-02 20:50 |  |  | S/O | Due to air compressure problem | 0 | 0 | No interruption
Barishal | 132/33 kV Transformer-T1 | 2020-01-04 08:45 | 2020-01-04 17:22 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Narail | 132/33 kV Transformer-T2 | 2020-01-04 10:16 | 2020-01-04 11:45 | 1:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T3 & 33 kV Bus | 2020-01-09 06:01 | 2020-01-09 09:09 | 3:08 | S/O | Due to D/W work | 18 | 56.4 | Power interruption
| 132/33 kV Transformer-T1 | 2020-01-09 09:09 | 2020-01-09 16:18 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus | 2020-01-09 14:29 | 2020-01-09 16:10 | 1:41 | S/O | Due to C/M work | 68 | 114.4667 | Power interruption
| 132/33 kV Transformer-T3 |  | 2020-01-11 10:39 |  | S/O | After maintenance work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T5 | 2020-01-12 12:14 | 2020-01-12 17:30 | 5:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T1 | 2020-01-13 10:29 | 2020-01-13 12:40 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-01-14 11:34 | 2020-01-14 12:09 | 0:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T5 | 2020-01-16 07:43 | 2020-01-16 15:58 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(O) | 132/33 kV Transformer-T2 with Bus-2 | 2020-01-17 08:34 | 2020-01-17 15:08 | 6:34 | S/O | Due to 33 kV Bus extension. | 25 | 164.1667 | Power interruption
Khulna | 132/33 kV Transformer-T2 | 2020-01-25 07:36 | 2020-01-25 13:38 | 6:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | 132/33 kV Transformer-T2 | 2020-01-31 08:31 | 2020-01-31 13:03 | 4:32 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 64:08 |  | Unserved Energy : |  | 335.0333
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformer-T01 | 2020-01-04 09:51 | 2020-01-04 17:33 | 7:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T2 | 2020-01-04 10:19 |  |  | S/O | Due to replacement work | 0 | 0 | No interruption
| 132/33 kV Transformer-T01 | 2020-01-08 10:25 | 2020-01-08 18:50 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2020-01-08 09:08 | 2020-01-08 15:28 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV new Transformer |  | 2019-01-09 18:13 |  | S/O | Due to new connection | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T3 | 2020-01-12 09:02 | 2020-01-12 18:13 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T3 | 2020-01-11 08:54 | 2020-01-11 15:15 | 6:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-12 13:23 | 2020-01-12 15:56 | 2:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara(G.K) | 132/33 kV Transformer-T2 | 2020-01-14 07:40 | 2020-01-19 17:40 | 130:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-01-18 08:33 | 2020-01-18 17:30 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-19 09:10 | 2020-01-19 16:22 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara HVDC 20DF 40 filter | 2020-01-25 10:47 | 2020-01-25 17:35 | 6:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC 20DF 40 filter | 2020-01-26 09:44 | 2020-01-26 16:10 | 6:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-2 | 2020-01-27 08:50 | 2020-01-27 18:19 | 9:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2020-01-28 08:42 | 2020-01-28 15:45 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T2 | 2020-01-29 10:48 | 2020-01-29 13:48 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC filter bay | 2020-01-29 11:35 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 211:45 |  | Unserved Energy : |  | 0
Page: 5/5 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Bogura(O) | 132 kV Bus-2 | 2020-01-01 10:35 | 2020-01-01 15:34 | 4:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132 kV main Bus | 2020-01-01 09:15 | 2020-01-01 13:05 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2020-01-02 08:34 | 2020-01-02 15:17 | 6:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-05 08:25 | 2020-01-05 13:38 | 5:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2020-01-05 09:28 | 2020-01-05 14:28 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T2 | 2020-01-06 09:15 | 2020-01-06 14:06 | 4:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T4 | 2020-01-07 13:49 | 2020-01-07 15:30 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 | 2020-01-07 08:18 | 2020-01-07 15:50 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2020-01-07 08:53 | 2020-01-07 13:47 | 4:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2020-01-07 10:20 | 2020-01-07 13:12 | 2:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 | 2020-01-08 08:35 | 2020-01-08 15:46 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-09 08:25 | 2020-01-09 16:20 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-11 08:11 | 2020-01-11 17:01 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T4 |  | 2020-01-11 14:36 |  | S/O | After maintenance work | 0 | 0 | No interruption
Purbasadipur | 132 kV Bus | 2020-01-12 07:07 | 2020-01-12 12:01 | 4:54 | S/O | Due to D/W work | 100 | 490 | Power interruption
Baghabari | 230/132 kV Transformer-TR2 | 2020-01-12 08:25 | 2020-01-12 17:17 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2020-01-12 08:25 | 2020-01-12 16:49 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-01-12 09:22 | 2020-01-19 16:45 | 175:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-TR2 | 2020-01-13 08:53 | 2020-01-13 16:49 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi(New) | 132 kV Bus-2 | 2020-01-13 08:45 | 2020-01-13 13:27 | 4:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T1 | 2020-01-14 12:48 | 2020-01-14 16:16 | 3:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-TR2 | 2020-01-14 09:50 | 2020-01-14 14:50 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T3 | 2020-01-16 10:01 | 2020-01-16 11:50 | 1:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 & 33 kV Bus-2 | 2020-01-17 08:48 | 2020-01-17 12:48 | 4:00 | S/O | Due to Bus extension work | 55 | 220 | Power interruption
Noagaon | 132 kV Bus-3 & 132/33 kV Transformer T3 | 2020-01-18 08:35 | 2020-01-18 12:28 | 3:53 | S/O | Due to distribution work | 0 | 0 | No interruption
Matarbari | 132/33 kV Transformer-T1 | 2020-01-20 10:56 | 2020-01-20 15:40 | 4:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132 kV Bus | 2020-01-20 08:30 | 2020-01-20 17:06 | 8:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi | 132 kV bay | 2020-01-20 09:57 | 2020-01-20 17:41 | 7:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Matarbari | 132/33 kV Transformer-T2 | 2020-01-21 10:28 | 2020-01-21 14:56 | 4:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | 132 kV main Bus | 2020-01-24 06:52 | 2020-01-24 10:35 | 3:43 | S/O | Due to D/W work | 75 | 278.75 | Power interruption
Barapukuria | 132/33 kV Transformer-T4 |  | 2020-01-24 13:07 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformers-T1 | 2020-01-24 14:53 | 2020-01-24 16:55 | 2:02 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2020-01-24 14:53 | 2020-01-24 16:56 | 2:03 | S/O |  | 0 | 0 | No interruption
| 132 kV main Bus | 2020-01-25 11:50 | 2020-01-31 12:50 | 145:00 | S/O |  | 0 | 0 | No interruption
Noagaon | 132/33 kV Transformer-T2 | 2020-01-25 12:14 | 2020-01-25 13:05 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T3 | 2020-01-28 11:30 | 2020-01-28 15:07 | 3:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-01-28 09:06 | 2020-01-28 11:28 | 2:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(O) | 132/33 kV Transformer-T2 | 2020-01-30 10:24 | 2020-01-30 17:02 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Joldhaka | 132/33 kV Transformer-T2 | 2020-01-31 09:22 | 2020-01-31 11:15 | 1:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-01-31 11:20 | 2020-01-31 12:25 | 1:05 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 494:38 |  | Unserved Energy : |  | 988.75
Others :
Kanrangirchar | 132/33 kV Transformer-GT1 | 2020-01-13 08:16 | 2020-01-13 20:22 | 12:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT1 | 2020-01-14 09:10 | 2020-01-14 17:12 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT1 | 2020-01-15 08:39 | 2020-01-15 15:56 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT2 | 2020-01-16 08:36 | 2020-01-16 21:16 | 12:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-01-18 08:46 | 2020-01-18 16:50 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-22 09:13 | 2020-01-22 21:30 | 12:17 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-01-22 08:32 | 2020-01-22 21:12 | 12:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2020-01-21 10:15 | 2020-01-21 14:50 | 4:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Matuail | 132/ kV Transformer-GT1 | 2020-01-24 09:17 | 2020-01-24 13:59 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/ kV Transformer-GT2 | 2020-01-31 09:16 | 2020-01-31 17:02 | 7:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total | 90:09 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2217:30 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-01-01 07:44 | 2020-01-01 15:50 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2020-01-01 08:58 | 2020-01-01 20:41 | 11:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-1 | 2020-01-01 08:23 | 2020-01-01 16:57 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2020-01-01 09:12 | 2020-01-01 16:18 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2020-01-02 09:24 | 2020-01-02 17:28 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line | 2020-01-02 08:33 | 2020-01-02 15:08 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132 kV line-2 | 2020-01-02 09:16 | 2020-01-02 16:36 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2020-01-02 08:53 | 2020-01-02 20:15 | 11:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kadda 230 kV line | 2020-01-02 09:05 | 2020-01-02 16:33 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2020-01-03 11:24 | 2020-01-03 16:45 | 5:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kadda 230 kV line | 2020-01-04 09:32 | 2020-01-04 16:42 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-2 | 2020-01-04 08:57 | 2020-01-04 21:36 | 12:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2020-01-04 08:37 | 2020-01-04 16:12 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-2 | 2020-01-05 08:45 | 2020-01-05 16:49 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2020-01-05 09:59 | 2020-01-05 15:30 | 5:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara(third phase) 132 kV line | 2020-01-05 08:10 | 2020-01-05 20:25 | 12:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2020-01-05 08:23 | 2020-01-05 15:42 | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-1 | 2020-01-05 09:07 | 2020-01-05 17:22 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line-2 | 2020-01-05 09:14 | 2020-01-05 17:02 | 7:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-2 | 2020-01-06 07:48 | 2020-01-06 16:55 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Joydevpur | Joydevpur-Ghorashal 132 kV line-1 | 2020-01-06 09:01 | 2020-01-06 15:54 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2020-01-06 08:13 | 2020-01-06 15:24 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-01-06 09:10 | 2020-01-06 17:16 | 8:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kaliakoir 230 kV line-2 | 2020-01-06 09:15 | 2020-01-06 17:28 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2020-01-07 10:15 | 2020-01-07 15:53 | 5:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kv line-2 | 2020-01-11 09:30 | 2020-01-11 18:25 | 8:55 | S/O | Due to D/W work | 0 | 0 | No interruption
| Aminbazar-Savar 132 kV line-2 | 2020-01-13 07:35 | 2020-01-13 21:53 | 14:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-01-13 09:10 | 2020-01-13 13:50 | 4:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh-Mymensingh RPCL 132 kV line | 2020-01-14 10:17 | 2020-01-14 18:11 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-01-15 08:56 | 2020-01-15 17:33 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2020-01-15 09:21 | 2020-01-15 17:48 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2020-01-16 09:09 | 2020-01-16 15:35 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-01-16 09:58 | 2020-01-16 12:26 | 2:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2020-01-16 09:01 | 2020-01-16 21:30 | 12:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2020-01-17 08:29 | 2020-01-17 17:07 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminbazar 132 kV line-2 | 2020-01-18 10:44 | 2020-01-18 13:01 | 2:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 | 2020-01-19 08:56 | 2020-01-19 20:07 | 11:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2020-01-20 08:36 | 2020-01-20 19:31 | 10:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-2 | 2020-01-20 09:52 | 2020-01-20 16:47 | 6:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 | 2020-01-20 13:44 | 2020-01-20 16:58 | 3:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara(third phase) 132 kV line | 2020-01-21 10:40 | 2020-01-21 14:40 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Uttara 132 kV line | 2020-01-21 10:41 | 2020-01-21 13:20 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2020-01-21 09:02 | 2020-01-21 13:52 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2020-01-21 09:10 | 2020-01-21 16:30 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Aminabazar 132 kV line-1 | 2020-01-21 08:55 | 2020-01-21 22:07 | 13:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-22 08:51 | 2020-01-22 17:24 | 8:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid GIS 132 kV line-2 | 2020-01-23 08:20 | 2020-01-23 11:56 | 3:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-23 08:28 | 2020-01-23 16:18 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt & Tongi -Uttara 3rd phase 132 kV line | 2020-01-23 11:05 | 2020-01-23 14:01 | 2:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 |  | 2020-01-24 16:18 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tongi 230 kV line | 2020-01-25 09:21 | 2020-01-25 17:22 | 8:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-25 08:38 | 2020-01-25 16:32 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 2/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2020-01-25 09:35 | 2020-01-26 17:31 | 31:56 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kaliakoir-Kabirpur 132 kV line-1 | 2020-01-25 10:22 | 2020-01-26 17:27 | 31:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | Kadda-Joydevpur 132 kV line-2 | 2020-01-26 08:38 | 2020-01-26 16:33 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-26 09:15 | 2020-01-26 16:44 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-2 | 2020-01-27 09:19 | 2020-01-27 16:32 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV line | 2020-01-27 08:00 | 2020-01-27 17:11 | 9:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-27 09:04 | 2020-01-27 12:13 | 3:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Bibiyana 400 kV line-2 | 2020-01-28 09:21 | 2020-01-28 16:32 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kaliakoir-Kabirpur 132 kV line-1 & 2 | 2020-01-27 09:45 | 2020-01-27 16:58 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-1 | 2020-01-28 07:44 | 2020-01-28 16:28 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2020-01-29 09:06 | 2020-01-29 10:13 | 1:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Jamalpur-Mymensingh 132 kV line-2 | 2020-01-29 10:15 | 2020-01-29 10:49 | 0:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kodda 230 kV line | 2020-01-31 10:05 | 2020-01-31 20:38 | 10:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Amibazar 230 kV line-2 | 2020-01-31 09:47 | 2020-01-31 16:11 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-01-31 12:23 |  |  | S/O | Due to re-conductoring work at 1 Month | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-2 | 2020-01-31 13:01 |  |  | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 531:22 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2020-01-01 08:54 | 2020-01-01 16:18 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Madartek 132 kV line-1 | 2020-01-01 10:14 | 2020-01-01 17:04 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Madartek 132 kV line-1 | 2020-01-02 08:52 | 2020-01-02 13:04 | 4:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Moghbazar 132 kV line-1 | 2020-01-03 12:20 | 2020-01-03 13:40 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV line-2 | 2020-01-04 08:35 | 2020-01-04 15:28 | 6:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur Gis | Shyampur Gis-Meghnaghat 230 kV line-1 | 2020-01-04 09:18 | 2020-01-04 18:05 | 8:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR Shyampur 230 kV line | 2020-01-05 07:07 | 2020-01-05 15:02 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur Gis | Shyampur Gis-Meghnaghat 230 kV line | 2020-01-06 07:09 | 2020-01-06 17:04 | 9:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV line-1 | 2020-01-06 12:00 | 2020-01-06 14:17 | 2:17 | S/O | Due to tree trimming | 0 | 0 | No interruption
| Ghorashal-Tongi 230 kV line-2 | 2020-01-07 07:38 | 2020-01-07 16:03 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Joydevpur 132 kV line-2 | 2020-01-07 08:45 | 2020-01-07 16:30 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 132 kV line-1 | 2020-01-07 08:03 | 2020-01-07 21:02 | 12:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV line-2 | 2020-01-08 07:26 | 2020-01-09 10:52 | 27:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 132 kV line-2 | 2020-01-08 08:32 | 2020-01-08 16:47 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV line-1 | 2020-01-09 09:44 | 2020-01-09 17:55 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2020-01-11 07:49 | 2020-01-11 15:17 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Narshingdi | Narshingdi-Ghorashal 132 kV line-1 | 2020-01-11 09:03 | 2020-01-11 17:31 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-2 | 2020-01-12 06:52 | 2020-01-12 14:37 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2020-01-13 10:08 | 2020-01-13 13:25 | 3:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-1 | 2020-01-13 10:05 | 2020-01-13 16:09 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-2 | 2020-01-14 10:29 | 2020-01-14 16:21 | 5:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-1 | 2020-01-14 09:30 | 2020-01-14 16:05 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-01-14 12:45 | 2020-01-14 17:47 | 5:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV line-2 | 2020-01-16 10:12 | 2020-01-16 15:15 | 5:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV line-1 | 2020-01-16 08:33 | 2020-01-16 20:35 | 12:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Haripur-Bhulta 230 kV line-1 | 2020-01-16 08:15 | 2020-01-16 14:16 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj CCPP P/S 230 kV line-2 | 2020-01-16 13:33 | 2020-01-16 14:46 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2020-01-16 14:46 | 2020-01-16 16:56 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2020-01-17 10:49 | 2020-01-17 12:25 | 1:36 | S/O | Due to bird nest | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2020-01-18 08:58 | 2020-01-18 14:44 | 5:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Gulshan 132 kV line-2 | 2020-01-19 10:54 | 2020-01-19 15:23 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-01-20 10:16 | 2020-01-20 17:28 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2020-01-21 08:32 | 2020-01-21 15:41 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Bhulta | Bhulta-Ghorashal 230 kV line-2 | 2020-01-21 08:17 | 2020-01-21 16:14 | 7:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Ghorashal 230 kV line-1 | 2020-01-22 08:17 | 2020-01-22 15:15 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bhulta-Asahuganj 400 kV line-2 | 2020-01-23 09:19 | 2020-01-23 15:19 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2020-01-24 08:06 | 2020-01-24 16:28 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur Gis | Shyampur Gis-Haripur-ShyampurGIS-Bramongaon 132 kV line | 2020-01-24 13:09 |  |  | S/O | Due to D/W work(for 10 days) | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2020-01-25 08:26 | 2020-01-25 16:12 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2020-01-26 09:18 | 2020-01-26 16:21 | 7:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-01-26 12:09 | 2020-01-26 16:58 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Madertek 132 kV line | 2020-01-26 08:23 | 2020-01-26 21:23 | 13:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Rampura-Madertek 132 kV line-1 | 2020-01-27 08:46 | 2020-01-27 21:26 | 12:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV line-2 | 2020-01-27 08:49 | 2020-01-27 16:45 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Shitalakhya | Shitalakhya-Hasnabad 132 kV line | 2020-01-28 09:51 | 2020-01-28 17:58 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Katpotti 132 kV line | 2020-01-28 07:20 | 2020-01-28 18:21 | 11:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.baria 132 kV line-1 | 2020-01-28 09:17 | 2020-01-28 17:04 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2020-01-28 09:11 | 2020-01-28 16:28 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-1 & 2 | 2020-01-29 07:35 | 2020-01-30 07:08 | 23:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2020-01-29 08:47 | 2020-01-29 17:32 | 8:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2020-01-30 08:42 | 2020-01-30 16:17 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 388:22 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2020-01-01 08:00 | 2020-01-01 16:22 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2020-01-01 08:59 | 2020-01-01 17:01 | 8:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-01-01 08:04 | 2020-01-01 15:55 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line | 2020-01-02 07:58 | 2020-01-02 16:04 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSML 230 kV line | 2020-01-03 09:42 | 2020-01-03 15:15 | 5:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2020-01-05 09:09 | 2020-01-05 14:57 | 5:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Khulshi-Madunaghat -Hathazari132 kV line | 2020-01-06 08:12 | 2020-01-06 15:57 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Hathazari 132 kV line-2 | 2020-01-07 08:13 | 2020-01-07 16:17 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2020-01-08 09:19 | 2020-01-08 16:19 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Hathazari 132 kV line | 2020-01-08 08:46 | 2020-01-08 16:19 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Hathazari 132 kV line | 2020-01-11 08:17 | 2020-01-11 15:47 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Hathazari 132 kV line | 2020-01-12 08:14 | 2020-01-12 16:43 | 8:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Abul khair-Barulia 132 kV line | 2020-01-13 07:55 | 2020-01-13 16:23 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2020-01-14 09:07 | 2020-01-14 14:44 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-01-14 08:26 | 2020-01-14 17:56 | 9:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Abul khair 132 kV line | 2020-01-14 08:22 | 2020-01-14 14:32 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-01-15 08:18 | 2020-01-15 16:55 | 8:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Abul khair | Abul khair-Baraulia 132 kV line-1 | 2020-01-15 08:25 | 2020-01-15 16:16 | 7:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV line | 2020-01-15 12:15 | 2020-01-15 13:33 | 1:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV line | 2020-01-16 07:54 | 2020-01-16 16:16 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Baraulia 132 kV line | 2020-01-19 08:47 | 2020-01-19 17:07 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Baraulia 132 kV line | 2020-01-20 08:11 | 2020-01-20 13:31 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-2 | 2020-01-22 08:33 | 2020-01-22 14:12 | 5:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line-1 | 2020-01-23 08:38 | 2020-01-23 12:14 | 3:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Kagrachari | Kagrachari-Rangamati 132 kV line-1 & 2 | 2020-01-25 09:46 | 2020-01-25 12:41 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kagrachari-Rangamati 132 kV line-2 | 2020-01-28 05:56 | 2020-01-28 16:19 | 10:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kagrachari-Rangamati 132 kV line-2 | 2020-01-27 09:19 | 2020-01-27 15:01 | 5:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Modern 132 kV line | 2020-01-29 08:25 | 2020-01-29 14:12 | 5:47 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bakulia-Modern 132 kV line | 2020-01-30 08:19 | 2020-01-30 14:50 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 200:09 |  | Unserved Energy: |  | 0
Page: 4/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2020-01-01 09:40 | 2020-01-01 17:06 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2020-01-01 08:48 | 2020-01-01 17:13 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2020-01-02 08:56 | 2020-01-02 15:23 | 6:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1 | 2020-01-02 09:29 | 2020-01-02 14:40 | 5:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2020-01-04 08:53 | 2020-01-04 15:25 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2020-01-05 08:48 | 2020-01-05 17:23 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV line-2 | 2020-01-06 09:17 | 2020-01-06 16:40 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Kulaura 132 kV line-2 | 2020-01-07 09:26 | 2020-01-07 16:06 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj -Sreemongal 132 kV line-2 | 2020-01-09 09:50 | 2020-01-09 16:29 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj -Sreemongal 132 kV line-2 | 2020-01-10 08:48 | 2020-01-10 15:42 | 6:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2020-01-11 08:50 | 2020-01-11 14:13 | 5:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV line-2 | 2020-01-12 08:44 | 2020-01-12 15:46 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Shahjibazar-Sreemongal 132 kV line-2 | 2020-01-13 08:08 | 2020-01-13 14:41 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2020-01-14 09:44 | 2020-01-14 12:32 | 2:48 | S/O | Due to A/M work | 15 | 42 | Power interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2020-01-14 09:30 | 2020-01-14 20:55 | 11:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-01-15 08:35 | 2020-01-15 16:31 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2020-01-15 09:09 | 2020-01-15 17:03 | 7:54 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2020-01-15 08:07 | 2020-01-15 17:03 | 8:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-1 | 2020-01-16 09:15 | 2020-01-16 17:04 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2020-01-16 08:41 | 2020-01-16 17:00 | 8:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Shahjibazar 230 kV line-1 | 2020-01-17 08:33 | 2020-01-17 15:24 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-01-17 07:41 | 2020-01-17 14:23 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-1 | 2020-01-18 09:21 | 2020-01-18 16:36 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Cumilla(N) 132 kV line-1 | 2020-01-19 10:46 | 2020-01-19 11:21 | 0:35 | S/O | Due to removing nest | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2020-01-19 08:31 | 2020-01-19 17:12 | 8:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-2 | 2020-01-19 09:22 | 2020-01-19 15:52 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
B.baria | B.baria-Narshingdi 132 kV line-2 | 2020-01-19 08:52 | 2020-01-19 15:44 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj P/S 132 kV line |  | 2020-01-19 16:20 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2020-01-20 09:04 | 2020-01-20 15:48 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchugan P/S 132 kV line-2 | 2020-01-20 09:32 | 2020-01-20 14:04 | 4:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV line-2 | 2020-01-21 09:06 | 2020-01-21 15:18 | 6:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV line-1 | 2020-01-21 10:40 | 2020-01-21 11:04 | 0:24 | S/O | Due to removing nest | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV line-2 | 2020-01-21 11:09 | 2020-01-21 11:25 | 0:16 | S/O | Due to removing nest | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2020-01-21 09:45 | 2020-01-21 12:28 | 2:43 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Sreemongal 132 kV line-2 | 2020-01-21 12:31 | 2020-01-21 15:10 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
| Fenchuganj-Bibiyana 230 kV line-1 | 2020-01-25 10:03 | 2020-01-25 15:23 | 5:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Sreemongal 132 kV line-2 | 2020-01-25 08:30 | 2020-01-25 16:42 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2020-01-26 08:30 | 2020-01-26 18:14 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2020-01-27 10:15 | 2020-01-27 11:02 | 0:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line | 2020-01-29 09:06 | 2020-01-29 16:38 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV line-2 | 2020-01-29 09:40 | 2020-01-29 10:56 | 1:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2020-01-31 07:38 | 2020-01-31 11:44 | 4:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-01-31 11:45 | 2020-01-31 15:09 | 3:24 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 251:34 |  | Unserved Energy: |  | 42
Page: 5/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | Madaripur-Sariatpur 132 kV line-1 | 2020-01-01 08:32 | 2020-01-01 15:57 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Sariatpur 132 kV line-2 | 2020-01-02 08:23 | 2020-01-02 16:01 | 7:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj 400 | Gopalganj 400-Payra 400 kV line-2 |  | 2020-01-04 20:00 |  |  | New connection | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-1 | 2020-01-04 08:09 | 2020-01-04 17:22 | 9:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhola P/S | Bhola P/S-Barishal(N) 230 kV line-2 | 2020-01-04 09:39 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-1 & 2 | 2020-01-04 08:34 | 2020-01-04 17:57 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-01-05 07:30 | 2020-01-05 15:52 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna(C) | Khulna©-NWPGCL 132 kV line-1 | 2020-01-05 09:10 | 2020-01-05 16:24 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Kustia 132 kV line-2 | 2020-01-07 08:00 | 2020-01-07 15:43 | 7:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-1 | 2020-01-07 12:39 | 2020-01-07 17:45 | 5:06 | S/O | Due to project work | 0 | 0 | No interruption
Barishal | Barishal-Patuakhlai 132 kV line | 2020-01-08 07:30 | 2020-01-08 17:12 | 9:42 | S/O | Due to A/M work | 35 | 339.5 | Power interruption
Goalapara | Goalapara-NWPGCL 132 kV line | 2020-01-08 08:18 | 2020-01-08 16:45 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal | Barishal-Patuakhlai 132 kV line | 2020-01-09 06:53 | 2020-01-09 17:16 | 10:23 | S/O | Due to A/M work | 40 | 415.3333 | Power interruption
Khulna(C) | Khulna©-KPCL -2 132 kV line | 2020-01-09 09:26 | 2020-01-09 15:30 | 6:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-2 |  | 2020-01-09 13:44 |  | S/O | After maintenance work | 0 | 0 | No interruption
Barishal | Barishal-Bhola 230 kV line-2 |  | 2020-01-11 14:26 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Barishal-Patuakhlai 132 kV line | 2020-01-12 07:02 | 2020-01-12 17:12 | 10:10 | S/O | Due to D/W work | 30 | 305 | Power interruption
| Barishal-Patuakhlai 132 kV line | 2020-01-13 06:50 | 2020-01-13 17:53 | 11:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barishal-Patuakhlai 132 kV line | 2020-01-14 06:54 | 2020-01-14 16:51 | 9:57 | S/O | Due to C/M work | 35 | 348.25 | Power interruption
| Barishal-Barishal Summit 132 kV line | 2020-01-14 09:37 | 2020-01-14 15:47 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal-Patuakhlai 132 kV line | 2020-01-15 06:57 | 2020-01-15 17:55 | 10:58 | S/O | Due to C/M work | 30 | 329 | Power interruption
Faridpur S/S | Faridpur S/S-Faridpur P/S 132 kV line | 2020-01-15 09:10 | 2020-01-15 15:28 | 6:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-01-16 07:22 | 2020-01-16 17:08 | 9:46 | S/O | Due to C/M work | 32 | 312.5333 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-01-16 07:20 | 2020-01-16 09:36 | 2:16 | S/O | Due to Bhandaria shift to Barishal(S) | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-01-17 07:13 | 2020-01-17 16:34 | 9:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(O) | Barishal(O)-Baraishal Summit P/S 132 kV line | 2020-01-17 08:28 | 2020-01-17 16:55 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-01-18 06:57 | 2020-01-18 18:26 | 11:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line | 2020-01-18 08:16 | 2020-01-18 16:50 | 8:34 | S/O | Due to D/W work | 40 | 342.6667 | Power interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-01-19 06:57 | 2020-01-19 17:45 | 10:48 | S/O | Due to C/M work | 40 | 432 | Power interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-01-20 06:49 | 2020-01-20 17:41 | 10:52 | S/O | Due to re-conductoring work | 40 | 434.6667 | Power interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-01-21 07:05 | 2020-01-21 17:26 | 10:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Shariatpur | Shariatpur-Madaripur 132 kV line-2 | 2020-01-22 10:28 | 2020-01-22 16:28 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-01-23 06:50 | 2020-01-23 17:54 | 11:04 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-01-24 06:50 | 2020-01-24 17:54 | 11:04 | S/O | Due to C/M work | 36 | 398.4 | Power interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-01-25 06:50 | 2020-01-25 17:55 | 11:05 | S/O | Due to C/M work | 31 | 343.5834 | Power interruption
| Barishal(S)-Bhandaria 132 kV line | 2020-01-25 07:46 | 2020-01-25 16:21 | 8:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(S)-Bhandaria 132 kV line | 2020-01-26 07:57 | 2020-01-26 16:47 | 8:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-01-26 06:58 | 2020-01-26 13:33 | 6:35 | S/O | Due to D/W work | 35 | 230.4167 | Power interruption
| Barishal(S)-Bhandaria 132 kV line | 2020-01-27 08:19 | 2020-01-27 16:35 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Bhandaria 132 kV line | 2020-01-28 08:17 | 2020-01-28 16:23 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barishal (N) 132 kV line-1 | 2020-01-30 10:54 | 2020-01-30 13:00 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madaripur-Barishal (N) 132 kV line-2 | 2020-01-30 13:04 | 2020-01-30 14:16 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV line-1 | 2020-01-31 09:32 | 2020-01-31 15:56 | 6:24 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 322:27 |  | Unserved Energy: |  | 4231.3501
HVDC Grid Circle :
Jhenidah | Jhenidah-Chuadanga 132 kV line | 2020-01-04 07:10 | 2020-01-04 18:06 | 10:56 | S/O | Due to D/W work | 35 | 382.6667 | Power interruption
Bheramara | Bheramara-Kustia 132 kV line-1 | 2020-01-04 07:02 | 2020-01-04 21:21 | 14:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Kustia 132 kV line-2 | 2020-01-08 08:08 | 2020-01-08 14:49 | 6:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/6 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Bheramara | Bheramara-Kustia 132 kV line-2 | 2020-01-09 08:08 | 2020-01-09 14:49 | 6:41 | S/O | Due to A/M work | 68 | 454.4667 | Power interruption
| Bheramara-Faridpur 132 kV line-1 | 2020-01-10 07:22 | 2020-01-10 15:17 | 7:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Pabna 132 kV line | 2020-01-10 08:24 | 2020-01-10 17:12 | 8:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shahjadpur-Pabna 132 kV line | 2020-01-11 07:50 | 2020-01-11 16:56 | 9:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2020-01-11 08:10 | 2020-01-11 16:37 | 8:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2020-01-11 07:52 | 2020-01-11 15:18 | 7:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV line |  | 2020-01-11 08:27 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line-1 | 2020-01-12 08:38 | 2020-01-12 16:11 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kustia-Jhenidah 132 kV line-1 | 2020-01-13 09:05 | 2020-01-13 16:07 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kustia-Jhenidah 132 kV line-2 | 2020-01-14 10:07 | 2020-01-14 17:31 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Kustia-Jhenidah 132 kV line-2 | 2020-01-15 09:42 | 2020-01-15 15:43 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 |  | 2020-01-15 20:32 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Kustia | Kustia-Jhenidah 132 kV line | 2020-01-16 09:12 | 2020-01-16 15:48 | 6:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 | 2020-01-17 09:21 | 2020-01-17 10:02 | 0:41 | S/O | Due to relay change | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV line-2 | 2020-01-17 11:27 | 2020-01-17 12:55 | 1:28 | S/O |  | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 132 kV line-1 | 2020-01-18 07:14 | 2020-01-20 16:35 | 57:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2020-01-19 08:45 | 2020-01-19 15:58 | 7:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 | 2020-01-21 07:04 | 2020-01-23 16:09 | 57:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2020-01-21 08:53 | 2020-01-21 18:09 | 9:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line-2 |  | 2020-01-23 16:09 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 247:59 |  | Unserved Energy: |  | 837.1333
Bogura Grid Circle :
Bogura(O) | Bogura (O)-Mohasthangarth 132 kV line-1 | 2020-01-01 10:05 | 2020-01-01 15:34 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2020-01-04 08:04 | 2020-01-04 15:37 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2020-01-10 06:26 | 2020-01-10 17:42 | 11:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Amnura | Amnura-Rajshahi(New) 132 kV line | 2020-01-13 11:08 | 2020-01-13 14:28 | 3:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Labonchura | Labonchura-Bagerhat 132 kV line | 2020-01-14 07:39 |  |  | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi(new) | Rajshahi(new)-Rajshahi(O) 132 kV line-2 | 2020-01-15 10:49 | 2020-01-15 13:24 | 2:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura (N) 132 kV line-2 | 2020-01-20 07:51 | 2020-01-20 14:36 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Bogura (N) 132 kV line-1 | 2020-01-21 08:55 | 2020-01-21 13:25 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Natore 132 kV line-2 | 2020-01-21 12:05 | 2020-01-21 17:30 | 5:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Naogaon 132 kV line-2 | 2020-01-21 12:05 | 2020-01-21 17:29 | 5:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Natore 132 kV line-1 | 2020-01-22 09:33 | 2020-01-22 17:18 | 7:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Naogaon 132 kV line-1 | 2020-01-22 09:27 | 2020-01-22 17:21 | 7:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Mohastanghor 132 kV line-2 | 2020-01-22 09:31 | 2020-01-22 17:19 | 7:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Mohasthangar 132 kV line-1 | 2020-01-23 12:50 | 2020-01-23 16:32 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-01-25 10:03 | 2020-01-25 10:52 | 0:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Bogura(N) 132 kV line-2 | 2020-01-26 07:51 | 2020-01-26 11:31 | 3:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Bogura(N) 132 kV line-1 | 2020-01-26 11:32 | 2020-01-26 17:25 | 5:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-2 | 2020-01-27 07:22 | 2020-01-27 10:10 | 2:48 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 | 2020-01-27 10:12 | 2020-01-27 16:40 | 6:28 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Amnura 132 kV line | 2020-01-27 08:03 | 2020-01-27 20:03 | 12:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Bogura(O) 132 kV line | 2020-01-29 10:31 | 2020-01-29 13:55 | 3:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Mohasthangar 132 kV line-2 | 2020-01-30 08:00 | 2020-01-30 10:20 | 2:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura(O)-Mohasthangar 132 kV line-1 | 2020-01-30 10:22 | 2020-01-30 16:58 | 6:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | Barapukuria P/S CB-802B | 2020-01-30 09:24 | 2020-01-30 14:15 | 4:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(new) | Rajshahi(New)-Rajshahi(O) 132 kV line-1 | 2020-01-30 16:04 | 2020-01-30 17:26 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2020-01-31 13:35 | 2020-01-31 14:31 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bogura-Natore 132 kV line-1 | 2020-01-31 13:36 | 2020-01-31 14:32 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 131:29 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2073:22 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January' 2020
| Area | Previous Month (December 2019) |  |  |  | Current Month (January 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 4 | 8 | 170 | 182 | 11 | 4 | 144 | 159
2 | Dhaka (South) Grid Circle. | 14 | 2 | 95 | 111 | 11 | 3 | 80 | 94
3 | Chattogram Grid Circle. | 13 |  | 70 | 83 | 3 | 2 | 56 | 61
4 | Cumilla Grid Circle. | 14 | 2 | 99 | 115 | 8 | 2 | 54 | 64
5 | Khulna Grid Circle. | 8 | 2 | 63 | 73 | 20 | 3 | 59 | 82
6 | Bheramara HVDC Grid Circle |  | 1 | 40 | 41 | 8 |  |  | 8
7 | Bogura Grid Circle. | 5 | 3 | 75 | 83 | 7 | 5 | 67 | 79
8 | Others | 2 | 1 | 7 | 10 |  |  | 10 | 10
9 | Total | 60 | 19 | 619 | 698 | 68 | 19 | 470 | 557
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January' 2020
| Area | Previous Month (December 2019) |  |  |  | Current Month (January 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 20.45 | 242.33 | 628.95 | 891.73 | 54.13 |  | 671.42 | 725.55
2 | Dhaka (South) Grid Circle. | 128.25 |  | 201 | 329.25 | 17.07 | 31.25 |  | 48.32
3 | Chattogram Grid Circle. | 199.83 | - | - | 199.83 |  |  | 359.23 | 359.23
4 | Cumilla Grid Circle. | 37.87 |  | 245.75 | 283.62 | 50.67 |  | 42 | 92.67
5 | Khulna Grid Circle. | 55.75 | - | - | 55.75 | 234.9 | 31.5 | 4566.38 | 4832.78
6 | Bheramara HVDC Grid Circle |  |  | 224.87 | 224.87 | 81.03 |  | 837.13 | 918.16
7 | Bogura Grid Circle. | 11.33 | 35.2 | 158.25 | 204.78 | 71.5 | 23.9 | 988.75 | 1084.15
8 | Others | - | 635.7 | - | 635.7 |  |  |  | 0
9 | Total | 453.48 | 913.23 | 1458.82 | 2825.53 | 509.3 | 86.65 | 7464.91 | 8060.86
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 3 | 2 | 5 | 3 |  | 2 | 716.55
2 | Dhaka (South) | 5031.6 | 2 |  | 2 | 2 |  |  | 48.32
3 | Chattogram | 2042 | 2 |  | 2 |  |  | 2 | 359.23
4 | Khulna | 2434 | 1 | 3 | 4 |  |  | 4 | 366.53
5 | Bheramara (HVDC) | 2423.3
6 | Bogura | 3145.6 | 2 | 3 | 5 | 1 | 1 | 4 | 1054.25
7 | Cumilla | 2981 | 1 |  | 1 |  | 1 |  | 22.8
8 | Others | -
| Total | 23365.5 | [6 empty] | 2567.68
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 100%
3 | Chattogram | 99.99%
4 | Khulna | 99.84%
5 | Bheramara (HVDC) | 99.86% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 |  | 1 | 1 |  |  | 9
2 | Dhaka (South) | 990.29 |  | - | - | - | - | - | - | -
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 2 | 12 | 14 | 1 |  | 13 | 4466.25
5 | Bheramara (HVDC) | 598.7 |  | 1 | 2 | 3 | 1 | - | 2 | 918.16
6 | Bogura | 1803.3 | 38 | 1 | 1 | 1 | 1 |  |  | 29.9
7 | Cumilla | 1648.16 | 17 | 3 | 1 | 4 | 3 | - | 1 | 69.87
7 | Others | - |  |  | - | - | - | - | - | -
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 5493.18
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.48%
3 | Chattogram | 100%
4 | Khulna | 99.58%
5 | Bheramara (HVDC) | 99.94% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.99% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-01-18 | 17 | - | 2 | 1 hr 57 min | - | - | - | - | 1 | 0 hr 17 min | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:January' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi | 1 | 0:26 | 30 | 13 | Due to tripping of 132/33 kV Transformers T1 & T2
Netrakona | 1 | 0:16 | 47 | 12.5333 | Due to tripping of 132/33 kV Transformer T3
Savar | 1 | 0:21 | 56 | 19.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Jamalpur | 1 | 0:09 | 60 | 9 | Due to tripping of Mymensingh-UMPL 132 kV line-1 & 2
Tangail | 1 | 6:19 | 35 | 221.0833 | Due to S/D of 132 kV full Bus
Kodda | 1 | 8:50 | 70 | 450.3333 | Due to S/D of 132 kV 33 kV Bus
Shyampur | 1 | 1:15 | 25 | 31.25 | Due to red-hot maintenance of 132 kV main Bus
Sonargaon | 1 | 0:16 | 64 | 17.0667 | Due to tipping of 33 kV feeder
Shahmirpur | 1 | 6:36 | 24 | 158.4 | Due to S/D of 132 kV Bus
Cox'sbazar | 1 | 8:02 | 25 | 200.8333 | Due to S/D of 132/33 kV Transformer T3
Daudkandi | 1 | 0:38 | 36 | 22.8 | Due to tripping of 132/33 kV Transformers T1 & T2
Sylhet | 1 | 0:22 | 26 | 9.5333 | Due to tripping of Sylhet-Fenchuganj 132 kV line-1 & 2
Fenchuganj | 1 | 0:22 | 25 | 9.1667 | Due to tripping of Fenchuganj-Sylhet 132 kV line
Sylhet |  | 0:25 | 22 | 9.1667 | Due to tripping of Sylhet-Fenchuganj 132 kV line
Fenchiganj | 1 | 2:48 | 15 | 42 | Due to S/D of Fenchuganj-Sylhet 132 kV line
Barishal(N) | 1 | 2:06 | 15 | 31.5 | Due to flashing of 33 kV Y-phase isolator
Bagerhat | 1 | 0:11 | 454 | 83.2333 | Due to trippig of Bagerhat-Bhandaria 132 kV line
Gopalganj(N) | 1 | 0:52 | 175 | 151.6667 | Due to tripping of Gopalganj(N)-Faridpur 132 kV line-1
Bagerhat | 1 | 3:08 | 18 | 56.4 | Due to S/D of 132/33 kV Transformer T3
| 1 | 1:41 | 68 | 114.4667 | Due to S/D of 132 kV Bus
Barishal | 7 | 6:34 | 25 | 164.1667 | Due to S/D of 132/33 kV Transformer T2 with Bus-2
|  | 9:42 | 35 | 339.5 | Due to S/D of Barishal-Patuakhali 132 kV line
|  | 10:23 | 40 | 415.3333
|  | 10:10 | 30 | 305
|  | 9:57 | 35 | 348.25
|  | 10:58 | 30 | 329
|  | 9:46 | 32 | 312.5333
Madaripur | 1 | 8:34 | 40 | 342.6667 | Due to S/D of Madaripur-Gopalganj 132 kV line
Barishal(S) |  | 10:48 | 40 | 432 | Due to S/D of Barishal-Patuakhali 132 kV line
|  | 10:52 | 40 | 434.6667
| 5 | 11:04 | 36 | 398.4
|  | 11:05 | 31 | 343.5834
|  | 6:35 | 35 | 230.4167
Bheramara |  | 0:17 | 286 | 81.0333 | Due to tripping of Bheramara-Faridpur 132 kV line-1 & 2
Jhenidah |  | 10:56 | 35 | 382.6667 | Due to S/D of Jhenidah-Chuadanga 132 kV line
Bheramara |  | 6:41 | 68 | 454.4667 | Due to S/D of Bheramara-Kustia 132 kV line-2
Bogura(O) | 1 | 0:06 | 20 | 2 | Due to tripping of 230/132 kV Transformers T03 & T04
Rajshahi |  | 4:57 | 8 | 39.6 | Due to tripping of 132/33 kV Transformer T2
Norall | 1 | 1:04 | 6 | 6.4 | Due to red-hot maintenance of 132/33 kV Transformer T1
Purbasadipur | 1 | 0:42 | 25 | 17.5
Bogura(O) | 1 | 0:53 | 46 | 29.9 | Due to tripping of Bogura(O)-Bogura(N) 132 kV line-1 & 2
Purbasadipur | 1 | 4:54 | 100 | 490 | Due to S/D of 132 kV Bus
Palashbari | 1 | 4:00 | 55 | 220 | Due to S/D of 132/33 kV Transformer T1 & 33 kV Bus
Bogura |  | 3:43 | 75 | 278.75 | Due to S/D of 132 kV Bus
| Total Unserved energy : |  |  | 8060.8668 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 110 | 9 | 2020-01-03 | 12:00
2 | Munsiganj | 86 | 9 | 2020-01-03 | 19:30
3 | Sonargaon | 79 | 28 | 2020-01-03 | 19:00
4 | Shyampur | 200 | 27 | 2020-01-03 | 0.54167
5 | Bhulta | 165 | 9 | 2020-01-03 | 12:00
6 | Madanganj | 57 | 23 | 2020-01-03 | 19:00
7 | Shitalakhya | 102 | 13 | 2020-01-03 | 12:00
8 | Rahim steel | 30 | 12 | 2020-01-03 | 16:00
9 | Matuail | 86 | 16 | 2020-01-03 | 0.41667
10 | Ghorasal | 74 | 30 | 2020-01-03 | 19:00
11 | Narsingdi | 125 | 7 | 2020-01-03 | 19:00
12 | Haripur (SBU) | 96 | 21 | 2020-01-03 | 15:00
13 | Ullon | 53 | 24 | 2020-01-03 | 0.5
14 | Hasnabad | 138 | 2 | 2020-01-03 | 0.79167
15 | Magbazar | 79 | 22 | 2020-01-03 | 18:30
16 | Maniknagar | 78 | 19 | 2020-01-03 | 0.5
17 | Bangabhaban | 20 | 26 | 2020-01-03 | 0.5
18 | Narinda | 76 | 18 | 2020-01-03 | 0.58333
19 | Dhanmondi | 100 | 8 | 2020-01-03 | 0.54167
20 | Lalbag | 86 | 8 | 2020-01-03 | 18:30
21 | Madartek | 44 | 19 | 2020-01-03 | 18:30
22 | Dhaka University | 0 | 28 | 2020-01-03
23 | Mirpur | 73 | 4 | 2020-01-03 | 0.77083
24 | Kalyanpur | 75 | 19 | 2020-01-03 | 18:00
25 | Gulshan | 94 | 2 | 2020-01-03 | 18:00
26 | Uttara | 66 | 5 | 2020-01-03 | 16:00
27 | Uttara(new) | 36 | 13 | 2020-01-03 | 0.77083
28 | Kamrangirchar | 73 | 27 | 2020-01-03 | 13:00
29 | Savar | 111 | 18 | 2020-01-03 | 18:00
30 | Bhasantec | 104 | 2 | 2020-01-03 | 18:00
31 | Agargaon | 39 | 16 | 2020-01-03 | 0.77083
32 | Satmosjid | 68 | 13 | 2020-01-03 | 0.79167
33 | Tongi | 100 | 26 | 2020-01-03 | 12:00
34 | Kabirpur | 198 | 27 | 2020-01-03 | 0.75
35 | Basundhara | 87 | 25 | 2020-01-03 | 19:00
36 | Manikganj | 68 | 27 | 2020-01-03 | 19:00
37 | Joydevpur | 173 | 28 | 2020-01-03 | 18:30
38 | New Tongi | 96 | 4 | 2020-01-03 | 18:00
39 | Kodda | 192 | 22 | 2020-01-03 | 12:00
40 | Dhamrai | 48 | 14 | 2020-01-03 | 18:30
41 | Valuka | 92 | 26 | 2020-01-03 | 0.77083
42 | Tangail | 152 | 27 | 2020-01-03 | 9:00
43 | Mymensing | 167 | 27 | 2020-01-03 | 18:30
44 | Kishorganj | 96 | 22 | 2020-01-03 | 18:30
45 | Netrokona | 111 | 22 | 2020-01-03 | 19:00
46 | Jamalpur | 101 | 27 | 2020-01-03 | 19:00
47 | Sherpur | 94 | 28 | 2020-01-03 | 18:30
48 | Srimongal | 27 | 23 | 2020-01-03 | 0.77083
49 | Shahjibazar | 85 | 27 | 2020-01-03 | 19:00
50 | Fenchuganj | 30 | 18 | 2020-01-03 | 18:00
51 | Kulawara | 30 | 4 | 2020-01-03 | 18:00
52 | Sylhet | 106 | 23 | 2020-01-03 | 18:30
53 | Chatak | 24 | 18 | 2020-01-03 | 18:00
54 | Sunamganj | 29 | 4 | 2020-01-03 | 19:30
55 | Bianibazar | 36 | 25 | 2020-01-03 | 18:00
56 | Cumilla (S) | 114 | 28 | 2020-01-03 | 0.79167
57 | Cumilla(N) | 83 | 16 | 2020-01-03 | 19:00
58 | Chandpur | 64 | 6 | 2020-01-03 | 19:30
59 | Feni | 91 | 19 | 2020-01-03 | 18:30
60 | Chowmuhani | 128 | 15 | 2020-01-03 | 19:30
61 | Ashuganj | 46 | 16 | 2020-01-03 | 7:00
62 | Daudkandi | 106 | 23 | 2020-01-03 | 0.83333
63 | B.Baria | 104 | 26 | 2020-01-03 | 19:30
64 | Ramganj | 72 | 16 | 2020-01-03 | 20:00
65 | Chaddagram | 24 | 21 | 2020-01-03 | 20:00
66 | PHP | 5 | 24 | 2020-01-03 | 23:00
67 | Madanhat | 51 | 2 | 2020-01-03 | 18:00
68 | Hathazari | 72 | 28 | 2020-01-03 | 0.77083
69 | Khulshi | 148 | 2 | 2020-01-03 | 13:00
70 | Halishahar | 94 | 28 | 2020-01-03 | 19:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
71 | Baraulia | 151 | 26 | 2020-01-03 | 11:00
72 | Sikalbaha | 23 | 2 | 2020-01-03 | 17:00
73 | Dohazari | 83 | 8 | 2020-01-03 | 19:00
74 | Cox'sbazar | 76 | 26 | 2020-01-03 | 20:00
75 | Chandraghona | 32 | 19 | 2020-01-03 | 18:00
76 | Kaptai | 4 | 5 | 2020-01-03 | 18:00
77 | A. Khaer Stl. | 60 | 29 | 2020-01-03 | 20:00
78 | Bakulia | 74 | 19 | 2020-01-03 | 0.77083
79 | Julda | 22 | 16 | 2020-01-03 | 0.79167
80 | TK chemical | 13 | 27 | 2020-01-03 | 18:00
81 | Modern Steel | 18 | 11 | 2020-01-03 | 10:00
82 | Shahmirpur | 24 | 21 | 2020-01-03 | 18:00
83 | Khagrachhari | 20 | 18 | 2020-01-03 | 15:00
84 | Matarbari | 25 | 27 | 2020-01-03 | 18:30
85 | Baroiar Hat | 26 | 23 | 2020-01-03 | 18:00
86 | Rangamati | 10 | 4 | 2020-01-03 | 0.83333
87 | Abul Khair 230 | 164 | 17 | 2020-01-03 | 2:00
88 | BSRM | 164 | 1 | 2020-01-03 | 24:00.
89 | GPH Ispat | 54 | 19 | 2020-01-03 | 12:00
90 | Goalpara | 21 | 13 | 2020-01-03 | 18:30
91 | Central s/s | 84 | 27 | 2020-01-03 | 18:30
92 | Noapara | 51 | 18 | 2020-01-03 | 0.79167
93 | Jashore | 101 | 21 | 2020-01-03 | 19:00
94 | Benapol | 38 | 12 | 2020-01-03 | 19:30
95 | Jhenidah | 88 | 24 | 2020-01-03 | 18:30
96 | Bottail | 108 | 4 | 2020-01-03 | 18:00
97 | G.K Project | 38 | 30 | 2020-01-03 | 18:30
98 | Faridpur | 134 | 13 | 2020-01-03 | 19:30
99 | Madaripur | 61 | 14 | 2020-01-03 | 20:00
100 | Sariatpur | 44 | 5 | 2020-01-03 | 20:00
101 | Gopalganj | 71 | 18 | 2020-01-03 | 19:00
102 | Bagerhat | 70 | 6 | 2020-01-03 | 19:30
103 | Mongla | 40 | 19 | 2020-01-03 | 9:00
104 | Satkhira | 71 | 19 | 2020-01-03 | 19:30
105 | Gallamari | 46 | 29 | 2020-01-03 | 13:00
106 | Magura | 39 | 22 | 2020-01-03 | 18:30
107 | Norail | 27 | 8 | 2020-01-03 | 18:30
108 | Chuadanga | 69 | 4 | 2020-01-03 | 19:00
109 | Barsal(N) | 34 | 12 | 2020-01-03 | 20:00
110 | Barsal(S) | 72 | 12 | 2020-01-03 | 18:00
111 | Patuakhali | 90 | 18 | 2020-01-03 | 19:00
112 | Bhandaria | 42 | 13 | 2020-01-03 | 20:00
113 | Borhan Uddin | 38 | 2 | 2020-01-03 | 18:00
114 | Ishurdi | 48 | 9 | 2020-01-03 | 18:30
115 | Ruppur Paromanobik | 1 | 1 | 2020-01-03 | 0.083333
116 | Natore | 93 | 20 | 2020-01-03 | 18:30
117 | Bogura | 131 | 29 | 2020-01-03 | 0.75
118 | Naogaon | 104 | 25 | 2020-01-03 | 19:30
119 | Rajshahi | 96 | 11 | 2020-01-03 | 20:00
120 | Rajshahi New | 12 | 26 | 2020-01-03 | 0.79167
121 | C.Nawabganj | 69 | 27 | 2020-01-03 | 19:00
122 | Amnura | 35 | 27 | 2020-01-03 | 12:00
123 | Pabna | 73 | 20 | 2020-01-03 | 19:30
124 | Shahjadpur | 84 | 28 | 2020-01-03 | 19:00
125 | Serajganj | 70 | 27 | 2020-01-03 | 19:30
126 | Niyamatpur | 88 | 25 | 2020-01-03 | 0.8125
127 | Joypurhat | 52 | 23 | 2020-01-03 | 18:30
128 | Sherpur(Bogura) | 40 | 22 | 2020-01-03 | 18:00
129 | Mohastangar | 32 | 18 | 2020-01-03 | 18:30
130 | Rangpur | 116 | 26 | 2020-01-03 | 19:00
131 | Lalmonirhat | 55 | 21 | 2020-01-03 | 0.77083
132 | Saidpur | 98 | 5 | 2020-01-03 | 19:00
133 | Purbasadipur | 99 | 28 | 2020-01-03 | 18:30
134 | Thakurgaon | 74 | 14 | 2020-01-03 | 19:30
135 | Palshbari | 96 | 29 | 2020-01-03 | 0.79167
136 | Barapukuria | 46 | 28 | 2020-01-03 | 20:00
137 | Panchugar | 39 | 25 | 2020-01-03 | 0.77083
138 | Joldhaka | 21 | 27 | 2020-01-03 | 0.79167
139 | Kurigram | 49 | 31 | 2020-01-03 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 3110 | 01.27.2020 | 19:00
Chattogram | 1058 | 14.01.2020 | 18:00
Khulna | 1095 | 22.01.2020 | 18:30
Rajshahi | 984 | 28.01.2020 | 19:00
Cumilla | 743..4 | 30.01.2020 | 19:30
Mymensingh | 790 | 27.01.2020 | 18:30
Sylhet | 333 | 25.01.2020 | 18:30
Barisal | 382 | 26.01.2020 | 1:00
Rangpur | 636 | 29.01.2020 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 408 | 5 | 2020-01-03 | 14:00 | 382 | 1 | 2020-01-03 | 16:00
2 | Bheramara | 400 | 409 | 19 | 2020-01-03 | 3:00 | 391 | 1 | 2020-01-03 | 10:00
3 | Ashuganj(N) | 400 | 403 | 28 | 2020-01-03 | 21:00 | 379 | 1 | 2020-01-03 | 1:00
4 | Payra | 400 | 418 | 29 | 2020-01-03 | 4:00 | 386 | 29 | 2020-01-03 | 18:30
5 | Kaliakoir | 400 | 417 | 31 | 2020-01-03 | 17:00 | 364 | 19 | 2020-01-03 | 16:00
6 | Bhulta | 400 | 402 | 29 | 2020-01-03 | 4:00 | 379 | 22 | 2020-01-03 | 12:00
7 | Gopalganj | 400 | 418 | 30 | 2020-01-03 | 15:00 | 389 | 28 | 2020-01-03 | 7:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 1 | 2020-01-03 | 1:00 | 224 | 27 | 2020-01-03 | 8:00
2 | Ishurdi | 230 | 244 | 3 | 2020-01-03 | 5:00 | 220 | 14 | 2020-01-03 | 14:00
3 | Ashuganj | 230 | 245 | 28 | 2020-01-03 | 21:00 | 234 | 19 | 2020-01-03 | 7:00
4 | Serajganj | 230 | 236 | 3 | 2020-01-03 | 4:00 | 225 | 29 | 2020-01-03 | 18:30
5 | Baghabari | 230 | 247 | 1 | 2020-01-03 | 6:00 | 224 | 18 | 2020-01-03 | 6:00
6 | Barapukuria | 230 | 236 | 3 | 2020-01-03 | 5:00 | 224 | 3 | 2020-01-03 | 18:30
7 | Bogura | 230 | 237 | 3 | 2020-01-03 | 5:00 | 218 | 24 | 2020-01-03 | 19:00
8 | Khulna South | 230 | 246 | 9 | 2020-01-03 | 5:00 | 213 | 13 | 2020-01-03 | 18:00
9 | Rampura | 230 | 233 | 11 | 2020-01-03 | 13:00 | 224 | 22 | 2020-01-03 | 12:00
10 | Haripur | 230 | 235 | 28 | 2020-01-03 | 18:30 | 223 | 8 | 2020-01-03 | 11:00
11 | Hasnabad | 230 | 238 | 25 | 2020-01-03 | 4:00 | 220 | 19 | 2020-01-03 | 12:00
12 | Shyampur | 230 | 237 | 29 | 2020-01-03 | 4:00 | 230 | 30 | 2020-01-03 | 12:00
13 | Aminbazar | 230 | 237 | 11 | 2020-01-03 | 4:00 | 222 | 19 | 2020-01-03 | 12:00
14 | Tongi | 230 | 241 | 29 | 2020-01-03 | 2:00 | 220 | 5 | 2020-01-03 | 9:00
15 | Comilla (N) | 230 | 242 | 6 | 2020-01-03 | 3:00 | 220 | 31 | 2020-01-03 | 23:00
16 | Hathazari | 230 | 240 | 31 | 2020-01-03 | 19:30 | 213 | 20 | 2020-01-03 | 10:00
17 | Megnaghat | 230 | 244 | 30 | 2020-01-03 | 24:00 | 225 | 22 | 2020-01-03 | 12:00
18 | Fenchuganj | 230 | 244 | 8 | 2020-01-03 | 9:00 | 223 | 29 | 2020-01-03 | 11:00
19 | Siddhirganj | 230 | 238 | 8 | 2020-01-03 | 4:00 | 225 | 22 | 2020-01-03 | 12:00
20 | Maniknagar | 230 | 236 | 11 | 2020-01-03 | 3:00 | 223 | 22 | 2020-01-03 | 12:00
21 | Old Airport | 230 | 247 | 31 | 2020-01-03 | 4:00 | 221 | 1 | 2020-01-03 | 12:00
22 | Barisal | 230 | 251 | 6 | 2020-01-03 | 22:00 | 208 | 5 | 2020-01-03 | 18:30
23 | AKSML | 230 | 230 | 30 | 2020-01-03 | 15:00 | 212 | 3 | 2020-01-03 | 3:00
24 | BSRM | 230 | 233 | 30 | 2020-01-03 | 13:00 | 213 | 20 | 2020-01-03 | 18:00
25 | Bibiyana | 230 | 242 | 5 | 2020-01-03 | 18:30 | 228 | 17 | 2020-01-03 | 15:00
26 | Bhulta | 230 | 241 | 29 | 2020-01-03 | 22:00 | 224 | 22 | 2020-01-03 | 12:00
27 | Ashuganj (S) | 230 | 242 | 28 | 2020-01-03 | 21:00 | 230 | 29 | 2020-01-03 | 10:00
28 | Kaliakoir | 230 | 239 | 3 | 2020-01-03 | 2:00 | 222 | 22 | 2020-01-03 | 12:00
29 | GPH | 230 | 242 | 30 | 2020-01-03 | 24:00 | 212 | 20 | 2020-01-03 | 11:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 27 | 2020-01-03 | 0.91667 | 127 | 22 | 2020-01-03 | 0.5
2 | Munsiganj | 132 | 141 | 28 | 2020-01-03 | 0.83333 | 126 | 22 | 2020-01-03 | 0.5
3 | Sonargaon | 132 | 136 | 28 | 2020-01-03 | 0.75 | 127 | 1 | 2020-01-03 | 0.5
4 | Shyampur | 132 | 138 | 3 | 2020-01-03 | 0.16667 | 125 | 24 | 2020-01-03 | 0.41667
5 | Bhulta | 132 | 139 | 3 | 2020-01-03 | 0.375 | 115 | 14 | 2020-01-03 | 0.625
6 | Madanganj | 132 | 140 | 24 | 2020-01-03 | 19:00 | 123 | 22 | 2020-01-03 | 0.45833
7 | Shitalakhya | 132 | 141 | 24 | 2020-01-03 | 0.375 | 124 | 22 | 2020-01-03 | 0.5
8 | Rahim Steal | 132 | 137 | 28 | 2020-01-03 | 11:00 | 128 | 20 | 2020-01-03 | 0.54167
9 | Matuail | 132 | 136 | 21 | 2020-01-03 | 0.875 | 111 | 22 | 2020-01-03 | 0.33333
10 | Ghorasal | 132 | 143 | 28 | 2020-01-03 | 0.625 | 124 | 7 | 2020-01-03 | 0.41667
11 | Narsinghdi | 132 | 138 | 3 | 2020-01-03 | 0.375 | 124 | 19 | 2020-01-03 | 0.33333
12 | Haripur (SBU) | 132 | 137 | 28 | 2020-01-03 | 0.58333 | 127 | 21 | 2020-01-03 | 0.54167
13 | Ullon | 132 | 138 | 8 | 2020-01-03 | 0.041667 | 122 | 2 | 2020-01-03 | 0.5
14 | Hasnabad | 132 | 137 | 25 | 2020-01-03 | 0.29167 | 125 | 22 | 2020-01-03 | 0.5
15 | Magbazar | 132 | 134 | 15 | 2020-01-03 | 0.25 | 123 | 2 | 2020-01-03 | 0.5
16 | Maniknagar | 132 | 139 | 11 | 2020-01-03 | 0.29167 | 131 | 22 | 2020-01-03 | 0.45833
17 | Bangabhaban | 132 | 139 | 11 | 2020-01-03 | 0.29167 | 131 | 22 | 2020-01-03 | 0.45833
18 | Narinda | 132 | 139 | 11 | 2020-01-03 | 0.29167 | 131 | 22 | 2020-01-03 | 0.45833
19 | Dhanmondi | 132 | 138 | 8 | 2020-01-03 | 1:00 | 122 | 2 | 2020-01-03 | 0.5
20 | Lalbag | 132 | 137 | 3 | 2020-01-03 | 5:00 | 121 | 22 | 2020-01-03 | 0.5
21 | Madartek | 132 | 132 | 3 | 2020-01-03 | 0.20833 | 122 | 22 | 2020-01-03 | 0.5
22 | Dhaka University | 132 |  | 28 | 2020-01-03 |  |  |  | 2020-01-03
23 | Mirpur | 132 | 139 | 4 | 2020-01-03 | 0.083333 | 125 | 19 | 2020-01-03 | 16:00
24 | Kalyanpur | 132 | 140 | 3 | 2020-01-03 | 0.20833 | 129 | 5 | 2020-01-03 | 12;00
25 | Gulshan | 132 | 131 | 7 | 2020-01-03 | 0.125 | 122 | 2 | 2020-01-03 | 0.5
26 | Uttara | 132 | 137 | 21 | 2020-01-03 | 0.95833 | 125 | 5 | 2020-01-03 | 0.5
27 | Uttara(New) | 132 | 137 | 21 | 2020-01-03 | 0.95833 | 125 | 5 | 2020-01-03 | 0.5
28 | Kamrangirchar | 132 | 137 | 11 | 2020-01-03 | 0.20833 | 124 | 19 | 2020-01-03 | 0.5
29 | Savar | 132 | 137 | 29 | 2020-01-03 | 0.25 | 124 | 5 | 2020-01-03 | 0.5
30 | Bhasantec | 132 | 138 | 11 | 2020-01-03 | 0.125 | 125 | 20 | 2020-01-03 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Agargaon | 132 | 138 | 11 | 2020-01-03 | 0.125 | 126 | 20 | 2020-01-03 | 0.5
32 | Satmosjid | 132 | 137 | 3 | 2020-01-03 | 0.20833 | 126 | 5 | 2020-01-03 | 0.5
33 | Tongi | 132 | 141 | 3 | 2020-01-03 | 0.33333 | 130 | 19 | 2020-01-03 | 0.79167
34 | Kabirpur | 132 | 138 | 28 | 2020-01-03 | 0.70833 | 123 | 22 | 2020-01-03 | 0.70833
35 | Basundhara | 132 | 134 | 1 | 2020-01-03 | 17:00 | 123 | 2 | 2020-01-03 | 0.45833
36 | Manikganj | 132 | 140 | 3 | 2020-01-03 | 8:00 | 126 | 22 | 2020-01-03 | 0.41667
37 | Joydevpur | 132 | 143 | 3 | 2020-01-03 | 0.29167 | 133 | 18 | 2020-01-03 | 0.5
38 | New Tongi | 132 | 141 | 3 | 2020-01-03 | 0.29167 | 129 | 22 | 2020-01-03 | 0.45833
39 | Kodda | 132 | 140 | 3 | 2020-01-03 | 0.20833 | 122 | 22 | 2020-01-03 | 0.5
40 | Dhamrai | 132 | 137 | 30 | 2020-01-03 | 0.54167 | 124 | 19 | 2020-01-03 | 0.66667
41 | Valuka | 133 | 134 | 3 | 2020-01-03 | 0.25 | 114 | 19 | 2020-01-03 | 0.375
42 | Tangail | 132 | 138 | 28 | 2020-01-03 | 0.70833 | 121 | 27 | 2020-01-03 | 0.5
43 | Mymensing | 132 | 136 | 3 | 2020-01-03 | 0.25 | 117 | 20 | 2020-01-03 | 0.33333
44 | Kishorganj | 132 | 136 | 3 | 2020-01-03 | 0.25 | 119 | 25 | 2020-01-03 | 0.5
45 | Netrokona | 132 | 136 | 3 | 2020-01-03 | 0.25 | 113 | 23 | 2020-01-03 | 0.29167
46 | Jamalpur | 132 | 140 | 16 | 2020-01-03 | 0.8125 | 114 | 19 | 2020-01-03 | 7:00
47 | Sherpur | 132 | 138 | 16 | 2020-01-03 | 0.8125 | 112 | 23 | 2020-01-03 | 8:00
48 | Srimongal | 132 | 141 | 17 | 2020-01-03 | 0.125 | 135 | 1 | 2020-01-03 | 0.5
49 | Shahjibazar | 132 | 139 | 6 | 2020-01-03 | 3:00 | 132 | 1 | 2020-01-03 | 0.5
50 | Fenchuganj | 132 | 141 | 30 | 2020-01-03 | 1899-12-31 | 131 | 12 | 2020-01-03 | 17:00
51 | Khulawara | 132 | 140 | 23 | 2020-01-03 | 1899-12-31 | 133 | 2 | 2020-01-03 | 0.45833
52 | Sylhet | 132 | 138 | 16 | 2020-01-03 | 0.95833 | 131 | 5 | 2020-01-03 | 0.375
53 | Chattak | 132 | 138 | 24 | 2020-01-03 | 0.083333 | 129 | 13 | 2020-01-03 | 0.77083
54 | Sunamganj | 132 | 138 | 24 | 2020-01-03 | 0.083333 | 129 | 13 | 2020-01-03 | 0.77083
55 | Biani Bazar | 132 | 139 | 17 | 2020-01-03 | 0.29167 | 131 | 5 | 2020-01-03 | 12:00
56 | Comilla(South) | 132 | 134 | 21 | 2020-01-03 | 0.041667 | 126 | 14 | 2020-01-03 | 0.75
57 | Comilla (North) | 132 | 142 | 5 | 2020-01-03 | 0.79167 | 134 | 16 | 2020-01-03 | 0.79167
58 | Chandpur | 132 | 140 | 16 | 2020-01-03 | 19:00 | 130 | 2 | 2020-01-03 | 0.83333
59 | Feni | 132 | 141 | 28 | 2020-01-03 | 0.875 | 129 | 20 | 2020-01-03 | 0.45833
60 | Chowmuhani | 132 | 140 | 16 | 2020-01-03 | 0.79167 | 126 | 1 | 2020-01-03 | 0.75
61 | Ashuganj | 132 | 141 | 29 | 2020-01-03 | 0.16667 | 131 | 1 | 2020-01-03 | 0.5
62 | Daudkandi | 132 | 139 | 28 | 2020-01-03 | 0.875 | 129 | 22 | 2020-01-03 | 0.5
63 | Brahminbaria | 132 | 138 | 3 | 2020-01-03 | 0.29167 | 129 | 1 | 2020-01-03 | 0.54167
64 | Ramganj | 132 | 138 | 16 | 2020-01-03 | 0.83333 | 121 | 1 | 2020-01-03 | 0.58333
65 | Chaddagram | 132 | 143 | 28 | 2020-01-03 | 0.875 | 131 | 4 | 2020-01-03 | 0.75
66 | PHP | 132 | 139 | 2 | 2020-01-03 | 0.58333 | 127 | 20 | 2020-01-03 | 0.41667
67 | Madanhat | 132 | 139 | 31 | 2020-01-03 | 0.77083 | 128 | 20 | 2020-01-03 | 0.41667
68 | Hathazari | 132 | 139 | 28 | 2020-01-03 | 0.875 | 128 | 20 | 2020-01-03 | 0.41667
69 | Khulshi | 132 | 148 | 2 | 2020-01-03 | 0.54167 | 123 | 20 | 2020-01-03 | 0.41667
70 | Halishahar | 132 | 139 | 30 | 2020-01-03 | 0.91667 | 124 | 20 | 2020-01-03 | 0.5
71 | Baraulia | 132 | 137 | 31 | 2020-01-03 | 0.79167 | 126 | 22 | 2020-01-03 | 0.5
72 | Sikalbaha | 132 | 138 | 30 | 2020-01-03 | 0.91667 | 124 | 20 | 2020-01-03 | 0.41667
73 | Dohazari | 132 | 135 | 16 | 2020-01-03 | 0.77083 | 124 | 22 | 2020-01-03 | 0.5
74 | Cox'sbazar | 132 | 131 | 26 | 2020-01-03 | 0.58333 | 118 | 15 | 2020-01-03 | 0.5
75 | Chandraghona | 132 | 137 | 28 | 2020-01-03 | 0.875 | 122 | 12 | 2020-01-03 | 0.75
76 | Kaptai | 132 | 136 | 28 | 2020-01-03 | 0.77083 | 128 | 9 | 2020-01-03 | 0.5
77 | A. Khaer Stl. | 132 | 135 | 26 | 2020-01-03 | 0.79167 | 126 | 22 | 2020-01-03 | 0.5
78 | Bakulia | 132 | 136 | 28 | 2020-01-03 | 0.79167 | 124 | 22 | 2020-01-03 | 0.5
79 | Julda | 132 | 136 | 13 | 2020-01-03 | 0.16667 | 125 | 22 | 2020-01-03 | 0.375
80 | TK Chemical | 132 | 138 | 29 | 2020-01-03 | 0.8125 | 125 | 20 | 2020-01-03 | 0.41667
81 | Modern Steel | 132 | 136 | 28 | 2020-01-03 | 0.8125 | 103 | 19 | 2020-01-03 | 0.75
82 | Shahmirpur | 132 | 137 | 31 | 2020-01-03 | 0.77083 | 125 | 22 | 2020-01-03 | 0.5
83 | Khagrachhari | 132 | 136 | 27 | 2020-01-03 | 0 | 125 | 20 | 2020-01-03 | 0.41667
84 | Matarbari | 132 | 132 | 26 | 2020-01-03 | 0.41667 | 121 | 4 | 2020-01-03 | 18:00
85 | Baroiar Hat | 132 | 139 | 28 | 2020-01-03 | 0.875 | 127 | 20 | 2020-01-03 | 0.375
86 | Rangamati | 133 | 137 | 30 | 2020-01-03 | 0.91667 | 125 | 20 | 2020-01-03 | 0.41667
87 | Goalpara | 132 | 141 | 4 | 2020-01-03 | 0.29167 | 120 | 6 | 2020-01-03 | 13:00
88 | Khulna Central | 132 | 139 | 2 | 2020-01-03 | 0.20833 | 120 | 6 | 2020-01-03 | 11:00
89 | Noapara | 132 | 139 | 3 | 2020-01-03 | 0.20833 | 118 | 6 | 2020-01-03 | 13:00
90 | Jessore | 132 | 136 | 21 | 2020-01-03 | 0.16667 | 114 | 6 | 2020-01-03 | 0.45833
91 | Benapol | 132 | 137 | 1 | 2020-01-03 | 0.16667 | 116 | 6 | 2020-01-03 | 0.54167
92 | Jhenida | 132 | 138 | 3 | 2020-01-03 | 0.29167 | 110 | 5 | 2020-01-03 | 0.79167
93 | Bottail | 132 | 139 | 3 | 2020-01-03 | 0.29167 | 120 | 21 | 2020-01-03 | 0.75
94 | G.K Project | 132 | 141 | 4 | 2020-01-03 | 0.125 | 126 | 21 | 2020-01-03 | 0.5
95 | Faridpur | 132 | 140 | 14 | 2020-01-03 | 0.125 | 123 | 4 | 2020-01-03 | 0.83333
96 | Madaripur | 132 | 141 | 6 | 2020-01-03 | 0.375 | 112 | 5 | 2020-01-03 | 0.5
97 | Sariatpur | 132 | 143 | 16 | 2020-01-03 | 0.41667 | 122 | 5 | 2020-01-03 | 0.5
98 | Gopalganj | 132 | 146 | 6 | 2020-01-03 | 0.083333 | 125 | 5 | 2020-01-03 | 0.5
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: January '2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
99 | Bagerhat | 132 | 139 | 3 | 2020-01-03 | 0.375 | 115 | 19 | 2020-01-03 | 0.33333
100 | Mongla | 132 | 135 | 2 | 2020-01-03 | 0.125 | 115 | 19 | 2020-01-03 | 0.33333
101 | Satkhira | 132 | 139 | 3 | 2020-01-03 | 0.29167 | 118 | 19 | 2020-01-03 | 0.33333
102 | Gallamari | 132 | 141 | 3 | 2020-01-03 | 0.29167 | 119 | 13 | 2020-01-03 | 0.75
103 | Magura | 132 | 136 | 3 | 2020-01-03 | 0.16667 | 112 | 5 | 2020-01-03 | 0.79167
104 | Norail | 132 | 137 | 3 | 2020-01-03 | 0.29167 | 110 | 5 | 2020-01-03 | 0.79167
105 | Chuadanga | 132 | 136 | 3 | 2020-01-03 | 0.25 | 110 | 6 | 2020-01-03 | 0.45833
106 | Barisal(N) | 132 | 144 | 25 | 2020-01-03 | 0.41667 | 117 | 5 | 2020-01-03 | 0.79167
107 | Barisal(S) | 132 | 145 | 25 | 2020-01-03 | 0.41667 | 125 | 1 | 2020-01-03 | 0.54167
108 | Patuakhali | 132 | 142 | 30 | 2020-01-03 | 0.625 | 119 | 8 | 2020-01-03 | 0.75
109 | Bhandaria | 132 | 139 | 15 | 2020-01-03 | 0.58333 | 120 | 15 | 2020-01-03 | 0.77083
110 | Ishurdi | 132 | 139 | 2 | 2020-01-03 | 0.125 | 126 | 8 | 2020-01-03 | 0.75
111 | Ruppur paromanobik | 132 | 140 | 3 | 2020-01-03 | 0.25 | 126 | 13 | 2020-01-03 | 0.77083
112 | Natore | 132 | 139 | 3 | 2020-01-03 | 0.25 | 121 | 20 | 2020-01-03 | 0.33333
113 | Bogra | 132 | 139 | 3 | 2020-01-03 | 0.25 | 127 | 10 | 2020-01-03 | 18:30
114 | Noagaon | 132 | 137 | 3 | 2020-01-03 | 0.20833 | 118 | 29 | 2020-01-03 | 0.5
115 | Rajshahi | 132 | 138 | 3 | 2020-01-03 | 0.25 | 119 | 26 | 2020-01-03 | 0.79167
116 | Rajshahi New | 132 | 136 | 3 | 2020-01-03 | 0.29167 | 117 | 19 | 2020-01-03 | 0.33333
117 | C.Nawabganj | 132 | 135 | 3 | 2020-01-03 | 0.25 | 113 | 20 | 2020-01-03 | 0.54167
118 | Amnura | 132 | 137 | 3 | 2020-01-03 | 0.20833 | 113 | 20 | 2020-01-03 | 0.33333
119 | Pabna | 132 | 140 | 3 | 2020-01-03 | 0.25 | 125 | 22 | 2020-01-03 | 0.5
120 | Shahjadpur | 132 | 145 | 6 | 2020-01-03 | 4:00 | 130 | 9 | 2020-01-03 | 10:00
121 | Serajganj | 132 | 138 | 1 | 2020-01-03 | 0.125 | 126 | 14 | 2020-01-03 | 12:00
122 | Niyamatpur | 132 | 138 | 3 | 2020-01-03 | 0.25 | 113 | 22 | 2020-01-03 | 0.5
123 | Joypurhat | 132 | 139 | 3 | 2020-01-03 | 0.20833 | 116 | 22 | 2020-01-03 | 0.5
124 | Sherpur(Bogura) | 132 | 140 | 3 | 2020-01-03 | 0.25 | 126 | 24 | 2020-01-03 | 0.77083
125 | Mohastangor | 132 | 138 | 3 | 2020-01-03 | 0.25 | 114 | 26 | 2020-01-03 | 0.33333
126 | Rangpur | 132 | 135 | 2 | 2020-01-03 | 0.20833 | 119 | 10 | 2020-01-03 | 0.79167
127 | Lalmonirhat | 132 | 131 | 2 | 2020-01-03 | 0.20833 | 115 | 24 | 2020-01-03 | 0.77083
128 | Saidpur | 132 | 135 | 2 | 2020-01-03 | 0.20833 | 118 | 4 | 2020-01-03 | 0.77083
129 | Purbasadipur | 132 | 131 | 2 | 2020-01-03 | 0.125 | 108 | 9 | 2020-01-03 | 0.77083
130 | Thakurgaon | 132 | 130 | 18 | 2020-01-03 | 0.20833 | 108 | 8 | 2020-01-03 | 0.75
131 | Palashbari | 132 | 135 | 4 | 2020-01-03 | 0.16667 | 115 | 24 | 2020-01-03 | 0.375
132 | Barapukuria | 132 | 136 | 3 | 2020-01-03 | 0.25 | 124 | 3 | 2020-01-03 | 0.77083
133 | Panchagar | 132 | 130 | 12 | 2020-01-03 | 0.29167 | 101 | 9 | 2020-01-03 | 0.77083
134 | Joldhaka | 132 | 132 | 2 | 2020-01-03 | 0.20833 | 116 | 3 | 2020-01-03 | 0.77083
135 | Kurigram | 132 | 135 | 2 | 2020-01-03 | 0.16667 | 118 | 4 | 2020-01-03 | 0.75
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:January' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 120 | 310
Hasnabad | TR2 | 225 | 100 | 310 | 25.01.2020 | 17:00
| TR3 | 225 | 100 | 310
| TR1 | 225 | 135 | 385
Tongi | TR2 | 225 | 135 | 385 | 27.01.2020 | 12:00
| TR3 | 225 | 135 | 385
Haripur | TR1 | 225 | 124 | 340
| TR1 | 225 |  |  | 13.01.2020 | 10:00 | S/D
| TR3 | 225 | 124 | 340
| TR1 | 225 | 100 | 365
Rampura | TR2 | 225 | 100 | 365 | 29.01.2020 | 13:00
| TR3 | 225 | 100 | 365
| TR1 | 225 | 125 | 351
Aminbazar | TR2 | 225 | 125 | 351 | 09.01.2020 | 11:00
| TR3 | 225 | 130 | 364
Maniknagar | TR1 | 300 | 82 | 220 | 30.01.2020 | 13:00
| TR2 | 300 | 82 | 220
Cumilla (N) | TR1 | 225 | 140 | 408 | 11.01.2020 | 9:00
| TR2 | 225 | 150 | 406
Fenchuganj | TR1 | 300 | 151 | 360 | 31.01.2020 | 12':00
| MT1 | 150 | 88 | 260
Hathazari | MT2 | 150 | 88 | 260 | 16.01.2020 | 09:00
| MT3 | 150 | 88 | 260
| MT4 | 150 | 88 | 260
| TR1 | 225 | 150 | 400
Ishurdi | TR2 | 225 | 150 | 400 | 24.01.2020 | 19:00
| TR3 | 225 | 150 | 400
Khulna(S) | TR1 | 225 | 148 | 400
| TR2 | 225 | 148 | 400 | 05.01.2020 | 19:00
| TR3 | 300 | 186 | 509
Bogra | TR1 | 225 | 166 | 784 | 24.01.2020 | 18:30
| TR2 | 225 | 166 | 784
| TR3 | 225 | 224 | 612
Baghabari | TR1 | 225 | 185 | 560 | 21.01.2020 | 18:00
Barapukuria | TR1 | 225 | 156 | 740 | 29.01.2020 | 18:30 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 135 | 660 |  |  | 132 kV current is being provided
| TR6 | 300 | 174 | 853
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:January' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 193.3 | 323 | 04.01.2020 | 8:45
| TR2(400/230 kV) | 520 | 196.7 | 327
| TR1(400/132 kV) | 325 | 215.1 | 348 | 14.01.2020 | 19:00
| TR2(400/132 kV) | 325 | 214.9 | 351
Bibiyana | ICT1(400/230 kV) | 520 | 108.6 | 164.4 | 04.01.2020 | 10:00
| ICT2(400/230kV) | 520 | 104.9 | 171
Bhulta | ATR1(400/230 kV) | 520 | 173 | 308 | 21.01.2020 | 11:15
| ATR2(400/230kV) | 520 | 173 | 308
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:January' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:January' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-01-20 | 8436 | 8436 | - | - | - | - | - | - | - | - | - | - | - | - | 01-01-20 | 6749.7 | 6749.7 | - | - | - | - | - | - | - | - | - | - | - | -
02-01-20 | 8774 | 8774 | - | - | - | - | - | - | - | - | - | - | - | - | 02-01-20 | 6968.1 | 6968.1 | - | - | - | - | - | - | - | - | - | - | - | -
03-01-20 | 7537 | 7537 | - | - | - | - | - | - | - | - | - | - | - | - | 03-01-20 | 5527.5 | 5527.5 | - | - | - | - | - | - | - | - | - | - | - | -
04-01-20 | 8397 | 8397 | - | - | - | - | - | - | - | - | - | - | - | - | 04-01-20 | 6108.5 | 6108.5 | - | - | - | - | - | - | - | - | - | - | - | -
05-01-20 | 8221 | 8221 | - | - | - | - | - | - | - | - | - | - | - | - | 05-01-20 | 6764.7 | 6764.7 | - | - | - | - | - | - | - | - | - | - | - | -
06-01-20 | 8575 | 8575 | - | - | - | - | - | - | - | - | - | - | - | - | 06-01-20 | 6528.5 | 6528.5 | - | - | - | - | - | - | - | - | - | - | - | -
07-01-20 | 8584 | 8584 | - | - | - | - | - | - | - | - | - | - | - | - | 07-01-20 | 6668 | 6668 | - | - | - | - | - | - | - | - | - | - | - | -
08-01-20 | 8689 | 8689 | - | - | - | - | - | - | - | - | - | - | - | - | 08-01-20 | 6792.8 | 6792.8 | - | - | - | - | - | - | - | - | - | - | - | -
09-01-20 | 8484 | 8484 | - | - | - | - | - | - | - | - | - | - | - | - | 09-01-20 | 6845.3 | 6845.3 | - | - | - | - | - | - | - | - | - | - | - | -
10-01-20 | 7680 | 7680 | - | - | - | - | - | - | - | - | - | - | - | - | 10-01-20 | 5895.8 | 5895.8 | - | - | - | - | - | - | - | - | - | - | - | -
11-01-20 | 8653 | 8653 | - | - | - | - | - | - | - | - | - | - | - | - | 11-01-20 | 6786 | 6786 | - | - | - | - | - | - | - | - | - | - | - | -
12-01-20 | 8561 | 8561 | - | - | - | - | - | - | - | - | - | - | - | - | 12-01-20 | 6493.1 | 6493.1 | - | - | - | - | - | - | - | - | - | - | - | -
13-01-20 | 8827 | 8827 | - | - | - | - | - | - | - | - | - | - | - | - | 13-01-20 | 6893.3 | 6893.3 | - | - | - | - | - | - | - | - | - | - | - | -
14-01-20 | 8727 | 8727 | - | - | - | - | - | - | - | - | - | - | - | - | 14-01-20 | 7100.7 | 7100.7 | - | - | - | - | - | - | - | - | - | - | - | -
15-01-20 | 8762 | 8762 | - | - | - | - | - | - | - | - | - | - | - | - | 15-01-20 | 7023 | 7023 | - | - | - | - | - | - | - | - | - | - | - | -
16-01-20 | 8908 | 8908 | - | - | - | - | - | - | - | - | - | - | - | - | 16-01-20 | 6946.5 | 6946.5 | - | - | - | - | - | - | - | - | - | - | - | -
17-01-20 | 7918 | 7918 | - | - | - | - | - | - | - | - | - | - | - | - | 17-01-20 | 6165.1 | 6165.1 | - | - | - | - | - | - | - | - | - | - | - | -
18-01-20 | 8805 | 8805 | - | - | - | - | - | - | - | - | - | - | - | - | 18-01-20 | 6586.4 | 6586.4 | - | - | - | - | - | - | - | - | - | - | - | -
19-01-20 | 8978 | 8978 | - | - | - | - | - | - | - | - | - | - | - | - | 19-01-20 | 7148.7 | 7148.7 | - | - | - | - | - | - | - | - | - | - | - | -
20-01-20 | 8959 | 8959 | - | - | - | - | - | - | - | - | - | - | - | - | 20-01-20 | 7042.4 | 7042.4 | - | - | - | - | - | - | - | - | - | - | - | -
21-01-20 | 9009 | 9009 | - | - | - | - | - | - | - | - | - | - | - | - | 21-01-20 | 6999.4 | 6999.4 | - | - | - | - | - | - | - | - | - | - | - | -
22-01-20 | 9076 | 9076 | - | - | - | - | - | - | - | - | - | - | - | - | 22-01-20 | 7107.6 | 7107.6 | - | - | - | - | - | - | - | - | - | - | - | -
23-01-20 | 8895 | 8895 | - | - | - | - | - | - | - | - | - | - | - | - | 23-01-20 | 7266 | 7266 | - | - | - | - | - | - | - | - | - | - | - | -
24-01-20 | 8121 | 8121 | - | - | - | - | - | - | - | - | - | - | - | - | 24-01-20 | 6011.8 | 6011.8 | - | - | - | - | - | - | - | - | - | - | - | -
25-01-20 | 8866 | 8866 | - | - | - | - | - | - | - | - | - | - | - | - | 25-01-20 | 6786 | 6786 | - | - | - | - | - | - | - | - | - | - | - | -
26-01-20 | 9019 | 9019 | - | - | - | - | - | - | - | - | - | - | - | - | 26-01-20 | 7308.5 | 7308.5 | - | - | - | - | - | - | - | - | - | - | - | -
27-01-20 | 9068 | 9068 | - | - | - | - | - | - | - | - | - | - | - | - | 27-01-20 | 7191.6 | 7191.6 | - | - | - | - | - | - | - | - | - | - | - | -
28-01-20 | 9196 | 9196 | - | - | - | - | - | - | - | - | - | - | - | - | 28-01-20 | 7366.5 | 7366.5 | - | - | - | - | - | - | - | - | - | - | - | -
29-01-20 | 9223 | 9223 | - | - | - | - | - | - | - | - | - | - | - | - | 29-01-20 | 7607.4 | 7607.4 | - | - | - | - | - | - | - | - | - | - | - | -
30-01-20 | 9077 | 9077 | - | - | - | - | - | - | - | - | - | - | - | - | 30-01-20 | 7826.5 | 7826.5 | - | - | - | - | - | - | - | - | - | - | - | -
31-01-20 | 8250 | 8250 | [12 empty] | 31-01-20 | 6681.1 | 6681.1

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 9223 | 29/01/20 | 19:00
2 | Maximum Day Peak Genaration | MW | 7826.5 | 30/01/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 9223 | 29/01/20 | 19:00
4 | Minimum Generation | MW | 4592 | 04/01/20 | 5:00
5 | Average of the daily evening peak Genaration | MW | 8654.0323
6 | Average of the daily day peak Genaration | MW | 6812.4677
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5074.97
12 | Total Generation by BPDB | MKWH | 3270.3498 | % of total Gen. | 64.44%
13 | Total Generation by IPP | MKWH | 1109.9465 | '' | 21.87%
14 | A) Total Generation by RPCL | MKWH | 93.5157 | '' | 1.843%
| B) Total Generation by REB | MKWH | 122.5711 | " | 2.415%
| C) Total Generation by RENTAL | MKWH | 192.4291 | " | 3.792%
| D) Total Imported from India (HVDC) | MKWH | 225.1188 | " | 4.436%
| E) Total Imported from Tripura, India (A.C) | MKWH | 61.0389 | " | 1.203%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4188.1368 | % of total Gen. | 82.53%
| B) Oil | MKWH | 327.4502 | '' | 6.452%
| C) Hydro | MKWH | 29.2644 | '' | 0.5766%
| D) Solar | MKWH | 4.9089 | '' | 0.09673%
| E) Coal | MKWH | 239.052 | '' | 4.71%
| F) HVDC (Import from India) | MKWH | 225.1188 | '' | 4.436%
| G) A.C (Import from Tripura, India) | MKWH | 61.0389 | '' | 1.203%
16 | Maximun of the daily total Generation . | MKWH | 204.8176 | 30/01/2020
17 | Monthly Load factor | % | 73.9585
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 7527.9138
| A) Gas | M.Taka | 3924.8234
| B) Liquid fuel | M.Taka | 2752.4776
| C) Coal | M.Taka | 850.6128
| D) HVDC (Import from India) | M.Taka | 1148.1057
| E) Tripura(Import from India) | M.Taka | 457.7916
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 420.9251 | 30/01/2020
| A) Gas | M.Taka | 157.0919 | 30/01/2020
| B) Liquid fuel | M.Taka | 248.9609 | 29/01/2020
| C) Coal | M.Taka | 45.7768 | 30/01/2020
| D) HVDC (Import from India) | M.Taka | 41.8237 | 26-01-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.3473
| B) Excluding Hydro & Solar | Taka/KWHR | 2.3629
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.2 | 31/01/2020 | 06:00
b) | Actual | FT (MSL) | 94.25 | 31/01/2020 | 06:00
22 | Peak Genaration of January 2019 | MW | 8893 | 30/01/19 | 19:00
23 | Peak Demand of January 2019 | MW | 8893 | 30/01/19 | 19:00
24 | Maximum peak Generation recorded upto 31/01/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/01/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/01/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.