## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-22 | Saturday
|  | Date (day): | 2020-02-22 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11912.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14653 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-21 | 2020-02-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  |  | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 104 | 124 | 130 | 170
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint |  | 27/02/2020
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 391 | 250 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 340 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 277 | 358 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 60 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 120 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 12 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 10 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 50 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 49 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 25
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 50 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1805 | 2148 | 3484 | 4126 | 991 | 584
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 100 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 205 | 203 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 70 | 110 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 37 | 42 | 15 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 71 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 561.6 | 665 | 1495 | 1655 | 400 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 140 | 100 | 100
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 167 | 189 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 275 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 46 | 46 | 45 | 45
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 20 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 36 | 46 | 46 | 149 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 90 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 100 | 99 | 114
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1206 | 1326 | 1688 | 2367 | 453 | 81
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 132 | 136 | 140 | 140 | 62 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 0 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 95 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 337 | 348 | 473.6 | 572 | 62 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 88 | 86 | 88 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 74 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 110 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 147 | 149 | 150 | 150 |  | 180 | GT-2 shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 27 | 28 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 22 | 51 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 62 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 60 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 127 | 0 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 23 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 80 | 233 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1168 | 1206 | 1509 | 1509 | 0 | 345
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 181 | 474 | 581 | 829
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 59 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 380 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 510 | 913 | 1269 | 2068 | 0 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 18 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 90 | 90 | 90 |  | 104 | GT-1 under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 86 | 98 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 188 | 222 | 275 | 345 | 0 | 117
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 180 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 375 | 434 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 51 | 51 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 716 | 814 | 1228 | 1494 | 611 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 92 | 91 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 35 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 412.6 | 406 | 491 | 517 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 6904.2 | 8048 | 11912.6 | 14653 | 2517 | 1337
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6289.1017 | 7331 | 10851.301 | 13347.5575
A. |  | 2020-02-21 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8048 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 5873 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8048 | MW
3 | Day peak Generation : |  |  | 6904.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7331 | MW
4 | Evening peak Generation : |  |  | 8048 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 161.2265 | MKWHr | By Solar | 0.21465 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.5263 | MKWHr |  | By Oil: | 10.9994 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.9441 | MKWHr |  | By Hydro: | 1.5911 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2517 | MW | Dhaka | 2346 | 2346 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1337 | MW | Chittagong | 665 | 665 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3854 | MW | Khulna | 950 | 950 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1029.1 | MMCFD |  |  | Rajshahi | 853 | 853 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121374535.956 | ii) Oil : | Taka | 68032526.6 | Comilla | 720 | 720 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 41501267.66 | Total | Taka | 230908330.216 | Mymensingh | 697 | 697 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7.2 | MKWHr. | Sylhet | 306 | 306 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -443 | MW (E to W) at | 20:00 | hrs | Barisal | 216 | 216 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -660 | MW at | 8:00 | hrs | Rangpur | 578 | 578 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.3° C |  |  | Total | 7331 | 7331 |  | 0
B. |  | 2020-02-22 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14653 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7800 | MW
4 | Reserve(Generation end) |  |  |  | 5653 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 180.298 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5326 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 5.9185 | MKWHr. | ii) HVDC Flow at Peak Time |  | 474 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0323 | MKWHr. | iii) Maximum HVDC Flow : |  | 474 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.14 |  | (b) Today: | 90.96 |  | (c) Rule Curve: |  | 94.05
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-02-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 200 | 0 | 0 | 301 | 0 | 0 | 340 | 334 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 20 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 300 | 280 | 179 | 8 | 91 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 19 | 86 | 102 | 57 | 22 | 0 | 85 | 73 | 50 | 51 | 130 | 150 | 45 | 80 | 0 | 148 | 0 | 0 | 0 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 81 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5120 | 1624 | 6744 | 3752 | 181 | 2010 | 275 | 372 | 68 | 0 | 86 | 0 | 0 | 91.17
2:00 | 37 | 189 | 0 | 0 | 320 | 0 | 0 | 350 | 334 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 20 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 213 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 310 | 290 | 165 | 8 | 90 | 5 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 8 | 19 | 82 | 104 | 65 | 22 | 0 | 87 | 73 | 5 | 5 | 130 | 148 | 45 | 10 | 0 | 147 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 182 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4896 | 1568 | 6464 | 3711 | 182 | 1822 | 228 | 371 | 68 | 0 | 82 | 0 | 0 | 91.16
3:00 | 37 | 189 | 0 | 0 | 302 | 0 | 0 | 355 | 353 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 20 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 285 | 270 | 215 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 80 | 118 | 48 | 22 | 0 | 87 | 73 | 5 | 5 | 130 | 149 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 92 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4619 | 1552 | 6171 | 3525 | 181 | 1777 | 168 | 372 | 68 | 0 | 80 | 0 | 0 | 91.16
4:00 | 37 | 158 | 0 | 0 | 300 | 0 | 0 | 342 | 314 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 285 | 265 | 167 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 76 | 117 | 16 | 22 | 0 | 86 | 73 | 5 | 5 | 130 | 149 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 91 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4374 | 1510 | 5884 | 3378 | 181 | 1673 | 136 | 371 | 69 | 0 | 76 | 0 | 0 | 91.15
5:00 | 37 | 129 | 0 | 0 | 300 | 0 | 0 | 340 | 314 |  | 0 | 340 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 285 | 265 | 167 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 76 | 117 | 16 | 22 | 0 | 88 | 73 | 5 | 5 | 130 | 149 | 45 | 10 | 0 | 48 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 182 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 91 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4362 | 1511 | 5873 | 3396 | 182 | 1643 | 136 | 371 | 69 | 0 | 76 | 0 | 0 | 91.15
6:00 | 37 | 114 | 0 | 0 | 325 | 0 | 0 | 353 | 343 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 335 | 290 | 184 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 76 | 125 | 17 | 22 | 0 | 88 | 73 | 5 | 5 | 130 | 154 | 45 | 10 | 0 | 48 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 180 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 92 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4574 | 1527 | 6101 | 3553 | 180 | 1714 | 137 | 372 | 69 | 0 | 76 | 0 | 0 | 91.14
7:00 | 37 | 114 | 0 | 0 | 332 | 0 | 0 | 364 | 345 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 215 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 100 | 0 | 360 | 345 | 185 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 68 | 127 | 42 | 22 | 0.1 | 84 | 73 | 5 | 5 | 130 | 155 | 45 | 10 | 0 | 48 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 |  | 180 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 11 | 88 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4759.9 | 1536.1 | 6296 | 3681 | 180 | 1752 | 176 | 368 | 69 | 0 | 68 | 2 | 0 | 91.14
8:00 | 37 | 134 | 0 | 0 | 303 | 0 | 0 | 366 | 345 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 100 | 0 | 310 | 345 | 184 | 8 | 91 | 33 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 0 | 33 | 19 | 70 | 127 | 50 | 22 | 0.5 | 85 | 73 | 5 | 0 | 163 | 145 | 45 | 10 | 0 | 48 | 0 | 0 | 10 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 7.3 | 0 | 0 | 0 | 80 | 89 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 |  | 177 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 11 | 90 | 0 | 280 | 0 | 0 | 175 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 36 | 0 | 1.2 | 15 | 0 |  | 4921.3 | 1731.2 | 6652.5 | 3705 | 177 | 1850 | 401 | 370 | 69 | 0 | 70 | 10.5 | 0 | 91.13
9:00 | 37 | 134 | 0 | 0 | 301 | 0 | 0 | 336 | 341 |  | 0 | 370 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 100 | 0 | 315 | 315 | 177 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 19 | 80 | 127 | 50 | 22 | 1.1 | 85 | 73 | 5 | 22 | 100 | 144 | 45 | 10 | 0 | 48 | 19 | 0 | 10 | 290 | 15 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12.1 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 |  | 177 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 86 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 36 | 0 | 2.8 | 70 | 0 |  | 4872.3 | 1803.8 | 6676.1 | 3679 | 177 | 1732 | 521 | 372 | 69 | 27 | 80 | 19.1 | 0 | 91.13
10:00 | 37 | 105 | 0 | 0 | 300 | 0 | 0 | 341 | 307 |  | 0 | 350 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 26 | 20 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 227 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 100 | 0 | 265 | 265 | 165 | 8 | 90 | 46 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 82 | 124 | 50 | 22 | 1.7 | 87 | 73 | 5 | 10 | 100 | 148 | 45 | 10 | 0 | 48 | 19 | 0 | 10 | 300 | 15 | 5 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 17.3 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 |  | 177 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 92 | 0 | 280 | 0 | 0 | 205 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 35 | 0 | 4.1 | 70 | 0 |  | 4655.1 | 1861.1 | 6516.2 | 3582 | 177 | 1674 | 481 | 372 | 70 | 51 | 82 | 27.2 | 0 | 91.12
11:00 | 37 | 104 | 0 | 0 | 338 | 0 | 0 | 351 | 277 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 12 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 218 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 100 | 0 | 305 | 310 | 185 | 8 | 90 | 46 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 8 | 20 | 82 | 121 | 50 | 22 | 1.9 | 86 | 73 | 5 | 10 | 100 | 160 | 45 | 10 | 0 | 48 | 19 | 0 | 10 | 310 | 15 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16.5 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 |  | 177 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 5.2 | 70 | 0 |  | 4751.2 | 1816.2 | 6567.4 | 3700 | 177 | 1632 | 455 | 372 | 70 | 51 | 82 | 28.4 | 0 | 91.12
12:00 | 37 | 104 | 0 | 0 | 391 | 0 | 0 | 367 | 277 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 12 | 25 | 12 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 100 | 0 | 265 | 315 | 167 | 36 | 92 | 46 | 5 | 0 | 20 | 0 | 0 | 0 | 22 | 8 | 28 | 18 | 84 | 132 | 50 | 22 | 2 | 88 | 73 | 27 | 22 | 130 | 147 | 60 | 40 | 0 | 127 | 19 | 0 | 10 | 325 | 15 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 19.5 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 5.1 | 16 | 0 | 0 | 0 | 0 |  | 181 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 35 | 0 | 5.6 | 70 | 0 |  | 5077.6 | 1826.6 | 6904.2 | 3810 | 181 | 1781 | 523 | 372 | 70 | 51 | 84 | 32.2 | 0 | 91.11
13:00 | 37 | 104 | 0 | 0 | 327 | 0 | 0 | 346 | 277 |  | 0 | 360 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 12 | 25 | 12 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 100 | 0 | 315 | 315 | 168 | 36 | 91 | 46 | 5 | 0 | 20 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 92 | 132 | 50 | 22 | 2.1 | 86 | 73 | 28 | 48 | 130 | 145 | 59 | 40 | 0 | 0 | 19 | 0 | 10 | 300 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.36 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 4.8 | 16 | 0 | 0 | 0 | 0 |  | 182 | 0 | 285 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 35 | 0 | 5.6 | 70 | 0 |  | 4942.26 | 1831.6 | 6773.86 | 3653 | 182 | 1800 | 530 | 371 | 70 | 44 | 92 | 31.86 | 0 | 91.11
14:00 | 37 | 104 | 0 | 0 | 281 | 0 | 0 | 340 | 277 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 25 | 6 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 275 | 265 | 167 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 80 | 133 | 50 | 22 | 1.8 | 86 | 74 | 11 | 10 | 100 | 148 | 59 | 10 | 0 | 0 | 19 | 0 | 10 | 280 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 80 | 50 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 |  | 182 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 6 | 0 | 4.6 | 0 | 0 |  | 4472.9 | 1576.6 | 6049.5 | 3458 | 182 | 1593 | 259 | 371 | 70 | 8 | 80 | 28.5 | 0 | 91.1
15:00 | 37 | 104 | 0 | 0 | 282 | 0 | 0 | 340 | 256 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 25 | 6 | 25 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 29 | 0 | 100 | 0 | 280 | 265 | 165 | 36 | 92 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 76 | 132 | 50 | 20 | 1.4 | 87 | 74 | 11 | 10 | 110 | 145 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 300 | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5 | 0 | 0 | 0 | 80 | 50 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 |  | 183 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 |  | 4433.9 | 1537.3 | 5971.2 | 3464 | 183 | 1551 | 237 | 371 | 68 | 0 | 76 | 21.2 | 0 | 91.1
16:00 | 37 | 104 | 0 | 0 | 220 | 0 | 0 | 305 | 237 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 25 | 6 | 25 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 85 | 0 | 270 | 270 | 172 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 18 | 74 | 132 | 50 | 22 | 0.4 | 88 | 74 | 11 | 10 | 110 | 150 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 280 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 75 | 50 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 |  | 186 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 |  | 4271.1 | 1498.8 | 5769.9 | 3286 | 186 | 1535 | 237 | 371 | 68 | 0 | 74 | 12.9 | 0 | 91.09
17:00 | 37 | 104 | 0 | 0 | 220 | 0 | 0 | 256 | 237 |  | 0 | 300 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 12 | 25 | 6 | 25 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 207 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 80 | 0 | 285 | 275 | 176 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 18 | 76 | 132 | 50 | 22 | 0.2 | 87 | 74 | 11 | 10 | 110 | 152 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 300 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 85 | 50 | 0 | 0 | 0.487 | 0 | 0 | 0 | 0 | 0 |  | 185 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4271.387 | 1465.1 | 5736.487 | 3262 | 185 | 1534 | 238 | 370 | 68 | 0 | 76 | 3.487 | 0 | 91.09
18:00 | 37 | 104 | 0 | 0 | 220 | 0 | 0 | 256 | 237 |  | 0 | 300 | 120 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 12 | 25 | 6 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 3 | 1 | 19 | 40 | 0 | 80 | 0 | 280 | 265 | 165 | 36 | 91 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 92 | 136 | 55 | 22 | 0 | 85 | 74 | 11 | 10 | 110 | 148 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 280 | 12 | 10 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 4 | 0 | 0 | 138 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 439 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 20 | 0 |  | 4506 | 1917 | 6423 | 3291 | 439 | 1516 | 625 | 370 | 69 | 21 | 92 | 0 | 0 | 91.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 123 | 0 | 0 | 230 | 0 | 0 | 325 | 276 |  | 0 | 450 | 150 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 8 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 90 | 0 |  | 0 | 0 | 0 | 0 | 16 | 21 | 19 | 42 | 0 | 140 | 0 | 315 | 300 | 184 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 136 | 95 | 22 | 0 | 85 | 74 | 28 | 30 | 110 | 145 | 62 | 58 | 0 | 0 | 19 | 0 | 10 | 290 | 13 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 53 | 0 | 40 | 0 | 0 | 205 | 75 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 |  | 474 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 155 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 100 | 0 |  | 5578 | 2314 | 7892 | 3778 | 474 | 1913 | 1139 | 372 | 69 | 51 | 96 | 0 | 0 | 91.07
19:30 | 37 | 124 | 0 | 0 | 220 | 0 | 0 | 338 | 277 |  | 0 | 450 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 24 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 90 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 42 | 0 | 140 | 0 | 310 | 275 | 184 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 135 | 95 | 22 | 0 | 85 | 74 | 28 | 51 | 110 | 145 | 62 | 58 | 0 | 0 | 19 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 40 | 0 | 0 | 235 | 100 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 |  | 474 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 5612 | 2363 | 7975 | 3830 | 474 | 1956 | 1121 | 371 | 70 | 51 | 102 | 0 | 0 | 0
20:00 | 37 | 124 | 0 | 0 | 250 | 0 | 0 | 340 | 358 |  | 0 | 450 | 150 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 24 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 30 | 19 | 42 | 0 | 140 | 0 | 315 | 275 | 189 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 136 | 95 | 22 | 0 | 86 | 74 | 28 | 51 | 110 | 149 | 62 | 60 | 0 | 0 | 19 | 0 | 10 | 290 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 233 | 95 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 |  | 474 | 0 | 380 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 5693 | 2355 | 8048 | 3947 | 474 | 2062 | 973 | 371 | 70 | 51 | 100 | 0 | 0 | 91.06
21:00 | 37 | 134 | 0 | 0 | 250 | 0 | 0 | 342 | 362 |  | 0 | 450 | 150 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 24 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 140 | 0 | 315 | 280 | 193 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 136 | 95 | 22 | 0 | 86 | 74 | 28 | 51 | 130 | 151 | 62 | 60 | 0 | 0 | 19 | 0 | 10 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 234 | 95 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 |  | 474 | 0 | 380 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 436 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 5654 | 2324 | 7978 | 3974 | 474 | 2085 | 851 | 371 | 70 | 51 | 102 | 0 | 0 | 91.05
22:00 | 37 | 134 | 0 | 0 | 250 | 0 | 0 | 339 | 365 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 25 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 43 | 0 | 140 | 0 | 310 | 265 | 184 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 137 | 95 | 22 | 0 | 84 | 74 | 28 | 51 | 130 | 145 | 64 | 60 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 234 | 45 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 474 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 |  | 5414 | 2124 | 7538 | 3929 | 474 | 2033 | 531 | 371 | 70 | 34 | 96 | 0 | 0 | 91.04
23:00 | 37 | 134 | 0 | 0 | 250 | 0 | 0 | 338 | 364 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 100 | 0 | 325 | 280 | 196 | 36 | 91 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 88 | 137 | 72 | 22 | 0 | 88 | 74 | 28 | 51 | 130 | 155 | 64 | 80 | 0 | 0 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 307 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5098 | 1829 | 6927 | 3865 | 307 | 1988 | 239 | 371 | 69 | 0 | 88 | 0 | 0 | 91.03
24:00 | 37 | 100 | 0 | 0 | 250 | 0 | 0 | 342 | 367 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 20 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 100 | 0 | 305 | 270 | 164 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 18 | 21 | 84 | 140 | 24 | 0 | 0 | 85 | 73 | 28 | 51 | 130 | 145 | 45 | 80 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 234 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 91 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4754 | 1649 | 6403 | 3602 | 234 | 1899 | 144 | 371 | 69 | 0 | 84 | 0 | 0 | 91.02
KWH | 926000 | 3239100 | 0 | 0 | 6926682 | 0 | 0 | 8201220 | 7437000 |  | 0 | 8948000 | 3332742 | 288000 | 0 | 0 | 0 | 0 | 0 | 0 | 400320 | 206784 | 0 | 0 | 0 | 0 | 0 | 447480 | 58832 | 0 | 242460 | 600000 | 486720 | 644600 | 798400 | 0 | 0 | 627120 | 964000 | 0 | 3000000 | 0 | 4896315 | 0 | 2308496 | 0 |  | 0 | 0 | 0 | 0 | 22080 | 62400 | 447456 | 985920 | 0 | 2543015 | 0 | 7484000 | 6980000 | 4332000 | 568727 | 2133830 | 757512 | 135360 | 0 | 771744 | 0 | 0 | 0 | 392148 | 148140 | 447000 | 504370 | 2032320 | 2985600 | 1450560 | 515160 | 13200 | 2037000 | 1752960 | 373800 | 596232 | 3150163 | 3472000 | 1240800 | 773760 | 0 | 840730 | 305000 | 0 | 164700 | 7510000 | 271248 | 97224 | 0 | 0 | 0 | 0 | 213600 | 0 | 233280 | 137295 | 60480 | 0 | 0 | 2809000 | 1420800 | 0 | 0 | 32520 | 371345 | 0 | 0 | 0 | 0 |  | 5918545 | 0 | 7092576 | 0 | 629760 | 0 | 0 | 0 | 0 | 0 | 9750 | 2148977 | 344400 | 152352 | 0 | 0 | 0 | 0 | 0 | 428228 | 0 | 0 | 0 | 0 | 0 | 323040 | 219168 | 258 | 2157818 | 0 | 6786300 | 0 | 0 | 4228600 | 0 | 0 | 0 | 1352350 | 0 | 0 | 0 | 9635327 | 0 | 0 | 0 | 0 | 343680 | 0 | 31639 | 866976 | 0 |  | 118556750 | 42669744 | 161226494 | 88236597 | 5918545 | 43289691 | 10571221 | 8944118 | 1591120 | 428228 | 2032320 | 214654 | 0
Fuel Cost | 1037120 | 3498228 | 0 | 0 | 5125744.68 | 0 | 0 | 5904878.4 | 5652120 |  | 0 | 7158400 | 2999467.8 | 2937600 | 0 | 0 | 0 | 0 | 0 | 0 | 4443552 | 2100925.44 | 0 | 0 | 0 | 0 | 0 | 4291333.2 | 561257.28 | 0 | 181845 | 450000 | 0 | 0 | 0 | 0 | 0 | 163051.2 | 250640 | 0 | 4590000 | 0 | 5141130.75 | 0 | 2931789.92 | 0 |  | 0 | 0 | 0 | 0 | 209980.8 | 584064 | 411659.52 | 2740857.6 | 0 | 2670165.75 | 0 | 5538160 | 5863200 | 3985440 | 557352.46 | 2837993.9 | 621159.84 | 139420.8 | 0 | 1103593.92 | 0 | 0 | 0 | 399990.96 | 111105 | 844830 | 378277.5 | 14023008 | 2448192 | 13794825.6 | 525463.2 | 216480 | 2770320 | 2384025.6 | 508368 | 745290 | 3906202.12 | 3194240 | 1848792 | 1361817.6 | 0 | 1277909.6 | 484950 | 0 | 387045 | 5332100 | 203436 | 73890.24 | 0 | 0 | 0 | 0 | 2054832 | 0 | 2353795.2 | 1584384.3 | 563673.6 | 0 | 0 | 2640460 | 12460416 | 0 | 0 | 0 | 3423800.9 | 0 | 0 | 0 | 0 |  | 15980071.5 | 0 | 5532209.28 | 0 | 6070886.4 | 0 | 0 | 0 | 0 | 0 | 96427.5 | 1719181.6 | 533820 | 1636260.48 | 0 | 0 | 0 | 0 | 0 | 4239457.2 | 0 | 0 | 0 | 0 | 0 | 355344 | 361627.2 | 195.306 | 13745300.66 | 0 | 27755967 | 0 | 0 | 3721168 | 0 | 0 | 0 | 2150236.5 | 0 | 0 | 0 | 7033788.71 | 0 | 0 | 0 | 0 | 3209971.2 | 0 | 0 | 0 | 0 |  | 168984052.68 | 94141912.536 | 263125965.216 | 81347152.046 | 15980071.5 | 40027383.91 | 63793069.4 | 41501267.66 | 413691.2 | 4239457.2 | 14023008 | 1800864.3 | 0
Yesterday Day Peak | 37 | 104 | 0 | 0 | 391 | 0 | 0 | 367 | 277 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 12 | 25 | 12 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 205 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 100 | 0 | 265 | 315 | 167 | 36 | 92 | 46 | 5 | 0 | 20 | 0 | 0 | 0 | 22 | 8 | 28 | 18 | 84 | 132 | 50 | 22 | 2 | 88 | 73 | 27 | 22 | 130 | 147 | 60 | 40 | 0 | 127 | 19 | 0 | 10 | 325 | 15 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 19.5 | 0 | 0 | 0 | 80 | 115 | 0 | 0 | 5.1 | 16 | 0 | 0 | 0 | 0 |  | 181 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 92 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 35 | 0 | 5.6 | 70 | 0 |  | 6904.2 | DayPeak
Yesterday Evening Peak | 37 | 124 | 0 | 0 | 250 | 0 | 0 | 340 | 358 | 0 | 0 | 450 | 150 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 24 | 25 | 33 | 0 | 0 | 30 | 40 | 0 | 120 | 0 | 203 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 19 | 42 | 0 | 140 | 0 | 315 | 275 | 189 | 36 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 136 | 95 | 22 | 0 | 86 | 74 | 28 | 51 | 110 | 149 | 62 | 60 | 0 | 0 | 19 | 0 | 10 | 290 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 233 | 95 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 |  | 474 | 0 | 380 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 8048 | EvPeak
Forecast for Evening | 37 | 170 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 30 | 40 | 0 | 120 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 100 | 0 | 360 | 360 | 225 | 46 | 90 | 45 | 20 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 114 | 140 | 95 | 22 | 0 | 88 | 73 | 51 | 50 | 163 | 150 | 66 | 80 | 0 | 150 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 829 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 90 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 40 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 90 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 37 | 130 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 30 | 40 | 0 | 100 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 15 | 0 | 100 | 0 | 360 | 360 | 225 | 46 | 90 | 45 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 99 | 140 | 95 | 22 | 1.6 | 88 | 73 | 51 | 50 | 163 | 150 | 66 | 80 | 0 | 150 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 581 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 90 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 40 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 90 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 95 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 37 | 99 | 0 | 0 | 285 | 0 | 0 | 349 | 313 | 0 | 0 | 350 | 150 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 201 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 0 | 100 | 0 | 280 | 320 | 193 | 8 | 90 | 45 | 5 | 0 | 15 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 80 | 140 | 50 | 22 | 0.3 | 58 | 61 | 28 | 25 | 163 | 153 | 35 | 80 | 0 | 0 | 0 | 0 | 9 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 23 | 6.1 | 0 | 0 | 0 | 233 | 107 | 0 | 0 | 1.4 | 16 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 50 | 0 | 0
199
| Minimum Generation |  | 5873 | 5:00
| Highest Generation |  | 8048 | 20:00
| Day Peak Generation |  | 6904.2 | 12:00
| Evening Peak Generation |  | 8048 | 20:00
| HVDC Max Flow |  | 474 | 19:00
| HVDC EvPeak Flow |  | 474 | 20:00
| Load factor L.F |  | 83.47%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6904.2 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5326 | MW
Evening Peak Generation : |  | 8048 | MW Hour : | 20:00 | Available Max Generation : |  | 14653 | MW
E.P. Demand (at gen end) : |  | 8048 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 8048 | MW Hour : | 20:00 | Reserve(Generation end) |  | 5653 | MW
Total Gen. (MKWH) : |  | 161.2265 | System Load Factor : | 83.47% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -660 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-22
Actual : | 90.96 | Ft.(MSL) , | Rule curve : | 94.05 | Ft.( MSL )
Gas Consumed : | Total = | 1029.1 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 121374535.956
: |  | Coal : | 41501267.66 | Oil : | 68032526.6 | Total : | 230908330.216
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3068.3465 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1037.0305 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 928.0086 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 838.1306 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 757.629 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 611.3637 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 350.0508 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 157.6269 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 471.4748 |  |  | 0 | 0%
Total | 0 |  | 8219.6615 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Bhola 225 MW GT-1
|  |  |  | 2) Meghnaghat GT-2 | 11) Chattrogram TPP-1
3) Ghorasal Unit-4&5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Aminbazar-Meghnaghat 230 kV Ckt-2 was under shut down from 08:41 to 21:22 for D/W.
b) BSRM 230/33 kV T-2 transformer was under shut down from 09:27 to 16:48 for C/M.
c) Bheramara HVDC 400 kV Bus-2 was switched on at 10:58.
d) Ishurdi 33 kV Bus-1 was under shut down from 08:27 to 13:28 for C/M.
e) Barapukuria 132/33 kV T-4 transformer was under shut down from 08:24 to 12:32 for C/M.
f) Sylhet 150 MW tripped at 12:19 due to generator protection.
g) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 08:22 to 08:48 for C/M.
h) Kallyanpur 132 kV main & reserve Bus tripped at 17:50 as R-phase, CT (reserve Bus) of Bus coupler |  |  |  |  | About 45 MW power interruption occurred under Kallyanpur S/S area
burst and Main Bus was switched on at 18:22 and 132/33 kV T-1 transformer was switched on at 18:37. |  |  |  |  | from 17:50 to 18:37.
i) Madunaghat-T.K. Chemical 132 kV Ckt was switched on at 14:28.
j) Mongla 132/33 kV T-1 & T-2 transformers tripped at 15:57 from 33 kV side showing E/F relay due to
Bashundhara ind. Feeder fault and was switched on at 16:15.
k) Ghorashal 132/33 kV T-2 tripped at 17:30 from 132 kV side showing 1P4 at R-phase and was switched
on at 17:48.
l) Bibiyana-3 CCPP ST was synchronized at 17:32.
m) Kallyanpur 132 kV main Bus was under shut down again from 19:15 to 19:37 for making bypass of |  |  |  |  | About 50 MW power interruption occurred under Kallyanpur S/S area
R-phase,PT of main Bus. |  |  |  |  | from 19:15 to 19:37.
n) Hathazari-Khulshi 132 kV Ckt was shut down at 06:30(22/02/2020) for D/W.
o) Khulshi-Madunaghat 132 kV Ckt was shut down at 06:36(22/02/2020) for D/W.
p) Rampura 230/132 kV T-2 transformer was shut down at 07:03(22/02/2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 926000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 124 | 3239100
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6926682 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8201220 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 358 | 7437000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8948000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 60 | 288000 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3332742 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 242460
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 400320
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 206784 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 447480
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 58832 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1086720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 644600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 798400 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 50 | 233280 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2148 | 43417620
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137295
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 62400 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1591120 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4896315 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2308496 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 60480 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 447456
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 985920
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 22080 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32520
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 71 | 371345 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 665 | 13915427
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 140 | 2543015
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4332000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7484000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6980000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 757512
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 135360 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 568727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 771744 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2133830
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 392148
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 148140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 100 | 2032320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 447000
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 504370
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1326 | 29230166
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 136 | 2985600 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515160
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1450560
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 213600 | Reserve
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 1420800 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 348 | 6598920
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2037000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1752960
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 3150163 | frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 149 | 3472000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 28 | 373800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 596232
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 97224
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1240800 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 60 | 773760 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 840730 | Under maint.
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 305000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 23 | 271248
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7510000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 233 | 2809000 | Machine Problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 164700
| Sylhet Area Total |  |  |  | 1949 | 1206 | 25394617
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 474 | 5918545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 59 | 629760 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 380 | 7092576 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 9750 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 913 | 13650631
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 152352 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 18 | 344400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 2148977 | GT-1 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 1352350
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 222 | 3998079
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4228600 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 434 | 9635327 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 323040 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 219168
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 258
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 428228 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 866976
| Rajshahi Area Total |  |  |  | 2183 | 814 | 15701597
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 91 | 2157818
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6786300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 343680 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31639
| Rangpur Area Total |  |  |  | 605 | 406 | 9319437
| Total |  |  |  | 19107 | 8048 | 161226494
| Eastern Grid Total |  |  |  | 13543 | 5693 | 118556750
| Western Grid Total |  |  |  | 5564 | 2355 | 42669744
| National Grid Total |  |  |  | 19107 | 8048 | 161226494
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-21
(a) ENTIRE EASTERN GRID : |  | 4734 | MW | (b) ENTIRE WESTERN GRID : |  | 2597 | MW
i) Dhaka area |  | 2346 | MW | i) Khulna area |  | 950 | MW
ii) Chittagong area |  | 665 | MW | ii) Rajshahi area |  | 853 | MW
iii) Comilla area |  | 720 | MW | iii) Barisal area |  | 216 | MW
iv) Mymensingh area |  | 697 | MW | iv) Rangpur area |  | 578 | MW
v) Sylhet area |  | 306 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7331 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 90 | 1:00 | Srimongal | 23 | 19:00 | Jhenida | 78 | 19:00
Munsiganj | 72 | 18:30 | Shahjibazar | 78 | 19:30 | Bottail | 76 | 18:30
Sonargaon | 66 | 20:00 | Fenchuganj | 22 | 19:30 | G.K Project | 36 | 19:00
Shyampur | 172 | 1:00 | Kulawara | 26 | 18:30 | Faridpur | 110 | 19:00
Bhulta | 162 | 3:00 | Sylhet | 88 | 19:30 | Madaripur | 57 | 20:00
Madanganj | 45 | 19:00 | Chatak | 16 | 18:30 | Sariatpur | 38 | 20:00
Shitalakhya | 76 | 1:00 | Sunamganj | 28 | 19:00 | Gopalganj | 64 | 19:00
Rahim steel | 2 | 1:00 | Biani Bazar | 31 | 18:00 | Bagerhat | 63 | 19:30
Matuail | 70 | 1:00 | Comilla (S) | 102 | 18:30 | Mongla | 28 | 1:00
Ghorasal | 40 | 19:30 | Comilla(N) | 73 | 19:00 | Satkhira | 67 | 19:00
Narsingdi | 107 | 20:00 | Chandpur | 63 | 18:30 | Gallamari | 39 | 13:00
Haripur (SBU) | 88 | 4:00 | Feni | 88 | 19:30 | Magura | 36 | 19:30
Ullon | 51 | 19:00 | Chowmuhani | 106 | 18:30 | Norail | 25 | 19:00
Hasnabad | 118 | 20:00 | Ashuganj | 41 | 19:00 | Chuadanga | 60 | 19:00
Magbazar | 62 | 20:00 | Daudkandi | 90 | 20:00 | Barisal(N) | 28 | 19:00
Maniknagar | 60 | 20:00 | B.Baria | 92 | 18:30 | Barisal (S) | 64 | 19:00
Bangabhaban | 12 | 18:00 | Ramganj | 58 | 20:00 | Patuakhali | 69 | 19:30
Narinda | 60 | 20:00 | Chaddagram | 16 | 18:00 | Bhandaria | 38 | 19:30
Dhanmondi | 62 | 20:00 | PHP | 4 | 9:00 | Borhan Uddin | 23 | 19:00
Lalbag | 59 | 1:00 | Madunaghat | 34 | 19:00 | Ishurdi | 29 | 19:00
Madartek | 44 | 18:30 | Hathazari | 59 | 19:30 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 114 | 19:30 | Natore | 83 | 19:00
Mirpur | 72 | 18:30 | Halishahar | 83 | 19:00 | Bogra | 125 | 19:00
Kalyanpur | 54 | 13:00 | Baraulia | 139 | 1:00 | Noagaon | 89 | 19:00
Gulshan | 76 | 18:30 | Sikalbaha | 17 | 19:00 | Rajshahi | 83 | 19:30
Uttara | 42 | 18:30 | Dohazari | 66 | 19:00 | Rajshahi New | 8 | 18:30
Uttara New | 28 | 18:30 | Cox'sbazar | 73 | 19:00 | C.Nawabganj | 60 | 9:00
Kamrangirchar | 57 | 18:30 | Chandraghona | 22 | 18:30 | Amnura | 27 | 10:00
Savar | 64 | 18:30 | Kaptai | 3.5 | 18:30 | Pabna | 64 | 19:00
Bhasantec | 98 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 68 | 19:00
Agargaon | 34 | 18:30 | Bakulia | 58 | 19:30 | Serajganj | 60 | 7:00
Satmosjid | 81 | 19:00 | Julda | 15 | 7:00 | Niyamatpur | 77 | 9:00
Tongi | 67 | 1:00 | TK chemical | 9.6 | 18:30 | Joypurhat | 52 | 8:00
Kabirpur | 116 | 12:00 | Modern Steel | 14 | 2:00 | Sherpur(Bogura) | 25 | 1:00
Basundhara | 77 | 21:00 | Shahmirpur | 19 | 1:00 | Mohastangor | 34 | 19:00
Manikganj | 50 | 21:00 | Khagrachhari | 18 | 18:30 | Rangpur | 100 | 19:00
Joydevpur | 116 | 20:00 | Matarbari | 23 | 18:30 | Lalmonirhat | 44 | 18:30
New Tongi | 56 | 1:00 | Baroiar Hat | 16 | 18:00 | Saidpur | 78 | 19:00
Korda | 137 | 1:00 | Rangamati | 8 | 12:00 | Purbasadipur | 93 | 12:00
Dhamrai | 44 | 19:00 | Abul Khair 230 | 161 | 13:00 | Thakurgaon | 70 | 19:0
Valuka | 60 | 1:00 | BSRM | 55 | 2:00 | Palashbari | 97 | 18:30
Tangail | 151 | 8:00 | GPH Ispat | 8 | 1:00 | Barapukuria | 45 | 8:00
Mymensing | 169 | 19:00 | Goalpara | 15 | 13:00 | Panchagar | 36 | 19:00
Kishorganj | 84 | 19:00 | Central s/s | 54 | 19:00 | Joldhaka | 30 | 18:30
Netrokona | 94 | 19:00 | Noapara | 40 | 19:00 | Kurigram | 42 | 0.77083
Jamalpur | 107 | 8:00 | Jessore | 84 | 18:30
Sherpur | 88 | 8:00 | Benapol | 30 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-21 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 404 | 0.125 | 400 | 0.41667 | Kaliakoir | 390 | 0.16667 | 385 | 0.45833
Bheramara | 406 | 0.45833 | 399 | 0.375 | Bhulta | 397 | 0.5 | 393 | 0.41667
Ashuganj(N) | 402 | 0.75 | 398 | 0.41667 | Gopalganj | 426 | 0.625 | 391 | 0.875
Payra | 431 | 0.20833 | 392 | 0.83333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 236 | 0.45833 | Hathazari | 227 | 0.375 | 223 | 0.45833
Ishurdi | 239 | 0.16667 | 226 | 0.29167 | Megnaghat | 240 | 0.77083 | 235 | 0.041667
Ashuganj | 242 | 0.16667 | 240 | 0.041667 | Fenchuganj | 243 | 0.54167 | 240 | 0.29167
Serajganj | 233 | 0.58333 | 227 | 0.33333 | Siddhirganj | 236 | 0.125 | 234 | 0.29167
Baghabari | 238 | 0.083333 | 232 | 0.29167 | Maniknagar | 235 | 0.75 | 232 | 0.041667
Barapukuria | 238 | 0.20833 | 230 | 0.33333 | Old Airport | 236 | 0.20833 | 231 | 0.45833
Bogra | 227 | 0.041667 | 217 | 0.33333 | Barisal | 249 | 0.79167 | 238 | 0.875
Khulna South | 241 | 0.20833 | 218 | 0.83333 | AKSML | 224 | 0.33333 | 221 | 0.041667
Rampura | 232 | 0.70833 | 230 | 0.041667 | BSRM | 228 | 0.16667 | 225 | 0.041667
Haripur | 235 | 0.77083 | 231 | 0.041667 | Bibiyana | 242 | 0.375 | 239 | 0.125
Hasnabad | 233 | 0.20833 | 232 | 0.041667 | Bhulta | 236 | 0.77083 | 233 | 0.5
Shyampur | 233 | 0.75 | 230 | 0.041667 | Ashuganj (S) | 234 | 0.625 | 230 | 0.91667
Aminbazar | 235 | 0.083333 | 233 | 0.33333 | Kaliakoir | 237 | 0.16667 | 234 | 0.45833
Tongi | 232 | 0.54167 | 228 | 0.041667 | GPH | 224 | 0.16667 | 221 | 0.41667
Comilla (N) | 240 | 0.66667 | 238 | 0.041667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.75 | 133 | 0.041667 | Khulshi | 132 | 0.125 | 130 | 0.45833
Munsiganj | 136 | 0.77083 | 131 | 0.45833 | Halishahar | 134 | 0.33333 | 130 | 0.45833
Sonargaon | 136 | 0.75 | 132 | 0.041667 | Baraulia | 134 | 0.79167 | 132 | 0.041667
Shyampur | 137 | 0.75 | 134 | 0.041667 | Sikalbaha | 133 | 0.33333 | 131 | 0.45833
Bhulta | 130 | 0.54167 | 127 | 0.041667 | Dohazari | 132 | 0.041667 | 130 | 0.125
Madanganj | 137 | 0.77083 | 130 | 0.45833 | Cox'sbazar | 127 | 0.16667 | 122 | 0.77083
Shitalakhya | 140 | 0.79167 | 133 | 0.041667 | Chandraghona | 134 | 0.041667 | 133 | 0.083333
Rahim steal | 137 | 18:30 | 134 | 0.041667 | Kaptai | 134 | 0.75 | 132 | 0.41667
Matuail | 136 | 0.75 | 132 | 0.041667 | A. Khaer Stl. | 134 | 0.77083 | 131 | 0.041667
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | Bakulia | 132 | 0.375 | 130 | 0.041667
Narsinghdi | 135 | 0.54167 | 128 | 0.083333 | Julda | 132 | 0.33333 | 130 | 0.041667
Haripur (SBU) | 137 | 0.20833 | 134 | 0.33333 | TK Chemical | 133 | 0.58333 | 131 | 0.125
Ullon | 130 | 0.25 | 128 | 0.5 | Modern Steel | 133 | 0.125 | 131 | 0.41667
Hasnabad | 136 | 0.75 | 134 | 0.5 | Shahmirpur | 132 | 0.125 | 130 | 0.041667
Magbazar | 131 | 0.25 | 128 | 0.5 | Khagrachhari | 133 | 0.041667 | 132 | 0.45833
Maniknagar | 137 | 0.25 | 136 | 0.5 | Matarbari | 130 | 0.125 | 125 | 0.83333
Bangabhaban | 137 | 0.25 | 136 | 0.5 | Baroiar Hat | 135 | 0.29167 | 132 | 0.8125
Narinda | 137 | 0.25 | 136 | 0.5 | Rangamati | 134 | 0.375 | 132 | 11:00
Dhanmondi | 130 | 0.25 | 128 | 0.5 | Goalpara | 137 | 0.041667 | 124 | 20:00
Lalbag | 136 | 0.083333 | 133 | 0.083333 | Central s/s | 135 | 0.041667 | 123 | 0.83333
Madartek | 130 | 0.375 | 128 | 0.45833 | Noapara | 136 | 0.041667 | 123 | 0.83333
Dhaka University |  |  |  |  | Jessore | 132 | 0.041667 | 120 | 0.83333
Mirpur | 139 | 0.083333 | 133 | 0.5 | Benapol | 136 | 0.125 | 121 | 0.83333
Kalyanpur | 139 | 0.20833 | 137 | 0.5 | Jhenida | 132 | 0.041667 | 119 | 0.83333
Gulshan | 129 | 0.083333 | 127 | 0.5 | Bottail | 136 | 0.083333 | 126 | 0.83333
Uttara | 135 | 0.20833 | 132 | 0.45833 | G.K Project | 140 | 0.75 | 133 | 0.83333
Uttara New | 136 | 0.25 | 133 | 0.5 | Faridpur | 137 | 0.125 | 128 | 0.83333
Kamrangirchar | 135 | 0.75 | 132 | 0.54167 | Madaripur | 138 | 0.375 | 128 | 0.83333
Savar | 136 | 0.25 | 134 | 0.5 | Sariatpur | 142 | 0.20833 | 130 | 0.83333
Bhasantec | 135 | 0.20833 | 130 | 0.5 | Gopalganj | 144 | 0.20833 | 132 | 0.83333
Agargaon | 136 | 0.20833 | 133 | 0.5 | Bagerhat | 132 | 0.041667 | 122 | 0.83333
Satmosjid | 136 | 0.20833 | 131 | 0.54167 | Mongla | 132 | 0.625 | 121 | 0.83333
Tongi | 140 | 0.75 | 137 | 0.79167 | Satkhira | 135 | 0.16667 | 121 | 0.83333
Kabirpur | 134 | 24:00 | 132 | 0.875 | Gallamari | 138 | 0.20833 | 123 | 0.83333
Basundhara | 131 | 9:00 | 128 | 0.95833 | Magura | 136 | 0.20833 | 120 | 0.83333
Manikganj | 141 | 0.375 | 137 | 0.45833 | Norail | 132 | 0.20833 | 117 | 0.83333
Joydevpur | 142 | 0.75 | 140 | 0.041667 | Chuadanga | 130 | 0.041667 | 114 | 0.83333
New Tongi | 139 | 0.75 | 136 | 0.91667 | Barisal(N) | 141 | 0.58333 | 134 | 0.83333
Kodda | 136 | 0.79167 | 132 | 0.041667 | Barisal (S) | 140 | 0.375 | 132 | 0.83333
Dhamrai | 134 | 0.041667 | 132 | 0.875 | Patuakhali | 137 | 0.375 | 128 | 0.83333
Valuka | 125 | 0.8125 | 117 | 0.25 | Bhandaria | 138 | 0.125 | 127 | 0.83333
Tangail | 131 | 0.58333 | 124 | 0.29167 | Ishurdi | 137 | 0.16667 | 129 | 0.29167
Mymensing | 125 | 0.79167 | 117 | 0.29167 | Ruppur Paromanobik | 136 | 0.125 | 130 | 0.29167
Kishorganj | 128 | 0.083333 | 124 | 0.29167 | Natore | 133 | 14:0 | 126 | 0.33333
Netrokona | 122 | 0.79167 | 114 | 0.29167 | Bogra | 137 | 0.041667 | 127 | 0.33333
Jamalpur | 131 | 0.77083 | 118 | 0.25 | Noagaon | 132 | 0.125 | 119 | 0.33333
Sherpur | 132 | 0.79167 | 116 | 0.25 | Rajshahi | 130 | 0.041667 | 122 | 0.33333
Srimongal | 140 | 0.16667 | 135 | 0.54167 | Rajshahi New | 131 | 0.041667 | 120 | 0.33333
Shahjibazar | 136 | 0.625 | 134 | 0.041667 | C.Nawabganj | 129 | 0.125 | 117 | 0.33333
Fenchuganj | 138 | 0.041667 | 136 | 14:00 | Amnura | 128 | 0.58333 | 117 | 0.33333
Khulawara | 137 | 0.041667 | 135 | 0.75 | Pabna | 135 | 0.125 | 130 | 0.29167
Sylhet | 136 | 0.041667 | 133 | 0.75 | Shahjadpur | 142 | 0.75 | 134 | 0.33333
Chatak | 135 | 0.041667 | 133 | 0.54167 | Serajganj | 136 | 0.041667 | 130 | 0.29167
Sunamganj | 135 | 0.041667 | 133 | 0.54167 | Niyamatpur | 129 | 0.125 | 115 | 0.33333
Biani Bazar | 136 | 0.33333 | 132 | 0.77083 | Joypurhat | 130 | 0.58333 | 117 | 0.33333
Comilla(s) | 132 | 0 | 128 | 0.41667 | Sherpur(Bogura) | 138 | 0.16667 | 128 | 0.33333
Comilla(n) | 141 | 7:00 | 140 | 0.41667 | Mohastangor | 136 | 0.16667 | 126 | 0.33333
Chandpur | 137 | 0.625 | 136 | 0.79167 | Rangpur | 134 | 0.125 | 124 | 0.33333
Feni | 136 | 0.41667 | 134 | 0.875 | Lalmonirhat | 127 | 0.625 | 119 | 0.33333
Chowmuhani | 133 | 0.29167 | 131 | 0.75 | Saidpur | 133 | 0.20833 | 124 | 0.33333
Ashuganj | 137 | 0.625 | 135 | 0.041667 | Purbasadipur | 130 | 0.083333 | 119 | 0.33333
Daudkandi | 136 | 0.33333 | 135 | 0.29167 | Thakurgaon | 128 | 0.041667 | 118 | 0.375
B.Baria | 135 | 0.54167 | 132 | 0.83333 | Palashbari | 133 | 0.125 | 125 | 0.79167
Ramganj | 131 | 0.54167 | 130 | 0.875 | Barapukuria | 138 | 0.20833 | 130 | 0.33333
Chaddagram | 138 | 0.625 | 135 | 0.83333 | Panchagar | 126 | 0.625 | 115 | 0.41667
PHP | 135 | 0.54167 | 133 | 0.75 | Joldhaka | 132 | 0.16667 | 122 | 0.33333
Madanhat | 135 | 0.25 | 133 | 0.95833 | Kurigram | 132 | 0.125 | 119 | 0.33333
Hathazari | 135 | 0.125 | 134 | 0.041667

## L-Curve
Date | 2020-02-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 400 | 4754 | 1649 | 6403 |  |  |  | QF-LDC-12
0:30 | 420 | 4937 | 1636.5 | 6573.5 | Date: | 2020-02-21
1:00 | 440 | 5120 | 1624 | 6744
1:30 | 416.5 | 5008 | 1596 | 6604
2:00 | 393 | 4896 | 1568 | 6464
2:30 | 356.5 | 4757.5 | 1560 | 6317.5 | [5 empty] | Gen. at Eve. Peak | 8048 | 8048 MW (20:00 )
3:00 | 320 | 4619 | 1552 | 6171 | [6 empty] | 20:00
3:30 | 321 | 4496.5 | 1531 | 6027.5 | [5 empty] | Gen. at Day Peak | 6904.2 | 6904.2 MW (12:00 )
4:00 | 322 | 4374 | 1510 | 5884 | [6 empty] | 12:00
4:30 | 338.5 | 4368 | 1510.5 | 5878.5 | [5 empty] | Highest Generation | 8048
5:00 | 355 | 4362 | 1511 | 5873 | [6 empty] | 20:00
5:30 | 387.5 | 4468 | 1519 | 5987
6:00 | 420 | 4574 | 1527 | 6101
6:30 | 425.5 | 4666.95 | 1531.55 | 6198.5
7:00 | 431 | 4759.9 | 1536.1 | 6296
7:30 | 545.5 | 4840.6 | 1633.65 | 6474.25
8:00 | 660 | 4921.3 | 1731.2 | 6652.5
8:30 | 511.5 | 4896.8 | 1767.5 | 6664.3
9:00 | 363 | 4872.3 | 1803.8 | 6676.1
9:30 | 356 | 4763.7 | 1832.45 | 6596.15
10:00 | 349 | 4655.1 | 1861.1 | 6516.2
10:30 | 362 | 4703.15 | 1838.65 | 6541.8
11:00 | 375 | 4751.2 | 1816.2 | 6567.4
11:30 | 416 | 4914.4 | 1821.4 | 6735.8
12:00 | 457 | 5077.6 | 1826.6 | 6904.2
12:30 | 437.5 | 5009.93 | 1829.1 | 6839.03
13:00 | 418 | 4942.26 | 1831.6 | 6773.86
13:30 | 350 | 4707.58 | 1704.1 | 6411.68
14:00 | 282 | 4472.9 | 1576.6 | 6049.5
14:30 | 295 | 4453.4 | 1556.95 | 6010.35
15:00 | 308 | 4433.9 | 1537.3 | 5971.2
15:30 | 280 | 4352.5 | 1518.05 | 5870.55
16:00 | 252 | 4271.1 | 1498.8 | 5769.9
16:30 | 294 | 4271.2435 | 1481.95 | 5753.1935
17:00 | 336 | 4271.387 | 1465.1 | 5736.487
17:30 | 272 | 4388.6935 | 1691.05 | 6079.7435
18:00 | 208 | 4506 | 1917 | 6423
18:30 | 366 | 5042 | 2115.5 | 7157.5
19:00 | 524 | 5578 | 2314 | 7892
19:30 | 490 | 5612 | 2363 | 7975
20:00 | 443 | 5693 | 2355 | 8048 |  |  |  | Executive Engineer
20:30 | 418.5 | 5673.5 | 2339.5 | 8013 |  |  |  | Network Operation Division
21:00 | 394 | 5654 | 2324 | 7978
21:30 | 378.5 | 5534 | 2224 | 7758
22:00 | 363 | 5414 | 2124 | 7538 |  |  |  |  | Page 6 of 7
22:30 | 401.5 | 5256 | 1976.5 | 7232.5
23:00 | 440 | 5098 | 1829 | 6927
23:30 | 420 | 4926 | 1739 | 6665
24:00 | 400 | 4754 | 1649 | 6403
8048 MW (20:00 )
6904.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-21 |  | Energy | 161226494
[10 empty] | 2020-02-21 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3602 | 234 | 1899 | 239 | 371 | 69 | 0 | 0 | 84
0:30 | 3677 | 207.5 | 1954.5 | 257 | 371.5 | 68.5 | 0 | 0 | 85 | Date: | 2020-02-21
1:00 | 3752 | 181 | 2010 | 275 | 372 | 68 | 0 | 0 | 86
1:30 | 3731.5 | 181.5 | 1916 | 251.5 | 371.5 | 68 | 0 | 0 | 84 | [7 empty] | Total Energy | 161.2265 | Total Energy Gen 161.226 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.226 MKWHr
2:00 | 3711 | 182 | 1822 | 228 | 371 | 68 | 0 | 0 | 82 | [7 empty] | Energy not Served | 0
2:30 | 3618 | 181.5 | 1799.5 | 198 | 371.5 | 68 | 0 | 0 | 81 | [7 empty] | Energy Requirement | 161.2265
3:00 | 3525 | 181 | 1777 | 168 | 372 | 68 | 0 | 0 | 80
3:30 | 3451.5 | 181 | 1725 | 152 | 371.5 | 68.5 | 0 | 0 | 78 | [6 empty] | Shortage
4:00 | 3378 | 181 | 1673 | 136 | 371 | 69 | 0 | 0 | 76
4:30 | 3387 | 181.5 | 1658 | 136 | 371 | 69 | 0 | 0 | 76
5:00 | 3396 | 182 | 1643 | 136 | 371 | 69 | 0 | 0 | 76
5:30 | 3474.5 | 181 | 1678.5 | 136.5 | 371.5 | 69 | 0 | 0 | 76
6:00 | 3553 | 180 | 1714 | 137 | 372 | 69 | 0 | 0 | 76
6:30 | 3617 | 180 | 1733 | 156.5 | 370 | 69 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 3681 | 180 | 1752 | 176 | 368 | 69 | 0 | 0 | 68
7:30 | 3693 | 178.5 | 1801 | 288.5 | 369 | 69 | 0 | 0 | 69 |  |  |  | Oil |  |  |  | ,
8:00 | 3705 | 177 | 1850 | 401 | 370 | 69 | 0 | 0 | 70
8:30 | 3692 | 177 | 1791 | 461 | 371 | 69 | 13.5 | 0 | 75
9:00 | 3679 | 177 | 1732 | 521 | 372 | 69 | 27 | 0 | 80
9:30 | 3630.5 | 177 | 1703 | 501 | 372 | 69.5 | 39 | 0 | 81
10:00 | 3582 | 177 | 1674 | 481 | 372 | 70 | 51 | 0 | 82
10:30 | 3641 | 177 | 1653 | 468 | 372 | 70 | 51 | 0 | 82
11:00 | 3700 | 177 | 1632 | 455 | 372 | 70 | 51 | 0 | 82
11:30 | 3755 | 179 | 1706.5 | 489 | 372 | 70 | 51 | 0 | 83
12:00 | 3810 | 181 | 1781 | 523 | 372 | 70 | 51 | 0 | 84
12:30 | 3731.5 | 181.5 | 1790.5 | 526.5 | 371.5 | 70 | 47.5 | 0 | 88
13:00 | 3653 | 182 | 1800 | 530 | 371 | 70 | 44 | 0 | 92
13:30 | 3653 | 182 | 1800 | 530 | 371 | 70 | 44 | 0 | 92
14:00 | 3653 | 182 | 1800 | 530 | 371 | 70 | 44 | 0 | 92
14:30 | 3558.5 | 182.5 | 1675.5 | 383.5 | 371 | 69 | 22 | 0 | 84
15:00 | 3464 | 183 | 1551 | 237 | 371 | 68 | 0 | 0 | 76
15:30 | 3375 | 184.5 | 1543 | 237 | 371 | 68 | 0 | 0 | 75
16:00 | 3286 | 186 | 1535 | 237 | 371 | 68 | 0 | 0 | 74
16:30 | 3274 | 185.5 | 1534.5 | 237.5 | 370.5 | 68 | 0 | 0 | 75
17:00 | 3262 | 185 | 1534 | 238 | 370 | 68 | 0 | 0 | 76
17:30 | 3276.5 | 312 | 1525 | 431.5 | 370 | 68.5 | 10.5 | 0 | 84
18:00 | 3291 | 439 | 1516 | 625 | 370 | 69 | 21 | 0 | 92
18:30 | 3534.5 | 456.5 | 1714.5 | 882 | 371 | 69 | 36 | 0 | 94
19:00 | 3778 | 474 | 1913 | 1139 | 372 | 69 | 51 | 0 | 96
19:30 | 3830 | 474 | 1956 | 1121 | 371 | 70 | 51 | 0 | 102
20:00 | 3947 | 474 | 2062 | 973 | 371 | 70 | 51 | 0 | 100
20:30 | 3960.5 | 474 | 2073.5 | 912 | 371 | 70 | 51 | 0 | 101
21:00 | 3974 | 474 | 2085 | 851 | 371 | 70 | 51 | 0 | 102
21:30 | 3951.5 | 474 | 2059 | 691 | 371 | 70 | 42.5 | 0 | 99
22:00 | 3929 | 474 | 2033 | 531 | 371 | 70 | 34 | 0 | 96
22:30 | 3897 | 390.5 | 2010.5 | 385 | 371 | 69.5 | 17 | 0 | 92
23:00 | 3865 | 307 | 1988 | 239 | 371 | 69 | 0 | 0 | 88
23:30 | 3733.5 | 270.5 | 1943.5 | 239 | 371 | 69 | 0 | 0 | 86 | Max Temp. in Dhaka |  | 30.3° C
24:00 | 3602 | 234 | 1899 | 239 | 371 | 69 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 161.226 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.226 MKWHr
Note on W13: Author:

## Generation
g | 2020-02-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 29 |  | 29 | 30 | 30 | 30 | 30 | 29 | 29 | 627120
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.6 | 7.3 | 12.1 | 17.3 | 16.5 | 19.5 | 19.36 | 18 | 15.5 | 9 | 2.7 | [9 empty] | 137295
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 213 | 203 | 203 | 202 | 216 | 215 | 204 | 203 | 227 | 218 | 205 | 205 | 204 | 205 | 204 | 207 | 205 |  | 203 | 203 | 203 | 203 | 203 | 204 | 202 | 4896315
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 104 | 105 | 104 | 104 | 104 | 115 | 104 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 90 | 90 | 110 | 110 | 110 | 110 | 70 | 2308496
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 8 | 568727
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 926000
21 | Ghorasal Repowered CCPP Unit-3 | 200 | 189 | 189 | 158 | 129 | 114 | 114 | 134 | 134 | 105 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 123 | 124 | 124 | 134 | 134 | 134 | 100 | 3239100
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 301 | 320 | 302 | 300 | 300 | 325 | 332 | 303 | 301 | 300 | 338 | 391 | 327 | 281 | 282 | 220 | 220 | 220 |  | 230 | 220 | 250 | 250 | 250 | 250 | 250 | 6926682
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 85 | 80 | 80 |  | 140 | 140 | 140 | 140 | 140 | 100 | 100 | 2543015
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 33 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 757512
33 | Ashuganj 225 MW CCPP | 179 | 165 | 215 | 167 | 167 | 184 | 185 | 184 | 177 | 165 | 185 | 167 | 168 | 167 | 165 | 172 | 176 | 165 |  | 184 | 184 | 189 | 193 | 184 | 196 | 164 | 4332000
34 | Ashuganj 450 MW CCPP(South) | 280 | 290 | 270 | 265 | 265 | 290 | 345 | 345 | 315 | 265 | 310 | 315 | 315 | 265 | 265 | 270 | 275 | 265 |  | 300 | 275 | 275 | 280 | 265 | 280 | 270 | 6980000
| Ashuganj 450 MW CCPP(North) | 300 | 310 | 285 | 285 | 285 | 335 | 360 | 310 | 315 | 265 | 305 | 265 | 315 | 275 | 280 | 270 | 285 | 280 |  | 315 | 310 | 315 | 315 | 310 | 325 | 305 | 7484000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 135360
36 | Chandpur 150 MW CCPP | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 90 | 90 | 92 | 91 | 90 | 92 | 90 | 90 | 91 |  | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 2133830
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 350 | 355 | 342 | 340 | 353 | 364 | 366 | 336 | 341 | 351 | 367 | 346 | 340 | 340 | 305 | 256 | 256 |  | 325 | 338 | 340 | 342 | 339 | 338 | 342 | 8201220
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 420 | 370 | 340 | 380 | 400 | 400 | 370 | 350 | 350 | 350 | 360 | 320 | 300 | 300 | 300 | 300 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 8948000
41 | Haripur 360MW CCPP(HPL) | 334 | 334 | 353 | 314 | 314 | 343 | 345 | 345 | 341 | 307 | 277 | 277 | 277 | 277 | 256 | 237 | 237 | 237 |  | 276 | 277 | 358 | 362 | 365 | 364 | 367 | 7437000
42 | RPCL 210MW CCPP | 102 | 104 | 118 | 117 | 117 | 125 | 127 | 127 | 127 | 124 | 121 | 132 | 132 | 133 | 132 | 132 | 132 | 136 |  | 136 | 135 | 136 | 136 | 137 | 137 | 140 | 2985600
43
44 | Fenchugonj CCPP Phase-1 | 85 | 87 | 87 | 86 | 88 | 88 | 84 | 85 | 85 | 87 | 86 | 88 | 86 | 86 | 87 | 88 | 87 | 85 |  | 85 | 85 | 86 | 86 | 84 | 88 | 85 | 2037000
45 | Fenchugonj CCPP Phase-2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 1752960
46 | Shajibazar 330 MW CCPP | 150 | 148 | 149 | 149 | 149 | 154 | 155 | 145 | 144 | 148 | 160 | 147 | 145 | 148 | 145 | 150 | 152 | 148 |  | 145 | 145 | 149 | 151 | 145 | 155 | 145 | 3472000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 60 | 59 | 59 | 45 | 45 | 45 | 45 |  | 62 | 62 | 62 | 62 | 64 | 64 | 45 | 1240800
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 10 | 10 | 10 | 10 | 10 |  | 58 | 58 | 60 | 60 | 60 | 80 | 80 | 773760
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 148 | 147 |  | 0 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 127 | 0 | [13 empty] | 840730
51 | Sylhet 20 MW GTPP | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 305000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 164700
54 | Hobiganj 11MW PP Cofidence-E | 5 | [7 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 10 |  | 11 | 11 | 11 | 11 | 11 |  | 0 | 97224
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 27 | 28 | 11 | 11 | 11 | 11 | 11 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 373800
56 | Shahjahanulla 25 MW PP | 8 | [7 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10 | 11 | 12 |  | 13 | 16 | 23 | 23 | 24 |  | 0 | 271248
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 315 | 320 | 305 | 305 | 305 | 320 | 325 | 290 | 300 | 310 | 325 | 300 | 280 | 300 | 280 | 300 | 280 |  | 290 | 300 | 290 | 310 | 300 | 290 | 300 | 7510000
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447456
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 19 | 19 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 22 | 22 | 19 | 22 | 22 |  | 0 | 242460
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 515160
63 | Impoprt (Tripura) | 86 | 82 | 80 | 76 | 76 | 76 | 68 | 70 | 80 | 82 | 82 | 84 | 92 | 80 | 76 | 74 | 76 | 92 |  | 96 | 102 | 100 | 102 | 96 | 88 | 84 | 2032320
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 41 | 41 | 41 | 41 | 41 | 37 | 37 | 38 | 29 | 34 | 34 | 40 |  | 42 | 42 | 42 | 42 | 43 | 40 | 40 | 985920
65 | Feni 22MW PP (Doreen) | 22 | 22 | [5 empty] | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 392148
66 | Feni 11 MW PP (Doreen) | [8 empty] | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 |  |  | 148140
67 | Jangalia 33MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 8 | 8 | 28 | 33 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 18 | 447000
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 18 | 18 | 21 | 21 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504370
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 12 | 12 | 12 | 6 | 6 | 6 | 6 | 6 |  | 8 | 24 | 24 | 24 | 25 | 28 | 28 | 486720
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 644600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 798400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
Chowmuhani 113 MW
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 10 | 16 |  |  |  |  | 2 |  | 55 | 100 | 100 | 100 | 50 |  | 0 | 400320
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 57 | 65 | 48 | 16 | 16 | 17 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 |  | 95 | 95 | 95 | 95 | 95 | 72 | 24 | 1450560
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [6 empty] | 0.2 | 1.5 | 3.1 | 4.1 | 4.8 | 5.1 | 4.8 | 4.1 | 3 | 1.7 | 0.487 | [9 empty] | 32520
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 120 | 120 | 120 | 120 | 120 | 150 | 135 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 3332742
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 0 | 7 |  |  |  | 1 | 63 |  | 100 | 50 | 60 | 32 |  |  |  | 288000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 22 | 10 | 10 | 22 | 48 | 10 | 10 | 10 | 10 | 10 |  | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 596232
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 10 | 43 | 10 | 10 | 20 | 20 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 771744
94 | Gagnagar 102 MW PP (Digital Power) | 0 | [10 empty] | 7 | 7 |  |  |  |  | 40 |  | 50 | 50 | 50 | 16 |  |  | 0 | 206784
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 21 | 19 | 30 |  |  |  | 0 | 62400
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 3 |  | 16 | [5 empty] | 0 | 22080
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 35 | 35 |  |  |  |  | 0 | 58832
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 100 | 100 | 100 | 130 | 130 | 100 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 3150163
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.5 | 1.1 | 1.7 | 1.9 | 2 | 2.1 | 1.8 | 1.4 | 0.4 | 0.2 | [9 empty] | 13200
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [10 empty] | 35 | 45 | 17 | 17 | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 35 | 17 | 0 | 447480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 12 | 50 | 32 | 16 | 16 | [5 empty] | 7 |  | 32 | [5 empty] | 0 | 213600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 13 | [15 empty] | 14 |  | 53 | 50 | 50 | 30 | 23 |  | 0 | 233280
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 4 |  | 40 | 40 |  |  |  |  | 0 | 60480
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 75 | 85 | 138 |  | 205 | 235 | 233 | 234 | 234 | 234 | 235 | 2809000
| Jamalpur 115 MW PP (United) | 16 | [5 empty] | 14 | 89 | 115 | 115 | 115 | 115 | 115 | 50 | 50 | 50 | 50 | 50 |  | 75 | 100 | 95 | 95 | 45 |  | 0 | 1420800
| Anwara 300 MW PP (United) | [11 empty] | 16 | 16 |  |  |  |  | 50 |  | 66 | 72 | 71 | 71 | 51 |  | 0 | 371345
120 | Eastern Zone Total | 5120 | 4896 | 4619 | 4374 | 4362 | 4574 | 4759.9 | 4921.3 | 4872.3 | 4655.1 | 4751.2 | 5077.6 | 4942.26 | 4472.9 | 4433.9 | 4271.1 | 4271.387 | 4506 |  | 5578 | 5612 | 5693 | 5654 | 5414 | 5098 | 4754 | 118556750
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 49 | 49 | 49 | 49 | 49 | 49 | 16 |  |  |  | 115 |  | 115 | 115 | 59 | 49 | 16 |  | 0 | 629760
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 32 |  | 48 | 48 | 16 | 16 | 16 | 0 | 0 | 152352
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 72 | 22 | 22 | 22 | 23 | 23 | 23 | 73 | 76 | 77 | 76 | 86 | 90 | 62 | 63 | 35 | 13 | 13 |  | 96 | 96 | 98 | 73 | 71 | 71 | 32 | 1352350
| Bhola 225 MW CCPP | 89 | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 86 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 |  | 78 | 83 | 90 | 90 | 90 | 89 | 89 | 2148977
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 15 | 15 | 15 | 16 | 14 | 13 | 12 | 11 | 11 | 12 | 12 | 12 | 11 | 11 | 11 | 15 |  | 20 | 20 | 18 | 20 | 20 | 18 | 17 | 344400
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [8 empty] | 16 | [17 empty] | 9750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 181 | 182 | 181 | 181 | 182 | 180 | 180 | 177 | 177 | 177 | 177 | 181 | 182 | 182 | 183 | 186 | 185 | 439 |  | 474 | 474 | 474 | 474 | 474 | 307 | 234 | 5918545
147 | Bheramara 410 MW CCPP | 265 | 265 | 250 | 250 | 250 | 265 | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 285 | 300 | 250 | 250 | 250 |  | 340 | 340 | 380 | 380 | 370 | 360 | 360 | 7092576
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 92 | 91 | 92 | 91 | 91 | 92 | 88 | 90 | 92 | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 90 | 90 |  | 92 | 91 | 91 | 91 | 91 | 91 | 91 | 2157818
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6786300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 170 | 130 | 130 | 130 | 130 | 175 | 190 | 205 | 180 | 180 | 180 | 150 | 150 | 140 | 130 | 130 |  | 155 | 180 | 180 | 180 | 180 | 180 | 140 | 4228600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 434 | 435 | 435 | 435 | 434 | 435 | 435 | 418 | 370 | 402 | 380 | 375 | 378 | 351 | 329 | 375 | 376 | 368 |  | 390 | 401 | 434 | 436 | 392 | 392 | 398 | 9635327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 323040
163 | Bogura 20 MW PP (Energyprima) | 11 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 11 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 12 |  | 219168
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 258
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 27 | 51 | 51 | 51 | 44 | 8 |  |  |  | 21 |  | 51 | 51 | 51 | 51 | 34 |  | 0 | 428228
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 15 | 70 | 70 | 70 | 70 | 70 |  |  |  |  | 20 |  | 100 | 109 | 109 | 109 | 50 |  | 0 | 866976
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 36 | 36 | 35 | 35 | 35 | 35 | 6 |  |  |  | 15 |  | 35 | 35 | 35 | 35 |  |  | 0 | 343680
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 1.2 | 2.8 | 4.1 | 5.2 | 5.6 | 5.6 | 4.6 | 1.3 | 1.8 | 0.1 | [9 empty] | 31639
178
178