## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-23 | Sunday
|  | Date (day): | 2020-02-23 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11744.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14463 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-22 | 2020-02-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  |  | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 134 | 204 | 170 | 170
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint |  | 27/02/2020
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 304 | 281 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 340 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 354 | 323 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 40 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 32 | 40 | 40 | 170 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 65 | 91 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 71 | 71 |  | 37 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 57 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 25 | 25
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 32 | 100 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2078 | 2447 | 3564 | 4166 | 951 | 584
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 100 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 69 | 69 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 207 | 204 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 149 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.5 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 102 | 228 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 711 | 945 | 1490 | 1655 | 400 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 120 | 100 | 100
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 310 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 310 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 46 | 46 | 45 | 45
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 20 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 46 | 46 | 149 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 118 | 87 | 115
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 24 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1273 | 1331 | 1676 | 2368 | 453 | 81
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 132 | 126 | 140 | 140 | 62 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 100 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 361.1 | 458 | 473.6 | 572 | 62 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 85 | 88 | 88 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 73 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 155 | 145 | 150 | 150 |  | 180 | GT-2 shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 28 | 25 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 51 | 50 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 63 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 97 | 0 | 0 |  |  | Under shut down
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 17 | 17
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 15 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 235 | 233 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1258 | 1372 | 1359 | 1359 | 0 | 345
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 565 | 816 | 590 | 838
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 70 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 325 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 67 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 906 | 1302 | 1278 | 2077 | 0 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 100 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 85 | 98 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 97 | 218 | 185 | 255 | 0 | 207
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 216 | 214 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 420 | 422 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 42 | 100 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 827 | 910 | 1228 | 1494 | 611 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 91 | 89 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 354.5 | 439 | 491 | 517 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7865.6 | 9422 | 11744.6 | 14463 | 2477 | 1427
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7404.7837 | 8870 | 11056.5275 | 13615.6665
A. |  | 2020-02-22 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 9422 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5326 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9422 | MW
3 | Day peak Generation : |  |  | 7865.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8870 | MW
4 | Evening peak Generation : |  |  | 9422 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 176.3036 | MKWHr | By Solar | 0.18417 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 134.5947 | MKWHr |  | By Oil: | 17.1743 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.5455 | MKWHr |  | By Hydro: | 1.5969 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2477 | MW | Dhaka | 3192 | 3192 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1427 | MW | Chittagong | 914 | 914 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3904 | MW | Khulna | 1072 | 1072 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1118.38 | MMCFD |  |  | Rajshahi | 962 | 962 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 123684998.95 | ii) Oil : | Taka | 122091339.99 | Comilla | 763 | 763 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 39825337.65 | Total | Taka | 285601676.59 | Mymensingh | 758 | 758 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.9 | MKWHr. | Sylhet | 346 | 346 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -238 | MW (E to W) at | 19:30 | hrs | Barisal | 234 | 234 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -418 | MW at | 5:00 | hrs | Rangpur | 629 | 629 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.7° C |  |  | Total | 8870 | 8870 |  | 0
B. |  | 2020-02-23 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14463 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 4863 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 179.6343 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6054 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.1171 | MKWHr. | ii) HVDC Flow at Peak Time |  | 816 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0909 | MKWHr. | iii) Maximum HVDC Flow : |  | 816 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.96 |  | (b) Today: | 90.75 |  | (c) Rule Curve: |  | 93.9
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-02-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 99 | 0 | 0 | 220 | 0 | 0 | 341 | 313 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 280 | 270 | 171 | 8 | 90 | 46 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 140 | 8 | 22 | 0 | 85 | 73 | 5 | 5 | 130 | 127 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 180 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 91 | 0 | 279 | 0 | 0 | 140 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4298 | 1597 | 5895 | 3520 | 180 | 1550 | 128 | 370 | 69 | 0 | 78 | 0 | 0 | 91.01
2:00 | 37 | 100 | 0 | 0 | 220 | 0 | 0 | 340 | 314 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 0 | 280 | 265 | 176 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 70 | 140 | 8 | 22 | 0 | 58 | 61 | 5 | 5 | 100 | 124 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4083 | 1542 | 5625 | 3356 | 181 | 1452 | 128 | 370 | 68 | 0 | 70 | 0 | 0 | 91
3:00 | 37 | 100 | 0 | 0 | 219 | 0 | 0 | 343 | 263 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 0 | 280 | 270 | 176 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 70 | 140 | 0 | 0 | 0 | 57 | 61 | 5 | 5 | 100 | 127 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 91 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4028 | 1402 | 5430 | 3240 | 181 | 1380 | 120 | 371 | 68 | 0 | 70 | 0 | 0 | 90.99
4:00 | 37 | 100 | 0 | 0 | 220 | 0 | 0 | 340 | 265 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 17 | 33 | 0 | 0 | 28 | 40 | 0 | 120 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 0 | 275 | 260 | 164 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 140 | 0 | 0 | 0 | 57 | 61 | 5 | 5 | 100 | 123 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 91 | 0 | 265 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3983 | 1374 | 5357 | 3204 | 181 | 1360 | 120 | 356 | 68 | 0 | 68 | 0 | 0 | 90.98
5:00 | 37 | 100 | 0 | 0 | 220 | 0 | 0 | 338 | 264 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 17 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 80 | 0 | 275 | 260 | 174 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 68 | 140 | 0 | 0 | 0 | 57 | 61 | 5 | 5 | 130 | 127 | 25 | 5 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 91 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4008 | 1318 | 5326 | 3196 | 181 | 1391 | 120 | 301 | 69 | 0 | 68 | 0 | 0 | 90.97
6:00 | 37 | 99 | 0 | 0 | 218 | 0 | 0 | 350 | 364 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 17 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 80 | 0 | 330 | 275 | 177 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 74 | 140 | 13 | 22 | 0 | 57 | 61 | 5 | 5 | 130 | 152 | 25 | 5 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 186 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 91 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4277 | 1434 | 5711 | 3374 | 186 | 1574 | 133 | 301 | 69 | 0 | 74 | 0 | 0 | 90.96
7:00 | 37 | 99 | 0 | 0 | 308 | 0 | 0 | 346 | 364 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 17 | 26 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 216 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 80 | 0 | 350 | 320 | 185 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 76 | 140 | 50 | 22 | 0.1 | 57 | 61 | 5 | 5 | 130 | 159 | 25 | 5 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 233 | 14 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 |  | 573 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 91 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 4498.8 | 1904.1 | 6402.9 | 3627 | 573 | 1571 | 184 | 301 | 69 | 0 | 76 | 1.9 | 0 | 90.95
8:00 | 37 | 99 | 0 | 0 | 285 | 0 | 0 | 349 | 313 |  | 0 | 350 | 150 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 28 | 17 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 201 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 0 | 100 | 0 | 280 | 320 | 193 | 8 | 90 | 45 | 5 | 0 | 15 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 80 | 140 | 50 | 22 | 0.3 | 58 | 61 | 28 | 25 | 163 | 153 | 35 | 80 | 0 | 0 | 0 | 0 | 9 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 23 | 6.1 | 0 | 0 | 0 | 233 | 107 | 0 | 0 | 1.4 | 16 | 0 | 0 | 0 | 0 |  | 574 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 50 | 0 |  | 5013.8 | 2018.6 | 7032.4 | 3682 | 574 | 1825 | 494 | 300 | 69 | 0 | 80 | 8.4 | 0 | 90.94
9:00 | 37 | 99 | 0 | 0 | 301 | 0 | 0 | 357 | 314 |  | 0 | 350 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 0 | 28 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 211 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 0 | 285 | 335 | 203 | 8 | 90 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 78 | 138 | 50 | 22 | 1.1 | 86 | 73 | 28 | 48 | 163 | 154 | 33 | 78 | 0 | 0 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 11.5 | 0 | 0 | 0 | 233 | 115 | 0 | 0 | 2.8 | 16 | 0 | 0 | 0 | 0 |  | 574 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 260 | 0 | 0 | 145 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 109 | 0 |  | 5210.4 | 2147.7 | 7358.1 | 3779 | 574 | 1876 | 605 | 350 | 69 | 10 | 78 | 17.1 | 0 | 90.93
10:00 | 37 | 99 | 0 | 0 | 289 | 0 | 0 | 354 | 313 |  | 0 | 350 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 0 | 28 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 100 | 0 | 290 | 315 | 185 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 84 | 136 | 50 | 22 | 1.5 | 86 | 73 | 28 | 51 | 163 | 147 | 32 | 78 | 0 | 0 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 15.15 | 0 | 0 | 0 | 233 | 115 | 0 | 0 | 3.8 | 16 | 0 | 0 | 0 | 0 |  | 565 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 91 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 109 | 0 |  | 5207.45 | 2125.3 | 7332.75 | 3736 | 565 | 1861 | 602 | 351 | 69 | 42 | 84 | 22.75 | 0 | 90.92
11:00 | 37 | 118 | 0 | 0 | 296 | 0 | 0 | 361 | 313 |  | 0 | 380 | 150 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 0 | 32 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 210 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 3 | 0 | 100 | 0 | 265 | 335 | 199 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 80 | 134 | 50 | 22 | 1 | 87 | 73 | 25 | 48 | 163 | 155 | 32 | 78 | 0 | 0 | 0 | 0 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 17 | 10 | 0 | 0 | 234 | 115 | 0 | 0 | 4 | 50 | 0 | 0 | 0 | 0 |  | 565 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 205 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 109 | 0 |  | 5372 | 2137 | 7509 | 3780 | 565 | 1925 | 673 | 351 | 69 | 42 | 80 | 24 | 0 | 90.91
12:00 | 37 | 134 | 0 | 0 | 304 | 0 | 0 | 367 | 354 |  | 0 | 380 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 0 | 32 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 207 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 3 | 0 | 100 | 0 | 275 | 325 | 197 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 17 | 84 | 132 | 50 | 22 | 2.1 | 85 | 73 | 28 | 51 | 163 | 155 | 31 | 78 | 0 | 0 | 0 | 0 | 10 | 325 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 18.5 | 10 | 0 | 0 | 235 | 115 | 0 | 0 | 4.5 | 102 | 0 | 0 | 0 | 0 |  | 565 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 216 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 109 | 0 |  | 5681.1 | 2184.5 | 7865.6 | 3847 | 565 | 2012 | 867 | 351 | 69 | 42 | 84 | 28.6 | 0 | 90.9
13:00 | 37 | 133 | 0 | 0 | 283 | 0 | 0 | 357 | 355 |  | 0 | 380 | 150 | 50 | 0 | 0 | 0 | 0 | 37 | 0 | 91 | 80 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 206 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 9 | 0 | 100 | 0 | 295 | 305 | 183 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 86 | 132 | 50 | 20 | 2.1 | 85 | 73 | 28 | 51 | 163 | 148 | 51 | 80 | 0 | 0 | 0 | 0 | 9 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 17.7 | 10 | 0 | 0 | 235 | 115 | 0 | 0 | 4.3 | 108 | 0 | 0 | 0 | 0 |  | 565 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 109 | 0 |  | 5788.1 | 2185.1 | 7973.2 | 3875 | 565 | 2018 | 940 | 351 | 69 | 42 | 86 | 27.2 | 0 | 90.89
14:00 | 37 | 134 | 0 | 0 | 281 | 0 | 0 | 341 | 308 |  | 0 | 350 | 120 | 25 | 0 | 0 | 0 | 0 | 37 | 0 | 60 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 19 | 4 | 0 | 100 | 0 | 295 | 290 | 182 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 86 | 132 | 50 | 20 | 2 | 86 | 73 | 28 | 48 | 120 | 150 | 45 | 78 | 0 | 0 | 0 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 15.12 | 0 | 0 | 0 | 235 | 115 | 0 | 0 | 3.7 | 80 | 0 | 0 | 0 | 0 |  | 571 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 70 | 0 |  | 5419.82 | 2045.2 | 7465.02 | 3779 | 571 | 1783 | 742 | 370 | 69 | 42 | 86 | 23.02 | 0 | 90.88
15:00 | 37 | 134 | 0 | 0 | 287 | 0 | 0 | 348 | 308 |  | 0 | 350 | 120 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 8 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 205 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 2 | 0 | 100 | 0 | 305 | 300 | 192 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 88 | 130 | 50 | 20 | 1.2 | 82 | 73 | 22 | 48 | 120 | 154 | 45 | 80 | 0 | 0 | 0 | 0 | 10 | 310 | 14 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 11.7 | 0 | 0 | 0 | 236 | 115 | 0 | 0 | 2.7 | 71 | 0 | 0 | 0 | 0 |  | 571 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 35 | 0 |  | 5415.6 | 2075 | 7490.6 | 3833 | 571 | 1850 | 648 | 371 | 69 | 42 | 88 | 18.6 | 0 | 90.87
16:00 | 37 | 134 | 0 | 0 | 282 | 0 | 0 | 343 | 307 |  | 0 | 350 | 120 | 16 | 0 | 0 | 0 | 0 | 32 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 9 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 206 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 2 | 0 | 100 | 0 | 295 | 285 | 182 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 84 | 130 | 50 | 22 | 0.8 | 81 | 73 | 25 | 50 | 120 | 149 | 45 | 76 | 0 | 0 | 0 | 0 | 10 | 310 | 14 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 6.9 | 0 | 0 | 0 | 236 | 85 | 0 | 0 | 1.5 | 50 | 0 | 0 | 0 | 0 |  | 571 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 35 | 0 |  | 5245.2 | 2033.3 | 7278.5 | 3734 | 571 | 1836 | 562 | 370 | 69 | 42 | 84 | 10.5 | 0 | 90.86
17:00 | 37 | 134 | 0 | 0 | 283 | 0 | 0 | 348 | 307 |  | 0 | 350 | 120 | 16 | 0 | 0 | 0 | 0 | 37 | 0 | 7 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 9 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 204 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 10 | 0 | 100 | 0 | 295 | 290 | 188 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 80 | 131 | 50 | 22 | 0.2 | 83 | 73 | 25 | 10 | 120 | 148 | 45 | 10 | 0 | 0 | 19 | 0 | 8 | 310 | 15 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 15 | 2.2 | 0 | 0 | 0 | 236 | 65 | 0 | 0 | 0.5 | 33 | 0 | 0 | 0 | 0 |  | 571 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 35 | 0 |  | 5107.9 | 2036.6 | 7144.5 | 3780 | 571 | 1757 | 489 | 370 | 69 | 25 | 80 | 3.5 | 0 | 90.85
18:00 | 37 | 134 | 0 | 0 | 315 | 0 | 0 | 356 | 289 |  | 0 | 350 | 120 | 27 | 13 | 0 | 0 | 0 | 37 | 0 | 10 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 16 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 217 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 19 | 0 | 100 | 0 | 340 | 320 | 186 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 24 | 21 | 112 | 133 | 95 | 22 | 0 | 86 | 73 | 25 | 10 | 120 | 185 | 45 | 10 | 0 | 48 | 19 | 0 | 8 | 300 | 14 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 20 | 0 | 10 | 0 | 0 | 235 | 77 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 |  | 647 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 64 | 0 | 0 | 0 | 8 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 45 | 0 |  | 5502 | 2223.1 | 7725.1 | 3947 | 647 | 1752 | 783 | 369 | 69 | 46 | 112 | 0.1 | 0 | 90.84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 198 | 0 | 0 | 290 | 0 | 0 | 377 | 342 |  | 0 | 450 | 120 | 80 | 15 | 0 | 0 | 0 | 37 | 0 | 70 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 205 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 16 | 31 | 19 | 27 | 0 | 120 | 0 | 325 | 310 | 197 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 24 | 21 | 118 | 133 | 95 | 22 | 0 | 87 | 73 | 25 | 41 | 163 | 150 | 63 | 80 | 0 | 97 | 19 | 0 | 10 | 325 | 14 | 11 | 0 | 0 | 0 | 0 | 86 | 0 | 70 | 0 | 50 | 0 | 0 | 234 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 |  | 815 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 100 | 0 | 0 | 0 | 25 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 205 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 429 | 0 | 0 | 0 | 67 | 70 | 0 | 0 | 100 | 0 |  | 6495 | 2818 | 9313 | 4194 | 815 | 2114 | 1524 | 369 | 69 | 110 | 118 | 0 | 0 | 90.83
19:30 | 37 | 204 | 0 | 0 | 281 | 0 | 0 | 340 | 323 |  | 0 | 450 | 150 | 100 | 15 | 0 | 0 | 0 | 32 | 0 | 91 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 204 | 0 | 149 | 0 |  | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 26 | 0 | 120 | 0 | 310 | 310 | 184 | 26 | 91 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 24 | 21 | 118 | 126 | 95 | 22 | 0 | 88 | 73 | 25 | 50 | 163 | 145 | 63 | 80 | 0 | 97 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 50 | 0 | 0 | 233 | 115 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 |  | 816 | 0 | 325 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 100 | 0 | 0 | 0 | 25 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 67 | 70 | 0 | 0 | 109 | 0 |  | 6553 | 2869 | 9422 | 4101 | 816 | 2070 | 1754 | 369 | 69 | 125 | 118 | 0 | 0 | 0
20:00 | 37 | 204 | 0 | 0 | 280 | 0 | 0 | 340 | 313 |  | 0 | 400 | 150 | 100 | 12 | 0 | 0 | 0 | 32 | 0 | 92 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 34 | 0 | 120 | 0 | 310 | 305 | 184 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 24 | 21 | 118 | 115 | 95 | 22 | 0 | 88 | 73 | 25 | 50 | 130 | 148 | 63 | 80 | 0 | 110 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 115 | 0 | 50 | 0 | 0 | 235 | 115 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 |  | 816 | 0 | 325 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 110 | 0 | 0 | 0 | 25 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 109 | 0 |  | 6442 | 2833 | 9275 | 4066 | 816 | 1962 | 1747 | 370 | 69 | 127 | 118 | 0 | 0 | 90.82
21:00 | 37 | 204 | 0 | 0 | 280 | 0 | 0 | 342 | 303 |  | 0 | 400 | 150 | 100 | 0 | 0 | 0 | 0 | 32 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 32 | 19 | 36 | 0 | 120 | 0 | 310 | 305 | 185 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 110 | 115 | 95 | 22 | 0 | 88 | 73 | 25 | 50 | 130 | 147 | 64 | 80 | 0 | 0 | 19 | 0 | 10 | 310 | 15 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 100 | 0 | 30 | 0 | 0 | 254 | 115 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 |  | 816 | 0 | 325 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 429 | 0 | 0 | 0 | 32 | 70 | 0 | 0 | 109 | 0 |  | 6224 | 2797 | 9021 | 3990 | 816 | 1995 | 1569 | 370 | 69 | 102 | 110 | 0 | 0 | 90.81
22:00 | 37 | 204 | 0 | 0 | 280 | 0 | 0 | 339 | 292 |  | 0 | 400 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 150 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 120 | 0 | 315 | 310 | 184 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 100 | 117 | 95 | 22 | 0 | 85 | 73 | 25 | 50 | 130 | 144 | 65 | 80 | 0 | 0 | 19 | 0 | 10 | 290 | 15 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 79 | 0 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 |  | 816 | 0 | 325 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 5829 | 2641 | 8470 | 3941 | 816 | 1931 | 1193 | 369 | 69 | 51 | 100 | 0 | 0 | 0
23:00 | 37 | 204 | 0 | 0 | 280 | 0 | 0 | 338 | 322 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 152 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 120 | 0 | 315 | 305 | 169 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 116 | 95 | 22 | 0 | 87 | 73 | 25 | 50 | 130 | 152 | 65 | 80 | 0 | 0 | 19 | 0 | 10 | 290 | 15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 234 | 48 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 |  | 579 | 0 | 330 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 |  | 5618 | 2223 | 7841 | 3944 | 579 | 1988 | 777 | 371 | 69 | 17 | 96 | 0 | 0 | 0
24:00 | 37 | 204 | 0 | 0 | 281 | 0 | 0 | 344 | 350 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 203 | 0 | 151 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 120 | 0 | 315 | 305 | 163 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 86 | 117 | 95 | 22 | 0 | 87 | 73 | 25 | 50 | 130 | 146 | 66 | 80 | 0 | 0 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 234 | 25 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 338 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 93 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 |  | 5491 | 1867 | 7358 | 3937 | 338 | 1976 | 576 | 373 | 69 | 3 | 86 | 0 | 0 | 0
KWH | 900000 | 3366400 | 0 | 0 | 6623764 | 0 | 0 | 8487930 | 7499000 |  | 0 | 8623500 | 3394298 | 584640 | 46920 | 0 | 0 | 0 | 369000 | 0 | 813120 | 1079280 | 0 | 0 | 0 | 0 | 0 | 835560 | 106020 | 0 | 315684 | 600000 | 621540 | 692600 | 630800 | 1956 | 0 | 624900 | 972000 | 0 | 2900000 | 0 | 5102077 | 0 | 2662020 | 0 |  | 0 | 0 | 0 | 0 | 58560 | 198720 | 288432 | 520800 | 0 | 2404485 | 0 | 7469300 | 7340500 | 4488000 | 485090 | 2167910 | 840600 | 135360 | 0 | 801916 | 0 | 0 | 0 | 372852 | 167220 | 518500 | 521330 | 2090880 | 3119280 | 1217280 | 442188 | 12550 | 1848000 | 1679160 | 483600 | 840528 | 3451254 | 3345000 | 1069920 | 1294080 | 0 | 198620 | 139000 | 0 | 162720 | 7522950 | 285648 | 156360 | 0 | 0 | 0 | 0 | 664800 | 0 | 748800 | 123065 | 164160 | 0 | 0 | 5632000 | 1801200 | 0 | 0 | 29760 | 1693636 | 0 | 0 | 0 | 0 |  | 12117090 | 0 | 7920000 | 0 | 523200 | 0 | 0 | 0 | 0 | 0 | 24375 | 645000 | 342300 | 516480 | 0 | 0 | 0 | 41360 | 0 | 747276 | 0 | 0 | 0 | 0 | 0 | 294000 | 187776 | 230130 | 2137745 | 0 | 6407800 | 0 | 0 | 4332818 | 0 | 0 | 0 | 1517005 | 0 | 0 | 0 | 9538727 | 0 | 0 | 0 | 185184 | 246720 | 0 | 18798 | 1480800 | 0 |  | 126849023 | 49454584 | 176303607 | 90894068 | 12117090 | 43700606 | 16385709 | 8545545 | 1596900 | 788636 | 2090880 | 184173 | 0
Fuel Cost | 1008000 | 3635712 | 0 | 0 | 4901585.36 | 0 | 0 | 6111309.6 | 5699240 |  | 0 | 6898800 | 3054868.2 | 5963328 | 508143.6 | 0 | 0 | 0 | 461250 | 0 | 9025632 | 10965484.8 | 0 | 0 | 0 | 0 | 0 | 8013020.4 | 1011430.8 | 0 | 236763 | 450000 | 0 | 0 | 0 | 18738.48 | 0 | 162474 | 252720 | 0 | 4437000 | 0 | 5357180.85 | 0 | 3380765.4 | 0 |  | 0 | 0 | 0 | 0 | 556905.6 | 1860019.2 | 265357.44 | 1447824 | 0 | 2524709.25 | 0 | 5527282 | 6166020 | 4128960 | 475388.2 | 2883320.3 | 689292 | 139420.8 | 0 | 1146739.88 | 0 | 0 | 0 | 380309.04 | 125415 | 979965 | 390997.5 | 14427072 | 2557809.6 | 11576332.8 | 451031.76 | 205820 | 2513280 | 2283657.6 | 657696 | 1050660 | 4279554.96 | 3077400 | 1594180.8 | 2277580.8 | 0 | 301902.4 | 221010 | 0 | 382392 | 5341294.5 | 214236 | 118833.6 | 0 | 0 | 0 | 0 | 6395376 | 0 | 7555392 | 1420170.1 | 1529971.2 | 0 | 0 | 5294080 | 15796524 | 0 | 0 | 0 | 15615323.92 | 0 | 0 | 0 | 0 |  | 32716143 | 0 | 6177600 | 0 | 5043648 | 0 | 0 | 0 | 0 | 0 | 241068.75 | 516000 | 530565 | 5546995.2 | 0 | 0 | 0 | 460750.4 | 0 | 7398032.4 | 0 | 0 | 0 | 0 | 0 | 323400 | 309830.4 | 174208.41 | 13617435.65 | 0 | 26207902 | 0 | 0 | 3812879.84 | 0 | 0 | 0 | 2412037.95 | 0 | 0 | 0 | 6963270.71 | 0 | 0 | 0 | 1649989.44 | 2304364.8 | 0 | 0 | 0 | 0 |  | 218379953.74 | 116406121.95 | 334786075.69 | 83349303.75 | 32716143 | 40335695.2 | 114232557.19 | 39825337.65 | 415194 | 7858782.8 | 14427072 | 1625990.1 | 0
Yesterday Day Peak | 37 | 134 | 0 | 0 | 304 | 0 | 0 | 367 | 354 |  | 0 | 380 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 50 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 0 | 32 | 25 | 16 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 207 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 3 | 0 | 100 | 0 | 275 | 325 | 197 | 26 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 17 | 84 | 132 | 50 | 22 | 2.1 | 85 | 73 | 28 | 51 | 163 | 155 | 31 | 78 | 0 | 0 | 0 | 0 | 10 | 325 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 18.5 | 10 | 0 | 0 | 235 | 115 | 0 | 0 | 4.5 | 102 | 0 | 0 | 0 | 0 |  | 565 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 216 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 109 | 0 |  | 7865.6 | DayPeak
Yesterday Evening Peak | 37 | 204 | 0 | 0 | 281 | 0 | 0 | 340 | 323 | 0 | 0 | 450 | 150 | 100 | 15 | 0 | 0 | 0 | 32 | 0 | 91 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 32 | 25 | 33 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 204 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 19 | 26 | 0 | 120 | 0 | 310 | 310 | 184 | 26 | 91 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 24 | 21 | 118 | 126 | 95 | 22 | 0 | 88 | 73 | 25 | 50 | 163 | 145 | 63 | 80 | 0 | 97 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 50 | 0 | 0 | 233 | 115 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 |  | 816 | 0 | 325 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 20 | 100 | 0 | 0 | 0 | 25 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 67 | 70 | 0 | 0 | 109 | 0 |  | 9422 | EvPeak
Forecast for Evening | 37 | 170 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 40 | 0 | 100 | 102 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 30 | 40 | 0 | 120 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 100 | 0 | 360 | 360 | 225 | 46 | 90 | 45 | 20 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 115 | 140 | 95 | 22 | 0 | 88 | 73 | 51 | 50 | 163 | 150 | 66 | 80 | 0 | 0 | 17 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 838 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 0 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 40 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 90 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 37 | 170 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 40 | 0 | 100 | 100 | 149 | 100 | 71 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 30 | 40 | 0 | 100 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 46 | 90 | 45 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 87 | 140 | 95 | 22 | 1.6 | 88 | 73 | 51 | 50 | 163 | 150 | 66 | 80 | 0 | 0 | 17 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 590 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 0 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 40 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 90 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 95 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 37 | 169 | 0 | 0 | 280 | 0 | 0 | 350 | 323 | 0 | 0 | 340 | 120 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 58 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 32 | 25 | 25 | 0 | 0 | 29 | 40 | 0 | 120 | 0 | 53 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 19 | 10 | 0 | 100 | 0 | 325 | 320 | 172 | 8 | 90 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 80 | 139 | 50 | 22 | 0.2 | 86 | 73 | 25 | 50 | 130 | 148 | 56 | 80 | 0 | 0 | 0 | 0 | 10 | 310 | 22 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 51 | 5.18 | 30 | 0 | 0 | 234 | 105 | 0 | 5 | 1.4 | 206 | 0 | 0 | 0 | 0 | 0 | 583 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 90 | 0 | 270 | 0 | 0 | 150 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 8 | 0 | 1.4 | 85 | 0 | 0
199
| Minimum Generation |  | 5326 | 5:00
| Highest Generation |  | 9422 | 19:30
| Day Peak Generation |  | 7865.6 | 12:00
| Evening Peak Generation |  | 9422 | 19:30
| HVDC Max Flow |  | 816 | 19:30
| HVDC EvPeak Flow |  | 816 | 19:30
| Load factor L.F |  | 77.97%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7865.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6054 | MW
Evening Peak Generation : |  | 9422 | MW Hour : | 19:30 | Available Max Generation : |  | 14463 | MW
E.P. Demand (at gen end) : |  | 9422 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9600 | MW
Maximum Generation : |  | 9422 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4863 | MW
Total Gen. (MKWH) : |  | 176.3036 | System Load Factor : | 77.97% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -418 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-23
Actual : | 90.75 | Ft.(MSL) , | Rule curve : | 93.9 | Ft.( MSL )
Gas Consumed : | Total = | 1118.38 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 123684998.95
: |  | Coal : | 39825337.65 | Oil : | 122091339.99 | Total : | 285601676.59
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3373.935 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1143.163 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1023.4947 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 924.5505 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 835.6481 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 674.3279 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 382.4063 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 173.763 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 520.0495 |  |  | 0 | 0%
Total | 0 |  | 9051.338 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Bhola 225 MW
|  |  |  | 2) Meghnaghat GT-2 | 11) Chattrogram TPP-1
3) Ghorasal Unit-4&5
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Khulna(s) 230/132 kV T02 transformer was under shut down from 10:11 to 10:57 for C/M.
b) Shympur-Hasnabad 230 kV Ckt was under shut down from 11:38 to 17:14 for C/M.
c) Cumilla(N)-Shahjibazar 230 kV Ckt-1 was under shut down from 09:05 to 16:31 for A/M.
d) Siddhirganj (PP) GT-1 was synchronized at 12:14 and was shut down at 21:13 for gas shortage.
e) Bhola-Barishal(N) 230 kV Ckt-2 tripped at 10:18 from Bhola end and was switched on at
12:09(23/02/2020).
f) Bhola CCPP forced shut down at 10:30 for axiliary fail.
g) Barapukuria 132/33 kV T-5 transformer tripped at 13:08 due to 33 kV Cable burst showing E/F,O/C,
INST. relay and was switched on at 13:58.
h) Shahzadpur 132/33 kV T-3 transformer was under shut down from 10:05 to 13:37 for C/M.
i) Bhandaria 132/33 kV T-1 transformer tripped at 11:55 showing PRD and was switched on at 13:11.
j) B.Baria-Shahjibazar 132 kV Ckt-2 was under shut down from 13:33 to 14:18 for emergency tree trimming.
k) Sylhet 150 MW tripped at 20:01 due to generator protection.
k) Rangpur 132 kV Bus-2 was shut down at 06:50(23/02/2020) for D/W.
l) Barishal(N)-Madaripur 132 kV Ckt was under shut down from 07:26(23/02/2020) to 09:16 for C/M at
Madaripur end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 900000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 204 | 3366400
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 281 | 6623764 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8487930 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 7499000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8623500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 584640
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3394298 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 46920 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 315684
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 32 | 369000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 813120
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1079280
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 835560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 106020 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1221540 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 692600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 630800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 1956 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 100 | 748800 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2447 | 46340812
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123065
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 198720
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 69 | 1596900 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 5102077 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 149 | 2662020 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 164160 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 288432
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 520800
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 58560 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29760
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 228 | 1693636 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 945 | 15338130
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2404485
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4488000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7469300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7340500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 840600
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 135360 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 485090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 801916 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2167910
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 372852
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167220
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2090880
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 518500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 521330
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1331 | 29803943
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3119280 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 442188
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1217280
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 664800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1801200
| Mymensingh Area Total |  |  |  | 637 | 458 | 7257298
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 1848000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 73 | 1679160
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3451254
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 145 | 3345000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 483600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 840528
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 156360
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1069920 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1294080 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 97 | 198620
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 139000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 15 | 285648
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7522950 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 233 | 5632000
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 162720
| Sylhet Area Total |  |  |  | 1949 | 1372 | 28108840
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 816 | 12117090
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 70 | 523200 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 325 | 7920000 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 24375 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 67 | 185184 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1302 | 20769849
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 100 | 516480 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 342300 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 645000 | GT-1 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 1517005
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 218 | 3020785
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 41360 | Low demand
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4332818 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 422 | 9538727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 294000 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 187776
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 230130
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 747276
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1480800
| Rajshahi Area Total |  |  |  | 2183 | 910 | 16852887
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 89 | 2137745
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6407800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 246720 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 18798
| Rangpur Area Total |  |  |  | 605 | 439 | 8811063
| Total |  |  |  | 19107 | 9422 | 176303607
| Eastern Grid Total |  |  |  | 13543 | 6553 | 126849023
| Western Grid Total |  |  |  | 5564 | 2869 | 49454584
| National Grid Total |  |  |  | 19107 | 9422 | 176303607
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-22
(a) ENTIRE EASTERN GRID : |  | 5973 | MW | (b) ENTIRE WESTERN GRID : |  | 2897 | MW
i) Dhaka area |  | 3192 | MW | i) Khulna area |  | 1072 | MW
ii) Chittagong area |  | 914 | MW | ii) Rajshahi area |  | 962 | MW
iii) Comilla area |  | 763 | MW | iii) Barisal area |  | 234 | MW
iv) Mymensingh area |  | 758 | MW | iv) Rangpur area |  | 629 | MW
v) Sylhet area |  | 346 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8870 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 15:00 | Srimongal | 24 | 18:30 | Jhenida | 84 | 19:00
Munsiganj | 78 | 19:30 | Shahjibazar | 83 | 19:30 | Bottail | 102 | 18:30
Sonargaon | 66 | 10:00 | Fenchuganj | 26 | 18:30 | G.K Project | 39 | 19:30
Shyampur | 180 | 0:00 | Kulawara | 28 | 19:30 | Faridpur | 128 | 19:00
Bhulta | 163 | 21:00 | Sylhet | 109 | 19:30 | Madaripur | 61 | 18:00
Madanganj | 53 | 19:00 | Chatak | 18 | 18:30 | Sariatpur | 38 | 19:00
Shitalakhya | 98 | 11:00 | Sunamganj | 27 | 20:00 | Gopalganj | 68 | 19:00
Rahim steel | 18 | 19:00 | Biani Bazar | 33 | 18:30 | Bagerhat | 66 | 19:00
Matuail | 82 | 10:00 | Comilla (S) | 120 | 18:30 | Mongla | 30 | 1:00
Ghorasal | 62 | 19:00 | Comilla(N) | 80 | 20:00 | Satkhira | 70 | 19:30
Narsingdi | 119 | 20:00 | Chandpur | 67 | 18:30 | Gallamari | 39 | 13:00
Haripur (SBU) | 86 | 17:00 | Feni | 93 | 19:30 | Magura | 38 | 19:30
Ullon | 54 | 19:00 | Chowmuhani | 112 | 19:00 | Norail | 37 | 19:00
Hasnabad | 144 | 19:00 | Ashuganj | 40 | 13:00 | Chuadanga | 62 | 18:30
Magbazar | 76 | 19:00 | Daudkandi | 102 | 20:00 | Barisal(N) | 31 | 20:00
Maniknagar | 74 | 19:00 | B.Baria | 94 | 19:00 | Barisal (S) | 74 | 18:30
Bangabhaban | 16 | 19:00 | Ramganj | 58 | 19:30 | Patuakhali | 75 | 21:00
Narinda | 84 | 13:00 | Chaddagram | 24 | 9:00 | Bhandaria | 40 | 20:00
Dhanmondi | 92 | 18:00 | PHP | 2 | 12:00 | Borhan Uddin | 26 | 21:00
Lalbag | 64 | 13:00 | Madunaghat | 41 | 18:30 | Ishurdi | 47 | 19:00
Madartek | 50 | 19:00 | Hathazari | 69 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Dhaka University |  |  | Khulshi | 138 | 13:00 | Natore | 94 | 19:00
Mirpur | 76 | 19:00 | Halishahar | 99 | 18:30 | Bogra | 129 | 19:00
Kalyanpur | 63 | 19:00 | Baraulia | 135 | 16:00 | Noagaon | 93 | 8:00
Gulshan | 92 | 18:30 | Sikalbaha | 16 | 18:00 | Rajshahi | 96 | 19:30
Uttara | 49 | 14:00 | Dohazari | 68 | 18:30 | Rajshahi New | 8 | 18:30
Uttara New | 35 | 18:30 | Cox'sbazar | 80 | 19:30 | C.Nawabganj | 64 | 9:00
Kamrangirchar | 83 | 19:00 | Chandraghona | 32 | 19:00 | Amnura | 28 | 18:00
Savar | 96 | 16:00 | Kaptai | 3.6 | 18:00 | Pabna | 93 | 20:00
Bhasantec | 110 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 68 | 9:00
Agargaon | 36 | 18:30 | Bakulia | 75 | 19:00 | Serajganj | 70 | 20:00
Satmosjid | 79 | 14:00 | Julda | 20 | 10:00 | Niyamatpur | 72 | 9:00
Tongi | 98 | 15:00 | TK chemical | 12.2 | 18:30 | Joypurhat | 53 | 9:00
Kabirpur | 176 | 18:00 | Modern Steel | 16 | 10:00 | Sherpur(Bogura) | 38 | 8:00
Basundhara | 89 | 18:00 | Shahmirpur | 23 | 18:00 | Mohastangor | 36 | 18:30
Manikganj | 56 | 18:30 | Khagrachhari | 20 | 18:30 | Rangpur | 113 | 19:00
Joydevpur | 152 | 19:00 | Matarbari | 23.5 | 19:00 | Lalmonirhat | 43 | 19:00
New Tongi | 87 | 18:30 | Baroiar Hat | 16 | 18:30 | Saidpur | 87 | 18:30
Korda | 188 | 20:00 | Rangamati | 6 | 7:00 | Purbasadipur | 90 | 19:00
Dhamrai | 56 | 19:30 | Abul Khair 230 | 118 | 2:00 | Thakurgaon | 68 | 19:00
Valuka | 78 | 12:00 | BSRM | 104 | 23:00 | Palashbari | 93 | 19:00
Tangail | 143 | 9:00 | GPH Ispat | 57 | 15:00 | Barapukuria | 47 | 8:00
Mymensing | 178 | 18:30 | Goalpara | 16 | 19:30 | Panchagar | 36 | 19:00
Kishorganj | 90 | 19:00 | Central s/s | 60 | 18:30 | Joldhaka | 30 | 19:00
Netrokona | 103 | 18:30 | Noapara | 44 | 19:30 | Kurigram | 43 | 0.77083
Jamalpur | 104 | 8:00 | Jessore | 94 | 18:30
Sherpur | 88 | 7:00 | Benapol | 32 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-22 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 404 | 0.083333 | 397 | 0.58333 | Kaliakoir | 390 | 0.041667 | 277 | 0.625
Bheramara | 409 | 0.125 | 396 | 0.8125 | Bhulta | 399 | 24:00 | 385 | 0.45833
Ashuganj(N) | 402 | 0.16667 | 392 | 0.5 | Gopalganj | 429 | 0.16667 | 398 | 0.5
Payra | 431 | 0.16667 | 393 | 0.77083
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 232 | 0.625 | Hathazari | 228 | 0.125 | 219 | 0.625
Ishurdi | 240 | 0.125 | 226 | 0.29167 | Megnaghat | 240 | 0.25 | 231 | 0.45833
Ashuganj | 242 | 0.125 | 237 | 0.5 | Fenchuganj | 243 | 0.041667 | 239 | 0.5
Serajganj | 233 | 0.041667 | 227 | 0.33333 | Siddhirganj | 236 | 0.083333 | 228 | 0.45833
Baghabari | 238 | 0.083333 | 230 | 0.29167 | Maniknagar | 235 | 0.16667 | 227 | 0.45833
Barapukuria | 238 | 0.041667 | 229 | 0.33333 | Old Airport | 235 | 0.16667 | 225 | 0.45833
Bogra | 227 | 0.041667 | 217 | 0.33333 | Barisal | 251 | 0.66667 | 238 | 0.5
Khulna South | 236 | 0.16667 | 216 | 0.29167 | AKSML | 224 | 0.125 | 217 | 0.54167
Rampura | 232 | 0.041667 | 228 | 0.45833 | BSRM | 229 | 0.20833 | 220 | 0.625
Haripur | 233 | 0.041667 | 229 | 0.45833 | Bibiyana | 241 | 0.16667 | 236 | 0.41667
Hasnabad | 232 | 0.041667 | 228 | 0.875 | Bhulta | 236 | 0.083333 | 228 | 0.45833
Shyampur | 233 | 0.125 | 224 | 0.45833 | Ashuganj (S) | 235 | 0.25 | 228 | 0.95833
Aminbazar | 236 | 0.083333 | 226 | 0.5 | Kaliakoir | 238 | 0.083333 | 228 | 0.5
Tongi | 231 | 0.041667 | 225 | 0.375 | GPH | 224 | 0.083333 | 216 | 0.625
Comilla (N) | 241 | 0.083333 | 234 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.083333 | 130 | 0.66667 | Khulshi | 131 | 0.041667 | 127 | 0.375
Munsiganj | 135 | 0.33333 | 130 | 0.66667 | Halishahar | 134 | 0.20833 | 127 | 0.41667
Sonargaon | 133 | 0.041667 | 130 | 0.45833 | Baraulia | 133 | 0.29167 | 129 | 0.41667
Shyampur | 136 | 0.20833 | 130 | 0.45833 | Sikalbaha | 132 | 0.041667 | 129 | 0.45833
Bhulta | 130 | 0.041667 | 124 | 0.45833 | Dohazari | 131 | 0.041667 | 127 | 0.77083
Madanganj | 133 | 0.125 | 127 | 0 | Cox'sbazar | 132 | 0.33333 | 119 | 0.77083
Shitalakhya | 136 | 0.041667 | 128 | 0.45833 | Chandraghona | 134 | 0.083333 | 131 | 0.41667
Rahim steal | 135 | 1:00 | 131 | 0.45833 | Kaptai | 133 | 0.041667 | 132 | 0.29167
Matuail | 135 | 0.16667 | 129 | 0.66667 | A. Khaer Stl. | 132 | 0.041667 | 130 | 0.29167
Ghorasal | 140 | 0.041667 | 138 | 0.625 | Bakulia | 132 | 0.25 | 127 | 0.58333
Narsinghdi | 132 | 0.16667 | 128 | 0.83333 | Julda | 132 | 0.16667 | 128 | 0.41667
Haripur (SBU) | 135 | 0.16667 | 131 | 0.45833 | TK Chemical | 133 | 0.16667 | 129 | 0.375
Ullon | 130 | 0.20833 | 124 | 0.375 | Modern Steel | 133 | 0.20833 | 128 | 0.33333
Hasnabad | 135 | 0.25 | 129 | 0.5 | Shahmirpur | 132 | 0.083333 | 128 | 0.625
Magbazar | 130 | 0.25 | 124 | 0.41667 | Khagrachhari | 133 | 0.041667 | 130 | 0.54167
Maniknagar | 137 | 0.25 | 132 | 0.5 | Matarbari | 130 | 0.125 | 121 | 0.77083
Bangabhaban | 137 | 0.25 | 132 | 0.5 | Baroiar Hat | 133 | 0.041667 | 130 | 0.77083
Narinda | 137 | 0.25 | 132 | 0.5 | Rangamati | 134 | 0.16667 | 130 | 15:00
Dhanmondi | 130 | 0.20833 | 124 | 0.375 | Goalpara | 136 | 0.125 | 124 | 18:30
Lalbag | 136 | 0.25 | 127 | 0.5 | Central s/s | 134 | 0.91667 | 123 | 0.29167
Madartek | 130 | 0.25 | 122 | 0.45833 | Noapara | 133 | 0.041667 | 122 | 0.79167
Dhaka University |  |  |  |  | Jessore | 132 | 0.041667 | 118 | 0.77083
Mirpur | 136 | 0.083333 | 129 | 0.5 | Benapol | 132 | 0.041667 | 119 | 0.79167
Kalyanpur | 136 | 0.083333 | 128 | 0.66667 | Jhenida | 136 | 0.125 | 117 | 0.79167
Gulshan | 130 | 0.125 | 123 | 0.41667 | Bottail | 136 | 0.125 | 125 | 0.77083
Uttara | 136 | 0.20833 | 129 | 0.45833 | G.K Project | 139 | 0.125 | 133 | 0.29167
Uttara New | 135 | 0.083333 | 125 | 0.5 | Faridpur | 137 | 0.125 | 126 | 0.77083
Kamrangirchar | 135 | 0.16667 | 125 | 0.45833 | Madaripur | 138 | 0.16667 | 127 | 0.75
Savar | 135 | 0.125 | 128 | 0.5 | Sariatpur | 142 | 0.041667 | 131 | 0.54167
Bhasantec | 136 | 0.20833 | 128 | 0.45833 | Gopalganj | 144 | 0.125 | 133 | 0.77083
Agargaon | 136 | 0.083333 | 129 | 0.5 | Bagerhat | 134 | 0.125 | 125 | 0.5
Satmosjid | 136 | 0.083333 | 129 | 0.45833 | Mongla | 132 | 0.083333 | 120 | 0.77083
Tongi | 139 | 0.041667 | 133 | 0.45833 | Satkhira | 132 | 0.041667 | 121 | 0.77083
Kabirpur | 134 | 24:00 | 135 | 0.5 | Gallamari | 134 | 0.16667 | 125 | 0.77083
Basundhara | 130 | 22:00 | 123 | 0.41667 | Magura | 133 | 0.083333 | 115 | 0.79167
Manikganj | 139 | 0.041667 | 134 | 0.79167 | Norail | 130 | 0.041667 | 115 | 0.77083
Joydevpur | 141 | 0.70833 | 137 | 0.66667 | Chuadanga | 129 | 0.125 | 111 | 0.77083
New Tongi | 138 | 0.041667 | 132 | 0.66667 | Barisal(N) | 141 | 0.125 | 133 | 0.5
Kodda | 134 | 0.29167 | 126 | 0.66667 | Barisal (S) | 140 | 0.54167 | 131 | 0.5
Dhamrai | 134 | 0.041667 | 126 | 0.5 | Patuakhali | 136 | 0.875 | 126 | 0.77083
Valuka | 124 | 0.41667 | 115 | 0.29167 | Bhandaria | 137 | 0.70833 | 128 | 0.77083
Tangail | 133 | 0.041667 | 120 | 0.5 | Ishurdi | 137 | 0.125 | 130 | 0.29167
Mymensing | 127 | 0.41667 | 116 | 0.041667 | Ruppur Paromanobik | 135 | 0.041667 | 129 | 0.29167
Kishorganj | 130 | 0.45833 | 125 | 0.041667 | Natore | 134 | 0.041667 | 125 | 0.29167
Netrokona | 125 | 0.41667 | 114 | 0.29167 | Bogra | 136 | 0.125 | 127 | 0.33333
Jamalpur | 137 | 0.875 | 117 | 0.041667 | Noagaon | 131 | 0.041667 | 118 | 0.33333
Sherpur | 134 | 0.8125 | 116 | 0.041667 | Rajshahi | 132 | 0.125 | 120 | 0.33333
Srimongal | 139 | 0.29167 | 137 | 0.125 | Rajshahi New | 132 | 0.125 | 119 | 0.33333
Shahjibazar | 133 | 0.79167 | 137 | 0.16667 | C.Nawabganj | 127 | 0.125 | 115 | 0.33333
Fenchuganj | 138 | 0.33333 | 136 | 12:00 | Amnura | 128 | 0.25 | 117 | 0.33333
Khulawara | 137 | 0.041667 | 134 | 0.70833 | Pabna | 135 | 0.083333 | 125 | 0.58333
Sylhet | 135 | 0.29167 | 132 | 0.66667 | Shahjadpur | 142 | 0.041667 | 133 | 0.375
Chatak | 135 | 0.16667 | 130 | 0.66667 | Serajganj | 137 | 0.125 | 128 | 0.33333
Sunamganj | 135 | 0.20833 | 130 | 0.5 | Niyamatpur | 130 | 0.083333 | 117 | 0.33333
Biani Bazar | 135 | 0.083333 | 132 | 0.66667 | Joypurhat | 131 | 0.083333 | 116 | 0.375
Comilla(s) | 133 | 0.041667 | 126 | 0.77083 | Sherpur(Bogura) | 138 | 0.125 | 128 | 0.29167
Comilla(n) | 141 | 11:00 | 137 | 0.66667 | Mohastangor | 136 | 0.083333 | 126 | 0.33333
Chandpur | 137 | 0.33333 | 132 | 0.79167 | Rangpur | 134 | 0.125 | 123 | 0.33333
Feni | 136 | 0.29167 | 132 | 0.875 | Lalmonirhat | 130 | 0.20833 | 115 | 0.375
Chowmuhani | 132 | 0.33333 | 127 | 0.625 | Saidpur | 133 | 0.20833 | 121 | 0.33333
Ashuganj | 136 | 0.5 | 135 | 0.75 | Purbasadipur | 132 | 0.083333 | 116 | 0.375
Daudkandi | 136 | 0.29167 | 131 | 0.45833 | Thakurgaon | 127 | 0.041667 | 116 | 0.375
B.Baria | 133 | 0.375 | 131 | 0.83333 | Palashbari | 128 | 0.041667 | 117 | 0.33333
Ramganj | 130 | 0.91667 | 128 | 0.77083 | Barapukuria | 138 | 0.041667 | 129 | 0.33333
Chaddagram | 137 | 0.29167 | 133 |  | Panchagar | 127 | 0.16667 | 111 | 0.375
PHP |  |  |  |  | Joldhaka | 132 | 0.083333 | 117 | 0.33333
Madanhat | 134 | 0.083333 | 131 | 0.625 | Kurigram | 132 | 0.16667 | 119 | 0.33333
Hathazari | 136 | 0.125 | 131 | 0.45833

## L-Curve
Date | 2020-02-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 369 | 5491 | 1867 | 7358 |  |  |  | QF-LDC-12
0:30 | 340.5 | 4894.5 | 1732 | 6626.5 | Date: | 2020-02-22
1:00 | 312 | 4298 | 1597 | 5895
1:30 | 290 | 4190.5 | 1569.5 | 5760
2:00 | 268 | 4083 | 1542 | 5625
2:30 | 294 | 4055.5 | 1472 | 5527.5 | [5 empty] | Gen. at Eve. Peak | 9422 | 9422 MW (19:30 )
3:00 | 320 | 4028 | 1402 | 5430 | [6 empty] | 19:30
3:30 | 346 | 4005.5 | 1388 | 5393.5 | [5 empty] | Gen. at Day Peak | 7865.6 | 7865.6 MW (12:00 )
4:00 | 372 | 3983 | 1374 | 5357 | [6 empty] | 12:00
4:30 | 395 | 3995.5 | 1346 | 5341.5 | [5 empty] | Highest Generation | 9422
5:00 | 418 | 4008 | 1318 | 5326 | [6 empty] | 19:30
5:30 | 395 | 4142.5 | 1376 | 5518.5
6:00 | 372 | 4277 | 1434 | 5711
6:30 | 360 | 4387.9 | 1669.05 | 6056.95
7:00 | 348 | 4498.8 | 1904.1 | 6402.9
7:30 | 363.5 | 4756.3 | 1961.35 | 6717.65
8:00 | 379 | 5013.8 | 2018.6 | 7032.4
8:30 | 327.5 | 5112.1 | 2083.15 | 7195.25
9:00 | 276 | 5210.4 | 2147.7 | 7358.1
9:30 | 218.5 | 5208.925 | 2136.5 | 7345.425
10:00 | 161 | 5207.45 | 2125.3 | 7332.75
10:30 | 131.5 | 5289.725 | 2131.15 | 7420.875
11:00 | 102 | 5372 | 2137 | 7509
11:30 | 143.5 | 5526.55 | 2160.75 | 7687.3
12:00 | 185 | 5681.1 | 2184.5 | 7865.6
12:30 | 167.5 | 5734.6 | 2184.8 | 7919.4
13:00 | 150 | 5788.1 | 2185.1 | 7973.2
13:30 | 157.5 | 5603.96 | 2115.15 | 7719.11
14:00 | 165 | 5419.82 | 2045.2 | 7465.02
14:30 | 91 | 5417.71 | 2060.1 | 7477.81
15:00 | 17 | 5415.6 | 2075 | 7490.6
15:30 | 38 | 5330.4 | 2054.15 | 7384.55
16:00 | 59 | 5245.2 | 2033.3 | 7278.5
16:30 | 60 | 5176.55 | 2034.95 | 7211.5
17:00 | 61 | 5107.9 | 2036.6 | 7144.5
17:30 | 53 | 5304.95 | 2129.85 | 7434.8
18:00 | 45 | 5502 | 2223.1 | 7725.1
18:30 | 152.5 | 5998.5 | 2520.55 | 8519.05
19:00 | 260 | 6495 | 2818 | 9313
19:30 | 238 | 6553 | 2869 | 9422
20:00 | 197 | 6442 | 2833 | 9275 |  |  |  | Executive Engineer
20:30 | 169.5 | 6333 | 2815 | 9148 |  |  |  | Network Operation Division
21:00 | 142 | 6224 | 2797 | 9021
21:30 | 102.5 | 6026.5 | 2719 | 8745.5
22:00 | 63 | 5829 | 2641 | 8470 |  |  |  |  | Page 6 of 7
22:30 | 122 | 5723.5 | 2432 | 8155.5
23:00 | 181 | 5618 | 2223 | 7841
23:30 | 275 | 5554.5 | 2045 | 7599.5
24:00 | 369 | 5491 | 1867 | 7358
9422 MW (19:30 )
7865.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-22 |  | Energy | 176303607
[10 empty] | 2020-02-22 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3937 | 338 | 1976 | 777 | 373 | 69 | 3 | 0 | 86
0:30 | 3728.5 | 259 | 1763 | 452.5 | 371.5 | 69 | 1.5 | 0 | 82 | Date: | 2020-02-22
1:00 | 3520 | 180 | 1550 | 128 | 370 | 69 | 0 | 0 | 78
1:30 | 3438 | 180.5 | 1501 | 128 | 370 | 68.5 | 0 | 0 | 74 | [7 empty] | Total Energy | 176.3036 | Total Energy Gen 176.304 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.304 MKWHr
2:00 | 3356 | 181 | 1452 | 128 | 370 | 68 | 0 | 0 | 70 | [7 empty] | Energy not Served | 0
2:30 | 3298 | 181 | 1416 | 124 | 370.5 | 68 | 0 | 0 | 70 | [7 empty] | Energy Requirement | 176.3036
3:00 | 3240 | 181 | 1380 | 120 | 371 | 68 | 0 | 0 | 70
3:30 | 3222 | 181 | 1370 | 120 | 363.5 | 68 | 0 | 0 | 69 | [6 empty] | Shortage
4:00 | 3204 | 181 | 1360 | 120 | 356 | 68 | 0 | 0 | 68
4:30 | 3200 | 181 | 1375.5 | 120 | 328.5 | 68.5 | 0 | 0 | 68
5:00 | 3196 | 181 | 1391 | 120 | 301 | 69 | 0 | 0 | 68
5:30 | 3285 | 183.5 | 1482.5 | 126.5 | 301 | 69 | 0 | 0 | 71
6:00 | 3374 | 186 | 1574 | 133 | 301 | 69 | 0 | 0 | 74
6:30 | 3500.5 | 379.5 | 1572.5 | 158.5 | 301 | 69 | 0 | 0 | 75 |  |  |  |  | Coal
7:00 | 3627 | 573 | 1571 | 184 | 301 | 69 | 0 | 0 | 76
7:30 | 3654.5 | 573.5 | 1698 | 339 | 300.5 | 69 | 0 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 3682 | 574 | 1825 | 494 | 300 | 69 | 0 | 0 | 80
8:30 | 3730.5 | 574 | 1850.5 | 549.5 | 325 | 69 | 5 | 0 | 79
9:00 | 3779 | 574 | 1876 | 605 | 350 | 69 | 10 | 0 | 78
9:30 | 3757.5 | 569.5 | 1868.5 | 603.5 | 350.5 | 69 | 26 | 0 | 81
10:00 | 3736 | 565 | 1861 | 602 | 351 | 69 | 42 | 0 | 84
10:30 | 3758 | 565 | 1893 | 637.5 | 351 | 69 | 42 | 0 | 82
11:00 | 3780 | 565 | 1925 | 673 | 351 | 69 | 42 | 0 | 80
11:30 | 3813.5 | 565 | 1968.5 | 770 | 351 | 69 | 42 | 0 | 82
12:00 | 3847 | 565 | 2012 | 867 | 351 | 69 | 42 | 0 | 84
12:30 | 3861 | 565 | 2015 | 903.5 | 351 | 69 | 42 | 0 | 85
13:00 | 3875 | 565 | 2018 | 940 | 351 | 69 | 42 | 0 | 86
13:30 | 3875 | 565 | 2018 | 940 | 351 | 69 | 42 | 0 | 86
14:00 | 3875 | 565 | 2018 | 940 | 351 | 69 | 42 | 0 | 86
14:30 | 3854 | 568 | 1934 | 794 | 361 | 69 | 42 | 0 | 87
15:00 | 3833 | 571 | 1850 | 648 | 371 | 69 | 42 | 0 | 88
15:30 | 3783.5 | 571 | 1843 | 605 | 370.5 | 69 | 42 | 0 | 86
16:00 | 3734 | 571 | 1836 | 562 | 370 | 69 | 42 | 0 | 84
16:30 | 3757 | 571 | 1796.5 | 525.5 | 370 | 69 | 33.5 | 0 | 82
17:00 | 3780 | 571 | 1757 | 489 | 370 | 69 | 25 | 0 | 80
17:30 | 3863.5 | 609 | 1754.5 | 636 | 369.5 | 69 | 35.5 | 0 | 96
18:00 | 3947 | 647 | 1752 | 783 | 369 | 69 | 46 | 0 | 112
18:30 | 4070.5 | 731 | 1933 | 1153.5 | 369 | 69 | 78 | 0 | 115
19:00 | 4194 | 815 | 2114 | 1524 | 369 | 69 | 110 | 0 | 118
19:30 | 4101 | 816 | 2070 | 1754 | 369 | 69 | 125 | 0 | 118
20:00 | 4066 | 816 | 1962 | 1747 | 370 | 69 | 127 | 0 | 118
20:30 | 4028 | 816 | 1978.5 | 1658 | 370 | 69 | 114.5 | 0 | 114
21:00 | 3990 | 816 | 1995 | 1569 | 370 | 69 | 102 | 0 | 110
21:30 | 3965.5 | 816 | 1963 | 1381 | 369.5 | 69 | 76.5 | 0 | 105
22:00 | 3941 | 816 | 1931 | 1193 | 369 | 69 | 51 | 0 | 100
22:30 | 3942.5 | 697.5 | 1959.5 | 985 | 370 | 69 | 34 | 0 | 98
23:00 | 3944 | 579 | 1988 | 777 | 371 | 69 | 17 | 0 | 96
23:30 | 3940.5 | 458.5 | 1982 | 777 | 372 | 69 | 10 | 0 | 91 | Max Temp. in Dhaka |  | 31.7° C
24:00 | 3937 | 338 | 1976 | 777 | 373 | 69 | 3 | 0 | 86
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 176.304 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 176.304 MKWHr
Note on W13: Author:

## Generation
g | 2020-02-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 29 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 624900
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.4 | 6.1 | 11.5 | 15.15 | 17 | 18.5 | 17.7 | 15.12 | 11.7 | 6.9 | 2.2 | [9 empty] | 123065
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 202 | 203 | 203 | 203 | 202 | 216 | 201 | 211 | 203 | 210 | 207 | 206 | 203 | 205 | 206 | 204 | 217 |  | 205 | 204 | 203 | 203 | 203 | 203 | 203 | 5102077
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 110 | 104 | 140 | 140 | 139 | 141 | 139 | 146 | 145 |  | 147 | 149 | 139 | 150 | 150 | 152 | 151 | 2662020
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [12 empty] | 37 | 37 | 40 | 32 | 37 | 37 |  | 37 | 32 | 32 | 32 | 0 |  |  | 369000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 485090
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 900000
21 | Ghorasal Repowered CCPP Unit-3 | 99 | 100 | 100 | 100 | 100 | 99 | 99 | 99 | 99 | 99 | 118 | 134 | 133 | 134 | 134 | 134 | 134 | 134 |  | 198 | 204 | 204 | 204 | 204 | 204 | 204 | 3366400
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 220 | 220 | 219 | 220 | 220 | 218 | 308 | 285 | 301 | 289 | 296 | 304 | 283 | 281 | 287 | 282 | 283 | 315 |  | 290 | 281 | 280 | 280 | 280 | 280 | 281 | 6623764
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2404485
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 46 | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 42 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 840600
33 | Ashuganj 225 MW CCPP | 171 | 176 | 176 | 164 | 174 | 177 | 185 | 193 | 203 | 185 | 199 | 197 | 183 | 182 | 192 | 182 | 188 | 186 |  | 197 | 184 | 184 | 185 | 184 | 169 | 163 | 4488000
34 | Ashuganj 450 MW CCPP(South) | 270 | 265 | 270 | 260 | 260 | 275 | 320 | 320 | 335 | 315 | 335 | 325 | 305 | 290 | 300 | 285 | 290 | 320 |  | 310 | 310 | 305 | 305 | 310 | 305 | 305 | 7340500
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 275 | 275 | 330 | 350 | 280 | 285 | 290 | 265 | 275 | 295 | 295 | 305 | 295 | 295 | 340 |  | 325 | 310 | 310 | 310 | 315 | 315 | 315 | 7469300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 135360
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 2167910
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 340 | 343 | 340 | 338 | 350 | 346 | 349 | 357 | 354 | 361 | 367 | 357 | 341 | 348 | 343 | 348 | 356 |  | 377 | 340 | 340 | 342 | 339 | 338 | 344 | 8487930
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 350 | 380 | 380 | 380 | 350 | 350 | 350 | 350 | 350 |  | 450 | 450 | 400 | 400 | 400 | 400 | 400 | 8623500
41 | Haripur 360MW CCPP(HPL) | 313 | 314 | 263 | 265 | 264 | 364 | 364 | 313 | 314 | 313 | 313 | 354 | 355 | 308 | 308 | 307 | 307 | 289 |  | 342 | 323 | 313 | 303 | 292 | 322 | 350 | 7499000
42 | RPCL 210MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 138 | 136 | 134 | 132 | 132 | 132 | 130 | 130 | 131 | 133 |  | 133 | 126 | 115 | 115 | 117 | 116 | 117 | 3119280
43
44 | Fenchugonj CCPP Phase-1 | 85 | 58 | 57 | 57 | 57 | 57 | 57 | 58 | 86 | 86 | 87 | 85 | 85 | 86 | 82 | 81 | 83 | 86 |  | 87 | 88 | 88 | 88 | 85 | 87 | 87 | 1848000
45 | Fenchugonj CCPP Phase-2 | 73 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1679160
46 | Shajibazar 330 MW CCPP | 127 | 124 | 127 | 123 | 127 | 152 | 159 | 153 | 154 | 147 | 155 | 155 | 148 | 150 | 154 | 149 | 148 | 185 |  | 150 | 145 | 148 | 147 | 144 | 152 | 146 | 3345000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 25 | 25 | 25 | 35 | 33 | 32 | 32 | 31 | 51 | 45 | 45 | 45 | 45 | 45 |  | 63 | 63 | 63 | 64 | 65 | 65 | 66 | 1069920
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 80 | 78 | 78 | 78 | 78 | 80 | 78 | 80 | 76 | 10 | 10 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1294080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | [16 empty] | 0 | 48 |  | 97 | 97 | 110 | 0 |  |  |  | 198620
51 | Sylhet 20 MW GTPP | [16 empty] | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 139000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 9 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 162720
54 | Hobiganj 11MW PP Cofidence-E | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 156360
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 28 | 28 | 25 | 28 | 28 | 28 | 22 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 483600
56 | Shahjahanulla 25 MW PP | [7 empty] | 23 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 15 | 14 |  | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 285648
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 290 | 280 | 280 | 300 | 290 | 300 | 320 | 320 | 320 | 325 | 320 | 285 | 310 | 310 | 310 | 300 |  | 325 | 300 | 300 | 310 | 290 | 290 | 300 | 7522950
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | [7 empty] | 19 |  | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 288432
61 | Narshingdi 22 MW PP (Doreen) | [7 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 315684
62 | Tangail 22 MW PP (Doreen) | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 442188
63 | Impoprt (Tripura) | 78 | 70 | 70 | 68 | 68 | 74 | 76 | 80 | 78 | 84 | 80 | 84 | 86 | 86 | 88 | 84 | 80 | 112 |  | 118 | 118 | 118 | 110 | 100 | 96 | 86 | 2090880
64 | Malancha, Ctg. EPZ (United) | 10 | 8 | 8 | 10 | 13 | 15 | 15 | 17 | 8 | 5 | 3 | 3 | 9 | 4 | 2 | 2 | 10 | 19 |  | 27 | 26 | 34 | 36 | 38 | 38 | 38 | 520800
65 | Feni 22MW PP (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 372852
66 | Feni 11 MW PP (Doreen) | [7 empty] | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 167220
67 | Jangalia 33MW PP (Summit) | [7 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 |  | 24 | 24 | 24 | 25 | 25 | 33 | 33 | 518500
68 | Cumilla 25 MW PP (Summit) | 21 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 521330
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 32 | 32 | 32 | 30 | 30 | 9 | 9 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 621540
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 692600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 630800
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [20 empty] | 0 | [5 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 2 | 7 | 7 | 10 | 65 | 91 | 60 | 24 | 7 | 7 | 10 |  | 70 | 91 | 92 | 100 | 100 | 75 |  | 813120
78 | Gazipur 52 MW PP | [26 empty] | 1956
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 |  |  |  | 13 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1217280
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.4 | 2.8 | 3.8 | 4 | 4.5 | 4.3 | 3.7 | 2.7 | 1.5 | 0.5 | [9 empty] | 29760
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 0 | 13 |  | 15 | 15 | 12 |  |  |  |  | 46920
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 120 | 120 | 120 |  | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 3394298
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 3 | 7 | 7 | 9 | 40 | 50 | 25 | 16 | 16 | 16 | 27 |  | 80 | 100 | 100 | 100 | 40 |  |  | 584640
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 48 | 51 | 48 | 51 | 51 | 48 | 48 | 50 | 10 | 10 |  | 41 | 50 | 50 | 50 | 50 | 50 | 50 | 840528
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 801916
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 7 | 7 | 7 | 24 | 50 | 80 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 32 | 16 | 7 | 1079280
95 | Patenga 50MW PP (Baraka) | [10 empty] | 6 | 18 | 19 | 11 | 6 | 6 | 6 | 6 |  | 31 | 50 | 50 | 32 |  |  |  | 198720
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 16 | 30 | 30 |  |  |  |  | 58560
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | [6 empty] | 35 | 35 | 35 |  |  |  |  | 106020
101 | Kushiara 163 MW CCPP (KP) | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 |  | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 3451254
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.3 | 1.1 | 1.5 | 1 | 2.1 | 2.1 | 2 | 1.2 | 0.8 | 0.2 | [9 empty] | 12550
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 835560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 17 | 40 | 40 | 40 | 40 | 40 | 24 | 24 | 7 | 7 | 17 |  | 86 | 100 | 70 | 70 | 32 |  |  | 664800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 23 | 35 | 32 | 31 | 32 | 32 | 16 | 16 | 15 | 15 | 20 |  | 70 | 100 | 115 | 100 | 79 | 58 | 35 | 748800
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 10 | 10 | 10 |  |  |  |  | 10 |  | 50 | 50 | 50 | 30 |  |  |  | 164160
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 234 | 234 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 234 | 235 | 235 | 235 | 236 | 236 | 236 | 235 |  | 234 | 233 | 235 | 254 | 234 | 234 | 234 | 5632000
| Jamalpur 115 MW PP (United) | [6 empty] | 14 | 107 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 85 | 65 | 77 |  | 115 | 115 | 115 | 115 | 115 | 48 | 25 | 1801200
| Anwara 300 MW PP (United) | [7 empty] | 16 | 16 | 16 | 50 | 102 | 108 | 80 | 71 | 50 | 33 | 60 |  | 200 | 228 | 230 | 216 | 160 | 126 | 105 | 1693636
120 | Eastern Zone Total | 4298 | 4083 | 4028 | 3983 | 4008 | 4277 | 4498.8 | 5013.8 | 5210.4 | 5207.45 | 5372 | 5681.1 | 5788.1 | 5419.82 | 5415.6 | 5245.2 | 5107.9 | 5502 |  | 6495 | 6553 | 6442 | 6224 | 5829 | 5618 | 5491 | 126849023
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 49 |  | 49 | 70 | 85 | 85 | 83 | 2 |  | 523200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 64 |  | 100 | 100 | 110 | 110 | 110 | 64 | 16 | 516480
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 13 |  |  |  |  | 90 | 75 | 43 | 85 | 85 | 94 | 91 | 87 | 94 | 95 | 97 |  | 99 | 98 | 98 | 98 | 98 | 98 | 98 | 1517005
| Bhola 225 MW CCPP | 90 | 89 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | [15 empty] | 645000
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 15 | 14 | 14 | 14 | 14 | 13 | 12 | 11 | 11 | 12 | 12 | 10 | 11 | 11 | 12 | 16 |  | 20 | 20 | 21 | 21 | 20 | 18 | 18 | 342300
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 24 | 24 |  |  |  |  | 24375
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 67 | 67 | 50 | 32 |  |  |  | 185184
146 | Bheramara HVDC | 180 | 181 | 181 | 181 | 181 | 186 | 573 | 574 | 574 | 565 | 565 | 565 | 565 | 571 | 571 | 571 | 571 | 647 |  | 815 | 816 | 816 | 816 | 816 | 579 | 338 | 12117090
147 | Bheramara 410 MW CCPP | 385 | 330 | 230 | 230 | 230 | 280 | 350 | 325 | 340 | 310 | 325 | 325 | 325 | 325 | 350 | 325 | 325 | 280 |  | 345 | 325 | 325 | 325 | 325 | 330 | 330 | 7920000
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 90 | 90 | 91 | 91 | 91 | 91 | 90 | 91 | 90 | 90 | 89 |  | 89 | 89 | 90 | 90 | 89 | 91 | 93 | 2137745
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 279 | 280 | 280 | 265 | 210 | 210 | 210 | 210 | 260 | 260 | 260 | 260 | 260 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6407800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 8 |  | 25 | 25 | 25 |  |  |  |  | 41360
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 145 | 160 | 205 | 216 | 214 | 160 | 150 | 150 | 150 | 150 |  | 205 | 214 | 190 | 190 | 190 | 190 | 190 | 4332818
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 398 | 358 | 358 | 357 | 418 | 425 | 383 | 385 | 385 | 386 | 420 | 414 | 349 | 400 | 379 | 397 | 405 |  | 429 | 422 | 398 | 429 | 395 | 424 | 374 | 9538727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | [6 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 294000
163 | Bogura 20 MW PP (Energyprima) | [7 empty] | 8 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 187776
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 230130
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [8 empty] | 10 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 25 | 38 |  | 85 | 100 | 102 | 102 | 51 | 17 | 3 | 747276
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 50 | 109 | 109 | 109 | 109 | 109 | 70 | 35 | 35 | 35 | 45 |  | 100 | 109 | 109 | 109 | 109 | 90 | 90 | 1480800
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 70 | 70 | 70 | 70 | 35 |  |  | 246720
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.6 | 1.7 | 2.3 | 2 | 3.5 | 3.1 | 2.2 | 3 | 1.3 | 0.6 | 0.1 | [8 empty] | 18798
178
178