## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-02-27 | Thursday
|  | Date (day): | 2020-02-27 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11584.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14405 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-02-26 | 2020-02-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 45 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 155 | 165 | 178 | 178
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 290 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 387 | 360 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 324 | 355 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 15 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 45 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 35 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 8 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 34 | 90 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 41 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 32 | 133 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2024 | 2536 | 3547 | 4149 | 991 | 630
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 78 | 67 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under S/D for Project work
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 148 | 103 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 13 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 90 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 38 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 190 | 300 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 581.3 | 817 | 1275 | 1420 | 400 | 333
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 100 | 100 | 100 |  |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 151 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 305 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 46 | 46 | 46
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 26 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 38 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 108 | 104 | 115
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 8 | 21 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1221 | 1279 | 1649 | 2324 | 506 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 142 | 155 | 155 | 47 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 17 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 83 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 97 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 279.2 | 389 | 488.6 | 587 | 47 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 72 | 69 | 70 | 70
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 73 | 73 | 73
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 164 | 145 | 150 | 150 |  | 180 | GT-2 shut down.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 51 | 51 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 67 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 80 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 12 | 100 | 120
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 305 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 234 | 234 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1328 | 1316 | 1438 | 1458 | 0 | 345
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 589 | 833 | 495 | 842
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 365 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 33 | 33 |  | 7 | Engine problem
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 976 | 1313 | 1183 | 2081 | 0 | 7
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 19 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 70 | 88 | 90 | 90 |  | 104 | GT-1 under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 75 | 95 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 159 | 266 | 275 | 345 | 0 | 117
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 190 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 247 | 273 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 25 | 85 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 100 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 581 | 682 | 1228 | 1494 | 611 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 91 | 117 | 100 | 120
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 260 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 100 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 319.3 | 477 | 501 | 547 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7468.8 | 9075 | 11584.6 | 14405 | 2555 | 1610
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7142.0657 | 8678 | 11077.8136 | 13774.8309
A. |  | 2020-02-26 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9075 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5716 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9075 | MW
3 | Day peak Generation : |  |  | 7468.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8678 | MW
4 | Evening peak Generation : |  |  | 9075 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 174.5718 | MKWHr | By Solar | 0.1127 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.0123 | MKWHr |  | By Oil: | 18.4848 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.1877 | MKWHr |  | By Hydro: | 1.5917 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2555 | MW | Dhaka | 3180 | 3180 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1610 | MW | Chittagong | 877 | 877 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4165 | MW | Khulna | 1077 | 1077 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1083.58 | MMCFD |  |  | Rajshahi | 941 | 941 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 121672763.342 | ii) Oil : | Taka | 132036159.87 | Comilla | 704 | 704 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 38681923.98 | Total | Taka | 292390847.192 | Mymensingh | 712 | 712 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.3035 | MKWHr. | Sylhet | 323 | 323 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -313 | MW (E to W) at | 19:00 | hrs | Barisal | 230 | 230 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -360 | MW at | 1:00 | hrs | Rangpur | 634 | 634 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27° C |  |  | Total | 8678 | 8678 |  | 0
B. |  | 2020-02-27 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 28° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14405 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 5005 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 180.8237 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5889 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.1571 | MKWHr. | ii) HVDC Flow at Peak Time |  | 833 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0256 | MKWHr. | iii) Maximum HVDC Flow : |  | 834 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.27 |  | (b) Today: | 90.12 |  | (c) Rule Curve: |  | 93.3
.

## YesterdayGen
2020-02-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 174 | 0 | 0 | 290 | 0 | 0 | 356 | 328 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 32 | 16 | 33 | 0 | 0 | 30 | 40 | 115 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 80 | 0 | 300 | 265 | 169 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 84 | 155 | 8 | 22 | 0 | 71 | 73 | 53 | 51 | 163 | 148 | 66 | 77 | 0 | 0 | 20 | 0 | 10 | 320 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 |  | 179 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 |  | 4994 | 1495 | 6489 | 3530 | 179 | 1978 | 278 | 370 | 70 | 0 | 84 | 0 | 0 | 90.32
2:00 | 37 | 174 | 0 | 0 | 286 | 0 | 0 | 338 | 327 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 16 | 33 | 0 | 0 | 30 | 40 | 115 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 33 | 0 | 80 | 0 | 310 | 255 | 181 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 76 | 156 | 0 | 22 | 0 | 71 | 73 | 53 | 51 | 130 | 146 | 66 | 50 | 0 | 0 | 0 | 0 | 0 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4717 | 1464 | 6181 | 3502 | 181 | 1832 | 150 | 370 | 70 | 0 | 76 | 0 | 0 | 90.31
3:00 | 37 | 165 | 0 | 0 | 275 | 0 | 0 | 338 | 288 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 16 | 33 | 0 | 0 | 30 | 40 | 115 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 265 | 260 | 199 | 8 | 90 | 10 | 5 | 0 | 8 | 0 | 0 | 0 | 19 | 8 | 8 | 21 | 74 | 156 | 0 | 22 | 0 | 71 | 73 | 11 | 10 | 130 | 145 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 290 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4397 | 1493 | 5890 | 3446 | 181 | 1628 | 120 | 371 | 70 | 0 | 74 | 0 | 0 | 90.3
4:00 | 37 | 148 | 0 | 0 | 275 | 0 | 0 | 342 | 288 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 29 | 40 | 115 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 265 | 255 | 200 | 8 | 90 | 10 | 5 | 0 | 8 | 0 | 0 | 0 | 19 | 8 | 8 | 15 | 76 | 157 | 0 | 22 | 0 | 71 | 73 | 11 | 10 | 130 | 147 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 5 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4392 | 1441 | 5833 | 3440 | 181 | 1577 | 120 | 370 | 69 | 0 | 76 | 0 | 0 | 90.29
5:00 | 37 | 148 | 0 | 0 | 274 | 0 | 0 | 337 | 256 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 29 | 40 | 115 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 265 | 260 | 200 | 8 | 90 | 10 | 5 | 0 | 8 | 0 | 0 | 0 | 19 | 8 | 8 | 15 | 76 | 158 | 0 | 22 | 0 | 71 | 73 | 11 | 10 | 100 | 152 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 5 | 90 | 0 | 264 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4255 | 1461 | 5716 | 3460 | 181 | 1456 | 120 | 354 | 69 | 0 | 76 | 0 | 0 | 90.28
6:00 | 37 | 148 | 0 | 0 | 291 | 0 | 0 | 357 | 299 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 28 | 25 | 25 | 0 | 0 | 29 | 40 | 115 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 80 | 0 | 280 | 275 | 200 | 8 | 90 | 10 | 5 | 0 | 8 | 0 | 0 | 0 | 19 | 8 | 8 | 15 | 78 | 157 | 20 | 22 | 0 | 71 | 73 | 11 | 10 | 130 | 155 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 181 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11 | 5 | 90 | 0 | 220 | 0 | 0 | 130 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 |  | 4513 | 1429 | 5942 | 3526 | 181 | 1609 | 169 | 310 | 69 | 0 | 78 | 0 | 0 | 90.27
7:00 | 37 | 169 | 0 | 0 | 314 | 0 | 0 | 380 | 337 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 25 | 25 | 0 | 0 | 28 | 40 | 115 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 41 | 0 | 80 | 0 | 290 | 260 | 189 | 8 | 90 | 10 | 5 | 0 | 8 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 78 | 157 | 50 | 22 | 0.1 | 70 | 73 | 46 | 30 | 163 | 146 | 66 | 40 | 0 | 0 | 0 | 0 | 0 | 320 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.4 | 0 | 0 | 0 | 232 | 2 | 0 | 0 | 0.1 | 50 | 0 | 0 | 0 | 0 |  | 386 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 155 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 4892.6 | 1697 | 6589.6 | 3634 | 386 | 1818 | 295 | 310 | 68 | 0 | 78 | 0.6 | 0 | 90.26
8:00 | 37 | 178 | 0 | 0 | 335 | 0 | 0 | 352 | 337 |  | 0 | 400 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 115 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 80 | 0 | 320 | 290 | 202 | 8 | 89 | 10 | 5 | 0 | 38 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 157 | 50 | 22 | 0.6 | 71 | 73 | 48 | 51 | 130 | 154 | 65 | 77 | 0 | 0 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0.6 | 0 | 0 | 0 | 233 | 57 | 0 | 0 | 0.277 | 50 | 0 | 0 | 0 | 0 |  | 583 | 0 | 355 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 90 | 0 | 220 | 0 | 0 | 180 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 |  | 5156.477 | 2044 | 7200.477 | 3807 | 583 | 1864 | 447 | 310 | 68 | 32 | 88 | 1.477 | 0 | 90.26
9:00 | 37 | 178 | 0 | 0 | 318 | 0 | 0 | 352 | 304 |  | 0 | 450 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 33 | 0 | 0 | 28 | 40 | 115 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 80 | 0 | 300 | 265 | 192 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 80 | 155 | 50 | 0 | 1.2 | 70 | 73 | 48 | 51 | 130 | 153 | 65 | 80 | 0 | 0 | 0 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 4.6 | 0 | 0 | 0 | 233 | 115 | 0 | 0 | 0.272 | 87 | 0 | 0 | 0 | 0 |  | 583 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 90 | 0 | 220 | 0 | 0 | 180 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 5194.072 | 2018 | 7212.072 | 3683 | 583 | 1807 | 633 | 310 | 68 | 42 | 80 | 6.072 | 0 | 90.25
10:00 | 37 | 178 | 0 | 0 | 300 | 0 | 0 | 349 | 305 |  | 0 | 450 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 33 | 0 | 0 | 28 | 40 | 115 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 2 | 0 | 80 | 0 | 375 | 320 | 202 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 19 | 82 | 153 | 50 | 0 | 1.7 | 70 | 73 | 47 | 51 | 110 | 153 | 64 | 80 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 9.1 | 0 | 0 | 0 | 233 | 75 | 0 | 0 | 1.2 | 140 | 0 | 0 | 0 | 0 |  | 588 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 90 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 70 | 0 |  | 5317 | 1987.2 | 7304.2 | 3782 | 588 | 1776 | 659 | 310 | 68 | 25 | 82 | 14.2 | 0 | 90.25
11:00 | 37 | 179 | 0 | 0 | 300 | 0 | 0 | 354 | 304 |  | 0 | 450 | 120 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 33 | 0 | 0 | 45 | 40 | 120 | 0 | 0 | 0 | 0 | 151 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 2 | 0 | 80 | 0 | 330 | 305 | 202 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 19 | 80 | 152 | 50 | 0 | 2 | 72 | 73 | 50 | 51 | 130 | 153 | 63 | 77 | 0 | 0 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 14.8 | 0 | 0 | 0 | 234 | 75 | 0 | 0 | 1.2 | 157 | 0 | 0 | 0 | 0 |  | 588 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 91 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 70 | 0 |  | 5319 | 1989.3 | 7308.3 | 3745 | 588 | 1811 | 643 | 311 | 85 | 25 | 80 | 20.3 | 0 | 90.24
12:00 | 37 | 155 | 0 | 0 | 300 | 0 | 0 | 387 | 324 |  | 0 | 450 | 150 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 33 | 0 | 0 | 38 | 40 | 120 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 2 | 0 | 80 | 0 | 360 | 340 | 181 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 0 | 8 | 72 | 152 | 50 | 0 | 2.2 | 72 | 73 | 51 | 51 | 163 | 164 | 62 | 77 | 0 | 0 | 19 | 0 | 10 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 14.7 | 0 | 0 | 0 | 234 | 75 | 0 | 0 | 0.6 | 190 | 0 | 0 | 0 | 0 |  | 589 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 220 | 0 | 0 | 200 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 80 | 0 |  | 5433.5 | 2035.3 | 7468.8 | 3783 | 589 | 1874 | 711 | 311 | 78 | 25 | 72 | 25.8 | 0 | 90.24
13:00 | 37 | 134 | 0 | 0 | 300 | 0 | 0 | 369 | 345 |  | 0 | 450 | 150 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 28 | 40 | 120 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 9 | 0 | 80 | 0 | 315 | 290 | 195 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 72 | 139 | 50 | 0 | 1.8 | 71 | 73 | 51 | 51 | 130 | 148 | 65 | 80 | 0 | 0 | 19 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 6.1 | 50 | 0 | 0 | 235 | 75 | 0 | 0 | 0.212 | 301 | 0 | 0 | 0 | 0 |  | 589 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 220 | 0 | 0 | 214 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 108 | 0 |  | 5578.112 | 2041.7 | 7619.812 | 3608 | 589 | 1845 | 1088 | 310 | 68 | 25 | 72 | 14.812 | 0 | 90.23
14:00 | 37 | 134 | 0 | 0 | 300 | 0 | 0 | 339 | 263 |  | 0 | 370 | 150 | 82 | 0 | 15 | 0 | 0 | 0 | 0 | 84 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 28 | 40 | 120 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 46 | 16 | 6 | 0 | 80 | 0 | 315 | 290 | 164 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 82 | 139 | 50 | 0 | 1.6 | 70 | 73 | 53 | 51 | 110 | 152 | 45 | 20 | 0 | 0 | 19 | 0 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4.8 | 30 | 0 | 0 | 234 | 75 | 0 | 0 | 1 | 160 | 0 | 0 | 0 | 0 |  | 589 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 220 | 0 | 0 | 180 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 109 | 0 |  | 5151.4 | 2008.5 | 7159.9 | 3482 | 589 | 1579 | 1015 | 310 | 68 | 25 | 82 | 9.9 | 0 | 90.23
15:00 | 37 | 135 | 0 | 0 | 300 | 0 | 0 | 348 | 264 |  | 0 | 370 | 150 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 80 | 0 | 315 | 290 | 164 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 76 | 139 | 50 | 0 | 0.9 | 72 | 73 | 53 | 51 | 110 | 146 | 45 | 20 | 0 | 0 | 19 | 0 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 3.2 | 10 | 0 | 0 | 236 | 75 | 0 | 0 | 0.2 | 125 | 0 | 0 | 0 | 0 |  | 589 | 0 | 340 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 109 | 0 |  | 5024.3 | 1974.1 | 6998.4 | 3501 | 589 | 1618 | 804 | 311 | 67 | 25 | 76 | 7.4 | 0 | 90.22
16:00 | 37 | 134 | 0 | 0 | 300 | 0 | 0 | 357 | 295 |  | 0 | 370 | 150 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 80 | 0 | 330 | 305 | 179 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 74 | 138 | 50 | 0 | 0.5 | 72 | 73 | 53 | 51 | 110 | 145 | 45 | 20 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 3.7 | 10 | 0 | 0 | 234 | 75 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 |  | 589 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 92 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 109 | 0 |  | 5102.2 | 1957.2 | 7059.4 | 3561 | 589 | 1672 | 752 | 312 | 67 | 25 | 74 | 7.4 | 0 | 90.22
17:00 | 37 | 134 | 0 | 0 | 270 | 0 | 0 | 265 | 338 |  | 0 | 360 | 150 | 7 | 0 | 15 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 26 | 40 | 120 | 0 | 0 | 0 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 5 | 0 | 19 | 0 | 0 | 100 | 0 | 290 | 310 | 152 | 8 | 91 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 14 | 74 | 140 | 50 | 0 | 0.1 | 71 | 73 | 53 | 51 | 100 | 145 | 65 | 50 | 0 | 0 | 19 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1.6 | 10 | 0 | 2 | 235 | 75 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 |  | 589 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 110 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 70 | 0 |  | 4884.7 | 1965.2 | 6849.9 | 3400 | 589 | 1684 | 679 | 330 | 66 | 25 | 74 | 2.9 | 0 | 90.21
18:00 | 37 | 133 | 0 | 0 | 270 | 0 | 0 | 359 | 349 |  | 0 | 360 | 150 | 28 | 10 | 15 | 0 | 0 | 0 | 0 | 60 | 74 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 26 | 40 | 120 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 12 | 17 | 19 | 12 | 0 | 100 | 0 | 295 | 290 | 195 | 26 | 90 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 26 | 14 | 102 | 140 | 90 | 0 | 0 | 70 | 73 | 32 | 35 | 100 | 154 | 64 | 80 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 50 | 0 | 56 | 0 | 18 | 233 | 75 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 |  | 721 | 0 | 345 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 114 | 0 | 236 | 0 | 0 | 160 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 30 | 0 | 0.1 | 60 | 0 |  | 5424 | 2216.1 | 7640.1 | 3571 | 721 | 1704 | 1084 | 350 | 66 | 42 | 102 | 0.1 | 0 | 90.21
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 165 | 0 | 0 | 290 | 0 | 0 | 360 | 355 |  | 0 | 450 | 150 | 100 | 45 | 35 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 8 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 38 | 50 | 19 | 17 | 0 | 100 | 0 | 305 | 305 | 151 | 26 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 108 | 142 | 83 | 17 | 0 | 69 | 73 | 53 | 51 | 163 | 145 | 67 | 80 | 0 | 12 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 133 | 0 | 90 | 0 | 38 | 234 | 97 | 0 | 13 | 0 | 300 | 0 | 0 | 0 | 0 |  | 833 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 117 | 0 | 260 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  | 6337 | 2738 | 9075 | 3732 | 833 | 1982 | 1891 | 377 | 67 | 85 | 108 | 0 | 0 | 90.2
19:30 | 37 | 178 | 0 | 0 | 290 | 0 | 0 | 334 | 334 |  | 0 | 420 | 150 | 100 | 16 | 30 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 0 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 70 | 50 | 19 | 20 | 0 | 100 | 0 | 305 | 305 | 145 | 26 | 91 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 108 | 142 | 83 | 17 | 0 | 71 | 73 | 53 | 51 | 100 | 148 | 55 | 80 | 0 | 52 | 20 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 85 | 0 | 107 | 0 | 90 | 0 | 50 | 235 | 115 | 0 | 34 | 0 | 301 | 0 | 0 | 0 | 0 |  | 834 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 120 | 0 | 270 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 269 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 0 |  | 6262 | 2772 | 9034 | 3753 | 834 | 1865 | 1920 | 390 | 67 | 97 | 108 | 0 | 0 | 0
20:00 | 37 | 178 | 0 | 0 | 290 | 0 | 0 | 334 | 334 |  | 0 | 420 | 150 | 75 | 16 | 30 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 0 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 71 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 50 | 50 | 19 | 30 | 0 | 100 | 0 | 305 | 305 | 134 | 26 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 106 | 143 | 90 | 22 | 0 | 72 | 73 | 53 | 51 | 100 | 143 | 55 | 80 | 0 | 53 | 20 | 0 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 123 | 0 | 70 | 0 | 40 | 236 | 115 | 0 | 34 | 0 | 301 | 0 | 0 | 0 | 0 |  | 833 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 121 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 109 | 0 |  | 6223 | 2840 | 9063 | 3828 | 833 | 1893 | 1833 | 401 | 67 | 102 | 106 | 0 | 0 | 90.2
21:00 | 37 | 178 | 0 | 0 | 290 | 0 | 0 | 341 | 323 |  | 0 | 420 | 150 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 86 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 30 | 0 | 100 | 0 | 315 | 320 | 147 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 10 | 11 | 33 | 21 | 106 | 142 | 82 | 22 | 0 | 72 | 73 | 53 | 51 | 100 | 150 | 55 | 80 | 0 | 53 | 20 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 92 | 0 | 20 | 0 | 19 | 234 | 115 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 |  | 833 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 120 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 109 | 0 |  | 5935 | 2860 | 8795 | 3870 | 833 | 2012 | 1439 | 400 | 67 | 68 | 106 | 0 | 0 | 90.19
22:00 | 37 | 178 | 0 | 0 | 289 | 0 | 0 | 335 | 318 |  | 0 | 420 | 150 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 86 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 38 | 0 | 100 | 0 | 305 | 305 | 159 | 8 | 90 | 26 | 5 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 21 | 96 | 144 | 59 | 22 | 0 | 72 | 73 | 53 | 51 | 100 | 146 | 55 | 80 | 0 | 55 | 20 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 233 | 75 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 |  | 833 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5531 | 2591 | 8122 | 3828 | 833 | 1900 | 959 | 371 | 67 | 68 | 96 | 0 | 0 | 90.19
23:00 | 37 | 178 | 0 | 0 | 290 | 0 | 0 | 336 | 330 |  | 0 | 400 | 150 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 32 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 85 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 320 | 320 | 165 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 21 | 90 | 144 | 59 | 22 | 0 | 70 | 73 | 53 | 51 | 163 | 146 | 54 | 80 | 0 | 53 | 20 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 |  | 589 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5329 | 2179 | 7508 | 3835 | 589 | 2002 | 554 | 371 | 67 | 0 | 90 | 0 | 0 | 90.18
24:00 | 37 | 178 | 0 | 0 | 290 | 0 | 0 | 351 | 335 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 32 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 86 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 100 | 0 | 310 | 315 | 158 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 21 | 82 | 145 | 58 | 22 | 0 | 70 | 73 | 53 | 51 | 163 | 150 | 65 | 80 | 0 | 53 | 20 | 0 | 10 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 344 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 5174 | 1896 | 7070 | 3865 | 344 | 2039 | 302 | 371 | 67 | 0 | 82 | 0 | 0 | 90.18
KWH | 902000 | 4081300 | 0 | 0 | 7002545 | 0 | 0 | 8438790 | 7518000 |  | 0 | 9308000 | 3476596 | 599040 | 146280 | 166093 | 0 | 0 | 0 | 0 | 1204800 | 587808 | 0 | 63461 | 0 | 0 | 0 | 414000 | 175250 | 0 | 427608 | 600000 | 389340 | 688600 | 808400 | 0 | 0 | 627655 | 964000 | 2800000 | 0 | 0 | 358729 | 0 | 3107338 | 0 |  | 0 | 0 | 0 | 0 | 141120 | 316320 | 430992 | 536640 | 0 | 2087845 | 0 | 7729400 | 7252500 | 4358000 | 267636 | 2147450 | 370008 | 136800 | 0 | 994120 | 0 | 0 | 0 | 371592 | 182700 | 639400 | 43040 | 2025600 | 3471040 | 1135680 | 298224 | 10850 | 1685000 | 1763880 | 1021800 | 1072800 | 3373051 | 3468000 | 1380096 | 1316160 | 0 | 254980 | 303000 | 0 | 190620 | 7599000 | 492960 | 235081 | 0 | 0 | 0 | 0 | 177600 | 0 | 1064160 | 69120 | 351360 | 0 | 162254 | 5628000 | 1356000 | 0 | 64399 | 5760 | 3053564 | 0 | 0 | 0 | 0 |  | 12157091 | 0 | 7835040 | 0 | 767040 | 0 | 0 | 0 | 0 | 0 | 0 | 1807039 | 353500 | 286368 | 0 | 0 | 0 | 0 | 0 | 623580 | 0 | 0 | 0 | 0 | 0 | 374880 | 270900 | 121176 | 2278254 | 0 | 5909400 | 0 | 0 | 4453364 | 0 | 0 | 0 | 1406755 | 0 | 0 | 0 | 7857218 | 0 | 0 | 0 | 0 | 451200 | 0 | 26975 | 1700832 | 0 |  | 125891235 | 48680612 | 174571847 | 88414457 | 12157091 | 43597880 | 17861225 | 8187654 | 1591655 | 623580 | 2025600 | 112705 | 0
Fuel Cost | 1010240 | 4407804 | 0 | 0 | 5181883.3 | 0 | 0 | 6075928.8 | 5713680 |  | 0 | 7446400 | 3128936.4 | 6110208 | 1584212.4 | 1704114.18 | 0 | 0 | 0 | 0 | 13373280 | 5972129.28 | 0 | 665071.28 | 0 | 0 | 0 | 3970260 | 1671885 | 0 | 320706 | 450000 | 0 | 0 | 0 | 0 | 0 | 163190.3 | 250640 | 4284000 | 0 | 0 | 376665.45 | 0 | 3946319.26 | 0 |  | 0 | 0 | 0 | 0 | 1342051.2 | 2960755.2 | 396512.64 | 1491859.2 | 0 | 2192237.25 | 0 | 5719756 | 6092100 | 4009360 | 262283.28 | 2856108.5 | 303406.56 | 140904 | 0 | 1421591.6 | 0 | 0 | 0 | 379023.84 | 137025 | 1208466 | 32280 | 13976640 | 2846252.8 | 10800316.8 | 304188.48 | 177940 | 2291600 | 2398876.8 | 1389648 | 1341000 | 4182583.24 | 3190560 | 2056343.04 | 2316441.6 | 0 | 387569.6 | 481770 | 0 | 447957 | 5395290 | 369720 | 178661.56 | 0 | 0 | 0 | 0 | 1708512 | 0 | 10737374.4 | 797644.8 | 3274675.2 | 0 | 1520319.98 | 5290320 | 11892120 | 0 | 608570.55 | 0 | 28153860.08 | 0 | 0 | 0 | 0 |  | 32824145.7 | 0 | 6111331.2 | 0 | 7394265.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1445631.2 | 547925 | 3075592.32 | 0 | 0 | 0 | 0 | 0 | 6173442 | 0 | 0 | 0 | 0 | 0 | 412368 | 446985 | 91730.232 | 14512477.98 | 0 | 24169446 | 0 | 0 | 3918960.32 | 0 | 0 | 0 | 2236740.45 | 0 | 0 | 0 | 5735769.14 | 0 | 0 | 0 | 0 | 4214208 | 0 | 0 | 0 | 0 |  | 227270029.85 | 113311018.142 | 340581047.992 | 80743337.832 | 32824145.7 | 40929425.51 | 125862717.87 | 38681923.98 | 413830.3 | 6173442 | 13976640 | 975584.8 | 0
Yesterday Day Peak | 37 | 155 | 0 | 0 | 300 | 0 | 0 | 387 | 324 |  | 0 | 450 | 150 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 33 | 0 | 0 | 38 | 40 | 120 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 2 | 0 | 80 | 0 | 360 | 340 | 181 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 0 | 8 | 72 | 152 | 50 | 0 | 2.2 | 72 | 73 | 51 | 51 | 163 | 164 | 62 | 77 | 0 | 0 | 19 | 0 | 10 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 14.7 | 0 | 0 | 0 | 234 | 75 | 0 | 0 | 0.6 | 190 | 0 | 0 | 0 | 0 |  | 589 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 220 | 0 | 0 | 200 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 80 | 0 |  | 7468.8 | DayPeak
Yesterday Evening Peak | 37 | 165 | 0 | 0 | 290 | 0 | 0 | 360 | 355 | 0 | 0 | 450 | 150 | 100 | 45 | 35 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 8 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 50 | 19 | 17 | 0 | 100 | 0 | 305 | 305 | 151 | 26 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 108 | 142 | 83 | 17 | 0 | 69 | 73 | 53 | 51 | 163 | 145 | 67 | 80 | 0 | 12 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 133 | 0 | 90 | 0 | 38 | 234 | 97 | 0 | 13 | 0 | 300 | 0 | 0 | 0 | 0 |  | 833 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 64 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 117 | 0 | 260 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  | 9075 | EvPeak
Forecast for Evening | 37 | 178 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 120 | 0 | 25 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 115 | 155 | 95 | 22 | 0 | 70 | 73 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 120 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 842 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 33 | 90 | 20 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 40 | 40 | 40 | 52 | 38 | 22 | 10 | 11 | 120 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 37 | 178 | 0 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 120 | 0 | 25 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 155 | 95 | 22 | 1.6 | 70 | 73 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 100 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 90 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 495 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 33 | 90 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 40 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 100 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 95 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 37 | 170 | 0 | 0 | 300 | 0 | 0 | 337 | 330 | 0 | 0 | 350 | 150 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 86 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 80 | 0 | 310 | 310 | 184 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 13 | 8 | 33 | 20 | 68 | 160 | 50 | 22 | 0.1 | 70 | 73 | 53 | 50 | 130 | 149 | 45 | 80 | 0 | 52 | 19 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 6.87 | 0 | 0 | 0 | 233 | 71 | 0 | 0 | 1.1 | 33 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 92 | 0 | 265 | 0 | 0 | 190 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 80 | 0 | 0
199
| Minimum Generation |  | 5716 | 5:00
| Highest Generation |  | 9075 | 19:00
| Day Peak Generation |  | 7468.8 | 12:00
| Evening Peak Generation |  | 9075 | 19:00
| HVDC Max Flow |  | 834 | 19:30
| HVDC EvPeak Flow |  | 833 | 19:00
| Load factor L.F |  | 80.15%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-02-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-02-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7468.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5889 | MW
Evening Peak Generation : |  | 9075 | MW Hour : | 19:00 | Available Max Generation : |  | 14405 | MW
E.P. Demand (at gen end) : |  | 9075 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9400 | MW
Maximum Generation : |  | 9075 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5005 | MW
Total Gen. (MKWH) : |  | 174.5718 | System Load Factor : | 80.15% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -360 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-02-27
Actual : | 90.12 | Ft.(MSL) , | Rule curve : | 93.3 | Ft.( MSL )
Gas Consumed : | Total = | 1083.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 121672763.342
: |  | Coal : | 38681923.98 | Oil : | 132036159.87 | Total : | 292390847.192
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3354.6468 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1136.4641 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1017.4677 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 919.0958 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 830.7236 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 670.3537 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 380.3641 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.7445 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 516.9836 |  |  | 0 | 0%
Total | 0 |  | 8998.844 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Bhola 225 MW GT-1
|  |  |  | 2) Meghnaghat GT-2 | 11) Sikalbaha 225 MW CCPP
3) Ghorasal Unit-2,4 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Shahjibazar-Cumilla(N) 132 kV Ckt-1 & 2 were under shut down from 09:21 to 17:07 for A/M.
b) Sikalbaha-225 MW P/S-Sikalbaha S/S 230 kV Ckt-1 was under shut down from 09:10 to 13:52 for D/W.
c) Kaliakoir 400/132 kV T-1 transformer was under shut down from 08:07 to 16:57 for C/M.
d) Rangamati 132/33 kV T-2 transformer was under shut down from 12:32 to 15:07 for C/M.
e) Hathazari-AKS 230 kV Ckt was under shut down at 11:52 for D/W.
f) Khulna(S) 230/132 kV T-2 transformer was under shut down from 12:08 to 13:15 for C/M.
g) Rajshahi 230/132 kV T-1 transformer was under shut down from 08:51 to 18:26 for D/W.
h) Bhola 230 kV Bus-2 was under shut down at 11:53 for D/W.
i) Haripur-Meghnaghat 230 kV Ckt-2 tripped at 11:50 showing dir.E/F relay and was switched on at 12:26.
j) Meghnaghat-Cumilla(N) 230 kV Ckt-1 & 2 tripped at 11:50 showing TCS,discortance and were switched
on at 12:24 & 12:25 respectively.
k) Shyampur-Meghnaghat 230 kV Ckt tripped at 11:50 showing differential relay and was switched on at 12:17.
l) Uttara 132/33 kV T-3 transformer was under shut down at 10:06 for D/W.
m) Ghorasal-Ishurdi 230 kV Ckt-1 & 2 were shut down from 10:40 to 17:05 for C/M.
n) Lalbagh 132/33 kV T-1 transformer was under shut down at 10:24 for C/M.
o) Kodda-Rajendrapur 132 kV Ckt-1 & 2 were under shut down from 13:14 to 15:05 for C/M.
p) After maintenance Sylhet-150 MW GT was synchronized at 18:55.
q) After maintenance Sikalbaha-225 MW was synchronized at 19:30.
r) Bhola-225 MW CCPP ST was synchronized at 17:12.
s) Hasnabad 132/33 kV T-2 transformer was shut down at 10:42 due to rd hot maintenance at 33 kV
incomer R-phase bus isolator and was switched on at 17:26.
t) Sherpur 132/33 kV T-3 transformer was under shut down from 08:37 to 18:02 for replacing 33 kV CB.
u) Halishahar 132/33 kV T-1 & T-3 transformers tripped at 16:07 showing O/C & E/F relays due to 33 kV |  |  |  |  | About 40 MW power interruption occurred under Halishahar S/S area
New Mooring -2 feeder fault and were switched on at 16:30. |  |  |  |  | from 16:07 to 16:30.
v) Halishahar 132/33 kV T-2 transformer tripped at 16:07 showing E/F relay due to 33 kV TSP feeder |  |  |  |  | About 30 MW power interruption occurred under Halishahar S/S area
fault and was switched on at 16:59. |  |  |  |  | from 16:07 to 16:59.
w) Palashbari-Rangpur Confidence 132 kV Ckt is under shut down since 07:01(27/2/20) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-02-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 902000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 165 | 4081300
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 290 | 7002545 | FGMO
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8438790 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 355 | 7518000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9308000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 599040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3476596 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 45 | 146280 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 35 | 166093 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 8 | 63461 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 427608
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1204800 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 587808
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 414000 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 175250
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 989340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 688600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 808400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 1064160
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2536 | 48062071
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 69120
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 316320
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 67 | 1591655 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 358729 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 103 | 3107338 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 13 | 64399 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 351360 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 430992
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 536640
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 141120 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 5760
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 300 | 3053564
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 817 | 12826997
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2087845 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 151 | 4358000 | Gas shortage.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7729400 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7252500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 370008
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 136800 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 267636 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 994120
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 38 | 162254 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2147450
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 371592 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 182700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2025600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 639400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 43040
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1279 | 28768345
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 142 | 3471040 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 298224 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 83 | 1135680 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10850
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 50 | 177600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 97 | 1356000 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 389 | 6449394
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 69 | 1685000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 73 | 1763880
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3373051
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 145 | 3468000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1021800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 1072800
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 235081
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1380096 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1316160
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 12 | 254980
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 303000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 492960
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7599000 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 234 | 5628000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 190620
| Sylhet Area Total |  |  |  | 1949 | 1316 | 29784428
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 833 | 12157091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 767040
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 7835040 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1313 | 20759171
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 286368 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 19 | 353500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 1807039 | GT-1 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 1406755
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | On test
| Barisal Area Total |  |  |  | 462 | 266 | 3853662
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 190 | 4453364 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 273 | 7857218 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 374880 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 270900
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 121176 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 623580
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 100 | 1700832 | Engine problem
| Rajshahi Area Total |  |  |  | 2183 | 682 | 15401950
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 117 | 2278254
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 5909400
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 100 | 451200 | Engine problem
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26975
| Rangpur Area Total |  |  |  | 605 | 477 | 8665829
| Total |  |  |  | 19107 | 9075 | 174571847
| Eastern Grid Total |  |  |  | 13543 | 6337 | 125891235
| Western Grid Total |  |  |  | 5564 | 2738 | 48680612
| National Grid Total |  |  |  | 19107 | 9075 | 174571847
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-02-26
(a) ENTIRE EASTERN GRID : |  | 5796 | MW | (b) ENTIRE WESTERN GRID : |  | 2882 | MW
i) Dhaka area |  | 3180 | MW | i) Khulna area |  | 1077 | MW
ii) Chittagong area |  | 877 | MW | ii) Rajshahi area |  | 941 | MW
iii) Comilla area |  | 704 | MW | iii) Barisal area |  | 230 | MW
iv) Mymensingh area |  | 712 | MW | iv) Rangpur area |  | 634 | MW
v) Sylhet area |  | 323 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8678 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 15:00 | Srimongal | 22 | 21:00 | Jhenida | 83 | 19:00
Munsiganj | 89 | 20:00 | Shahjibazar | 80 | 21:00 | Bottail | 94 | 19:00
Sonargaon | 70 | 20:00 | Fenchuganj | 25 | 18:00 | G.K Project | 37 | 19:30
Shyampur | 170 | 4:00 | Kulawara | 29 | 18:30 | Faridpur | 130 | 19:00
Bhulta | 150 | 0:00 | Sylhet | 95 | 19:00 | Madaripur | 61 | 19:00
Madanganj | 59 | 20:00 | Chatak | 17 | 21:00 | Sariatpur | 38 | 19:30
Shitalakhya | 96 | 15:00 | Sunamganj | 29 | 19:30 | Gopalganj | 65 | 19:30
Rahim steel | 13 | 12:00 | Biani Bazar | 33 | 19:00 | Bagerhat | 70 | 22:00
Matuail | 88 | 12:00 | Comilla (S) | 114 | 18:30 | Mongla | 36 | 18:30
Ghorasal | 62 | 20:00 | Comilla(N) | 61 | 20:00 | Satkhira | 68 | 19:30
Narsingdi | 120 | 19:30 | Chandpur | 74 | 19:30 | Gallamari | 36 | 19:00
Haripur (SBU) | 89 | 17:00 | Feni | 87 | 20:00 | Magura | 36 | 19:00
Ullon | 54 | 19:00 | Chowmuhani | 110 | 18:30 | Norail | 26 | 18:30
Hasnabad | 144 | 20:00 | Ashuganj | 40 | 19:00 | Chuadanga | 63 | 19:00
Magbazar | 81 | 13:00 | Daudkandi | 82 | 20:00 | Barisal(N) | 29 | 20:00
Maniknagar | 78 | 13:00 | B.Baria | 92 | 18:00 | Barisal (S) | 76 | 19:00
Bangabhaban | 24 | 13:00 | Ramganj | 62 | 20:00 | Patuakhali | 72 | 19:30
Narinda | 82 | 12:00 | Chaddagram | 20 | 13:00 | Bhandaria | 38 | 22:00
Dhanmondi | 114 | 12:00 | PHP | 2 | 10:00 | Borhan Uddin | 24 | 20:00
Lalbag | 47 | 13:00 | Madunaghat | 40 | 18:30 | Ishurdi | 41 | 19:00
Madartek | 46 | 20:00 | Hathazari | 64 | 18:30 | Ruppur Paromanobik | 2 | 17:00
Dhaka University |  |  | Khulshi | 144 | 14:00 | Natore | 93 | 19:00
Mirpur | 73 | 19:00 | Halishahar | 95 | 7:00 | Bogra | 132 | 19:00
Kalyanpur | 60 | 18:30 | Baraulia | 140 | 8:00 | Noagaon | 90 | 20:00
Gulshan | 88 | 13:00 | Sikalbaha | 24 | 18:30 | Rajshahi | 92 | 19:00
Uttara | 40 | 13:00 | Dohazari | 62 | 20:00 | Rajshahi New | 9 | 19:30
Uttara New | 31 | 18:00 | Cox'sbazar | 76 | 18:30 | C.Nawabganj | 57 | 19:00
Kamrangirchar | 69 | 13:00 | Chandraghona | 18 | 18:30 | Amnura | 25 | 19:30
Savar | 96 | 16:00 | Kaptai | 3.2 | 18:30 | Pabna | 77 | 19:00
Bhasantec | 112 | 18:30 | A. Khaer Stl. | 9 | 3:00 | Shahjadpur | 83 | 20:00
Agargaon | 37 | 13:00 | Bakulia | 72 | 12:00 | Serajganj | 77 | 19:00
Satmosjid | 73 | 14:00 | Julda | 21 | 14:00 | Niyamatpur | 55 | 19:00
Tongi | 109 | 12:00 | TK chemical | 10.7 | 12:00 | Joypurhat | 52 | 18:30
Kabirpur | 189 | 18:00 | Modern Steel | 16 | 9:00 | Sherpur(Bogura) | 36 | 19:00
Basundhara | 78 | 18:00 | Shahmirpur | 47 | 18:00 | Mohastangor | 31 | 8:00
Manikganj | 62 | 19:30 | Khagrachhari | 16 | 19:30 | Rangpur | 113 | 19:00
Joydevpur | 163 | 12:00 | Matarbari | 21 | 18:30 | Lalmonirhat | 45 | 19:00
New Tongi | 81 | 18:30 | Baroiar Hat | 20 | 19:00 | Saidpur | 91 | 19:00
Korda | 184 | 19:00 | Rangamati | 8 | 18:00 | Purbasadipur | 92 | 20:00
Dhamrai | 58 | 19:00 | Abul Khair 230 | 155 | 16:00 | Thakurgaon | 65 | 19:00
Valuka | 78 | 19:00 | BSRM | 148 | 15:00 | Palashbari | 95 | 18:30
Tangail | 141 | 20:00 | GPH Ispat | 64 | 16:00 | Barapukuria | 44 | 19:00
Mymensing | 173 | 19:30 | Goalpara | 22 | 12:00 | Panchagar | 34 | 19:00
Kishorganj | 84 | 21:00 | Central s/s | 63 | 19:00 | Joldhaka | 20 | 19:00
Netrokona | 91 | 18:30 | Noapara | 42 | 19:30 | Kurigram | 45 | 0.77083
Jamalpur | 106 | 19:00 | Jessore | 90 | 19:00
Sherpur | 82 | 20:00 | Benapol | 32 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-02-26 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 406 | 0.16667 | 397 | 0.5 | Kaliakoir | 389 | 0.041667 | 374 | 0.5
Bheramara | 410 | 0.083333 | 395 | 0.79167 | Bhulta | 397 | 0.125 | 387 | 0.5
Ashuganj(N) | 402 | 0.083333 | 393 | 0.5 | Gopalganj | 408 | 0.91667 | 269 | 0.77083
Payra | 409 | 0.20833 | 371 | 0.77083
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 232 | 0.41667 | Hathazari | 226 | 0.77083 | 217 | 0.29167
Ishurdi | 241 | 0.125 | 225 | 0.29167 | Megnaghat | 240 | 0.16667 | 230 | 0.45833
Ashuganj | 242 | 0.083333 | 238 | 0.41667 | Fenchuganj | 243 | 0.16667 | 239 | 0.5
Serajganj | 233 | 0.16667 | 228 | 0.83333 | Siddhirganj | 236 | 0.041667 | 229 | 0.5
Baghabari | 245 | 0.91667 | 236 | 0.29167 | Maniknagar | 234 | 0.083333 | 226 | 0.5
Barapukuria | 243 | 0.125 | 234 | 0.77083 | Old Airport | 234 | 0.083333 | 224 | 0.5
Bogra | 231 | 0.083333 | 224 | 0.33333 | Barisal | 252 | 0.91667 | 237 | 0.77083
Khulna South | 238 | 0.16667 | 223 | 0.29167 | AKSML | 227 | 0.8125 | 214 | 0.33333
Rampura | 232 | 0.041667 | 229 | 0.45833 | BSRM | 228 | 0.8125 | 218 | 0.33333
Haripur | 233 | 0.041667 | 226 | 0.45833 | Bibiyana | 241 | 0.083333 | 236 | 0.29167
Hasnabad | 234 | 0.083333 | 225 | 0.5 | Bhulta | 235 | 0.875 | 229 | 0.5
Shyampur | 232 | 0.083333 | 222 | 0.5 | Ashuganj (S) | 239 | 0.79167 | 230 | 0.33333
Aminbazar | 236 | 0.16667 | 225 | 0.5 | Kaliakoir | 237 | 0.083333 | 227 | 0.5
Tongi | 233 | 0.16667 | 222 | 0.45833 | GPH | 223 | 0.8125 | 214 | 0.41667
Comilla (N) | 239 | 0.16667 | 232 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.20833 | 129 | 0.5 | Khulshi | 133 | 0.79167 | 115 | 0.91667
Munsiganj | 135 | 0.79167 | 128 | 0.5 | Halishahar | 136 | 0.79167 | 125 | 0.33333
Sonargaon | 135 | 0.041667 | 130 | 0.41667 | Baraulia | 135 | 0.54167 | 126 | 0.29167
Shyampur | 136 | 0.91667 | 129 | 0.5 | Sikalbaha | 136 | 0.79167 | 128 | 0.041667
Bhulta | 130 | 0.125 | 123 | 0.45833 | Dohazari | 135 | 0.79167 | 128 | 0.041667
Madanganj | 136 | 0.77083 | 128 | 0.5 | Cox'sbazar | 129 | 0.79167 | 120 | 0.041667
Shitalakhya | 139 | 0.79167 | 128 | 0.5 | Chandraghona | 136 | 0.79167 | 129 | 0.33333
Rahim steal | 135 | 12:00 | 130 | 0.45833 | Kaptai | 135 | 0.54167 | 130 | 0.33333
Matuail | 134 | 0.8125 | 128 | 0.5 | A. Khaer Stl. | 134 | 0.77083 | 127 | 0.29167
Ghorasal | 140 | 0.041667 | 135 | 0.5 | Bakulia | 133 | 0.54167 | 125 | 0.041667
Narsinghdi | 135 | 0.16667 | 129 | 0.5 | Julda | 136 | 0.79167 | 126 | 0.041667
Haripur (SBU) | 135 | 0.58333 | 130 | 0.66667 | TK Chemical | 137 | 0.79167 | 127 | 0.375
Ullon | 133 | 0.20833 | 126 | 0.5 | Modern Steel | 137 | 0.16667 | 127 | 0.125
Hasnabad | 135 | 0.20833 | 128 | 0.5 | Shahmirpur | 135 | 0.79167 | 127 | 0.33333
Magbazar | 133 | 0.20833 | 127 | 0.5 | Khagrachhari | 135 | 0.79167 | 128 | 0.33333
Maniknagar | 136 | 0.20833 | 130 | 0.5 | Matarbari | 131 | 0.83333 | 121 | 0.33333
Bangabhaban | 136 | 0.20833 | 130 | 0.5 | Baroiar Hat | 132 | 0.041667 | 130 | 0.29167
Narinda | 136 | 0.20833 | 130 | 0.5 | Rangamati | 135 | 0.79167 | 129 | 9:00
Dhanmondi | 133 | 0.20833 | 126 | 0.5 | Goalpara | 138 | 0.625 | 126 | 7:00
Lalbag | 136 | 0.20833 | 128 | 0.5 | Central s/s | 135 | 0.083333 | 126 | 0.29167
Madartek | 133 | 0.20833 | 126 | 0.5 | Noapara | 135 | 0.58333 | 126 | 0.29167
Dhaka University |  |  |  |  | Jessore | 132 | 0.70833 | 123 | 0.29167
Mirpur | 136 | 0.20833 | 127 | 0.5 | Benapol | 135 | 0.16667 | 123 | 0.29167
Kalyanpur | 134 | 0.125 | 126 | 0.5 | Jhenida | 133 | 0.16667 | 123 | 0.77083
Gulshan | 132 | 0.125 | 127 | 0.45833 | Bottail | 136 | 0.25 | 129 | 0.33333
Uttara | 136 | 0.20833 | 129 | 0.45833 | G.K Project | 141 | 0.125 | 135 | 0.77083
Uttara New | 136 | 0.125 | 127 | 0.5 | Faridpur | 138 | 0.16667 | 127 | 0.77083
Kamrangirchar | 135 | 0.125 | 126 | 0.5 | Madaripur | 138 | 0.45833 | 128 | 0.77083
Savar | 136 | 0.16667 | 128 | 0.5 | Sariatpur | 142 | 0.16667 | 128 | 0.77083
Bhasantec | 136 | 0.16667 | 128 | 0.5 | Gopalganj | 146 | 0.16667 | 131 | 0.77083
Agargaon | 136 | 0.083333 | 129 | 0.5 | Bagerhat | 135 | 0.16667 | 124 | 0.77083
Satmosjid | 135 | 0.083333 | 129 | 0.5 | Mongla | 133 | 0.125 | 123 | 0.77083
Tongi | 139 | 0.16667 | 132 | 0.45833 | Satkhira | 134 | 0.58333 | 125 | 0.29167
Kabirpur | 135 | 0.083333 | 126 | 0.45833 | Gallamari | 136 | 0.625 | 127 | 0.29167
Basundhara | 133 | 4:00 | 126 | 0.5 | Magura | 134 | 0.125 | 120 | 0.77083
Manikganj | 140 | 0.125 | 131 | 0.5 | Norail | 132 | 0.20833 | 120 | 0.77083
Joydevpur | 142 | 0.125 | 136 | 0.5 | Chuadanga | 131 | 0.083333 | 119 | 0.77083
New Tongi | 138 | 0.041667 | 131 | 0.5 | Barisal(N) | 142 | 0.16667 | 133 | 0.77083
Kodda | 135 | 0.75 | 125 | 0.5 | Barisal (S) | 139 | 0.66667 | 132 | 0.77083
Dhamrai | 135 | 0.083333 | 125 | 0.5 | Patuakhali | 138 | 0.041667 | 129 | 0.77083
Valuka | 130 | 0.83333 | 120 | 0.29167 | Bhandaria | 137 | 0.16667 | 129 | 0.77083
Tangail | 131 | 0.041667 | 123 | 0.5 | Ishurdi | 138 | 0.125 | 130 | 0.29167
Mymensing | 132 | 0.83333 | 120 | 0.29167 | Ruppur Paromanobik | 137 | 0.20833 | 132 | 0.29167
Kishorganj | 132 | 0.20833 | 127 | 0.5 | Natore | 135 | 0.125 | 128 | 0.33333
Netrokona | 131 | 0.83333 | 120 | 0.77083 | Bogra | 139 | 0.125 | 133 | 0.5
Jamalpur | 138 | 0.83333 | 117 | 0.29167 | Noagaon | 134 | 0.125 | 127 | 0.33333
Sherpur | 136 | 0.83333 | 120 | 0.125 | Rajshahi | 132 | 0.041667 | 125 | 0.33333
Srimongal | 140 | 0.16667 | 137 | 0.625 | Rajshahi New | 133 | 0.125 | 125 | 0.29167
Shahjibazar | 136 | 0.041667 | 134 | 0.5 | C.Nawabganj | 131 | 0.083333 | 123 | 0.5
Fenchuganj | 139 | 1904-01-02 | 136 | 3:00 | Amnura | 130 | 0.20833 | 122 | 0.29167
Khulawara | 138 | 0.041667 | 136 | 0.5 | Pabna | 138 | 0.16667 | 131 | 0.77083
Sylhet | 137 | 0.95833 | 133 | 0.75 | Shahjadpur | 140 | 0.041667 | 135 | 0.29167
Chatak | 136 | 0.083333 | 132 | 0.5 | Serajganj | 137 | 0.125 | 130 | 0.33333
Sunamganj | 137 | 1904-01-02 | 131 | 0.77083 | Niyamatpur | 134 | 0.125 | 124 | 0.33333
Biani Bazar | 137 | 1904-01-02 | 132 | 0.77083 | Joypurhat | 136 | 0.16667 | 124 | 0.33333
Comilla(s) | 132 | 0.29167 | 128 | 0.77083 | Sherpur(Bogura) | 139 | 0.16667 | 132 | 0.33333
Comilla(n) | 139 | 0.29167 | 137 | 0.45833 | Mohastangor | 139 | 0.20833 | 130 | 0.33333
Chandpur | 137 | 0.70833 | 135 | 0.33333 | Rangpur | 139 | 0.16667 | 130 | 0.5
Feni | 135 | 0.625 | 131 | 0.83333 | Lalmonirhat | 135 | 0.25 | 124 | 0.79167
Chowmuhani | 131 | 0.33333 | 129 | 0.91667 | Saidpur | 138 | 0.25 | 127 | 0.79167
Ashuganj | 138 | 0.29167 | 136 | 0.5 | Purbasadipur | 135 | 0.20833 | 120 | 0.70833
Daudkandi | 135 | 0.54167 | 131 | 0.41667 | Thakurgaon | 136 | 0.20833 | 121 | 0.79167
B.Baria | 135 | 0.25 | 133 | 0.54167 | Palashbari | 135 | 0.20833 | 124 | 0.33333
Ramganj | 131 | 0.625 | 128 | 0.79167 | Barapukuria | 143 | 0.125 | 134 | 0.77083
Chaddagram | 135 | 0.70833 | 133 | 0.33333 | Panchagar | 135 | 0.16667 | 119 | 0.54167
PHP | 134 | 0.58333 | 129 | 0.33333 | Joldhaka | 140 | 0.20833 | 122 | 0.375
Madanhat | 138 | 0.79167 | 129 | 0.375 | Kurigram | 138 | 0.25 | 125 | 0.77083
Hathazari | 136 | 0.77083 | 130 | 0.16667

## L-Curve
Date | 2020-02-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 201 | 5174 | 1896 | 7070 |  |  |  | QF-LDC-12
0:30 | 280.5 | 5084 | 1695.5 | 6779.5 | Date: | 2020-02-26
1:00 | 360 | 4994 | 1495 | 6489
1:30 | 336.5 | 4855.5 | 1479.5 | 6335
2:00 | 313 | 4717 | 1464 | 6181
2:30 | 287.5 | 4557 | 1478.5 | 6035.5 | [5 empty] | Gen. at Eve. Peak | 9075 | 9075 MW (19:00 )
3:00 | 262 | 4397 | 1493 | 5890 | [6 empty] | 19:00
3:30 | 191 | 4394.5 | 1467 | 5861.5 | [5 empty] | Gen. at Day Peak | 7468.8 | 7468.8 MW (12:00 )
4:00 | 120 | 4392 | 1441 | 5833 | [6 empty] | 12:00
4:30 | 115 | 4323.5 | 1451 | 5774.5 | [5 empty] | Highest Generation | 9075
5:00 | 110 | 4255 | 1461 | 5716 | [6 empty] | 19:00
5:30 | 155 | 4384 | 1445 | 5829
6:00 | 200 | 4513 | 1429 | 5942
6:30 | 210 | 4702.8 | 1563 | 6265.8
7:00 | 220 | 4892.6 | 1697 | 6589.6
7:30 | 170 | 5024.5385 | 1870.5 | 6895.0385
8:00 | 120 | 5156.477 | 2044 | 7200.477
8:30 | 110 | 5175.2745 | 2031 | 7206.2745
9:00 | 100 | 5194.072 | 2018 | 7212.072
9:30 | 70 | 5255.536 | 2002.6 | 7258.136
10:00 | 40 | 5317 | 1987.2 | 7304.2
10:30 | 70 | 5318 | 1988.25 | 7306.25
11:00 | 100 | 5319 | 1989.3 | 7308.3
11:30 | 100 | 5376.25 | 2012.3 | 7388.55
12:00 | 100 | 5433.5 | 2035.3 | 7468.8
12:30 | 130 | 5505.806 | 2038.5 | 7544.306
13:00 | 160 | 5578.112 | 2041.7 | 7619.812
13:30 | 110 | 5364.756 | 2025.1 | 7389.856
14:00 | 60 | 5151.4 | 2008.5 | 7159.9
14:30 | 40 | 5087.85 | 1991.3 | 7079.15
15:00 | 20 | 5024.3 | 1974.1 | 6998.4
15:30 | 30 | 5063.25 | 1965.65 | 7028.9
16:00 | 40 | 5102.2 | 1957.2 | 7059.4
16:30 | 25 | 4993.45 | 1961.2 | 6954.65
17:00 | 10 | 4884.7 | 1965.2 | 6849.9
17:30 | 37.5 | 5154.35 | 2090.65 | 7245
18:00 | 65 | 5424 | 2216.1 | 7640.1
18:30 | 189 | 5880.5 | 2477.05 | 8357.55
19:00 | 313 | 6337 | 2738 | 9075
19:30 | 277 | 6262 | 2772 | 9034
20:00 | 215 | 6223 | 2840 | 9063 |  |  |  | Executive Engineer
20:30 | 149.5 | 6079 | 2850 | 8929 |  |  |  | Network Operation Division
21:00 | 84 | 5935 | 2860 | 8795
21:30 | 69.5 | 5733 | 2725.5 | 8458.5
22:00 | 55 | 5531 | 2591 | 8122 |  |  |  |  | Page 6 of 7
22:30 | 112 | 5430 | 2385 | 7815
23:00 | 169 | 5329 | 2179 | 7508
23:30 | 185 | 5251.5 | 2037.5 | 7289
24:00 | 201 | 5174 | 1896 | 7070
9075 MW (19:00 )
7468.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-02-26 |  | Energy | 174571847
[10 empty] | 2020-02-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3865 | 344 | 2039 | 554 | 371 | 67 | 0 | 0 | 82
0:30 | 3697.5 | 261.5 | 2008.5 | 416 | 370.5 | 68.5 | 0 | 0 | 83 | Date: | 2020-02-26
1:00 | 3530 | 179 | 1978 | 278 | 370 | 70 | 0 | 0 | 84
1:30 | 3516 | 180 | 1905 | 214 | 370 | 70 | 0 | 0 | 80 | [7 empty] | Total Energy | 174.5718 | Total Energy Gen 174.572 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 174.572 MKWHr
2:00 | 3502 | 181 | 1832 | 150 | 370 | 70 | 0 | 0 | 76 | [7 empty] | Energy not Served | 0
2:30 | 3474 | 181 | 1730 | 135 | 370.5 | 70 | 0 | 0 | 75 | [7 empty] | Energy Requirement | 174.5718
3:00 | 3446 | 181 | 1628 | 120 | 371 | 70 | 0 | 0 | 74
3:30 | 3443 | 181 | 1602.5 | 120 | 370.5 | 69.5 | 0 | 0 | 75 | [6 empty] | Shortage
4:00 | 3440 | 181 | 1577 | 120 | 370 | 69 | 0 | 0 | 76
4:30 | 3450 | 181 | 1516.5 | 120 | 362 | 69 | 0 | 0 | 76
5:00 | 3460 | 181 | 1456 | 120 | 354 | 69 | 0 | 0 | 76
5:30 | 3493 | 181 | 1532.5 | 144.5 | 332 | 69 | 0 | 0 | 77
6:00 | 3526 | 181 | 1609 | 169 | 310 | 69 | 0 | 0 | 78
6:30 | 3580 | 283.5 | 1713.5 | 232 | 310 | 68.5 | 0 | 0 | 78 |  |  |  |  | Coal
7:00 | 3634 | 386 | 1818 | 295 | 310 | 68 | 0 | 0 | 78
7:30 | 3720.5 | 484.5 | 1841 | 371 | 310 | 68 | 16 | 0 | 83 |  |  |  | Oil |  |  |  | ,
8:00 | 3807 | 583 | 1864 | 447 | 310 | 68 | 32 | 0 | 88
8:30 | 3745 | 583 | 1835.5 | 540 | 310 | 68 | 37 | 0 | 84
9:00 | 3683 | 583 | 1807 | 633 | 310 | 68 | 42 | 0 | 80
9:30 | 3732.5 | 585.5 | 1791.5 | 646 | 310 | 68 | 33.5 | 0 | 81
10:00 | 3782 | 588 | 1776 | 659 | 310 | 68 | 25 | 0 | 82
10:30 | 3763.5 | 588 | 1793.5 | 651 | 310.5 | 76.5 | 25 | 0 | 81
11:00 | 3745 | 588 | 1811 | 643 | 311 | 85 | 25 | 0 | 80
11:30 | 3764 | 588.5 | 1842.5 | 677 | 311 | 81.5 | 25 | 0 | 76
12:00 | 3783 | 589 | 1874 | 711 | 311 | 78 | 25 | 0 | 72
12:30 | 3695.5 | 589 | 1859.5 | 899.5 | 310.5 | 73 | 25 | 0 | 72
13:00 | 3608 | 589 | 1845 | 1088 | 310 | 68 | 25 | 0 | 72
13:30 | 3608 | 589 | 1845 | 1088 | 310 | 68 | 25 | 0 | 72
14:00 | 3608 | 589 | 1845 | 1088 | 310 | 68 | 25 | 0 | 72
14:30 | 3554.5 | 589 | 1731.5 | 946 | 310.5 | 67.5 | 25 | 0 | 74
15:00 | 3501 | 589 | 1618 | 804 | 311 | 67 | 25 | 0 | 76
15:30 | 3531 | 589 | 1645 | 778 | 311.5 | 67 | 25 | 0 | 75
16:00 | 3561 | 589 | 1672 | 752 | 312 | 67 | 25 | 0 | 74
16:30 | 3480.5 | 589 | 1678 | 715.5 | 321 | 66.5 | 25 | 0 | 74
17:00 | 3400 | 589 | 1684 | 679 | 330 | 66 | 25 | 0 | 74
17:30 | 3485.5 | 655 | 1694 | 881.5 | 340 | 66 | 33.5 | 0 | 88
18:00 | 3571 | 721 | 1704 | 1084 | 350 | 66 | 42 | 0 | 102
18:30 | 3651.5 | 777 | 1843 | 1487.5 | 363.5 | 66.5 | 63.5 | 0 | 105
19:00 | 3732 | 833 | 1982 | 1891 | 377 | 67 | 85 | 0 | 108
19:30 | 3753 | 834 | 1865 | 1920 | 390 | 67 | 97 | 0 | 108
20:00 | 3828 | 833 | 1893 | 1833 | 401 | 67 | 102 | 0 | 106
20:30 | 3849 | 833 | 1952.5 | 1636 | 400.5 | 67 | 85 | 0 | 106
21:00 | 3870 | 833 | 2012 | 1439 | 400 | 67 | 68 | 0 | 106
21:30 | 3849 | 833 | 1956 | 1199 | 385.5 | 67 | 68 | 0 | 101
22:00 | 3828 | 833 | 1900 | 959 | 371 | 67 | 68 | 0 | 96
22:30 | 3831.5 | 711 | 1951 | 756.5 | 371 | 67 | 34 | 0 | 93
23:00 | 3835 | 589 | 2002 | 554 | 371 | 67 | 0 | 0 | 90
23:30 | 3850 | 466.5 | 2020.5 | 554 | 371 | 67 | 0 | 0 | 86 | Max Temp. in Dhaka |  | 27° C
24:00 | 3865 | 344 | 2039 | 554 | 371 | 67 | 0 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 174.572 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 174.572 MKWHr
Note on W13: Author:

## Generation
g | 2020-02-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 45 | 38 | 28 | 28 | 27 | 27 | 26 | 26 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 627655
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0.4 | 0.6 | 4.6 | 9.1 | 14.8 | 14.7 | 6.1 | 4.8 | 3.2 | 3.7 | 1.6 | [9 empty] | 69120
6 | Sikalbaha 225MW CCPP (Gas) | [21 empty] | 71 | 86 | 86 | 85 | 86 | 358729
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 139 | 141 | 141 | 146 | 146 | 140 | 151 | 148 | 140 | 104 | 139 | 141 | 105 | 104 |  | 103 | 103 | 104 | 104 | 104 | 104 | 104 | 3107338
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 13 | 34 | 34 |  |  |  |  | 64399
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 |  | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 267636
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 902000
21 | Ghorasal Repowered CCPP Unit-3 | 174 | 174 | 165 | 148 | 148 | 148 | 169 | 178 | 178 | 178 | 179 | 155 | 134 | 134 | 135 | 134 | 134 | 133 |  | 165 | 178 | 178 | 178 | 178 | 178 | 178 | 4081300
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 290 | 286 | 275 | 275 | 274 | 291 | 314 | 335 | 318 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 270 | 270 |  | 290 | 290 | 290 | 290 | 289 | 290 | 290 | 7002545
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2087845
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 |  | 46 | 46 | 46 | 26 | 26 | 23 | 23 | 370008
33 | Ashuganj 225 MW CCPP | 169 | 181 | 199 | 200 | 200 | 200 | 189 | 202 | 192 | 202 | 202 | 181 | 195 | 164 | 164 | 179 | 152 | 195 |  | 151 | 145 | 134 | 147 | 159 | 165 | 158 | 4358000
34 | Ashuganj 450 MW CCPP(South) | 265 | 255 | 260 | 255 | 260 | 275 | 260 | 290 | 265 | 320 | 305 | 340 | 290 | 290 | 290 | 305 | 310 | 290 |  | 305 | 305 | 305 | 320 | 305 | 320 | 315 | 7252500
| Ashuganj 450 MW CCPP(North) | 300 | 310 | 265 | 265 | 265 | 280 | 290 | 320 | 300 | 375 | 330 | 360 | 315 | 315 | 315 | 330 | 290 | 295 |  | 305 | 305 | 305 | 315 | 305 | 320 | 310 | 7729400
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 136800
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 90 | 90 | 90 | 90 | 91 | 90 | 91 | 90 | 91 | 90 |  | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 2147450
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 356 | 338 | 338 | 342 | 337 | 357 | 380 | 352 | 352 | 349 | 354 | 387 | 369 | 339 | 348 | 357 | 265 | 359 |  | 360 | 334 | 334 | 341 | 335 | 336 | 351 | 8438790
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 380 | 380 | 380 | 300 | 350 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 370 | 370 | 370 | 360 | 360 |  | 450 | 420 | 420 | 420 | 420 | 400 | 400 | 9308000
41 | Haripur 360MW CCPP(HPL) | 328 | 327 | 288 | 288 | 256 | 299 | 337 | 337 | 304 | 305 | 304 | 324 | 345 | 263 | 264 | 295 | 338 | 349 |  | 355 | 334 | 334 | 323 | 318 | 330 | 335 | 7518000
42 | RPCL 210MW CCPP | 155 | 156 | 156 | 157 | 158 | 157 | 157 | 157 | 155 | 153 | 152 | 152 | 139 | 139 | 139 | 138 | 140 | 140 |  | 142 | 142 | 143 | 142 | 144 | 144 | 145 | 3471040
43
44 | Fenchugonj CCPP Phase-1 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 71 | 70 | 70 | 72 | 72 | 71 | 70 | 72 | 72 | 71 | 70 |  | 69 | 71 | 72 | 72 | 72 | 70 | 70 | 1685000
45 | Fenchugonj CCPP Phase-2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1763880
46 | Shajibazar 330 MW CCPP | 148 | 146 | 145 | 147 | 152 | 155 | 146 | 154 | 153 | 153 | 153 | 164 | 148 | 152 | 146 | 145 | 145 | 154 |  | 145 | 148 | 143 | 150 | 146 | 146 | 150 | 3468000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 45 | 45 | 45 | 65 | 66 | 65 | 65 | 64 | 63 | 62 | 65 | 45 | 45 | 45 | 65 | 64 |  | 67 | 55 | 55 | 55 | 55 | 54 | 65 | 1380096
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 50 | 10 | 10 | 10 | 10 | 40 | 77 | 80 | 80 | 77 | 77 | 80 | 20 | 20 | 20 | 50 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1316160
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | [19 empty] | 12 | 52 | 53 | 53 | 55 | 53 | 53 | 254980
51 | Sylhet 20 MW GTPP | 20 | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 303000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 190620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235081
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 11 | 11 | 11 | 11 | 46 | 48 | 48 | 47 | 50 | 51 | 51 | 53 | 53 | 53 | 53 | 32 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1021800
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 492960
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 300 | 290 | 300 | 300 | 310 | 320 | 310 | 315 | 300 | 315 | 325 | 295 | 265 | 290 | 310 | 270 | 300 |  | 305 | 300 | 265 | 300 | 270 | 280 | 310 | 7599000
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 430992
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 427608
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [11 empty] | 17 | 17 | 22 | 22 | 22 | 22 | 22 | 298224
63 | Impoprt (Tripura) | 84 | 76 | 74 | 76 | 76 | 78 | 78 | 88 | 80 | 82 | 80 | 72 | 72 | 82 | 76 | 74 | 74 | 102 |  | 108 | 108 | 106 | 106 | 96 | 90 | 82 | 2025600
64 | Malancha, Ctg. EPZ (United) | 40 | 33 | 42 | 42 | 42 | 42 | 41 | 10 | 2 | 2 | 2 | 2 | 9 | 6 | 6 | 6 | 0 | 12 |  | 17 | 20 | 30 | 30 | 38 | 38 | 40 | 536640
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [5 empty] | 10 | 13 | 13 | 13 | 371592
66 | Feni 11 MW PP (Doreen) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 0 | 11 | 11 | 11 | 11 | 11 | 182700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 26 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 639400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 21 | 18 | 19 | 19 | 8 | 14 | 14 | 14 | 14 | 14 | 14 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 43040
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 28 | 28 | 0 | 0 | 0 | 0 | [7 empty] | 16 | 29 | 29 | 31 | 28 | 30 | 32 | 389340
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 688600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 808400
73 | Ghorashal 108MW PP (Regent)
Feni Lanka Power
| Chowmuhani 113 MW | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 20 | [5 empty] | 12 | 32 | 32 | 32 | 32 | 34 | 70 | 84 | 90 | 100 | 80 | 60 |  | 90 | 100 | 100 | 100 | 55 | 50 | 20 | 1204800
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 8 |  |  |  |  | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 |  | 83 | 83 | 90 | 82 | 59 | 59 | 58 | 1135680
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.1 | 0.277 | 0.272 | 1.2 | 1.2 | 0.6 | 0.212 | 1 | 0.2 | [11 empty] | 5760
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 10 |  | 45 | 16 | 16 | 15 | 15 | 15 |  | 146280
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 8 | 40 | 40 |  |  |  |  | 63461
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3476596
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 1 | 15 | 15 | 15 | 15 | 72 | 82 | 46 | 7 | 7 | 28 |  | 100 | 100 | 75 | 50 | 15 |  |  | 599040
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 51 | 51 | 10 | 10 | 10 | 10 | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 35 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1072800
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 38 | 43 | 43 | 43 | 43 | 43 | 51 | 43 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 994120
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 7 | 24 | 24 | 24 | 24 | 24 | 64 | 64 | 16 | 16 | 16 | 74 |  | 102 | 50 | 50 | 50 | 16 |  |  | 587808
95 | Patenga 50MW PP (Baraka) | [9 empty] | 1 | 12 | 12 | 23 | 46 |  |  |  | 17 |  | 50 | 50 | 50 | 50 | 35 |  |  | 316320
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 5 | 12 |  | 38 | 70 | 50 |  |  |  |  | 141120
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 15 | 15 | 15 | 15 | 15 |  | 35 | 30 | 30 |  |  |  |  | 166093
100 | Manikganj 55 MW PP (Northern) | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 55 | 17 | 17 |  |  |  |  | 175250
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 100 | 130 | 163 | 130 | 130 | 110 | 130 | 163 | 130 | 110 | 110 | 110 | 100 | 100 |  | 163 | 100 | 100 | 100 | 100 | 163 | 163 | 3373051
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.6 | 1.2 | 1.7 | 2 | 2.2 | 1.8 | 1.6 | 0.9 | 0.5 | 0.1 | [9 empty] | 10850
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 414000
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 7 |  | 50 | 85 | 50 | 7 |  |  |  | 177600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 18 | [5 empty] | 2 | 33 | 71 | 83 | 39 | 32 | 42 | 50 | 50 | 45 | 45 | 50 |  | 133 | 107 | 123 | 92 | 67 | 49 | 22 | 1064160
115 | Juldah 100 MW PP Unit-3 (Acorn) | [12 empty] | 50 | 30 | 10 | 10 | 10 | 56 |  | 90 | 90 | 70 | 20 |  |  |  | 351360
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 18 |  | 38 | 50 | 40 | 19 |  |  |  | 162254
118 | Bibiyana-III 400 MW CCPP | 235 | 233 | 235 | 234 | 234 | 234 | 232 | 233 | 233 | 233 | 234 | 234 | 235 | 234 | 236 | 234 | 235 | 233 |  | 234 | 235 | 236 | 234 | 233 | 234 | 232 | 5628000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 57 | 115 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 97 | 115 | 115 | 115 | 75 |  |  | 1356000
| Anwara 300 MW PP (United) | 52 | [5 empty] | 50 | 50 | 87 | 140 | 157 | 190 | 301 | 160 | 125 | 125 | 88 | 222 |  | 300 | 301 | 301 | 301 | 233 | 105 |  | 3053564
120 | Eastern Zone Total | 4994 | 4717 | 4397 | 4392 | 4255 | 4513 | 4892.6 | 5156.477 | 5194.072 | 5317 | 5319 | 5433.5 | 5578.112 | 5151.4 | 5024.3 | 5102.2 | 4884.7 | 5424 |  | 6337 | 6262 | 6223 | 5935 | 5531 | 5329 | 5174 | 125891235
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 18 | 32 | 32 | 32 | 32 | 66 | 66 | 34 | 16 | 16 | 60 |  | 115 | 115 | 115 | 66 | 49 |  |  | 767040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 64 | 64 | 64 | 64 | 64 |  |  | 286368
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 21 | 21 | 21 | 21 | 21 | 21 | 36 | 55 | 73 | 75 | 75 | 75 | 75 | 75 | 73 | 71 | 73 | 24 |  | 95 | 96 | 95 | 96 | 73 | 71 | 73 | 1406755
| Bhola 225 MW CCPP | 70 | 71 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 15 | 15 | 15 | 15 | 15 | 88 |  | 88 | 88 | 88 | 89 | 90 | 91 | 90 | 1807039
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 15 | 14 | 14 | 14 | 14 | 13 | 13 | 12 | 14 | 14 | 14 | 14 | 13 | 10 | 12 | 18 |  | 19 | 21 | 21 | 21 | 20 | 17 | 16 | 353500
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 179 | 181 | 181 | 181 | 181 | 181 | 386 | 583 | 583 | 588 | 588 | 589 | 589 | 589 | 589 | 589 | 589 | 721 |  | 833 | 834 | 833 | 833 | 833 | 589 | 344 | 12157091
147 | Bheramara 410 MW CCPP | 215 | 225 | 260 | 270 | 285 | 295 | 310 | 355 | 370 | 355 | 355 | 355 | 340 | 345 | 340 | 345 | 345 | 345 |  | 365 | 360 | 360 | 345 | 320 | 315 | 315 | 7835040
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 90 | 90 | 91 | 92 | 110 | 114 |  | 117 | 120 | 121 | 120 | 91 | 91 | 91 | 2278254
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 264 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 236 |  | 260 | 270 | 280 | 280 | 280 | 280 | 280 | 5909400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 160 | 160 | 160 | 160 | 160 | 130 | 155 | 180 | 180 | 170 | 170 | 200 | 214 | 180 | 160 | 160 | 170 | 160 |  | 190 | 180 | 180 | 180 | 180 | 160 | 200 | 4453364
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 386 | 394 | 334 | 355 | 375 | 340 | 342 | 245 | 248 | 247 | 247 | 250 | 249 | 273 | 273 | 274 | 273 |  | 273 | 269 | 323 | 435 | 374 | 416 | 414 | 7857218
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 5 | 5 | 5 | 5 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 374880
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 270900
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | [11 empty] | 5 | 11 | 11 | 11 | 11 | 11 | 8 | 121176
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 32 | 42 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 42 |  | 85 | 97 | 102 | 68 | 68 |  |  | 623580
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | 13 |  |  |  |  | 12 | 35 | 45 | 70 | 70 | 70 | 80 | 108 | 109 | 109 | 109 | 70 | 60 |  | 100 | 109 | 109 | 109 | 109 | 109 | 35 | 1700832
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 30 |  | 100 | 109 | 109 | 114 |  |  |  | 451200
177 | Sympa Solar Power 8MW | [9 empty] | 2.2 | 2.3 | 8.3 | 6.7 | 2.5 | 3.1 | 3.2 | 1.2 | 0.1 | [8 empty] | 26975
178
178