## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-02 | Monday
|  | Date (day): | 2020-03-02 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12459.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15365 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-01 | 2020-03-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 149 | 149 | 150 | 160
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 177 | 260 | 300 | 380
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 70 | 35 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 362 | 350 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 333 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 86 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 130 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 29 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 90 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 12 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 57 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 30 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 119 | 141 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1999 | 2539 | 3572 | 4264 | 913 | 633
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.6 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 26 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 67 | 68 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 210 | 210
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 116 | 100 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 80 | 90 | 90 |  | 10 | Engine problem
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 22 | 20 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 100 | 214 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 663.7 | 868 | 1485 | 1620 | 410 | 108
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 80 | 100 | 100 |  |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 315 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 46 | 46 | 46 | 46
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 43 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 24 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 122 | 102 | 119
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1340 | 1316 | 1647 | 2328 | 506 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 176 | 162 | 150 | 160 | 42 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 91 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 16 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 88 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 365.3 | 374 | 483.6 | 592 | 42 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 72 | 72 | 72 | 72
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22 |  | 68 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 144 | 144 | 150 | 150 |  | 180 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 48 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 60 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 24 | 231 | 130 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 235 | 235 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1244 | 1431 | 1419 | 1439 | 0 | 413
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 634 | 884 | 650 | 898
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 385 | 390 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1035 | 1389 | 1345 | 2144 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 20 | 21 |  | 12 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 68 | 90 | 100 | 100 |  | 94 | GT-2 under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 0 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 330 | 442 | 500 | 600 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 423 | 553 | 779 | 956 | 0 | 106
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 190 | 185 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 386 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 8 | 10 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 68 | 68 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 17 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 822 | 802 | 1228 | 1495 | 611 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 88 | 87 | 100 | 100
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 270 | 285 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 75 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 399.6 | 447 | 501 | 527 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 8291.6 | 9719 | 12459.6 | 15365 | 2482 | 1438
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7806.1673 | 9150 | 11730.1513 | 14465.4543
A. |  | 2020-03-01 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 9719 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6044 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9719 | MW
3 | Day peak Generation : |  |  | 8291.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9150 | MW
4 | Evening peak Generation : |  |  | 9719 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 187.5492 | MKWHr | By Solar | 0.17155 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 136.5477 | MKWHr |  | By Oil: | 16.6782 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.8432 | MKWHr |  | By Hydro: | 1.566 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2482 | MW | Dhaka | 3367 | 3367 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1438 | MW | Chittagong | 981 | 981 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3920 | MW | Khulna | 1118 | 1118 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1102.66 | MMCFD |  |  | Rajshahi | 976 | 976 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 126453589.832 | ii) Oil : | Taka | 117831751.63 | Comilla | 748 | 748 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 40889021.33 | Total | Taka | 285174362.792 | Mymensingh | 768 | 768 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.1625 | MKWHr. | Sylhet | 350 | 350 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -12 | MW (E to W) at | 19:00 | hrs | Barisal | 223 | 223 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -248 | MW at | 1:00 | hrs | Rangpur | 619 | 619 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.4° C |  |  | Total | 9150 | 9150 |  | 0
B. |  | 2020-03-02 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 32.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15365 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 5365 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 192.9717 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6308 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.4327 | MKWHr. | ii) HVDC Flow at Peak Time |  | 884 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3098 | MKWHr. | iii) Maximum HVDC Flow : |  | 887 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.67 |  | (b) Today: | 89.55 |  | (c) Rule Curve: |  | 92.84
.

## YesterdayGen
2020-03-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 159 | 0 | 0 | 185 | 0 | 35 | 353 | 315 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 25 | 32 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 202 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 80 | 0 | 285 | 265 | 184 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 84 | 199 | 95 | 17 | 0 | 70 | 22 | 51 | 50 | 100 | 136 | 45 | 79 | 0 | 140 | 0 | 0 | 0 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 90 | 0 | 270 | 0 | 0 | 170 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 |  | 5032 | 1809 | 6841 | 3816 | 203 | 1909 | 232 | 530 | 67 | 0 | 84 | 0 | 0 | 89.69
2:00 | 37 | 158 | 0 | 0 | 177 | 0 | 35 | 340 | 314 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 25 | 32 | 0 | 0 | 28 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 80 | 0 | 285 | 265 | 183 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 21 | 78 | 199 | 50 | 17 | 0 | 71 | 22 | 5 | 50 | 100 | 138 | 45 | 50 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 85 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 |  | 4675 | 1854 | 6529 | 3631 | 200 | 1786 | 170 | 596 | 68 | 0 | 78 | 0 | 0 | 89.69
3:00 | 37 | 158 | 0 | 0 | 177 | 0 | 35 | 338 | 315 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 25 | 32 | 0 | 0 | 28 | 40 | 120 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 38 | 0 | 80 | 0 | 285 | 265 | 182 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 21 | 76 | 200 | 30 | 17 | 0 | 70 | 22 | 5 | 5 | 100 | 132 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 89 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 |  | 4523 | 1858 | 6381 | 3590 | 201 | 1677 | 150 | 619 | 68 | 0 | 76 | 0 | 0 | 89.68
4:00 | 37 | 99 | 0 | 0 | 170 | 0 | 35 | 340 | 263 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 25 | 32 | 0 | 0 | 28 | 40 | 120 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 80 | 0 | 285 | 265 | 161 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 76 | 200 | 16 | 17 | 0 | 71 | 22 | 5 | 5 | 100 | 134 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 89 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4229 | 1825 | 6054 | 3442 | 200 | 1503 | 136 | 629 | 68 | 0 | 76 | 0 | 0 | 89.68
5:00 | 37 | 99 | 0 | 0 | 170 | 0 | 35 | 338 | 263 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 32 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 80 | 0 | 285 | 265 | 168 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 78 | 200 | 16 | 17 | 0 | 70 | 22 | 5 | 5 | 100 | 136 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 4251 | 1793 | 6044 | 3448 | 200 | 1487 | 136 | 628 | 67 | 0 | 78 | 0 | 0 | 89.67
6:00 | 37 | 99 | 0 | 0 | 170 | 0 | 60 | 357 | 264 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 32 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 80 | 0 | 320 | 325 | 182 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 80 | 200 | 16 | 17 | 0 | 71 | 22 | 5 | 5 | 100 | 143 | 56 | 5 | 0 | 80 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 88 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 |  | 4458 | 1862 | 6320 | 3647 | 199 | 1531 | 136 | 643 | 67 | 17 | 80 | 0 | 0 | 89.67
7:00 | 37 | 99 | 0 | 0 | 170 | 0 | 60 | 385 | 296 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 16 | 32 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 216 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 80 | 0 | 320 | 325 | 182 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 16 | 0 | 0 | 21 | 82 | 201 | 28 | 17 | 0.1 | 70 | 22 | 5 | 5 | 130 | 143 | 66 | 5 | 0 | 80 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 234 | 2 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 |  | 632 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 315 |  | 4694.6 | 2432.2 | 7126.8 | 3707 | 632 | 1759 | 167 | 685 | 67 | 25 | 82 | 2.8 | 0 | 89.66
8:00 | 37 | 135 | 0 | 0 | 170 | 0 | 60 | 357 | 364 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 16 | 32 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 0 | 80 | 0 | 285 | 295 | 182 | 8 | 90 | 42 | 5 | 0 | 25 | 0 | 0 | 0 | 16 | 5 | 33 | 21 | 88 | 201 | 48 | 17 | 0 | 72 | 22 | 45 | 30 | 130 | 134 | 65 | 79 | 0 | 80 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 2 | 0 | 36 | 7.4 | 0 | 0 | 0 | 234 | 70 | 0 | 0 | 1.7 | 16 | 0 | 0 | 0 | 0 |  | 632 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 87 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 4 | 0 | 1.8 | 35 | 329 |  | 5115.1 | 2475.8 | 7590.9 | 3763 | 632 | 1925 | 397 | 666 | 67 | 42 | 88 | 10.9 | 0 | 89.66
9:00 | 37 | 149 | 0 | 0 | 155 | 0 | 70 | 338 | 341 |  | 0 | 380 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 25 | 25 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 80 | 0 | 285 | 300 | 185 | 8 | 90 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 5 | 33 | 21 | 88 | 196 | 48 | 17 | 1.3 | 72 | 22 | 45 | 50 | 100 | 139 | 63 | 79 | 0 | 24 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 68 | 12.8 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 3.1 | 16 | 0 | 0 | 0 | 0 |  | 632 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 88 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 34 | 0 | 3.8 | 100 | 328 |  | 5164.2 | 2599.8 | 7764 | 3753 | 632 | 1895 | 572 | 676 | 67 | 60 | 88 | 21 | 0 | 89.65
10:00 | 37 | 148 | 0 | 0 | 177 | 0 | 70 | 344 | 335 |  | 0 | 380 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 16 | 16 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 204 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 290 | 305 | 192 | 8 | 90 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 92 | 181 | 48 | 17 | 1.8 | 72 | 22 | 45 | 50 | 100 | 138 | 61 | 79 | 0 | 18 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 98 | 17.1 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 4.2 | 16 | 0 | 0 | 0 | 0 |  | 632 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 90 | 0 | 260 | 0 | 0 | 190 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 35 | 0 | 5.2 | 109 | 331 |  | 5220.1 | 2619.2 | 7839.3 | 3739 | 632 | 1920 | 612 | 681 | 67 | 68 | 92 | 28.3 | 0 | 89.65
11:00 | 37 | 149 | 0 | 0 | 178 | 0 | 70 | 355 | 336 |  | 0 | 400 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 16 | 0 | 0 | 27 | 40 | 120 | 0 | 0 | 205 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 80 | 0 | 290 | 310 | 192 | 8 | 90 | 42 | 5 | 0 | 42 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 96 | 181 | 48 | 17 | 2.1 | 72 | 22 | 45 | 47 | 100 | 140 | 61 | 79 | 0 | 18 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 103 | 18.8 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 4.9 | 67 | 0 | 0 | 0 | 0 |  | 632 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 11 | 90 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 35 | 0 | 6.2 | 109 | 330 |  | 5371.8 | 2633.2 | 8005 | 3813 | 632 | 1921 | 686 | 690 | 67 | 68 | 96 | 32 | 0 | 89.64
12:00 | 37 | 149 | 0 | 0 | 177 | 0 | 70 | 362 | 335 |  | 0 | 400 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 22 | 25 | 8 | 0 | 0 | 27 | 40 | 115 | 0 | 0 | 218 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 100 | 0 | 325 | 330 | 205 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 102 | 176 | 48 | 17 | 2.3 | 72 | 22 | 48 | 47 | 130 | 144 | 59 | 79 | 0 | 24 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 119 | 18.6 | 0 | 0 | 0 | 235 | 115 | 0 | 0 | 5.1 | 100 | 0 | 0 | 0 | 0 |  | 634 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 88 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 35 | 0 | 6.6 | 109 | 330 |  | 5612 | 2679.6 | 8291.6 | 3926 | 634 | 1977 | 797 | 688 | 67 | 68 | 102 | 32.6 | 0 | 89.64
13:00 | 37 | 148 | 0 | 0 | 178 | 0 | 70 | 359 | 354 |  | 0 | 420 | 150 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 27 | 40 | 115 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 9 | 0 | 100 | 0 | 315 | 315 | 185 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 100 | 161 | 48 | 17 | 2.2 | 72 | 22 | 47 | 50 | 130 | 132 | 61 | 79 | 0 | 24 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 17 | 0 | 121 | 0 | 0 | 0 | 0 | 235 | 115 | 0 | 0 | 4.8 | 173 | 0 | 0 | 0 | 0 |  | 636 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 88 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 6.6 | 70 | 330 |  | 5758 | 2585.6 | 8343.6 | 3794 | 636 | 1987 | 990 | 688 | 67 | 68 | 100 | 13.6 | 0 | 89.63
14:00 | 37 | 149 | 0 | 0 | 178 | 0 | 70 | 344 | 306 |  | 0 | 225 | 150 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 115 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 5 | 0 | 100 | 0 | 275 | 280 | 196 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 104 | 162 | 48 | 17 | 1.8 | 73 | 22 | 48 | 50 | 130 | 138 | 59 | 79 | 0 | 145 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 85 | 0 | 0 | 0 | 0 | 235 | 115 | 0 | 0 | 4.1 | 173 | 0 | 0 | 0 | 0 |  | 636 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 91 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 35 | 0 | 6.1 | 70 | 332 |  | 5525.9 | 2570.1 | 8096 | 3852 | 636 | 1721 | 943 | 693 | 67 | 68 | 104 | 12 | 0 | 89.63
15:00 | 37 | 149 | 0 | 0 | 178 | 0 | 70 | 350 | 307 |  | 0 | 270 | 150 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 115 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 2 | 0 | 100 | 0 | 270 | 265 | 184 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 102 | 159 | 48 | 17 | 1.5 | 73 | 22 | 48 | 50 | 130 | 138 | 60 | 20 | 0 | 207 | 19 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 236 | 96 | 0 | 0 | 3.3 | 159 | 0 | 0 | 0 | 0 |  | 637 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 91 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 35 | 0 | 4.1 | 70 | 332 |  | 5491.8 | 2474.1 | 7965.9 | 3869 | 637 | 1659 | 904 | 693 | 67 | 26 | 102 | 8.9 | 0 | 89.62
16:00 | 37 | 149 | 0 | 0 | 178 | 0 | 70 | 340 | 275 |  | 0 | 350 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 3 | 0 | 100 | 0 | 260 | 265 | 184 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 21 | 94 | 161 | 48 | 0 | 0.9 | 73 | 22 | 48 | 50 | 110 | 140 | 45 | 20 | 0 | 229 | 19 | 0 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 234 | 57 | 0 | 0 | 2 | 88 | 0 | 0 | 0 | 0 |  | 637 | 0 | 335 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 270 | 0 | 0 | 160 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 20 | 0 | 2 | 70 | 332 |  | 5312.9 | 2461 | 7773.9 | 3811 | 637 | 1699 | 743 | 692 | 68 | 25 | 94 | 4.9 | 0 | 89.62
17:00 | 37 | 148 | 0 | 0 | 178 | 0 | 70 | 350 | 244 |  | 0 | 350 | 120 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 19 | 14 | 0 | 100 | 0 | 265 | 265 | 185 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 92 | 161 | 48 | 0 | 0.3 | 73 | 22 | 48 | 50 | 110 | 140 | 45 | 20 | 0 | 126 | 19 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 236 | 57 | 0 | 0 | 0.7 | 70 | 0 | 0 | 0 | 0 |  | 636 | 0 | 375 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 297 | 0 | 0 | 160 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 35 | 332 |  | 5099 | 2470.1 | 7569.1 | 3788 | 636 | 1684 | 555 | 719 | 68 | 25 | 92 | 2.1 | 0 | 89.61
18:00 | 37 | 149 | 0 | 0 | 178 | 0 | 70 | 344 | 244 |  | 0 | 400 | 120 | 36 | 0 | 3 | 0 | 0 | 0 | 0 | 32 | 48 | 0 | 5 | 0 | 0 | 2 | 17 | 17 | 0 | 22 | 25 | 15 | 25 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 5 | 6 | 19 | 10 | 0 | 100 | 0 | 290 | 265 | 184 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 114 | 162 | 82 | 0 | 0 | 73 | 22 | 47 | 50 | 110 | 146 | 45 | 20 | 0 | 226 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 5 | 0 | 0 | 3 | 0 | 118 | 0 | 40 | 0 | 1 | 235 | 57 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 |  | 636 | 0 | 350 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 285 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 11 | 0 | 10 | 0 | 0.1 | 70 | 374 |  | 5505 | 2580.1 | 8085.1 | 3863 | 636 | 1754 | 876 | 749 | 68 | 25 | 114 | 0.1 | 0 | 89.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 149 | 0 | 0 | 260 | 0 | 35 | 350 | 333 |  | 0 | 450 | 150 | 86 | 29 | 30 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 20 | 0 | 0 | 12 | 35 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 25 | 26 | 19 | 22 | 0 | 80 | 0 | 315 | 315 | 184 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 122 | 162 | 91 | 17 | 0 | 72 | 22 | 48 | 50 | 130 | 144 | 65 | 60 | 0 | 231 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 16 | 0 | 141 | 0 | 80 | 0 | 24 | 235 | 88 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 |  | 884 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 87 | 0 | 285 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 0 | 75 | 0 | 0 | 109 | 442 |  | 6528 | 3191 | 9719 | 4166 | 884 | 1937 | 1660 | 814 | 68 | 68 | 122 | 0 | 0 | 89.6
19:30 | 37 | 149 | 0 | 0 | 260 | 0 | 30 | 340 | 303 |  | 0 | 450 | 150 | 93 | 15 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 20 | 46 | 19 | 26 | 0 | 80 | 0 | 310 | 315 | 185 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 120 | 159 | 95 | 17 | 0 | 72 | 22 | 48 | 50 | 130 | 143 | 64 | 76 | 0 | 236 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 80 | 0 | 0 | 235 | 85 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 |  | 884 | 0 | 375 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 10 | 11 | 87 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 466 |  | 6375 | 3237 | 9612 | 4146 | 884 | 1913 | 1575 | 838 | 68 | 68 | 120 | 0 | 0 | 0
20:00 | 37 | 189 | 0 | 0 | 260 | 0 | 30 | 339 | 304 |  | 0 | 450 | 150 | 78 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 65 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 43 | 19 | 29 | 0 | 80 | 0 | 310 | 315 | 185 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 116 | 158 | 95 | 17 | 0 | 72 | 22 | 50 | 50 | 130 | 144 | 64 | 79 | 0 | 173 | 19 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 20 | 0 | 0 | 234 | 80 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 |  | 884 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 505 |  | 6113 | 3278 | 9391 | 4098 | 884 | 1922 | 1356 | 879 | 68 | 68 | 116 | 0 | 0 | 89.6
21:00 | 37 | 189 | 0 | 0 | 278 | 0 | 30 | 343 | 282 |  | 0 | 450 | 150 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 65 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 80 | 0 | 310 | 315 | 186 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 116 | 140 | 95 | 22 | 0 | 72 | 22 | 51 | 50 | 130 | 144 | 65 | 79 | 0 | 230 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 234 | 65 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 |  | 887 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 109 | 504 |  | 6059 | 3235 | 9294 | 4152 | 887 | 1953 | 1189 | 878 | 68 | 51 | 116 | 0 | 0 | 89.59
22:00 | 37 | 189 | 0 | 0 | 280 | 0 | 30 | 339 | 282 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 39 | 0 | 80 | 0 | 315 | 315 | 184 | 8 | 90 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 112 | 139 | 95 | 22 | 0 | 70 | 22 | 51 | 50 | 130 | 146 | 65 | 79 | 0 | 160 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 235 | 48 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 |  | 887 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 406 |  | 5698 | 2972 | 8670 | 4056 | 887 | 1916 | 816 | 781 | 68 | 34 | 112 | 0 | 0 | 89.59
23:00 | 37 | 189 | 0 | 0 | 280 | 0 | 30 | 338 | 282 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 208 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 80 | 0 | 290 | 305 | 197 | 8 | 90 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 100 | 138 | 95 | 22 | 0 | 72 | 22 | 51 | 50 | 130 | 147 | 64 | 79 | 0 | 158 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 |  | 788 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 400 |  | 5451 | 2675 | 8126 | 4035 | 788 | 1877 | 467 | 775 | 67 | 17 | 100 | 0 | 0 | 89.58
24:00 | 37 | 189 | 0 | 0 | 280 | 0 | 30 | 355 | 291 |  | 0 | 400 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 208 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 80 | 0 | 285 | 290 | 201 | 8 | 90 | 25 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 96 | 142 | 95 | 17 | 0 | 72 | 22 | 51 | 50 | 130 | 142 | 65 | 79 | 0 | 158 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 |  | 398 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 90 | 0 | 285 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 400 |  | 5412 | 2223 | 7635 | 3985 | 398 | 1897 | 417 | 775 | 67 | 0 | 96 | 0 | 0 | 89.58
KWH | 882000 | 3822500 | 0 | 0 | 4794000 | 0 | 1296736 | 8485890 | 7196000 |  | 0 | 8659000 | 3378240 | 579840 | 61464 | 48352 | 0 | 0 | 0 | 0 | 913920 | 580032 | 0 | 32379 | 0 | 0 | 22512 | 427320 | 93578 | 0 | 343656 | 600000 | 686160 | 678500 | 718300 | 0 | 0 | 590040 | 976000 | 2800000 | 0 | 0 | 4892071 | 0 | 2539270 | 0 |  | 0 | 0 | 40 | 0 | 46147 | 148320 | 366240 | 503520 | 0 | 2117530 | 0 | 7350900 | 7212000 | 4561000 | 217454 | 2168270 | 760032 | 134880 | 0 | 963968 | 0 | 0 | 0 | 397728 | 100080 | 597600 | 542870 | 2309760 | 4099040 | 1392000 | 346284 | 13950 | 1706000 | 528000 | 879000 | 984816 | 3012791 | 3282000 | 1350720 | 1271040 | 0 | 2323050 | 306000 | 0 | 195120 | 7545800 | 375600 | 195000 | 0 | 37640 | 0 | 0 | 98400 | 0 | 1761120 | 79110 | 156480 | 0 | 30109 | 5638000 | 1410000 | 0 | 0 | 34440 | 1768909 | 0 | 0 | 0 | 0 |  | 13432727 | 0 | 8551296 | 0 | 713280 | 0 | 0 | 0 | 0 | 0 | 0 | 1774000 | 353605 | 0 | 1545 | 0 | 0 | 0 | 0 | 813836 | 0 | 0 | 0 | 0 | 0 | 278880 | 150660 | 235296 | 2127709 | 0 | 6683500 | 0 | 0 | 4590491 | 0 | 0 | 0 | 621184 | 0 | 0 | 0 | 9565910 | 0 | 0 | 47616 | 0 | 655680 | 0 | 44047 | 1459392 | 8032000 |  | 127416518 | 60132654 | 187549172 | 92717374 | 13432727 | 43830364 | 15862730 | 16843209 | 1566040 | 815421 | 2309760 | 171547 | 0
Fuel Cost | 987840 | 4128300 | 0 | 0 | 3547560 | 0 | 1893234.56 | 6109840.8 | 5468960 |  | 0 | 6927200 | 3040416 | 5914368 | 665655.12 | 496091.52 | 0 | 0 | 0 | 0 | 10144512 | 5893125.12 | 0 | 339331.92 | 0 | 0 | 210712.32 | 4097998.8 | 892734.12 | 0 | 257742 | 450000 | 0 | 0 | 0 | 0 | 0 | 153410.4 | 253760 | 4284000 | 0 | 0 | 5136674.55 | 0 | 3224872.9 | 0 |  | 0 | 0 | 419.6 | 0 | 438857.97 | 1388275.2 | 336940.8 | 1399785.6 | 0 | 2223406.5 | 0 | 5439666 | 6058080 | 4196120 | 213104.92 | 2883799.1 | 623226.24 | 138926.4 | 0 | 1378474.24 | 0 | 0 | 0 | 405682.56 | 75060 | 1129464 | 407152.5 | 15937344 | 3361212.8 | 13237920 | 353209.68 | 228780 | 2320160 | 718080 | 1195440 | 1231020 | 3735860.84 | 3019440 | 2012572.8 | 2237030.4 | 0 | 3531036 | 486540 | 0 | 458532 | 5357518 | 281700 | 148200 | 0 | 394090.8 | 0 | 0 | 946608 | 0 | 17769700.8 | 912929.4 | 1458393.6 | 0 | 282121.33 | 5299720 | 12365700 | 0 | 0 | 0 | 16309340.98 | 0 | 0 | 0 | 0 |  | 36268362.9 | 0 | 6670010.88 | 0 | 6876019.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1419200 | 548087.75 | 0 | 51216.75 | 0 | 0 | 0 | 0 | 8056976.4 | 0 | 0 | 0 | 0 | 0 | 306768 | 248589 | 178119.072 | 13553506.33 | 0 | 27335515 | 0 | 0 | 4039632.08 | 0 | 0 | 0 | 987682.56 | 0 | 0 | 0 | 6983114.3 | 0 | 0 | 437114.88 | 0 | 6124051.2 | 0 | 0 | 0 | 0 |  | 218844983.19 | 120083966.302 | 338928949.492 | 85744261.262 | 36268362.9 | 40709328.57 | 109723138.88 | 40889021.33 | 407170.4 | 8108612.75 | 15937344 | 1141709.4 | 0
Yesterday Day Peak | 37 | 149 | 0 | 0 | 177 | 0 | 70 | 362 | 335 |  | 0 | 400 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 22 | 25 | 8 | 0 | 0 | 27 | 40 | 115 | 0 | 0 | 218 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 100 | 0 | 325 | 330 | 205 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 21 | 102 | 176 | 48 | 17 | 2.3 | 72 | 22 | 48 | 47 | 130 | 144 | 59 | 79 | 0 | 24 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 119 | 18.6 | 0 | 0 | 0 | 235 | 115 | 0 | 0 | 5.1 | 100 | 0 | 0 | 0 | 0 |  | 634 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 11 | 88 | 0 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 35 | 0 | 6.6 | 109 | 330 |  | 8291.6 | DayPeak
Yesterday Evening Peak | 37 | 149 | 0 | 0 | 260 | 0 | 35 | 350 | 333 | 0 | 0 | 450 | 150 | 86 | 29 | 30 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 20 | 0 | 0 | 12 | 35 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 19 | 22 | 0 | 80 | 0 | 315 | 315 | 184 | 8 | 90 | 46 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 122 | 162 | 91 | 17 | 0 | 72 | 22 | 48 | 50 | 130 | 144 | 65 | 60 | 0 | 231 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 30 | 0 | 0 | 16 | 0 | 141 | 0 | 80 | 0 | 24 | 235 | 88 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 |  | 884 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 87 | 0 | 285 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 17 | 0 | 75 | 0 | 0 | 109 | 442 |  | 9719 | EvPeak
Forecast for Evening | 37 | 160 | 0 | 0 | 380 | 0 | 78 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 30 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 119 | 160 | 95 | 22 | 0 | 72 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 898 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 40 | 100 | 21 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 40 | 40 | 40 | 52 | 38 | 22 | 11 | 11 | 100 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 600
Forecast for Day | 37 | 150 | 0 | 0 | 300 | 0 | 78 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 20 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 150 | 95 | 22 | 1.6 | 72 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 130 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 90 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 650 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 100 | 20 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 40 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 100 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 500
Generation at 08:00(Today) | 37 | 159 | 0 | 0 | 250 | 0 | 78 | 347 | 302 | 0 | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 280 | 260 | 182 | 8 | 90 | 30 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 90 | 148 | 49 | 17 | 0.6 | 71 | 22 | 48 | 37 | 130 | 145 | 67 | 79 | 0 | 158 | 0 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 7 | 0 | 0 | 0 | 234 | 78 | 0 | 0 | 1.6 | 16 | 0 | 0 | 0 | 0 | 0 | 642 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 18 | 0 | 1.7 | 28 | 345 | 0
199
| Minimum Generation |  | 6044 | 5:00
| Highest Generation |  | 9719 | 19:00
| Day Peak Generation |  | 8291.6 | 12:00
| Evening Peak Generation |  | 9719 | 19:00
| HVDC Max Flow |  | 887 | 21:00
| HVDC EvPeak Flow |  | 884 | 19:00
| Load factor L.F |  | 80.4%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-02
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8291.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6308 | MW
Evening Peak Generation : |  | 9719 | MW Hour : | 19:00 | Available Max Generation : |  | 15365 | MW
E.P. Demand (at gen end) : |  | 9719 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 9719 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5365 | MW
Total Gen. (MKWH) : |  | 187.5492 | System Load Factor : | 80.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -248 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-02
Actual : | 89.55 | Ft.(MSL) , | Rule curve : | 92.84 | Ft.( MSL )
Gas Consumed : | Total = | 1102.66 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 126453589.832
: |  | Coal : | 40889021.33 | Oil : | 117831751.63 | Total : | 285174362.792
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3512.4326 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1191.264 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1066.7704 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 963.7173 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 871.0076 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 702.8643 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 397.0703 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 181.0762 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 542.0644 |  |  | 0 | 0%
Total | 0 |  | 9428.2672 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Bhola 225 MW GT-2
3) Ghorasal Unit-2,4 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Dhamrai-Kaliakoir 132 kV Ckt-2 was under shut down from 08:38 to 16:53 for A/M.
b) Savar-Manikganj P/P 132 kV Ckt-1 was under shut down from 09:22 to 20:44 for A/M.
c) Kaliakoir 400/132 kV T-2 transformer was under shut down from 08:21 to 14:50 for C/M.
d) Sikalbaha 230 kV Bus coupler was under shut down from 08:47 to 12:52 for C/M.
e) Rangpur-Saidpur 132 kV Ckt-1 was under shut down from 10:17 to 10:55 for C/M.
f) Kulshi-Hathazari 132 kV Ckt was under shut down from 11:57 to 12:56 for C/M.
g) Megnaghat-450 MW GT-2 was shut down from 13:29 to 14:34 for C/M.
h) Tangail all 33 kV incoming CB tripped at 15:10 due to 33 kV Betka feeder fault (R-phase CT burst) |  |  |  |  | About 120 MW power interruption occurred under Tangail S/S
and were switched on at 16:22. |  |  |  |  | areas from 15:10 to 16:22.
i) Bhola-225 MW GT-1 was shut down at 23:14 for download data after HGPI and was synchronized at 00:34.
j) Mymensing-Jamalpur 132 kV Ckt-1 is under shut down since 07:13(2/3/20) for D/W.
k) Baraulia 132 kV main Bus section-1 is under shut down since 07:17(2/3/20) for D/W.
l) Dohazari-Cox'sbazar 132 kV Ckt-1 was under shut down from 06:43 to 10:04(2/3/20) for CT
replacement at Dohazari end.
m) Rangpur 132/33 kV T-3 transformer is under shut down since 06:52(2/3/20) for D/W.
n) Rangpur-Barapukuria 132 kV Ckt-1 is under shut down since 06:55(2/3/20) for D/W.
o) After reconductoring Kabirpur-Kaliakoir 132 kV Ckt-1 was switched on at 15:30.
p) After reconductoring Tangail-Kaliakoir 132 kV Ckt-2 was switched on at 17:20.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 882000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 149 | 3822500 | Gas shortage.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 4794000 | Gas shortage.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 35 | 1296736 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8485890 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7196000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8659000
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 86 | 579840 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3378240 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 29 | 61464 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 48352 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 20 | 32379 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 343656
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 913920 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 580032
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 12 | 22512 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 427320 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 93578
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1286160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 678500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 718300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 37640 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 141 | 1761120 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2539 | 46099139
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2800000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 79110
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 148320 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1566040 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4892071
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2539270 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 40 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 80 | 156480
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 366240
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 503520
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 46147 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 214 | 1768909 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 868 | 14900587
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2117530 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4561000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7350900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7212000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 760032
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 134880 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 963968
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 24 | 30109 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2168270
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 397728
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 100080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2309760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 597600
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 542870
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1316 | 29464181
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 162 | 4099040 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 346284
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 1392000
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13950
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 16 | 98400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 88 | 1410000
| Mymensingh Area Total |  |  |  | 637 | 374 | 7359674
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 72 | 1706000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 528000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3012791 | frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3282000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 879000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 984816
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 195000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1350720 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 60 | 1271040 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 231 | 2323050
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 306000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 375600
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7545800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 235 | 5638000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 195120
| Sylhet Area Total |  |  |  | 1949 | 1431 | 29592937
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 884 | 13432727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 713280
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 390 | 8551296 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1389 | 22697303
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 1545 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 353605
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 90 | 1774000 | High Voltage due to Payra test
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 621184 | High Voltage due to Payra test
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 442 | 8032000 | On test
| Barisal Area Total |  |  |  | 462 | 553 | 10782334
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 185 | 4590491 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 386 | 9565910 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 278880 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 150660
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235296
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 68 | 813836 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 17 | 47616 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1459392
| Rajshahi Area Total |  |  |  | 2183 | 802 | 17142081
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 87 | 2127709
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 285 | 6683500
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 75 | 655680
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44047
| Rangpur Area Total |  |  |  | 605 | 447 | 9510936
| Total |  |  |  | 19107 | 9719 | 187549172
| Eastern Grid Total |  |  |  | 13543 | 6528 | 127416518
| Western Grid Total |  |  |  | 5564 | 3191 | 60132654
| National Grid Total |  |  |  | 19107 | 9719 | 187549172
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-01
(a) ENTIRE EASTERN GRID : |  | 6214 | MW | (b) ENTIRE WESTERN GRID : |  | 2936 | MW
i) Dhaka area |  | 3367 | MW | i) Khulna area |  | 1118 | MW
ii) Chittagong area |  | 981 | MW | ii) Rajshahi area |  | 976 | MW
iii) Comilla area |  | 748 | MW | iii) Barisal area |  | 223 | MW
iv) Mymensingh area |  | 768 | MW | iv) Rangpur area |  | 619 | MW
v) Sylhet area |  | 350 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9150 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 16:00 | Sherpur | 86 | 18:30 | Benapol | 34 | 19:00
Munsiganj | 83 | 21:00 | Srimongal | 31 | 18:30 | Jhenida | 84 | 18:30
Sonargaon | 68 | 19:00 | Shahjibazar | 84 | 20:00 | Bottail | 92 | 19:00
Shyampur | 180 | 0:00 | Fenchuganj | 27 | 19:00 | G.K Project | 41 | 19:00
Bhulta | 168 | 11:00 | Kulawara | 28 | 18:30 | Faridpur | 134 | 18:30
Madanganj | 56 | 19:00 | Sylhet | 106 | 18:30 | Madaripur | 59 | 19:30
Shitalakhya | 103 | 11:00 | Chatak | 18 | 19:00 | Sariatpur | 40 | 20:00
Rahim steel | 6 | 9:00 | Sunamganj | 29 | 19:30 | Gopalganj | 69 | 19:00
Matuail | 86 | 12:00 | Biani Bazar | 31 | 19:00 | Bagerhat | 70 | 18:00
Ghorasal | 69 | 19:00 | Comilla (S) | 122 | 18:30 | Mongla | 44 | 14:00
Narsingdi | 117 | 19:00 | Comilla(N) | 81 | 20:00 | Satkhira | 73 | 19:30
Haripur (SBU) | 89 | 19:30 | Chandpur | 66 | 20:00 | Gallamari | 38 | 21:00
Ullon | 57 | 18:00 | Feni | 72 | 18:30 | Magura | 38 | 18:30
Hasnabad | 135 | 19:00 | Chowmuhani | 112 | 20:00 | Norail | 27 | 19:00
Magbazar | 85 | 15:00 | Ashuganj | 42 | 19:00 | Chuadanga | 64 | 19:00
Maniknagar | 80 | 18:00 | Daudkandi | 90 | 19:00 | Barisal(N) | 30 | 20:00
Bangabhaban | 28 | 12:00 | B.Baria | 94 | 18:30 | Barisal (S) | 70 | 18:30
Narinda | 88 | 18:00 | Ramganj | 60 | 18:30 | Patuakhali | 74 | 21:00
Dhanmondi | 114 | 12:00 | Chaddagram | 20 | 18:00 | Bhandaria | 40 | 21:00
Lalbag | 51 | 12:00 | PHP | 1 | 8:00 | Borhan Uddin | 25 | 21:00
Madartek | 51 | 21:00 | Madunaghat | 41 | 10:00 | Ishurdi | 45 | 19:00
Dhaka University |  |  | Hathazari | 71 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 73 | 18:30 | Khulshi | 145 | 19:00 | Natore | 96 | 19:00
Kalyanpur | 75 | 18:30 | Halishahar | 104 | 18:30 | Bogra | 135 | 18:30
Gulshan | 94 | 12:00 | Baraulia | 134 | 0:00 | Noagaon | 94 | 19:00
Uttara | 46 | 18:30 | Sikalbaha | 17 | 18:30 | Rajshahi | 96 | 19:30
Uttara New | 35 | 18:30 | Dohazari | 70 | 19:00 | Rajshahi New | 8 | 18:30
Kamrangirchar | 85 | 18:30 | Cox'sbazar | 81 | 18:30 | C.Nawabganj | 60 | 8:00
Savar | 106 | 18:30 | Chandraghona | 24 | 18:30 | Amnura | 26 | 19:00
Bhasantec | 106 | 18:30 | Kaptai | 3.5 | 18:30 | Pabna | 77 | 18:30
Agargaon | 39 | 18:30 | A. Khaer Stl. | 23 | 12:00 | Shahjadpur | 82 | 19:00
Satmosjid | 70 | 18:30 | Bakulia | 77 | 18:30 | Serajganj | 81 | 10:00
Tongi | 105 | 12:00 | Julda | 21 | 8:00 | Niyamatpur | 70 | 8:00
Kabirpur | 192 | 15:00 | TK chemical | 10.6 | 19:30 | Joypurhat | 53 | 19:00
Basundhara | 116 | 18:30 | Modern Steel | 17 | 23:00 | Sherpur(Bogura) | 40 | 18:30
Manikganj | 68 | 21:00 | Shahmirpur | 25.5 | 18:30 | Mohastangor | 40 | 19:00
Joydevpur | 127 | 12:00 | Khagrachhari | 20 | 18:30 | Rangpur | 113 | 18:30
New Tongi | 85 | 18:30 | Matarbari | 22 | 18:30 | Lalmonirhat | 44 | 19:30
Korda | 211 | 15:00 | Baroiar Hat | 34 | 18:30 | Saidpur | 91 | 19:00
Dhamrai | 58 | 20:00 | Rangamati | 10 | 18:30 | Purbasadipur | 93 | 19:00
Rajendrapur | 38 | 21:00 | Abul Khair 230 | 187 | 14:00 | Thakurgaon | 68 | 19:00
Valuka | 80 | 11:00 | BSRM | 109 | 5:00 | Palashbari | 96 | 8:00
Tangail | 152 | 19:00 | GPH Ispat | 60 | 17:00 | Barapukuria | 46 | 11:00
Mymensing | 178 | 18:30 | Goalpara | 14 | 13:00 | Panchagar | 37 | 19:30
Kishorganj | 88 | 22:00 | Central s/s | 69 | 19:00 | Joldhaka | 27 | 8:00
Netrokona | 95 | 18:30 | Noapara | 43 | 19:00 | Kurigram | 48 | 0.8125
Jamalpur | 107 | 8:00 | Jessore | 98 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-01 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 405 | 0.16667 | 394 | 0.5 | Kaliakoir | 389 | 0.125 | 372 | 0.5
Bheramara | 405 | 0.083333 | 391 | 0.79167 | Bhulta | 396 | 0.083333 | 378 | 0.5
Ashuganj(N) | 401 | 0.125 | 390 | 0.45833 | Gopalganj | 409 | 0.125 | 387 | 0.83333
Payra | 411 | 0.20833 | 400 | 0.83333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 238 | 0.041667 | Hathazari | 221 | 0.125 | 217 | 0.41667
Ishurdi | 240 | 0.083333 | 227 | 0.29167 | Megnaghat | 238 | 0.20833 | 230 | 0.41667
Ashuganj | 242 | 0.041667 | 235 | 0.41667 | Fenchuganj | 241 | 0.041667 | 239 | 0.5
Serajganj | 235 | 24:00 | 226 | 0.29167 | Siddhirganj | 236 | 0.125 | 226 | 0.41667
Baghabari | 245 | 0.041667 | 236 | 0.29167 | Maniknagar | 234 | 0.20833 | 224 | 0.45833
Barapukuria | 237 | 0.083333 | 225 | 0.29167 | Old Airport | 234 | 0.125 | 222 | 0.5
Bogra | 228 | 0.75 | 212 | 0.33333 | Barisal | 250 | 0.125 | 234 | 0.79167
Khulna South | 237 | 0.91667 | 218 | 0.29167 | AKSML | 229 | 0.25 | 212 | 0.58333
Rampura | 232 | 0.16667 | 224 | 0.5 | BSRM | 227 | 0.25 | 218 | 0.95833
Haripur | 231 | 0.041667 | 223 | 0.41667 | Bibiyana | 240 | 0.16667 | 235 | 0.70833
Hasnabad | 233 | 0.125 | 226 | 0.54167 | Bhulta | 236 | 0.20833 | 225 | 0.5
Shyampur | 231 | 0.125 | 221 | 0.5 | Ashuganj (S) | 239 | 0.083333 | 232 | 0.41667
Aminbazar | 233 | 0.083333 | 224 | 0.5 | Kaliakoir | 235 | 0.125 | 224 | 0.45833
Tongi | 230 | 0.041667 | 222 | 0.45833 | GPH | 220 | 0.125 | 214 | 0.5
Comilla (N) | 237 | 0.20833 | 230 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 0.041667 | 128 | 0.5 | Hathazari | 132 | 0.125 | 129 | 0.41667
Munsiganj | 133 | 0.79167 | 127 | 0.5 | Khulshi | 130 | 0.8125 | 125 | 0.41667
Sonargaon | 132 | 0.16667 | 128 | 0.45833 | Halishahar | 131 | 0.79167 | 127 | 0.41667
Shyampur | 135 | 0.16667 | 128 | 0.5 | Baraulia | 130 | 0.125 | 127 | 0.375
Bhulta | 129 | 0.20833 | 122 | 0.45833 | Sikalbaha | 131 | 0.79167 | 127 | 0.41667
Madanganj | 133 | 0.77083 | 125 | 0.41667 | Dohazari | 128 | 0.083333 | 126 | 0.41667
Shitalakhya | 136 | 0.79167 | 126 | 0.5 | Cox'sbazar | 124 | 0.16667 | 117 | 0.77083
Rahim steal | 134 | 1:00 | 129 | 0.41667 | Chandraghona | 132 | 0.8125 | 128 | 0.5
Matuail | 133 | 0.20833 | 127 | 0.45833 | Kaptai | 132 | 0.041667 | 129 | 0.41667
Ghorasal | 140 | 0.77083 | 134 | 0.041667 | A. Khaer Stl. | 133 | 0.54167 | 127 | 0.25
Narsinghdi | 131 | 0.041667 | 127 | 0.66667 | Bakulia | 129 | 0.125 | 125 | 0.5
Haripur (SBU) | 134 | 0.041667 | 128 | 0.45833 | Julda | 130 | 0.79167 | 126 | 0.41667
Ullon | 132 | 0.20833 | 124 | 0.5 | TK Chemical | 133 | 0.041667 | 127 | 0.375
Hasnabad | 134 | 0.29167 | 128 | 0.70833 | Modern Steel | 130 | 0.79167 | 125 | 0.5
Magbazar | 135 | 0.25 | 123 | 0.5 | Shahmirpur | 130 | 0.8125 | 127 | 0.33333
Maniknagar | 135 | 0.25 | 129 | 0.5 | Khagrachhari | 130 | 0.041667 | 127 | 0.5
Bangabhaban | 135 | 0.25 | 129 | 0.5 | Matarbari | 127 | 0.20833 | 120 | 0.79167
Narinda | 135 | 0.25 | 129 | 0.5 | Baroiar Hat | 130 | 0.041667 | 128 | 3:00
Dhanmondi | 132 | 0.20833 | 124 | 0.5 | Rangamati | 131 | 0.083333 | 128 | 10:00
Lalbag | 135 | 0.25 | 126 | 0.5 | Goalpara | 135 | 0.91667 | 123 | 0.29167
Madartek | 131 | 0.25 | 123 | 0.5 | Central s/s | 133 | 0.041667 | 127 | 0.5
Dhaka University |  |  |  |  | Noapara | 134 | 0.041667 | 124 | 0.29167
Mirpur | 136 | 0.20833 | 127 | 0.5 | Jessore | 130 | 0.125 | 118 | 0.79167
Kalyanpur | 134 | 0.20833 | 127 | 0.5 | Benapol | 133 | 0.125 | 122 | 0.29167
Gulshan | 129 | 0.20833 | 122 | 0.5 | Jhenida | 133 | 0.125 | 121 | 0.29167
Uttara | 135 | 0.20833 | 129 | 0.5 | Bottail | 135 | 0.041667 | 127 | 0.79167
Uttara New | 136 | 0.20833 | 128 | 0.5 | G.K Project | 140 | 0.16667 | 135 | 0.77083
Kamrangirchar | 133 | 0.20833 | 124 | 0.5 | Faridpur | 137 | 0.041667 | 131 | 0.79167
Savar | 135 | 0.20833 | 127 | 0.5 | Madaripur | 140 | 0.125 | 134 | 0.77083
Bhasantec | 135 | 0.20833 | 127 | 0.5 | Sariatpur | 141 | 0.16667 | 132 | 0.8125
Agargaon | 136 | 0.20833 | 128 | 0.5 | Gopalganj | 142 | 0.041667 | 134 | 0.83333
Satmosjid | 135 | 0.20833 | 124 | 0.5 | Bagerhat | 132 | 0.041667 | 122 | 0.75
Tongi | 136 | 0.041667 | 131 | 0.45833 | Mongla | 129 | 0.16667 | 121 | 0.79167
Kabirpur | 133 | 0.041667 | 123 | 0.45833 | Satkhira | 136 | 0.20833 | 123 | 0.29167
Basundhara | 131 | 3:00 | 123 | 0.58333 | Gallamari | 135 | 0.16667 | 125 | 0.29167
Manikganj | 136 | 0.20833 | 130 | 0.5 | Magura | 133 | 0.16667 | 119 | 0.77083
Joydevpur | 141 | 0.041667 | 136 | 0.5 | Norail | 132 | 0.041667 | 115 | 0.79167
New Tongi | 136 | 0.875 | 128 | 0.5 | Chuadanga | 130 | 0.16667 | 113 | 0.79167
Kodda | 131 | 1904-01-02 | 124 | 0.45833 | Barisal(N) | 142 | 0.125 | 131 | 0.79167
Dhamrai | 134 | 0.125 | 121 | 0.5 | Barisal (S) | 139 | 0.25 | 131 | 0.79167
Rajendrapur | 139 | 0.083333 | 133 | 0.45833 | Patuakhali | 137 | 0.125 | 127 | 0.83333
Valuka | 126 | 0.041667 | 113 | 0.29167 | Bhandaria | 136 | 0.041667 | 129 | 0.5
Tangail | 132 | 0.16667 | 117 | 0.45833 | Ishurdi | 137 | 0.083333 | 130 | 0.29167
Mymensing | 129 | 0.041667 | 115 | 0.29167 | Ruppur Paromanobik | 137 | 0.125 | 129 | 0.29167
Kishorganj | 130 | 0.125 | 122 | 0.29167 | Natore | 133 | 0.041667 | 124 | 0.29167
Netrokona | 126 | 0.041667 | 119 | 0.33333 | Bogra | 138 | 0.125 | 125 | 0.29167
Jamalpur | 135 | 0.54167 | 113 | 0.29167 | Noagaon | 131 | 0.75 | 116 | 0.33333
Sherpur | 134 | 0.54167 | 112 | 0.29167 | Rajshahi | 131 | 0.16667 | 120 | 0.29167
Srimongal | 138 | 0.041667 | 135 | 0.625 | Rajshahi New | 131 | 0.125 | 119 | 0.33333
Shahjibazar | 137 | 0.041667 | 135 | 17:00 | C.Nawabganj | 129 | 0.58333 | 119 | 0.33333
Fenchuganj | 136 | 0.041667 | 133 | 0.66667 | Amnura | 129 | 0.16667 | 116 | 0.29167
Khulawara | 136 | 0.33333 | 134 | 0.5 | Pabna | 135 | 0.083333 | 128 | 0.33333
Sylhet | 136 | 0.041667 | 133 | 0.41667 | Shahjadpur | 143 | 0.125 | 133 | 0.29167
Chatak | 140 | 0.16667 | 135 | 0.8125 | Serajganj | 137 | 0.125 | 127 | 0.33333
Sunamganj | 135 | 0.041667 | 133 | 0.54167 | Niyamatpur | 132 | 0.125 | 113 | 0.33333
Biani Bazar | 136 | 0.041667 | 134 | 0.45833 | Joypurhat | 134 | 0.75 | 116 | 0.29167
Comilla(s) | 130 | 0.041667 | 126 | 0.41667 | Sherpur(Bogura) | 137 | 0.125 | 130 | 0.5
Comilla(n) | 138 | 0.29167 | 135 | 0.45833 | Mohastangor | 136 | 0.125 | 123 | 0.33333
Chandpur | 136 | 0.33333 | 132 | 0.91667 | Rangpur | 132 | 0.16667 | 120 | 0.33333
Feni | 133 | 0.29167 | 129 | 0.79167 | Lalmonirhat | 127 | 0.125 | 111 | 0.33333
Chowmuhani | 131 | 0.33333 | 125 | 0.875 | Saidpur | 133 | 0.16667 | 118 | 0.33333
Ashuganj | 136 | 0.041667 | 135 | 0.29167 | Purbasadipur | 130 | 0.125 | 113 | 0.33333
Daudkandi | 133 | 0.29167 | 129 | 0.5 | Thakurgaon | 128 | 0.125 | 110 | 0.33333
B.Baria | 133 | 0.29167 | 130 | 0.8125 | Palashbari | 131 | 0.125 | 115 | 0.33333
Ramganj | 130 | 0.375 | 125 | 1904-01-02 | Barapukuria | 137 | 0.083333 | 125 | 0.29167
Chaddagram | 135 | 0.083333 | 130 | 0.83333 | Panchagar | 128 | 0.125 | 111 | 0.33333
PHP | 133 | 0.083333 | 128 | 0.5 | Joldhaka | 131 | 0.125 | 114 | 0.33333
Madanhat | 133 | 0.8125 | 129 | 0.5 | Kurigram

## L-Curve
Date | 2020-03-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 36 | 5412 | 2223 | 7635 |  |  |  | QF-LDC-12
0:30 | 142 | 5222 | 2016 | 7238 | Date: | 2020-03-01
1:00 | 248 | 5032 | 1809 | 6841
1:30 | 189 | 4853.5 | 1831.5 | 6685
2:00 | 130 | 4675 | 1854 | 6529
2:30 | 102.5 | 4599 | 1856 | 6455 | [5 empty] | Gen. at Eve. Peak | 9719 | 9719 MW (19:00 )
3:00 | 75 | 4523 | 1858 | 6381 | [6 empty] | 19:00
3:30 | 75 | 4376 | 1841.5 | 6217.5 | [5 empty] | Gen. at Day Peak | 8291.6 | 8291.6 MW (12:00 )
4:00 | 75 | 4229 | 1825 | 6054 | [6 empty] | 12:00
4:30 | 61.5 | 4240 | 1809 | 6049 | [5 empty] | Highest Generation | 9719
5:00 | 48 | 4251 | 1793 | 6044 | [6 empty] | 19:00
5:30 | 109.5 | 4354.5 | 1827.5 | 6182
6:00 | 171 | 4458 | 1862 | 6320
6:30 | 127 | 4576.3 | 2147.1 | 6723.4
7:00 | 83 | 4694.6 | 2432.2 | 7126.8
7:30 | 95 | 4904.85 | 2454 | 7358.85
8:00 | 107 | 5115.1 | 2475.8 | 7590.9
8:30 | 136 | 5139.65 | 2537.8 | 7677.45
9:00 | 165 | 5164.2 | 2599.8 | 7764
9:30 | 213.5 | 5192.15 | 2609.5 | 7801.65
10:00 | 262 | 5220.1 | 2619.2 | 7839.3
10:30 | 260 | 5295.95 | 2626.2 | 7922.15
11:00 | 258 | 5371.8 | 2633.2 | 8005
11:30 | 243 | 5491.9 | 2656.4 | 8148.3
12:00 | 228 | 5612 | 2679.6 | 8291.6
12:30 | 170.5 | 5685 | 2632.6 | 8317.6
13:00 | 113 | 5758 | 2585.6 | 8343.6
13:30 | 189 | 5641.95 | 2577.85 | 8219.8
14:00 | 265 | 5525.9 | 2570.1 | 8096
14:30 | 262.5 | 5508.85 | 2522.1 | 8030.95
15:00 | 260 | 5491.8 | 2474.1 | 7965.9
15:30 | 290 | 5402.35 | 2467.55 | 7869.9
16:00 | 320 | 5312.9 | 2461 | 7773.9
16:30 | 325 | 5205.95 | 2465.55 | 7671.5
17:00 | 330 | 5099 | 2470.1 | 7569.1
17:30 | 281.5 | 5302 | 2525.1 | 7827.1
18:00 | 233 | 5505 | 2580.1 | 8085.1
18:30 | 122.5 | 6016.5 | 2885.55 | 8902.05
19:00 | 12 | 6528 | 3191 | 9719
19:30 | 75 | 6375 | 3237 | 9612
20:00 | 150 | 6113 | 3278 | 9391 |  |  |  | Executive Engineer
20:30 | 148.5 | 6086 | 3256.5 | 9342.5 |  |  |  | Network Operation Division
21:00 | 147 | 6059 | 3235 | 9294
21:30 | 170 | 5878.5 | 3103.5 | 8982
22:00 | 193 | 5698 | 2972 | 8670 |  |  |  |  | Page 6 of 7
22:30 | 204 | 5574.5 | 2823.5 | 8398
23:00 | 215 | 5451 | 2675 | 8126
23:30 | 125.5 | 5431.5 | 2449 | 7880.5
24:00 | 36 | 5412 | 2223 | 7635
9719 MW (19:00 )
8291.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-01 |  | Energy | 187549172
[10 empty] | 2020-03-01 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3985 | 398 | 1897 | 467 | 775 | 67 | 0 | 0 | 96
0:30 | 3900.5 | 300.5 | 1903 | 349.5 | 652.5 | 67 | 0 | 0 | 90 | Date: | 2020-03-01
1:00 | 3816 | 203 | 1909 | 232 | 530 | 67 | 0 | 0 | 84
1:30 | 3723.5 | 201.5 | 1847.5 | 201 | 563 | 67.5 | 0 | 0 | 81 | [7 empty] | Total Energy | 187.5492 | Total Energy Gen 187.549 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.549 MKWHr
2:00 | 3631 | 200 | 1786 | 170 | 596 | 68 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3610.5 | 200.5 | 1731.5 | 160 | 607.5 | 68 | 0 | 0 | 77 | [7 empty] | Energy Requirement | 187.5492
3:00 | 3590 | 201 | 1677 | 150 | 619 | 68 | 0 | 0 | 76
3:30 | 3516 | 200.5 | 1590 | 143 | 624 | 68 | 0 | 0 | 76 | [6 empty] | Shortage
4:00 | 3442 | 200 | 1503 | 136 | 629 | 68 | 0 | 0 | 76
4:30 | 3445 | 200 | 1495 | 136 | 628.5 | 67.5 | 0 | 0 | 77
5:00 | 3448 | 200 | 1487 | 136 | 628 | 67 | 0 | 0 | 78
5:30 | 3547.5 | 199.5 | 1509 | 136 | 635.5 | 67 | 8.5 | 0 | 79
6:00 | 3647 | 199 | 1531 | 136 | 643 | 67 | 17 | 0 | 80
6:30 | 3677 | 415.5 | 1645 | 151.5 | 664 | 67 | 21 | 0 | 81 |  |  |  |  | Coal
7:00 | 3707 | 632 | 1759 | 167 | 685 | 67 | 25 | 0 | 82
7:30 | 3735 | 632 | 1842 | 282 | 675.5 | 67 | 33.5 | 0 | 85 |  |  |  | Oil |  |  |  | ,
8:00 | 3763 | 632 | 1925 | 397 | 666 | 67 | 42 | 0 | 88
8:30 | 3758 | 632 | 1910 | 484.5 | 671 | 67 | 51 | 0 | 88
9:00 | 3753 | 632 | 1895 | 572 | 676 | 67 | 60 | 0 | 88
9:30 | 3746 | 632 | 1907.5 | 592 | 678.5 | 67 | 64 | 0 | 90
10:00 | 3739 | 632 | 1920 | 612 | 681 | 67 | 68 | 0 | 92
10:30 | 3776 | 632 | 1920.5 | 649 | 685.5 | 67 | 68 | 0 | 94
11:00 | 3813 | 632 | 1921 | 686 | 690 | 67 | 68 | 0 | 96
11:30 | 3869.5 | 633 | 1949 | 741.5 | 689 | 67 | 68 | 0 | 99
12:00 | 3926 | 634 | 1977 | 797 | 688 | 67 | 68 | 0 | 102
12:30 | 3860 | 635 | 1982 | 893.5 | 688 | 67 | 68 | 0 | 101
13:00 | 3794 | 636 | 1987 | 990 | 688 | 67 | 68 | 0 | 100
13:30 | 3794 | 636 | 1987 | 990 | 688 | 67 | 68 | 0 | 100
14:00 | 3794 | 636 | 1987 | 990 | 688 | 67 | 68 | 0 | 100
14:30 | 3831.5 | 636.5 | 1823 | 947 | 690.5 | 67 | 47 | 0 | 101
15:00 | 3869 | 637 | 1659 | 904 | 693 | 67 | 26 | 0 | 102
15:30 | 3840 | 637 | 1679 | 823.5 | 692.5 | 67.5 | 25.5 | 0 | 98
16:00 | 3811 | 637 | 1699 | 743 | 692 | 68 | 25 | 0 | 94
16:30 | 3799.5 | 636.5 | 1691.5 | 649 | 705.5 | 68 | 25 | 0 | 93
17:00 | 3788 | 636 | 1684 | 555 | 719 | 68 | 25 | 0 | 92
17:30 | 3825.5 | 636 | 1719 | 715.5 | 734 | 68 | 25 | 0 | 103
18:00 | 3863 | 636 | 1754 | 876 | 749 | 68 | 25 | 0 | 114
18:30 | 4014.5 | 760 | 1845.5 | 1268 | 781.5 | 68 | 46.5 | 0 | 118
19:00 | 4166 | 884 | 1937 | 1660 | 814 | 68 | 68 | 0 | 122
19:30 | 4146 | 884 | 1913 | 1575 | 838 | 68 | 68 | 0 | 120
20:00 | 4098 | 884 | 1922 | 1356 | 879 | 68 | 68 | 0 | 116
20:30 | 4125 | 885.5 | 1937.5 | 1272.5 | 878.5 | 68 | 59.5 | 0 | 116
21:00 | 4152 | 887 | 1953 | 1189 | 878 | 68 | 51 | 0 | 116
21:30 | 4104 | 887 | 1934.5 | 1002.5 | 829.5 | 68 | 42.5 | 0 | 114
22:00 | 4056 | 887 | 1916 | 816 | 781 | 68 | 34 | 0 | 112
22:30 | 4045.5 | 837.5 | 1896.5 | 641.5 | 778 | 67.5 | 25.5 | 0 | 106
23:00 | 4035 | 788 | 1877 | 467 | 775 | 67 | 17 | 0 | 100
23:30 | 4010 | 593 | 1887 | 467 | 775 | 67 | 8.5 | 0 | 98 | Max Temp. in Dhaka |  | 31.4° C
24:00 | 3985 | 398 | 1897 | 467 | 775 | 67 | 0 | 0 | 96
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.549 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.549 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 27 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 590040
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 976000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 115 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.1 | 7.4 | 12.8 | 17.1 | 18.8 | 18.6 | [14 empty] | 79110
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 203 | 204 | 216 | 216 | 204 | 205 | 204 | 205 | 218 | 204 | 205 | 204 | 204 | 204 | 204 |  | 204 | 204 | 202 | 202 | 203 | 208 | 208 | 4892071
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 104 | 104 | 104 | 104 | 104 | 108 | 104 | 104 | 105 | 139 | 116 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 104 | 104 | 104 | 104 | 104 | 100 | 2539270
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 40
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 5 |  | 30 | [5 empty] | 0 | 37640
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 882000
21 | Ghorasal Repowered CCPP Unit-3 | 159 | 158 | 158 | 99 | 99 | 99 | 99 | 135 | 149 | 148 | 149 | 149 | 148 | 149 | 149 | 149 | 148 | 149 |  | 149 | 149 | 189 | 189 | 189 | 189 | 189 | 3822500
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 185 | 177 | 177 | 170 | 170 | 170 | 170 | 170 | 155 | 177 | 178 | 177 | 178 | 178 | 178 | 178 | 178 | 178 |  | 260 | 260 | 260 | 278 | 280 | 280 | 280 | 4794000
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2117530
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 42 | 42 | 42 | 42 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 41 | 41 | 25 | 760032
33 | Ashuganj 225 MW CCPP | 184 | 183 | 182 | 161 | 168 | 182 | 182 | 182 | 185 | 192 | 192 | 205 | 185 | 196 | 184 | 184 | 185 | 184 |  | 184 | 185 | 185 | 186 | 184 | 197 | 201 | 4561000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 325 | 325 | 295 | 300 | 305 | 310 | 330 | 315 | 280 | 265 | 265 | 265 | 265 |  | 315 | 315 | 315 | 315 | 315 | 305 | 290 | 7212000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 285 | 320 | 320 | 285 | 285 | 290 | 290 | 325 | 315 | 275 | 270 | 260 | 265 | 290 |  | 315 | 310 | 310 | 310 | 315 | 290 | 285 | 7350900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 134880
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2168270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 353 | 340 | 338 | 340 | 338 | 357 | 385 | 357 | 338 | 344 | 355 | 362 | 359 | 344 | 350 | 340 | 350 | 344 |  | 350 | 340 | 339 | 343 | 339 | 338 | 355 | 8485890
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 350 | 350 | 320 | 320 | 320 | 380 | 380 | 380 | 380 | 400 | 400 | 420 | 225 | 270 | 350 | 350 | 400 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 8659000
41 | Haripur 360MW CCPP(HPL) | 315 | 314 | 315 | 263 | 263 | 264 | 296 | 364 | 341 | 335 | 336 | 335 | 354 | 306 | 307 | 275 | 244 | 244 |  | 333 | 303 | 304 | 282 | 282 | 282 | 291 | 7196000
42 | RPCL 210MW CCPP | 199 | 199 | 200 | 200 | 200 | 200 | 201 | 201 | 196 | 181 | 181 | 176 | 161 | 162 | 159 | 161 | 161 | 162 |  | 162 | 159 | 158 | 140 | 139 | 138 | 142 | 4099040
43
44 | Fenchugonj CCPP Phase-1 | 70 | 71 | 70 | 71 | 70 | 71 | 70 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 73 |  | 72 | 72 | 72 | 72 | 70 | 72 | 72 | 1706000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
46 | Shajibazar 330 MW CCPP | 136 | 138 | 132 | 134 | 136 | 143 | 143 | 134 | 139 | 138 | 140 | 144 | 132 | 138 | 138 | 140 | 140 | 146 |  | 144 | 143 | 144 | 144 | 146 | 147 | 142 | 3282000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 56 | 66 | 65 | 63 | 61 | 61 | 59 | 61 | 59 | 60 | 45 | 45 | 45 |  | 65 | 64 | 64 | 65 | 65 | 64 | 65 | 1350720
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 50 | 5 | 5 | 5 | 5 | 5 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 20 | 20 | 20 | 20 |  | 60 | 76 | 79 | 79 | 79 | 79 | 79 | 1271040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 140 | 110 | 80 | 80 | 80 | 80 | 80 | 80 | 24 | 18 | 18 | 24 | 24 | 145 | 207 | 229 | 126 | 226 |  | 231 | 236 | 173 | 230 | 160 | 158 | 158 | 2323050
51 | Sylhet 20 MW GTPP | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 306000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 195120
54 | Hobiganj 11MW PP Cofidence-E | 11 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 |  | 11 | 11 | 11 | 11 | 195000
55 | Fenchugonj 51 MW PP (Barakatullah) | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 45 | 45 | 45 | 48 | 47 | 48 | 48 | 48 | 48 | 47 |  | 48 | 48 | 50 | 51 | 51 | 51 | 51 | 879000
56 | Shahjahanulla 25 MW PP | 23 | [6 empty] | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 375600
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 300 | 315 | 335 | 330 | 300 | 290 | 310 | 310 | 320 | 320 | 300 | 300 | 280 | 300 | 300 |  | 310 | 290 | 280 | 310 | 290 | 300 | 320 | 7545800
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 |  |  |  |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 366240
61 | Narshingdi 22 MW PP (Doreen) | 22 | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 343656
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 17 | 17 | 22 | 22 | 22 | 17 | 346284
63 | Impoprt (Tripura) | 84 | 78 | 76 | 76 | 78 | 80 | 82 | 88 | 88 | 92 | 96 | 102 | 100 | 104 | 102 | 94 | 92 | 114 |  | 122 | 120 | 116 | 116 | 112 | 100 | 96 | 2309760
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 4 | 4 | 4 | 39 | 15 | 8 | 5 | 3 | 5 | 9 | 5 | 2 | 3 | 14 | 10 |  | 22 | 26 | 29 | 34 | 39 | 40 | 40 | 503520
65 | Feni 22MW PP (Doreen) | 22 | 19 | 19 |  |  |  | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 22 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 397728
66 | Feni 11 MW PP (Doreen) | 5 | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 100080
67 | Jangalia 33MW PP (Summit) | 33 | [6 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 597600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 542870
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 29 | 29 | 29 | 28 | 28 | 28 | 32 | 32 | 31 | 31 | 22 | 31 | 31 | 31 | 31 | 31 | 15 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 686160
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 25 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 678500
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 16 | 16 | 8 | 25 | 33 | 33 | 33 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 718300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 1 | 7 | 7 | 16 | 70 | 95 | 70 | 70 | 60 | 20 | 32 |  | 90 | 100 | 100 | 100 | 65 | 40 | 0 | 913920
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 50 | 30 | 16 | 16 | 16 | 28 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 |  | 91 | 95 | 95 | 95 | 95 | 95 | 95 | 1392000
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.4 | 1.7 | 3.1 | 4.2 | 4.9 | 5.1 | 4.8 | 4.1 | 3.3 | 2 | 0.7 | [9 empty] | 34440
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 0 |  | 29 | 15 | 15 |  |  |  | 0 | 61464
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 5 |  | 20 | [5 empty] | 0 | 32379
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 130 | 130 | 130 | 130 | 150 | 150 | 150 | 150 | 120 | 120 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3378240
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 7 | 7 | 7 | 7 | 44 | 75 | 71 | 40 | 24 | 36 |  | 86 | 93 | 78 | 50 |  |  | 0 | 579840
88 | Ghorashal 78.5 MW PP(MAX) | 35 | 35 | 35 | 35 | 35 | 60 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 1296736
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 30 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 984816
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 25 | 51 | 51 | 42 | 51 | 51 | 51 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 51 | 963968
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 2 | 7 | 7 | 16 | 24 | 48 | 48 | 48 | 24 | 24 | 48 |  | 102 | 102 | 65 | 65 | 16 |  | 0 | 580032
95 | Patenga 50MW PP (Baraka) | [12 empty] | 8 | 18 | 18 | 17 | 6 | 6 |  | 26 | 46 | 43 |  |  |  | 0 | 148320
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 5 |  | 25 | 20 |  |  |  |  | 0 | 46147
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 2 |  | 12 | [5 empty] | 0 | 22512
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 3 |  | 30 | 15 |  |  |  |  | 0 | 48352
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 55 | 55 |  |  |  |  | 0 | 93578
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 110 | 110 | 110 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3012791
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0 | 1.3 | 1.8 | 2.1 | 2.3 | 2.2 | 1.8 | 1.5 | 0.9 | 0.3 | [9 empty] | 13950
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 427320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 2 | 7 | 7 | 7 | 7 | 17 | 7 |  |  |  | 3 |  | 16 | [5 empty] | 0 | 98400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 36 | 68 | 98 | 103 | 119 | 121 | 85 | 90 | 120 | 118 | 118 |  | 141 | 149 | 142 | 114 | 109 | 80 | 70 | 1761120
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 40 |  | 80 | 80 | 20 |  |  |  | 0 | 156480
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 1 |  | 24 | [5 empty] | 0 | 30109
118 | Bibiyana-III 400 MW CCPP | 234 | 236 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 235 | 235 | 235 | 236 | 234 | 236 | 235 |  | 235 | 235 | 234 | 234 | 235 | 233 | 235 | 5638000
| Jamalpur 115 MW PP (United) | [6 empty] | 2 | 70 | 115 | 115 | 115 | 115 | 115 | 115 | 96 | 57 | 57 | 57 |  | 88 | 85 | 80 | 65 | 48 |  | 0 | 1410000
| Anwara 300 MW PP (United) | [7 empty] | 16 | 16 | 16 | 67 | 100 | 173 | 173 | 159 | 88 | 70 | 137 |  | 214 | 198 | 196 | 198 | 88 | 32 | 32 | 1768909
120 | Eastern Zone Total | 5032 | 4675 | 4523 | 4229 | 4251 | 4458 | 4694.6 | 5115.1 | 5164.2 | 5220.1 | 5371.8 | 5612 | 5758 | 5525.9 | 5491.8 | 5312.9 | 5099 | 5505 |  | 6528 | 6375 | 6113 | 6059 | 5698 | 5451 | 5412 | 127416518
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 16 | 16 | 16 | 16 | 16 | 49 | 32 | 32 | 32 | 16 | 51 |  | 115 | 115 | 115 | 115 | 66 |  | 0 | 713280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2 | [26 empty] | 1545
137 | Bhola 95 MW PP (Aggreko) | 72 | 72 | 73 | 72 | 43 | 43 | 43 | 42 | 12 | 12 | 13 | 12 | 14 | 13 | 13 | 13 | 13 | [8 empty] | 0 | 621184
| Bhola 225 MW CCPP | 74 | 73 | 73 | 73 | 73 | 73 | 73 | 74 | 70 | 70 | 70 | 68 | 68 | 50 | 50 | 50 | 80 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 1774000
140 | Bhola 33 MW PP (Venture) | 16 | 15 | 13 | 13 | 14 | 14 | 14 | 13 | 11 | 12 | 12 | 13 | 14 | 14 | 14 | 13 | 12 | 15 |  | 21 | 21 | 21 | 22 | 20 | 20 | 18 | 353605
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 203 | 200 | 201 | 200 | 200 | 199 | 632 | 632 | 632 | 632 | 632 | 634 | 636 | 636 | 637 | 637 | 636 | 636 |  | 884 | 884 | 884 | 887 | 887 | 788 | 398 | 13432727
147 | Bheramara 410 MW CCPP | 330 | 330 | 330 | 330 | 330 | 370 | 375 | 330 | 325 | 330 | 340 | 385 | 330 | 345 | 330 | 335 | 375 | 350 |  | 390 | 375 | 365 | 340 | 320 | 320 | 315 | 8551296
148 | Payra 1320 MW | 170 | 231 | 250 | 260 | 260 | 275 | 315 | 329 | 328 | 331 | 330 | 330 | 330 | 332 | 332 | 332 | 332 | 374 |  | 442 | 466 | 505 | 504 | 406 | 400 | 400 | 8032000
149
150 | Barapukuria TPP Unit-1 | 90 | 85 | 89 | 89 | 88 | 88 | 90 | 87 | 88 | 90 | 90 | 88 | 88 | 91 | 91 | 90 | 90 | 90 |  | 87 | 87 | 89 | 89 | 90 | 90 | 90 | 2127709
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 260 | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 297 | 285 |  | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 6683500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 170 | 140 | 140 | 140 | 140 | 190 | 214 | 190 | 190 | 190 | 190 | 190 | 190 | 160 | 160 | 140 |  | 185 | 190 | 190 | 190 | 190 | 190 | 190 | 4590491
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 382 | 363 | 363 | 360 | 358 | 434 | 419 | 417 | 430 | 418 | 419 | 380 | 381 | 343 | 375 | 361 | 396 |  | 386 | 395 | 404 | 420 | 400 | 400 | 385 | 9565910
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | [6 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 278880
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | [7 empty] | 5 | 7 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 10 | 11 | 11 | 11 | 11 | 11 | 150660
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 235296
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [5 empty] | 17 | 25 | 42 | 60 | 68 | 68 | 68 | 68 | 68 | 26 | 25 | 25 | 25 |  | 68 | 68 | 68 | 51 | 34 | 17 | 0 | 813836
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 11 |  | 17 | [5 empty] | 0 | 47616
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 35 | 100 | 109 | 109 | 109 | 70 | 70 | 70 | 70 | 35 | 70 |  | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 1459392
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 4 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 20 | 0 | 10 |  | 75 | 113 | 113 | 93 | 35 |  | 0 | 655680
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.8 | 3.8 | 5.2 | 6.2 | 6.6 | 6.6 | 6.1 | 4.1 | 2 | 1.1 | 0.1 | [8 empty] | 44047
178
178