## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-04 | Wednesday
|  | Date (day): | 2020-03-04 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11923.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14630 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-03 | 2020-03-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 159 | 63 | 0 | 0 |  |  | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 200 | 200 |  | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 310 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 336 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 320 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 120 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 81 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 25 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 93 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 35 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 60 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 27 | 145 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1902 | 2562 | 3569 | 4171 | 991 | 633
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 67 | 68 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 210 | 210
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 114 | 139 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 34 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 21 | 21
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 100 | 100 |  |  | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.7 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 104 | 215 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 630.7 | 1002 | 1485 | 1620 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 80 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 198 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 285 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 275 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 5 | 33 | 33
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 116 | 102 | 113
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 22 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1267 | 1279 | 1615 | 2290 | 555 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 141 | 143 | 160 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 57 | 92 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 70 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 302.2 | 440 | 493.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 88 | 88 | 85 | 87
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 22 | 22 | 22 | 22 |  | 68 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 134 | 135 | 150 | 150 |  | 180 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 29 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 5 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 64 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 132 | 98 | 68 | 98
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 235 | 234 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1231 | 1281 | 1370 | 1402 | 0 | 413
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 443 | 730 | 647 | 895
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 37 | 83 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 36
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 365 | 320 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 68 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 845 | 1201 | 1342 | 2141 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 9 | 21 | 21 | 22 |  | 11 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 0 | 130 | 135 |  | 59 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 98 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 129 | 229 | 310 | 392 | 0 | 70
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 170 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 401 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 10 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 51 | 100 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 736 | 905 | 1238 | 1505 | 611 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 91 | 91 | 100 | 100
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 209 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 321.2 | 441 | 501 | 527 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7364.1 | 9340 | 11923.6 | 14630 | 2619 | 1382
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6948.5881 | 8813 | 11250.823 | 13804.5171
A. |  | 2020-03-03 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9340 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5676.1 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9340 | MW
3 | Day peak Generation : |  |  | 7364.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8813 | MW
4 | Evening peak Generation : |  |  | 9340 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 177.6318 | MKWHr | By Solar | 0.083944 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 133.2533 | MKWHr |  | By Oil: | 20.657 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.5056 | MKWHr |  | By Hydro: | 1.5665 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2619 | MW | Dhaka | 3189 | 3189 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1382 | MW | Chittagong | 877 | 877 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4001 | MW | Khulna | 1042 | 1042 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1175.35 | MMCFD |  |  | Rajshahi | 982 | 982 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 122881486.02 | ii) Oil : | Taka | 158066889.42 | Comilla | 732 | 732 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 39707802.66 | Total | Taka | 320656178.1 | Mymensingh | 800 | 800 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3.0905 | MKWHr. | Sylhet | 337 | 337 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -285 | MW (E to W) at | 19:30 | hrs | Barisal | 223 | 223 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -467 | MW at | 1:00 | hrs | Rangpur | 631 | 631 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.8° C |  |  | Total | 8813 | 8813 |  | 0
B. |  | 2020-03-04 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 29.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14630 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8300 | MW
4 | Reserve(Generation end) |  |  |  | 4830 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 186.3802 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6045 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.4073 | MKWHr. | ii) HVDC Flow at Peak Time |  | 730 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.1581 | MKWHr. | iii) Maximum HVDC Flow : |  | 737 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.43 |  | (b) Today: | 89.23 |  | (c) Rule Curve: |  | 92.52
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-03-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 174 | 0 | 0 | 300 | 0 | 0 | 397 | 303 |  | 0 | 450 | 120 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 24 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 38 | 0 | 80 | 0 | 285 | 280 | 164 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 96 | 130 | 56 | 20 | 0 | 85 | 22 | 53 | 51 | 130 | 139 | 63 | 79 | 0 | 110 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 235 | 7 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 212 | 0 | 275 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5595 | 1709 | 7304 | 3935 | 212 | 1883 | 739 | 371 | 68 | 0 | 96 | 0 | 0 | 89.45
2:00 | 72 | 174 | 0 | 0 | 300 | 0 | 0 | 395 | 314 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 24 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 80 | 0 | 285 | 280 | 166 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 92 | 130 | 8 | 20 | 0 | 85 | 22 | 53 | 51 | 130 | 140 | 64 | 79 | 0 | 110 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 7 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 |  | 212 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 5266 | 1664 | 6930 | 3924 | 212 | 1935 | 328 | 371 | 68 | 0 | 92 | 0 | 0 | 89.45
3:00 | 72 | 135 | 0 | 0 | 300 | 0 | 0 | 393 | 334 |  | 0 | 450 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 0 | 80 | 0 | 285 | 280 | 170 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 90 | 131 | 4 | 20 | 0 | 85 | 22 | 53 | 25 | 130 | 137 | 54 | 40 | 0 | 110 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 212 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5064 | 1652 | 6716 | 3870 | 212 | 1882 | 223 | 371 | 68 | 0 | 90 | 0 | 0 | 89.44
4:00 | 72 | 100 | 0 | 0 | 300 | 0 | 0 | 367 | 333 |  | 0 | 380 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 285 | 285 | 164 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 86 | 149 | 8 | 20 | 0 | 85 | 22 | 53 | 48 | 130 | 134 | 45 | 5 | 0 | 110 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 207 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4881 | 1608 | 6489 | 3791 | 207 | 1764 | 203 | 370 | 68 | 0 | 86 | 0 | 0 | 89.44
5:00 | 72 | 74 | 0 | 0 | 300 | 0 | 0 | 330 | 298 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 285 | 285 | 164 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 86 | 150 | 8 | 20 | 0 | 85 | 22 | 22 | 48 | 100 | 133 | 45 | 5 | 0 | 80 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 208 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4543 | 1559 | 6102 | 3664 | 208 | 1577 | 128 | 371 | 68 | 0 | 86 | 0 | 0 | 89.43
6:00 | 72 | 74 | 0 | 0 | 300 | 0 | 0 | 335 | 293 |  | 0 | 350 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 80 | 0 | 285 | 285 | 185 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 88 | 149 | 10 | 20 | 0 | 85 | 22 | 30 | 48 | 130 | 134 | 45 | 50 | 0 | 80 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 208 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 91 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4642 | 1629 | 6271 | 3720 | 208 | 1686 | 130 | 371 | 68 | 0 | 88 | 0 | 0 | 89.43
7:00 | 72 | 74 | 0 | 0 | 300 | 0 | 0 | 340 | 261 |  | 0 | 320 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 12 | 25 | 0 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 24 | 0 | 80 | 0 | 285 | 285 | 182 | 8 | 50 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 86 | 162 | 40 | 19 | 0.1 | 85 | 22 | 48 | 48 | 100 | 133 | 45 | 50 | 0 | 80 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 234 | 8 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 |  | 540 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 90 | 0 | 280 | 0 | 0 | 130 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 |  | 4615.4 | 1869.2 | 6484.6 | 3621 | 540 | 1596 | 203 | 370 | 67 | 0 | 86 | 1.6 | 0 | 89.42
8:00 | 37 | 75 | 0 | 0 | 177 | 0 | 0 | 328 | 241 |  | 0 | 300 | 120 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 161 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 80 | 0 | 235 | 250 | 161 | 8 | 50 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 88 | 110 | 48 | 20 | 0.4 | 85 | 22 | 5 | 5 | 100 | 132 | 45 | 5 | 0 | 79 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 60 | 0 | 0 | 1.4 | 66 | 0 | 0 | 0 | 0 |  | 464 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 88 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 70 | 0 |  | 3948.8 | 1727.3 | 5676.1 | 3086 | 464 | 1201 | 368 | 348 | 67 | 51 | 88 | 3.1 | 0 | 89.42
9:00 | 37 | 74 | 0 | 0 | 204 | 0 | 0 | 312 | 290 |  | 0 | 300 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 197 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 0 | 80 | 0 | 240 | 250 | 158 | 8 | 50 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 110 | 65 | 20 | 0.7 | 87 | 22 | 5 | 5 | 100 | 135 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 10 | 0 | 0 | 234 | 109 | 0 | 0 | 2.9 | 66 | 0 | 0 | 0 | 0 |  | 464 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 89 | 0 | 260 | 0 | 17 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 70 | 0 |  | 4095.6 | 1938.8 | 6034.4 | 3208 | 464 | 1395 | 459 | 349 | 67 | 68 | 18 | 6.4 | 0 | 89.41
10:00 | 37 | 73 | 0 | 0 | 204 | 0 | 0 | 360 | 300 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 0 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 216 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 80 | 0 | 300 | 270 | 170 | 8 | 50 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 148 | 73 | 20 | 1.3 | 87 | 22 | 5 | 5 | 100 | 132 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 234 | 75 | 0 | 0 | 3.6 | 71 | 0 | 0 | 0 | 0 |  | 451 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 91 | 0 | 260 | 0 | 17 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 70 | 0 |  | 4349.9 | 1991.9 | 6341.8 | 3423 | 451 | 1508 | 426 | 351 | 67 | 68 | 38 | 9.8 | 0 | 89.41
11:00 | 37 | 118 | 0 | 0 | 300 | 0 | 0 | 373 | 300 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 0 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 210 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 100 | 0 | 330 | 295 | 199 | 8 | 50 | 21 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 72 | 141 | 73 | 20 | 2 | 89 | 22 | 2 | 5 | 130 | 132 | 62 | 60 | 0 | 118 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 235 | 75 | 0 | 0 | 3.7 | 71 | 0 | 0 | 0 | 0 |  | 451 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 90 | 0 | 260 | 0 | 17 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 70 | 0 |  | 4865.7 | 2015.6 | 6881.3 | 3774 | 451 | 1632 | 456 | 350 | 67 | 68 | 72 | 11.3 | 0 | 89.4
12:00 | 37 | 159 | 0 | 0 | 300 | 0 | 0 | 365 | 330 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 15 | 25 | 25 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 218 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 350 | 320 | 204 | 26 | 90 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 141 | 57 | 20 | 2.2 | 88 | 22 | 29 | 5 | 130 | 134 | 60 | 76 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 27 | 0 | 10 | 0 | 0 | 235 | 75 | 0 | 0 | 4.7 | 104 | 0 | 0 | 0 | 0 |  | 443 | 0 | 365 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 91 | 0 | 209 | 0 | 15 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 80 | 0 |  | 5332.9 | 2031.2 | 7364.1 | 3996 | 443 | 1768 | 631 | 300 | 67 | 66 | 80 | 13.1 | 0 | 89.4
13:00 | 37 | 167 | 0 | 0 | 320 | 0 | 0 | 358 | 320 |  | 0 | 420 | 150 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 25 | 20 | 25 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9 | 0 | 80 | 0 | 320 | 315 | 147 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 84 | 124 | 56 | 20 | 2.1 | 88 | 22 | 53 | 5 | 163 | 134 | 61 | 78 | 0 | 150 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 42 | 0 | 10 | 0 | 0 | 233 | 112 | 0 | 0 | 5.1 | 108 | 0 | 0 | 0 | 0 |  | 544 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 3 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 91 | 0 | 210 | 0 | 15 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 12 | 0 | 0 | 5.5 | 109 | 0 |  | 5502.2 | 2065.5 | 7567.7 | 3771 | 544 | 1857 | 864 | 301 | 68 | 66 | 84 | 12.7 | 0 | 89.39
14:00 | 37 | 168 | 0 | 0 | 320 | 0 | 0 | 343 | 270 |  | 0 | 400 | 150 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | 80 | 0 | 270 | 330 | 159 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 96 | 126 | 58 | 20 | 1.9 | 89 | 22 | 53 | 5 | 163 | 134 | 59 | 78 | 0 | 118 | 19 | 0 | 8 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 0 | 10 | 0 | 0 | 234 | 85 | 0 | 0 | 4.9 | 70 | 0 | 0 | 0 | 0 |  | 574 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 18 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 91 | 0 | 220 | 0 | 15 | 200 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 32 | 0 | 0 | 1.9 | 50 | 0 |  | 5341.8 | 2148.9 | 7490.7 | 3751 | 574 | 1844 | 772 | 311 | 68 | 66 | 96 | 8.7 | 0 | 89.39
15:00 | 37 | 168 | 0 | 0 | 320 | 0 | 0 | 369 | 285 |  | 0 | 420 | 150 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 50 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 210 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 2 | 0 | 80 | 0 | 260 | 280 | 161 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 14 | 100 | 125 | 50 | 20 | 1.1 | 88 | 22 | 50 | 5 | 163 | 133 | 60 | 78 | 0 | 148 | 19 | 0 | 10 | 320 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 16 | 0 | 10 | 0 | 0 | 235 | 85 | 0 | 0 | 3.2 | 132 | 0 | 0 | 0 | 0 |  | 575 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 18 | 0 | 0 | 0 | 0 | 17 | 8 | 9 | 91 | 0 | 253 | 0 | 13 | 200 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 90 | 0 |  | 5486.3 | 2239.9 | 7726.2 | 3808 | 575 | 1937 | 821 | 344 | 68 | 64 | 100 | 9.2 | 0 | 0
16:00 | 37 | 168 | 0 | 0 | 320 | 0 | 0 | 341 | 300 |  | 0 | 380 | 120 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 59 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 3 | 0 | 80 | 0 | 280 | 270 | 187 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 92 | 126 | 48 | 20 | 0.8 | 88 | 22 | 24 | 5 | 130 | 134 | 45 | 40 | 0 | 118 | 19 | 0 | 10 | 315 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 16 | 0 | 10 | 0 | 0 | 235 | 64 | 0 | 0 | 2 | 140 | 0 | 0 | 0 | 0 |  | 575 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 35 | 0 | 0 | 0 | 0 | 17 | 8 | 9 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 109 | 0 |  | 5281.8 | 2227.8 | 7509.6 | 3723 | 575 | 1815 | 810 | 370 | 68 | 51 | 92 | 5.6 | 0 | 0
17:00 | 37 | 169 | 0 | 0 | 320 | 0 | 0 | 346 | 280 |  | 0 | 350 | 120 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 70 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 29 | 33 | 17 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 4 | 25 | 0 | 5 | 0 | 80 | 0 | 280 | 270 | 173 | 8 | 84 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 96 | 141 | 49 | 20 | 0.3 | 88 | 22 | 25 | 5 | 130 | 135 | 45 | 20 | 0 | 97 | 19 | 0 | 10 | 295 | 24 | 0 | 0 | 5 | 0 | 0 | 7 | 0 | 15 | 0 | 10 | 0 | 1 | 235 | 64 | 0 | 0 | 0.7 | 142 | 0 | 0 | 0 | 0 |  | 575 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 9 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 109 | 0 |  | 5164 | 2150.3 | 7314.3 | 3677 | 575 | 1646 | 828 | 371 | 68 | 51 | 96 | 2.3 | 0 | 0
18:00 | 37 | 169 | 0 | 0 | 270 | 0 | 0 | 298 | 280 |  | 0 | 320 | 120 | 22 | 15 | 9 | 0 | 0 | 0 | 0 | 70 | 74 | 0 | 14 | 0 | 0 | 2 | 35 | 30 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 14 | 0 | 80 | 0 | 280 | 270 | 184 | 8 | 85 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 19 | 110 | 142 | 58 | 20 | 0 | 87 | 22 | 25 | 5 | 100 | 135 | 45 | 60 | 0 | 67 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 16 | 0 | 0 | 7 | 0 | 18 | 0 | 68 | 0 | 8 | 234 | 77 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 |  | 575 | 0 | 320 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 14 | 34 | 0 | 0.1 | 109 | 0 |  | 5380 | 2250.1 | 7630.1 | 3594 | 575 | 1652 | 1190 | 371 | 68 | 70 | 110 | 0.1 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 168 | 0 | 0 | 270 | 0 | 0 | 350 | 320 |  | 0 | 400 | 120 | 100 | 60 | 50 | 0 | 0 | 0 | 0 | 95 | 93 | 16 | 40 | 0 | 0 | 33 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 44 | 50 | 0 | 20 | 0 | 80 | 0 | 285 | 275 | 198 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 22 | 116 | 143 | 92 | 20 | 0 | 88 | 22 | 51 | 5 | 130 | 134 | 64 | 78 | 0 | 99 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 60 | 0 | 0 | 43 | 0 | 124 | 0 | 100 | 0 | 68 | 234 | 115 | 0 | 28 | 0 | 214 | 0 | 0 | 0 | 0 |  | 737 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 94 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 67 | 73 | 0 | 0 | 109 | 0 |  | 6493 | 2774 | 9267 | 3742 | 737 | 1927 | 2180 | 370 | 68 | 127 | 116 | 0 | 0 | 0
19:30 | 37 | 63 | 0 | 0 | 310 | 0 | 0 | 336 | 320 |  | 0 | 400 | 120 | 100 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 40 | 0 | 0 | 35 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 45 | 50 | 0 | 20 | 0 | 80 | 0 | 285 | 275 | 198 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 116 | 143 | 92 | 20 | 0 | 88 | 22 | 53 | 5 | 130 | 135 | 64 | 78 | 0 | 98 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 60 | 0 | 0 | 70 | 0 | 145 | 0 | 100 | 0 | 80 | 234 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 730 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 68 | 70 | 0 | 0 | 109 | 0 |  | 6564 | 2776 | 9340 | 3720 | 730 | 1939 | 2263 | 371 | 68 | 133 | 116 | 0 | 0 | 0
20:00 | 37 | 0 | 0 | 0 | 320 | 0 | 0 | 340 | 320 |  | 0 | 400 | 120 | 100 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 40 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 45 | 50 | 16 | 31 | 0 | 80 | 0 | 285 | 275 | 206 | 8 | 84 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 114 | 144 | 92 | 20 | 0 | 88 | 22 | 53 | 5 | 130 | 135 | 64 | 78 | 0 | 97 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 60 | 0 | 0 | 70 | 0 | 146 | 0 | 100 | 0 | 80 | 234 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 737 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 50 | 72 | 0 | 0 | 109 | 0 |  | 6541 | 2765 | 9306 | 3688 | 737 | 1944 | 2253 | 370 | 67 | 133 | 114 | 0 | 0 | 0
21:00 | 37 | 0 | 0 | 0 | 302 | 0 | 0 | 342 | 319 |  | 0 | 400 | 120 | 100 | 48 | 30 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 40 | 50 | 19 | 31 | 0 | 80 | 0 | 285 | 290 | 200 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 116 | 144 | 91 | 20 | 0 | 89 | 22 | 53 | 34 | 130 | 133 | 64 | 78 | 0 | 98 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 145 | 0 | 100 | 0 | 40 | 234 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 737 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 96 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 109 | 0 |  | 6288 | 2608 | 8896 | 3735 | 737 | 1961 | 1904 | 351 | 67 | 25 | 116 | 0 | 0 | 0
22:00 | 37 | 0 | 0 | 0 | 300 | 0 | 0 | 342 | 320 |  | 0 | 400 | 120 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 50 | 19 | 30 | 0 | 80 | 0 | 280 | 290 | 195 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 104 | 130 | 91 | 20 | 0 | 88 | 22 | 53 | 48 | 130 | 134 | 65 | 78 | 0 | 98 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 10 | 0 | 0 | 234 | 88 | 0 | 17 | 0 | 216 | 0 | 0 | 0 | 0 |  | 737 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5882 | 2425 | 8307 | 3740 | 737 | 1965 | 1343 | 351 | 67 | 0 | 104 | 0 | 0 | 0
23:00 | 37 | 0 | 150 | 0 | 325 | 0 | 0 | 340 | 328 |  | 0 | 400 | 120 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 215 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 38 | 0 | 80 | 0 | 315 | 305 | 199 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 98 | 129 | 91 | 20 | 0 | 86 | 22 | 53 | 48 | 130 | 133 | 64 | 78 | 0 | 99 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 233 | 24 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 696 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 91 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5689 | 2202 | 7891 | 3978 | 696 | 1920 | 811 | 321 | 67 | 0 | 98 | 0 | 0 | 0
24:00 | 37 | 0 | 150 | 0 | 298 | 0 | 0 | 362 | 335 |  | 0 | 400 | 120 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 0 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 19 | 40 | 0 | 80 | 0 | 280 | 270 | 198 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 94 | 130 | 91 | 20 | 0 | 86 | 22 | 53 | 48 | 163 | 134 | 65 | 78 | 0 | 117 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 24 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 381 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 8 | 91 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5519 | 1910 | 7429 | 3880 | 381 | 1976 | 710 | 321 | 67 | 0 | 94 | 0 | 0 | 0
KWH | 1136000 | 2729900 | 299000 | 0 | 6925645 | 0 | 0 | 8557570 | 7241000 |  | 0 | 8968250 | 3214313 | 682560 | 251424 | 178144 | 0 | 0 | 0 | 0 | 1361280 | 815616 | 31200 | 111882 | 0 | 0 | 113520 | 704160 | 297686 | 0 | 313668 | 600000 | 577620 | 720800 | 600500 | 0 | 0 | 594480 | 972000 | 2600000 | 0 | 0 | 4859445 | 0 | 2614508 | 0 |  | 0 | 0 | 33193 | 0 | 172800 | 415200 | 251760 | 471840 | 0 | 1998790 | 0 | 7127000 | 6943000 | 4361000 | 250909 | 1701630 | 181944 | 136320 | 0 | 1103596 | 0 | 0 | 0 | 356040 | 100260 | 496500 | 429500 | 2158080 | 3166520 | 1335360 | 457488 | 13150 | 2050000 | 531216 | 935400 | 638856 | 3276245 | 3023000 | 1331328 | 1270080 | 0 | 2498700 | 241000 | 0 | 184680 | 7529750 | 382464 | 155096 | 0 | 160581 | 0 | 0 | 381600 | 0 | 806400 | 2565 | 473280 | 0 | 240873 | 5595000 | 1550400 | 0 | 137163 | 30360 | 2501564 | 0 | 0 | 0 | 0 |  | 11407272 | 0 | 7949376 | 0 | 626880 | 0 | 0 | 0 | 0 | 0 | 0 | 1863000 | 323400 | 497280 | 0 | 0 | 0 | 0 | 0 | 788304 | 391000 | 0 | 0 | 0 | 0 | 410160 | 230724 | 212980 | 2157818 | 0 | 6347800 | 0 | 115000 | 4254782 | 0 | 0 | 0 | 963358 | 0 | 0 | 0 | 9124727 | 0 | 0 | 95808 | 181728 | 262080 | 0 | 37869 | 1728768 | 0 |  | 127661652 | 49970114 | 177631766 | 90194030 | 11407272 | 43059295 | 19689350 | 8505618 | 1566480 | 967697 | 2158080 | 83944 | 0
Fuel Cost | 1272320 | 2948292 | 319930 | 0 | 5124977.3 | 0 | 0 | 6161450.4 | 5503160 |  | 0 | 7174600 | 2892881.7 | 6962112 | 2722921.92 | 1827757.44 | 0 | 0 | 0 | 0 | 15110208 | 8286658.56 | 309192 | 1172523.36 | 0 | 0 | 1062547.2 | 6752894.4 | 2839924.44 | 0 | 235251 | 450000 | 0 | 0 | 0 | 0 | 0 | 154564.8 | 252720 | 3978000 | 0 | 0 | 5102417.25 | 0 | 3320425.16 | 0 |  | 0 | 0 | 348194.57 | 0 | 1643328 | 3886272 | 231619.2 | 1311715.2 | 0 | 2098729.5 | 0 | 5273980 | 5832120 | 4012120 | 245890.82 | 2263167.9 | 149194.08 | 140409.6 | 0 | 1578142.28 | 0 | 0 | 0 | 363160.8 | 75195 | 938385 | 322125 | 14890752 | 2596546.4 | 12699273.6 | 466637.76 | 215660 | 2788000 | 722453.76 | 1272144 | 798570 | 4062543.8 | 2781160 | 1983678.72 | 2235340.8 | 0 | 3798024 | 383190 | 0 | 433998 | 5346122.5 | 286848 | 117872.96 | 0 | 1681283.07 | 0 | 0 | 3670992 | 0 | 8136576 | 29600.1 | 4410969.6 | 0 | 2256980.01 | 5259300 | 13597008 | 0 | 1296190.35 | 0 | 23064420.08 | 0 | 0 | 0 | 0 |  | 30799634.4 | 0 | 6200513.28 | 0 | 6043123.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1490400 | 501270 | 5340787.2 | 0 | 0 | 0 | 0 | 0 | 7804209.6 | 4054670 | 0 | 0 | 0 | 0 | 451176 | 380694.6 | 161225.86 | 13745300.66 | 0 | 25962502 | 0 | 3246450 | 3744208.16 | 0 | 0 | 0 | 1531739.22 | 0 | 0 | 0 | 6661050.71 | 0 | 0 | 879517.44 | 1619196.48 | 2447827.2 | 0 | 0 | 0 | 0 |  | 243933613.39 | 123065496.01 | 366999109.4 | 83252918.49 | 30799634.4 | 39628567.53 | 146358843.25 | 39707802.66 | 407284.8 | 11708046.17 | 14890752 | 245260.1 | 0
Yesterday Day Peak | 37 | 159 | 0 | 0 | 300 | 0 | 0 | 365 | 330 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 15 | 25 | 25 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 218 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 350 | 320 | 204 | 26 | 90 | 29 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 141 | 57 | 20 | 2.2 | 88 | 22 | 29 | 5 | 130 | 134 | 60 | 76 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 27 | 0 | 10 | 0 | 0 | 235 | 75 | 0 | 0 | 4.7 | 104 | 0 | 0 | 0 | 0 |  | 443 | 0 | 365 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 91 | 0 | 209 | 0 | 15 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 80 | 0 |  | 7364.1 | DayPeak
Yesterday Evening Peak | 37 | 63 | 0 | 0 | 310 | 0 | 0 | 336 | 320 | 0 | 0 | 400 | 120 | 100 | 81 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 16 | 40 | 0 | 0 | 35 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 | 0 | 0 | 0 | 17 | 0 | 45 | 50 | 0 | 20 | 0 | 80 | 0 | 285 | 275 | 198 | 8 | 91 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 116 | 143 | 92 | 20 | 0 | 88 | 22 | 53 | 5 | 130 | 135 | 64 | 78 | 0 | 98 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 60 | 0 | 0 | 70 | 0 | 145 | 0 | 100 | 0 | 80 | 234 | 115 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 730 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 68 | 70 | 0 | 0 | 109 | 0 |  | 9340 | EvPeak
Forecast for Evening | 37 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 21 | 20 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 113 | 150 | 95 | 22 | 0 | 87 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 98 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 895 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 36 | 70 | 40 | 135 | 22 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 11 | 11 | 100 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 37 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 21 | 10 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 102 | 160 | 95 | 22 | 1.6 | 85 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 68 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 647 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 130 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 100 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 37 | 0 | 200 | 0 | 325 | 0 | 0 | 348 | 367 | 0 | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 80 | 0 | 320 | 300 | 192 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 84 | 160 | 82 | 20 | 0.6 | 87 | 22 | 50 | 48 | 110 | 126 | 65 | 50 | 0 | 68 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6.5 | 0 | 0 | 0 | 233 | 36 | 0 | 0 | 1.7 | 33 | 0 | 0 | 0 | 0 | 0 | 641 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 90 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 0 | 9 | 0 | 0.8 | 50 | 0 | 0
199
| Minimum Generation |  | 5676.1 | 8:00
| Highest Generation |  | 9340 | 19:30
| Day Peak Generation |  | 7364.1 | 12:00
| Evening Peak Generation |  | 9340 | 19:30
| HVDC Max Flow |  | 737 | 19:00
| HVDC EvPeak Flow |  | 730 | 19:30
| Load factor L.F |  | 79.24%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-04
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7364.1 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6045 | MW
Evening Peak Generation : |  | 9340 | MW Hour : | 19:30 | Available Max Generation : |  | 14630 | MW
E.P. Demand (at gen end) : |  | 9340 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 9340 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4830 | MW
Total Gen. (MKWH) : |  | 177.6318 | System Load Factor : | 79.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -467 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-04
Actual : | 89.23 | Ft.(MSL) , | Rule curve : | 92.52 | Ft.( MSL )
Gas Consumed : | Total = | 1175.35 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 122881486.02
: |  | Coal : | 39707802.66 | Oil : | 158066889.42 | Total : | 320656178.1
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3450.6969 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1169.8229 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1047.4801 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 946.2586 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 855.246 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 690.1441 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 390.5338 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 177.8163 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 532.2512 |  |  | 0 | 0%
Total | 0 |  | 9260.2498 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Bhola 225 MW STG
3) Ghorasal Unit-2,3 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) After maintenance Gopalganj 132/33 kV T2 transformer was switched on at 09:30.
b) Chauddagram 132/33 kV T1 transformer & associated Bus were under shut down from 10:55 to
14:33 for D/W.
c) Comilla(N) 132/33 kV T3 & T4 transformers tripped at 08:47 showing E/F relays at 33 kV end and |  |  |  |  | About 56 MW power interruption occurred under Comilla(N) S/S areas
was switched on at 09:06. |  |  |  |  | from 08:37 to 09:06.
d) Aminbazar-Savar 132 kV Ckt-2 was under shut down from 09:21 to 20:42 for D/W.
e) Mymensingh-Jamalpur 132 kV Ckt-2 was under shut down from 09:40 to 17:36 for D/W.
f) Bhola 225 MW CCPP GT-1 & 2 tripped at 12:30 due to gas pressure low and were synchronized at
20:00,21:28 respectively.
g) Kallyanpur-Lalbagh 132 kV Ckt-1 & 2 were under shut down from 13:30 to 15:13 for line maintenance.
h) Ghorashal unit-3 was force shut down at 19:32 due to LP OTC leakage.
i) Uttara 132/33 kV T-2 transformer tripped at 19:49 showing AC Directional Over current Relay at 33 V
end.
j) Ghorashal unit-4 was synchronized at 22:04.
k) Shahjibazar 132/33 kV T-2 transformer tripped at 03:48(04-03-2020) showing operation buchholz |  |  |  |  | About 15 MW power interruption occurred under Shahjibazar S/S areas
relay at 33 kV end and was switched on at 04:17(4/3/2020). |  |  |  |  | from 03:48 to 04:17(4/3/2020).
l) Kodda S/S-Gazipur 100 MW P/P 132 kV Ckt was shut down at 07:03(04/03/2020) for D/W.
m) Ashuganj-Kishoreganj 132 kV Ckt-1 was shut down at 07:54(04/03/2020) for D/W.
n) Kishoreganj 132/33 kV T1 transformer was shut down at 07:51(04/03/2020) for D/W.
o) Jamalpur-Mymensingh 132 kV Ckt-1 was shut down at 07:47(04/03/2020) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 1136000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 63 | 2729900
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 299000 | Gas shortage.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 6925645 | Gas shortage.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 8557570 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7241000 | spinning reserve
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8968250 | spinning reserve
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 682560
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3214313 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 81 | 251424 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 178144
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 40 | 111882 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 313668
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1361280
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 815616 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 35 | 113520 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 704160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 31200 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 297686
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1177620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 720800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 600500
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 60 | 160581 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 145 | 806400
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2562 | 47398719
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 2565
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 415200
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1566480 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4859445
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2614508 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 137163 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 33193 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 473280
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 251760
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 471840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 172800 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30360
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 215 | 2501564 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 1002 | 16130158
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1998790 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4361000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7127000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6943000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 181944
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 136320 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 250909 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1103596
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 240873 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 1701630
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 356040
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 100260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2158080
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 496500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 429500
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1279 | 27585442
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 143 | 3166520 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 457488
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 92 | 1335360
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 70 | 381600 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1550400
| Mymensingh Area Total |  |  |  | 637 | 440 | 6904518
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2050000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 531216
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3276245 | spinning reserve
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 135 | 3023000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 935400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 5 | 638856 | spinning reserve
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 155096
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1331328 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1270080 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 98 | 2498700
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 241000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 382464
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7529750 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 234 | 5595000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 184680
| Sylhet Area Total |  |  |  | 1949 | 1281 | 29642815
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 730 | 11407272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 626880 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7949376 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 68 | 181728 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1201 | 20165256
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 497280
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 323400 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 1863000 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 963358 | Gas shortage.
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | Machine problem
| Barisal Area Total |  |  |  | 462 | 229 | 3647038
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 391000
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4254782 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 401 | 9124727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 410160 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 230724
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212980
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 788304
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 95808 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1728768
| Rajshahi Area Total |  |  |  | 2183 | 905 | 17237253
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 91 | 2157818
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6347800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 115000 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 262080 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37869
| Rangpur Area Total |  |  |  | 605 | 441 | 8920567
| Total |  |  |  | 19107 | 9340 | 177631766
| Eastern Grid Total |  |  |  | 13543 | 6564 | 127661652
| Western Grid Total |  |  |  | 5564 | 2776 | 49970114
| National Grid Total |  |  |  | 19107 | 9340 | 177631766
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-03
(a) ENTIRE EASTERN GRID : |  | 5935 | MW | (b) ENTIRE WESTERN GRID : |  | 2878 | MW
i) Dhaka area |  | 3189 | MW | i) Khulna area |  | 1042 | MW
ii) Chittagong area |  | 877 | MW | ii) Rajshahi area |  | 982 | MW
iii) Comilla area |  | 732 | MW | iii) Barisal area |  | 223 | MW
iv) Mymensingh area |  | 800 | MW | iv) Rangpur area |  | 631 | MW
v) Sylhet area |  | 337 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8813 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 96 | 16:00 | Sherpur | 88 | 18:30 | Benapol | 34 | 19:00
Munsiganj | 84 | 20:00 | Srimongal | 30 | 19:30 | Jhenida | 82 | 19:00
Sonargaon | 71 | 22:00 | Shahjibazar | 78 | 18:30 | Bottail | 94 | 18:30
Shyampur | 168 | 1:00 | Fenchuganj | 28 | 19:00 | G.K Project | 38 | 19:00
Bhulta | 162 | 20:00 | Kulawara | 28 | 19:00 | Faridpur | 120 | 19:00
Madanganj | 56 | 19:30 | Sylhet | 104 | 19:00 | Madaripur | 57 | 21:00
Shitalakhya | 101 | 16:00 | Chatak | 17 | 18:30 | Sariatpur | 38 | 19:00
Rahim steel | 19 | 13:00 | Sunamganj | 28 | 19:30 | Gopalganj | 66 | 19:30
Matuail | 86 | 10:00 | Biani Bazar | 31 | 20:00 | Bagerhat | 68 | 19:30
Ghorasal | 48 | 1:00 | Comilla (S) | 118 | 18:30 | Mongla | 36 | 9:00
Narsingdi | 129 | 19:30 | Comilla(N) | 79 | 18:30 | Satkhira | 76 | 19:00
Haripur (SBU) | 92 | 21:00 | Chandpur | 53 | 19:00 | Gallamari | 37 | 13:00
Ullon | 54 | 20:00 | Feni | 80 | 19:00 | Magura | 34 | 18:30
Hasnabad | 135 | 20:00 | Chowmuhani | 94 | 18:30 | Norail | 26 | 19:00
Magbazar | 85 | 13:00 | Ashuganj | 43 | 19:00 | Chuadanga | 63 | 18:30
Maniknagar | 88 | 13:00 | Daudkandi | 94 | 21:00 | Barisal(N) | 28 | 21:00
Bangabhaban | 28 | 13:00 | B.Baria | 100 | 20:00 | Barisal (S) | 72 | 18:30
Narinda | 80 | 14:00 | Ramganj | 68 | 21:00 | Patuakhali | 74 | 21:00
Dhanmondi | 106 | 14:00 | Chaddagram | 22 | 18:30 | Bhandaria | 36 | 19:30
Lalbag | 53 | 17:00 | PHP | 2 | 12:00 | Borhan Uddin | 24 | 23:00
Madartek | 51 | 20:00 | Madunaghat | 44 | 17:00 | Ishurdi | 45 | 18:30
Dhaka University |  |  | Hathazari | 70 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 80 | 18:00 | Khulshi | 158 | 12:00 | Natore | 99 | 19:00
Kalyanpur | 78 | 18:00 | Halishahar | 105 | 19:00 | Bogra | 147 | 19:00
Gulshan | 96 | 18:00 | Baraulia | 132 | 0:00 | Noagaon | 90 | 19:00
Uttara | 63 | 18:00 | Sikalbaha | 26 | 20:00 | Rajshahi | 98 | 19:30
Uttara New | 21 | 18:00 | Dohazari | 70 | 20:00 | Rajshahi New | 9 | 19:30
Kamrangirchar | 72 | 18:00 | Cox'sbazar | 81 | 20:00 | C.Nawabganj | 59 | 19:30
Savar | 101 | 18:00 | Chandraghona | 24 | 19:00 | Amnura | 27 | 19:00
Bhasantec | 108 | 18:00 | Kaptai | 3.5 | 18:00 | Pabna | 78 | 19:30
Agargaon | 39 | 18:00 | A. Khaer Stl. | 22 | 10:00 | Shahjadpur | 81 | 18:30
Satmosjid | 66 | 18:00 | Bakulia | 80 | 14:00 | Serajganj | 81 | 11:00
Tongi | 108 | 12:00 | Julda | 21 | 8:00 | Niyamatpur | 75 | 8:00
Kabirpur | 174 | 19:00 | TK chemical | 8 | 2:00 | Joypurhat | 54 | 19:00
Basundhara | 111 | 18:30 | Modern Steel | 16 | 11:00 | Sherpur(Bogura) | 38 | 19:00
Manikganj | 64 | 21:00 | Shahmirpur | 25 | 18:00 | Mohastangor | 39 | 19:00
Joydevpur | 136 | 13:00 | Khagrachhari | 16 | 18:30 | Rangpur | 114 | 19:30
New Tongi | 85 | 12:00 | Matarbari | 24 | 19:00 | Lalmonirhat | 41 | 8:00
Korda | 163 | 21:00 | Baroiar Hat | 30 | 18:00 | Saidpur | 95 | 18:30
Dhamrai | 54 | 15:00 | Rangamati | 10 | 18:30 | Purbasadipur | 94 | 8:00
Rajendrapur | 70 | 19:30 | Abul Khair 230 | 162 | 23:00 | Thakurgaon | 66 | 20:00
Valuka | 86 | 19:00 | BSRM | 109 | 15:00 | Palashbari | 100 | 19:00
Tangail | 166 | 21:00 | GPH Ispat | 50 | 9:00 | Barapukuria | 47 | 20:00
Mymensing | 190 | 18:30 | Goalpara | 19 | 19:00 | Panchagar | 39 | 19:00
Kishorganj | 98 | 19:30 | Central s/s | 49 | 19:00 | Joldhaka | 23 | 19:30
Netrokona | 92 | 19:00 | Noapara | 63 | 19:00 | Kurigram | 44 | 0.8125
Jamalpur | 109 | 19:00 | Jessore | 89 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-03 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.875 | 395 | 0.625 | Kaliakoir | 387 | 0.20833 | 371 | 0.625
Bheramara | 404 | 0.041667 | 395 | 0.79167 | Bhulta | 400 | 0.33333 | 385 | 0.625
Ashuganj(N) | 404 | 0.33333 | 390 | 0.625 | Gopalganj | 433 | 0.29167 | 361 | 0.45833
Payra | 435 | 0.29167 | 0 | 0.33333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 236 | 0.041667 | 235 | 0.29167 | Hathazari | 224 | 0.91667 | 220 | 0.16667
Ishurdi | 242 | 0.20833 | 228 | 0.8125 | Megnaghat | 238 | 0.8125 | 232 | 0.041667
Ashuganj | 242 | 0.083333 | 236 | 0.625 | Fenchuganj | 242 | 0.20833 | 238 | 0.45833
Serajganj | 236 | 0.083333 | 228 | 0.54167 | Siddhirganj | 239 | 0.33333 | 228 | 0.66667
Baghabari | 245 | 0.083333 | 238 | 0.79167 | Maniknagar | 239 | 0.33333 | 226 | 0.625
Barapukuria | 237 | 0.70833 | 229 | 0.33333 | Old Airport | 237 | 0.33333 | 225 | 0.625
Bogra | 229 | 0.041667 | 220 | 0.29167 | Barisal | 255 | 0.70833 | 235 | 0.45833
Khulna South | 241 | 0.16667 | 222 | 0.79167 | AKSML | 221 | 0.16667 | 217 | 0.625
Rampura | 233 | 0.33333 | 227 | 0.625 | BSRM | 225 | 0.33333 | 220 | 0.20833
Haripur | 236 | 0.33333 | 227 | 0.66667 | Bibiyana | 239 | 0.041667 | 234 | 0.70833
Hasnabad | 235 | 0.33333 | 227 | 0.70833 | Bhulta | 239 | 0.33333 | 227 | 0.625
Shyampur | 236 | 0.33333 | 219 | 0.58333 | Ashuganj (S) | 239 | 0.33333 | 234 | 0.5
Aminbazar | 233 | 0.25 | 227 | 0.66667 | Kaliakoir | 237 | 0.20833 | 225 | 0.625
Tongi | 235 | 0.33333 | 221 | 0.625 | GPH | 222 | 0.875 | 218 | 0.58333
Comilla (N) | 239 | 0.375 | 233 | 0.58333
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 140 | 0.375 | 130 | 0.5 | Hathazari | 133 | 0.45833 | 131 | 0.16667
Munsiganj | 139 | 0.33333 | 129 | 0.66667 | Khulshi | 130 | 0.8125 | 126 | 0.58333
Sonargaon | 135 | 0.79167 | 130 | 0.20833 | Halishahar | 133 | 0.83333 | 127 | 0.58333
Shyampur | 141 | 0.33333 | 131 | 0.5 | Baraulia | 132 | 0.79167 | 125 | 0.33333
Bhulta | 130 | 0.33333 | 123 | 0.66667 | Sikalbaha | 133 | 0.8125 | 129 | 0.125
Madanganj | 139 | 0.33333 | 129 | 0.625 | Dohazari | 130 | 0.5 | 126 | 0.20833
Shitalakhya | 141 | 0.33333 | 130 | 0.45833 | Cox'sbazar | 127 | 0.5 | 119 | 0.83333
Rahim steal | 138 | 8:00 | 130 | 0.66667 | Chandraghona | 133 | 0.83333 | 130 | 0.29167
Matuail | 138 | 0.33333 | 129 | 0.41667 | Kaptai | 133 | 0.041667 | 132 | 0.29167
Ghorasal | 140 | 0.29167 | 138 | 0.041667 | A. Khaer Stl. | 131 | 0.77083 | 127 | 0.041667
Narsinghdi | 134 | 0.25 | 127 | 0.45833 | Bakulia | 131 | 0.77083 | 127 | 0.25
Haripur (SBU) | 138 | 0.33333 | 131 | 0.70833 | Julda | 132 | 0.79167 | 128 | 0.16667
Ullon | 134 | 0.33333 | 127 | 0.5 | TK Chemical | 132 | 0.79167 | 129 | 0.20833
Hasnabad | 140 | 0.33333 | 130 | 0.5 | Modern Steel | 132 | 0.83333 | 128 | 0.20833
Magbazar | 135 | 0.33333 | 125 | 0.66667 | Shahmirpur | 132 | 0.83333 | 128 | 0.25
Maniknagar | 138 | 0.33333 | 132 | 0.5 | Khagrachhari | 133 | 0.45833 | 130 | 0.125
Bangabhaban | 138 | 0.33333 | 132 | 0.5 | Matarbari | 129 | 0.5 | 121 | 0.95833
Narinda | 138 | 0.33333 | 132 | 0.5 | Baroiar Hat | 136 | 0.41667 | 130 | 1:00
Dhanmondi | 134 | 0.33333 | 127 | 0.5 | Rangamati | 132 | 0.041667 | 130 | 7:00
Lalbag | 138 | 0.375 | 129 | 0.5 | Goalpara | 139 | 0.041667 | 127 | 0.41667
Madartek | 133 | 0.33333 | 124 | 0.625 | Central s/s | 136 | 0.041667 | 125 | 0.77083
Dhaka University |  |  |  |  | Noapara | 137 | 0.875 | 124 | 0.77083
Mirpur | 135 | 0.25 | 130 | 0.5 | Jessore | 135 | 0.16667 | 119 | 0.79167
Kalyanpur | 135 | 0.25 | 132 | 0.5 | Benapol | 136 | 0.25 | 123 | 0.77083
Gulshan | 130 | 0.25 | 127 | 0.5 | Jhenida | 137 | 0.25 | 120 | 0.77083
Uttara | 136 | 0.25 | 129 | 0.5 | Bottail | 139 | 0.25 | 128 | 0.77083
Uttara New | 134 | 0.25 | 130 | 0.5 | G.K Project | 141 | 0.25 | 135 | 0.77083
Kamrangirchar | 132 | 0.25 | 127 | 0.5 | Faridpur | 140 | 0.25 | 130 | 0.45833
Savar | 134 | 0.25 | 128 | 0.5 | Madaripur | 144 | 0.29167 | 130 | 0.45833
Bhasantec | 134 | 0.25 | 129 | 0.5 | Sariatpur | 148 | 0.29167 | 130 | 0.45833
Agargaon | 134 | 0.25 | 130 | 0.5 | Gopalganj | 151 | 0.29167 | 132 | 0.45833
Satmosjid | 135 | 0.25 | 130 | 0.5 | Bagerhat | 137 | 0.91667 | 122 | 0.8125
Tongi | 141 | 0.33333 | 130 | 0.625 | Mongla | 133 | 0.25 | 123 | 0.45833
Kabirpur | 135 | 0.20833 | 125 | 0.625 | Satkhira | 136 | 0.25 | 127 | 0.77083
Basundhara | 134 | 8:00 | 125 | 0.625 | Gallamari | 138 | 0.25 | 127 | 0.41667
Manikganj | 141 | 0.20833 | 130 | 0.66667 | Magura | 138 | 0.25 | 120 | 0.77083
Joydevpur | 142 | 0.33333 | 136 | 0.77083 | Norail | 135 | 0.25 | 116 | 0.77083
New Tongi | 139 | 0.33333 | 128 | 0.66667 | Chuadanga | 136 | 0.25 | 114 | 0.79167
Kodda | 139 | 0.041667 | 122 | 0.041667 | Barisal(N) | 142 | 0.29167 | 136 | 0.45833
Dhamrai | 134 | 0.83333 | 125 | 0.125 | Barisal (S) | 143 | 0.29167 | 130 | 0.45833
Rajendrapur | 140 | 0.25 | 132 | 0.54167 | Patuakhali | 141 | 0.29167 | 128 | 0.45833
Valuka | 127 | 0.70833 | 117 | 0.29167 | Bhandaria | 140 | 0.20833 | 129 | 0.45833
Tangail | 132 | 0.125 | 125 | 0.625 | Ishurdi | 138 | 0.16667 | 131 | 0.77083
Mymensing | 128 | 0.375 | 120 | 0.33333 | Ruppur Paromanobik | 138 | 0.125 | 130 | 0.77083
Kishorganj | 130 | 0.20833 | 125 | 0.29167 | Natore | 135 | 0.16667 | 128 | 0.29167
Netrokona | 125 | 0.20833 | 116 | 0.29167 | Bogra | 137 | 0.041667 | 130 | 0.29167
Jamalpur | 138 | 0.83333 | 122 | 0.29167 | Noagaon | 133 | 0.125 | 121 | 0.29167
Sherpur | 136 | 0.83333 | 120 | 0.29167 | Rajshahi | 133 | 0.70833 | 125 | 0.45833
Srimongal | 138 | 0.083333 | 135 | 0.75 | Rajshahi New | 132 | 0.66667 | 123 | 0.54167
Shahjibazar | 136 | 0.25 | 133 | 18:30 | C.Nawabganj | 132 | 0.70833 | 120 | 0.29167
Fenchuganj | 137 | 0.25 | 135 | 0.083333 | Amnura | 135 | 0.70833 | 123 | 0.29167
Khulawara | 138 | 0.125 | 134 | 0.625 | Pabna | 136 | 0.125 | 128 | 0.79167
Sylhet | 135 | 0.041667 | 133 | 0.625 | Shahjadpur | 136 | 0.041667 | 130 | 0.45833
Chatak | 136 | 0.20833 | 132 | 0.54167 | Serajganj | 135 | 0.041667 | 127 | 0.8125
Sunamganj | 135 | 0.125 | 132 | 0.58333 | Niyamatpur | 130 | 0.083333 | 119 | 0.33333
Biani Bazar | 136 | 0.16667 | 132 | 0.083333 | Joypurhat | 133 | 0.041667 | 120 | 0.29167
Comilla(s) | 132 | 0.375 | 127 | 0.45833 | Sherpur(Bogura) | 137 | 0.041667 | 129 | 0.375
Comilla(n) | 140 | 0.8125 | 137 | 0.54167 | Mohastangor | 136 | 0.16667 | 126 | 0.29167
Chandpur | 137 | 0.33333 | 135 | 0.79167 | Rangpur | 133 | 0.041667 | 116 | 0.33333
Feni | 137 | 0.41667 | 130 | 0.625 | Lalmonirhat | 130 | 0.54167 | 115 | 0.33333
Chowmuhani | 134 | 0.29167 | 129 | 0.77083 | Saidpur | 132 | 0.16667 | 121 | 0.33333
Ashuganj | 138 | 0.33333 | 135 | 0.54167 | Purbasadipur | 129 | 0.16667 | 113 | 0.33333
Daudkandi | 139 | 0.33333 | 131 | 0.625 | Thakurgaon | 129 | 0.25 | 114 | 0.29167
B.Baria | 134 | 0.25 | 131 | 0.91667 | Palashbari | 130 | 0.125 | 120 | 0.29167
Ramganj | 133 | 0.375 | 128 | 0.79167 | Barapukuria | 137 | 0.70833 | 129 | 0.33333
Chaddagram | 136 | 0.375 | 132 | 0.58333 | Panchagar | 126 | 0.16667 | 108 | 0.29167
PHP | 135 | 0.375 | 129 | 0.625 | Joldhaka | 131 | 0.083333 | 118 | 0.33333
Madanhat | 134 | 0.41667 | 130 | 0.66667 | Kurigram | 131 | 0.16667 | 115 | 0.33333

## L-Curve
Date | 2020-03-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 184 | 5519 | 1910 | 7429 |  |  |  | QF-LDC-12
0:30 | 325.5 | 5557 | 1809.5 | 7366.5 | Date: | 2020-03-03
1:00 | 467 | 5595 | 1709 | 7304
1:30 | 435 | 5430.5 | 1686.5 | 7117
2:00 | 403 | 5266 | 1664 | 6930
2:30 | 346.5 | 5165 | 1658 | 6823 | [5 empty] | Gen. at Eve. Peak | 9340 | 9340 MW (19:30 )
3:00 | 290 | 5064 | 1652 | 6716 | [6 empty] | 19:30
3:30 | 275 | 4972.5 | 1630 | 6602.5 | [5 empty] | Gen. at Day Peak | 7364.1 | 7364.1 MW (12:00 )
4:00 | 260 | 4881 | 1608 | 6489 | [6 empty] | 12:00
4:30 | 255.5 | 4712 | 1583.5 | 6295.5 | [5 empty] | Highest Generation | 9340
5:00 | 251 | 4543 | 1559 | 6102 | [6 empty] | 19:30
5:30 | 223.5 | 4592.5 | 1594 | 6186.5
6:00 | 196 | 4642 | 1629 | 6271
6:30 | 157 | 4628.7 | 1749.1 | 6377.8
7:00 | 118 | 4615.4 | 1869.2 | 6484.6
7:30 | 200.5 | 4282.1 | 1798.25 | 6080.35
8:00 | 283 | 3948.8 | 1727.3 | 5676.1
8:30 | 222.5 | 4022.2 | 1833.05 | 5855.25
9:00 | 162 | 4095.6 | 1938.8 | 6034.4
9:30 | 102.5 | 4222.75 | 1965.35 | 6188.1
10:00 | 43 | 4349.9 | 1991.9 | 6341.8
10:30 | 108 | 4607.8 | 2003.75 | 6611.55
11:00 | 173 | 4865.7 | 2015.6 | 6881.3
11:30 | 224.5 | 5099.3 | 2023.4 | 7122.7
12:00 | 276 | 5332.9 | 2031.2 | 7364.1
12:30 | 237 | 5417.55 | 2048.35 | 7465.9
13:00 | 198 | 5502.2 | 2065.5 | 7567.7
13:30 | 128 | 5422 | 2107.2 | 7529.2
14:00 | 58 | 5341.8 | 2148.9 | 7490.7
14:30 | 84.5 | 5414.05 | 2194.4 | 7608.45
15:00 | 111 | 5486.3 | 2239.9 | 7726.2
15:30 | 139.5 | 5384.05 | 2233.85 | 7617.9
16:00 | 168 | 5281.8 | 2227.8 | 7509.6
16:30 | 107.5 | 5222.9 | 2189.05 | 7411.95
17:00 | 47 | 5164 | 2150.3 | 7314.3
17:30 | 66 | 5272 | 2200.2 | 7472.2
18:00 | 85 | 5380 | 2250.1 | 7630.1
18:30 | 202.5 | 5936.5 | 2512.05 | 8448.55
19:00 | 320 | 6493 | 2774 | 9267
19:30 | 285 | 6564 | 2776 | 9340
20:00 | 308 | 6541 | 2765 | 9306 |  |  |  | Executive Engineer
20:30 | 192 | 6414.5 | 2686.5 | 9101 |  |  |  | Network Operation Division
21:00 | 76 | 6288 | 2608 | 8896
21:30 | 51 | 6085 | 2516.5 | 8601.5
22:00 | 26 | 5882 | 2425 | 8307 |  |  |  |  | Page 6 of 7
22:30 | 39 | 5785.5 | 2313.5 | 8099
23:00 | 52 | 5689 | 2202 | 7891
23:30 | 118 | 5604 | 2056 | 7660
24:00 | 184 | 5519 | 1910 | 7429
9340 MW (19:30 )
7364.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-03 |  | Energy | 177631766
[10 empty] | 2020-03-03 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3880 | 381 | 1976 | 811 | 321 | 67 | 0 | 0 | 94
0:30 | 3907.5 | 296.5 | 1929.5 | 775 | 346 | 67.5 | 0 | 0 | 95 | Date: | 2020-03-03
1:00 | 3935 | 212 | 1883 | 739 | 371 | 68 | 0 | 0 | 96
1:30 | 3929.5 | 212 | 1909 | 533.5 | 371 | 68 | 0 | 0 | 94 | [7 empty] | Total Energy | 177.6318 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3924 | 212 | 1935 | 328 | 371 | 68 | 0 | 0 | 92 | [7 empty] | Energy not Served | 0
2:30 | 3897 | 212 | 1908.5 | 275.5 | 371 | 68 | 0 | 0 | 91 | [7 empty] | Energy Requirement | 177.6318
3:00 | 3870 | 212 | 1882 | 223 | 371 | 68 | 0 | 0 | 90
3:30 | 3830.5 | 209.5 | 1823 | 213 | 370.5 | 68 | 0 | 0 | 88 | [6 empty] | Shortage
4:00 | 3791 | 207 | 1764 | 203 | 370 | 68 | 0 | 0 | 86
4:30 | 3727.5 | 207.5 | 1670.5 | 165.5 | 370.5 | 68 | 0 | 0 | 86
5:00 | 3664 | 208 | 1577 | 128 | 371 | 68 | 0 | 0 | 86
5:30 | 3692 | 208 | 1631.5 | 129 | 371 | 68 | 0 | 0 | 87
6:00 | 3720 | 208 | 1686 | 130 | 371 | 68 | 0 | 0 | 88
6:30 | 3670.5 | 374 | 1641 | 166.5 | 370.5 | 67.5 | 0 | 0 | 87 |  |  |  |  | Coal
7:00 | 3621 | 540 | 1596 | 203 | 370 | 67 | 0 | 0 | 86
7:30 | 3353.5 | 502 | 1398.5 | 285.5 | 359 | 67 | 25.5 | 0 | 87 |  |  |  | Oil |  |  |  | ,
8:00 | 3086 | 464 | 1201 | 368 | 348 | 67 | 51 | 0 | 88
8:30 | 3147 | 464 | 1298 | 413.5 | 348.5 | 67 | 59.5 | 0 | 53
9:00 | 3208 | 464 | 1395 | 459 | 349 | 67 | 68 | 0 | 18
9:30 | 3315.5 | 457.5 | 1451.5 | 442.5 | 350 | 67 | 68 | 0 | 28
10:00 | 3423 | 451 | 1508 | 426 | 351 | 67 | 68 | 0 | 38
10:30 | 3598.5 | 451 | 1570 | 441 | 350.5 | 67 | 68 | 0 | 55
11:00 | 3774 | 451 | 1632 | 456 | 350 | 67 | 68 | 0 | 72
11:30 | 3885 | 447 | 1700 | 543.5 | 325 | 67 | 67 | 0 | 76
12:00 | 3996 | 443 | 1768 | 631 | 300 | 67 | 66 | 0 | 80
12:30 | 3883.5 | 493.5 | 1812.5 | 747.5 | 300.5 | 67.5 | 66 | 0 | 82
13:00 | 3771 | 544 | 1857 | 864 | 301 | 68 | 66 | 0 | 84
13:30 | 3771 | 544 | 1857 | 864 | 301 | 68 | 66 | 0 | 84
14:00 | 3771 | 544 | 1857 | 864 | 301 | 68 | 66 | 0 | 84
14:30 | 3789.5 | 559.5 | 1897 | 842.5 | 322.5 | 68 | 65 | 0 | 92
15:00 | 3808 | 575 | 1937 | 821 | 344 | 68 | 64 | 0 | 100
15:30 | 3765.5 | 575 | 1876 | 815.5 | 357 | 68 | 57.5 | 0 | 96
16:00 | 3723 | 575 | 1815 | 810 | 370 | 68 | 51 | 0 | 92
16:30 | 3700 | 575 | 1730.5 | 819 | 370.5 | 68 | 51 | 0 | 94
17:00 | 3677 | 575 | 1646 | 828 | 371 | 68 | 51 | 0 | 96
17:30 | 3635.5 | 575 | 1649 | 1009 | 371 | 68 | 60.5 | 0 | 103
18:00 | 3594 | 575 | 1652 | 1190 | 371 | 68 | 70 | 0 | 110
18:30 | 3668 | 656 | 1789.5 | 1685 | 370.5 | 68 | 98.5 | 0 | 113
19:00 | 3742 | 737 | 1927 | 2180 | 370 | 68 | 127 | 0 | 116
19:30 | 3720 | 730 | 1939 | 2263 | 371 | 68 | 133 | 0 | 116
20:00 | 3688 | 737 | 1944 | 2253 | 370 | 67 | 133 | 0 | 114
20:30 | 3711.5 | 737 | 1952.5 | 2078.5 | 360.5 | 67 | 79 | 0 | 115
21:00 | 3735 | 737 | 1961 | 1904 | 351 | 67 | 25 | 0 | 116
21:30 | 3737.5 | 737 | 1963 | 1623.5 | 351 | 67 | 12.5 | 0 | 110
22:00 | 3740 | 737 | 1965 | 1343 | 351 | 67 | 0 | 0 | 104
22:30 | 3859 | 716.5 | 1942.5 | 1077 | 336 | 67 | 0 | 0 | 101
23:00 | 3978 | 696 | 1920 | 811 | 321 | 67 | 0 | 0 | 98
23:30 | 3929 | 538.5 | 1948 | 811 | 321 | 67 | 0 | 0 | 96 | Max Temp. in Dhaka |  | 29.8° C
24:00 | 3880 | 381 | 1976 | 811 | 321 | 67 | 0 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 27 | 27 | 27 | 27 | 27 | 594480
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | [19 empty] | 2565
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 204 | 204 | 204 | 204 | 161 | 197 | 216 | 210 | 218 | 203 | 205 | 210 | 205 | 204 | 204 |  | 204 | 204 | 204 | 204 | 203 | 215 | 203 | 4859445
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 104 | 104 | 104 | 80 | 80 | 80 | 80 | 80 | 80 | 104 | 114 | 139 | 103 | 139 | 110 | 110 | 110 |  | 104 | 139 | 139 | 139 | 139 | 146 | 105 | 2614508
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 17 | 17 | 17 | 0 |  |  |  | 33193
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 28 | 34 | 34 | 34 | 17 |  |  | 137163
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 5 | 16 |  | 60 | 60 | 60 |  |  |  |  | 160581
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 250909
20 | Ghorasal TPP (Unit-1&2) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 1136000
21 | Ghorasal Repowered CCPP Unit-3 | 174 | 174 | 135 | 100 | 74 | 74 | 74 | 75 | 74 | 73 | 118 | 159 | 167 | 168 | 168 | 168 | 169 | 169 |  | 168 | 63 | [5 empty] | 2729900
22 | Ghorasal Repowered CCPP Unit-4 | [24 empty] | 150 | 150 | 299000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 177 | 204 | 204 | 300 | 300 | 320 | 320 | 320 | 320 | 320 | 270 |  | 270 | 310 | 320 | 302 | 300 | 325 | 298 | 6925645
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1998790
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 21 | 29 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 181944
33 | Ashuganj 225 MW CCPP | 164 | 166 | 170 | 164 | 164 | 185 | 182 | 161 | 158 | 170 | 199 | 204 | 147 | 159 | 161 | 187 | 173 | 184 |  | 198 | 198 | 206 | 200 | 195 | 199 | 198 | 4361000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 285 | 285 | 285 | 285 | 250 | 250 | 270 | 295 | 320 | 315 | 330 | 280 | 270 | 270 | 270 |  | 275 | 275 | 275 | 290 | 290 | 305 | 270 | 6943000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 235 | 240 | 300 | 330 | 350 | 320 | 270 | 260 | 280 | 280 | 280 |  | 285 | 285 | 285 | 285 | 280 | 315 | 280 | 7127000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 136320
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 90 | 84 | 85 |  | 90 | 91 | 84 | 90 | 90 | 90 | 90 | 1701630
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 397 | 395 | 393 | 367 | 330 | 335 | 340 | 328 | 312 | 360 | 373 | 365 | 358 | 343 | 369 | 341 | 346 | 298 |  | 350 | 336 | 340 | 342 | 342 | 340 | 362 | 8557570
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 380 | 350 | 350 | 320 | 300 | 300 | 360 | 360 | 360 | 420 | 400 | 420 | 380 | 350 | 320 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8968250
41 | Haripur 360MW CCPP(HPL) | 303 | 314 | 334 | 333 | 298 | 293 | 261 | 241 | 290 | 300 | 300 | 330 | 320 | 270 | 285 | 300 | 280 | 280 |  | 320 | 320 | 320 | 319 | 320 | 328 | 335 | 7241000
42 | RPCL 210MW CCPP | 130 | 130 | 131 | 149 | 150 | 149 | 162 | 110 | 110 | 148 | 141 | 141 | 124 | 126 | 125 | 126 | 141 | 142 |  | 143 | 143 | 144 | 144 | 130 | 129 | 130 | 3166520
43
44 | Fenchugonj CCPP Phase-1 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 87 | 87 | 89 | 88 | 88 | 89 | 88 | 88 | 88 | 87 |  | 88 | 88 | 88 | 89 | 88 | 86 | 86 | 2050000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 531216
46 | Shajibazar 330 MW CCPP | 139 | 140 | 137 | 134 | 133 | 134 | 133 | 132 | 135 | 132 | 132 | 134 | 134 | 134 | 133 | 134 | 135 | 135 |  | 134 | 135 | 135 | 133 | 134 | 133 | 134 | 3023000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 64 | 54 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 62 | 60 | 61 | 59 | 60 | 45 | 45 | 45 |  | 64 | 64 | 64 | 64 | 65 | 64 | 65 | 1331328
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 40 | 5 | 5 | 50 | 50 | 5 | 5 | 5 | 60 | 76 | 78 | 78 | 78 | 40 | 20 | 60 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1270080
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 110 | 110 | 110 | 110 | 80 | 80 | 80 | 79 | 80 | 80 | 118 | 132 | 150 | 118 | 148 | 118 | 97 | 67 |  | 99 | 98 | 97 | 98 | 98 | 99 | 117 | 2498700
51 | Sylhet 20 MW GTPP | 18 | 19 | [11 empty] | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 241000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [6 empty] | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 184680
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [10 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 155096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 22 | 30 | 48 | 5 | 5 | 5 | 2 | 29 | 53 | 53 | 50 | 24 | 25 | 25 |  | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 935400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | [6 empty] | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 382464
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 300 | 305 | 300 | 280 | 300 | 290 | 270 | 290 | 300 | 320 | 320 | 310 | 310 | 320 | 315 | 295 | 300 |  | 300 | 310 | 305 | 300 | 310 | 300 | 320 | 7529750
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 22 | [12 empty] | 16 | 19 | 19 | 19 | 19 | 251760
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | [8 empty] | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 313668
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 457488
63 | Impoprt (Tripura) | 96 | 92 | 90 | 86 | 86 | 88 | 86 | 88 | 18 | 38 | 72 | 80 | 84 | 96 | 100 | 92 | 96 | 110 |  | 116 | 116 | 114 | 116 | 104 | 98 | 94 | 2158080
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 17 | 5 | 5 | 6 | 24 | 5 | 3 | 4 | 2 | 3 | 9 | 3 | 2 | 3 | 5 | 14 |  | 20 | 20 | 31 | 31 | 30 | 38 | 40 | 471840
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | [7 empty] | 19 | 19 | 19 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 356040
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 |  | 8 | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 100260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | [10 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 496500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 |  |  | 3 | 12 | 12 | 12 | 14 | 19 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 429500
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 28 | 28 | 28 | 12 | 0 | 0 | 14 | 14 | 15 | 20 | 28 | 28 | 29 | 29 | 29 |  | 30 | 30 | 30 | 30 | 31 | 31 | 30 | 577620
71 | Maona 33 MW PP(Summit) | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 720800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  |  |  |  | 25 | 25 | 33 | 25 | 33 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 600500
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [20 empty] | 0 | [5 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 86 | 91 | 92 | 75 | 0 | [6 empty] | 25 | 60 | 40 | 38 | 70 | 70 | 70 |  | 95 | 100 | 100 | 100 | 100 | 100 | 100 | 1361280
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [19 empty] | 16 | 16 | 16 |  |  |  |  | 31200
80 | Jamalpur 95 MW PP(Powerpac) | 56 | 8 | 4 | 8 | 8 | 10 | 40 | 48 | 65 | 73 | 73 | 57 | 56 | 58 | 50 | 48 | 49 | 58 |  | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 1335360
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.4 | 2.9 | 3.6 | 3.7 | 4.7 | 5.1 | 4.9 | 3.2 | 2 | 0.7 | [9 empty] | 30360
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [16 empty] | 1 | 15 |  | 60 | 81 | 81 | 48 |  |  |  | 251424
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 14 |  | 40 | 40 | 40 |  |  |  |  | 111882
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3214313
87 | Meghnaghat 100 MW(IEL) | 34 | 0 | [5 empty] | 4 |  |  |  |  | 30 | 33 | 33 | 23 | 8 | 22 |  | 100 | 100 | 100 | 100 | 100 | 45 | 10 | 682560
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 51 | 51 | 25 | 48 | 48 | 48 | 48 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 34 | 48 | 48 | 48 | 638856
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 10 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1103596
94 | Gagnagar 102 MW PP (Digital Power) | 32 | 0 | [9 empty] | 24 | 40 | 40 | 50 | 59 | 64 | 74 |  | 93 | 93 | 93 | 93 | 93 | 7 | 7 | 815616
95 | Patenga 50MW PP (Baraka) | 18 | 0 | [10 empty] | 19 | 24 | 25 | 25 | 25 | 30 |  | 50 | 50 | 50 | 50 | 50 | 24 | 19 | 415200
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 4 | 17 |  | 44 | 45 | 45 | 40 | 12 |  |  | 172800
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 2 |  | 33 | 35 | 40 | 18 |  |  |  | 113520
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 9 |  | 50 | 55 | 55 | 30 |  |  |  | 178144
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 30 |  | 55 | 55 | 55 | 55 | 17 |  |  | 297686
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 163 | 130 | 130 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 3276245
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.4 | 0.7 | 1.3 | 2 | 2.2 | 2.1 | 1.9 | 1.1 | 0.8 | 0.3 | [9 empty] | 13150
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 0 |  |  |  | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 704160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 19 | 7 | 7 | 7 | 12 | 24 | 7 | 7 | 7 | 7 |  | 43 | 70 | 70 | 50 |  |  |  | 381600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 30 | 0 | [9 empty] | 27 | 42 | 21 | 16 | 16 | 15 | 18 |  | 124 | 145 | 146 | 145 | 137 | 45 |  | 806400
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 68 |  | 100 | 100 | 100 | 100 | 10 |  |  | 473280
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 1 | 8 |  | 68 | 80 | 80 | 40 |  |  |  | 240873
118 | Bibiyana-III 400 MW CCPP | 235 | 236 | 234 | 234 | 234 | 234 | 234 | 233 | 234 | 234 | 235 | 235 | 233 | 234 | 235 | 235 | 235 | 234 |  | 234 | 234 | 234 | 234 | 234 | 233 | 233 | 5595000
| Jamalpur 115 MW PP (United) | 7 | 7 | 7 | 0 |  |  | 8 | 60 | 109 | 75 | 75 | 75 | 112 | 85 | 85 | 64 | 64 | 77 |  | 115 | 115 | 115 | 115 | 88 | 24 | 24 | 1550400
| Anwara 300 MW PP (United) | 180 | 50 | 0 |  |  |  |  | 66 | 66 | 71 | 71 | 104 | 108 | 70 | 132 | 140 | 142 | 211 |  | 214 | 215 | 215 | 215 | 216 | 161 | 161 | 2501564
120 | Eastern Zone Total | 5595 | 5266 | 5064 | 4881 | 4543 | 4642 | 4615.4 | 3948.8 | 4095.6 | 4349.9 | 4865.7 | 5332.9 | 5502.2 | 5341.8 | 5486.3 | 5281.8 | 5164 | 5380 |  | 6493 | 6564 | 6541 | 6288 | 5882 | 5689 | 5519 | 127661652
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | 0 | [9 empty] | 37 | 49 | 49 | 49 | 16 | 16 | 50 |  | 99 | 83 | 83 | 83 | 32 | 0 | 0 | 626880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [13 empty] | 16 | 16 | 16 | 16 | 32 |  | 110 | 110 | 110 | 96 | 48 | 16 | 16 | 497280
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 14 | 13 | 13 | 13 | 13 | 13 | 11 | [6 empty] | 70 | 80 | 92 | 98 | 74 |  | 98 | 98 | 98 | 96 | 97 | 24 | 42 | 963358
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | [10 empty] | 50 | 85 | 85 | 130 | 1863000
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 16 | 16 | 15 | 13 | 13 | 11 | 1 | 3 | 6 | 9 | 11 | 12 | 13 | 12 | 12 | 16 |  | 20 | 21 | 21 | 20 | 21 | 19 | 18 | 323400
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [12 empty] | 12 | 32 |  |  |  | 14 |  | 67 | 68 | 50 |  |  |  |  | 181728
146 | Bheramara HVDC | 212 | 212 | 212 | 207 | 208 | 208 | 540 | 464 | 464 | 451 | 451 | 443 | 544 | 574 | 575 | 575 | 575 | 575 |  | 737 | 730 | 737 | 737 | 737 | 696 | 381 | 11407272
147 | Bheramara 410 MW CCPP | 275 | 295 | 310 | 320 | 320 | 380 | 320 | 280 | 345 | 345 | 340 | 365 | 350 | 330 | 330 | 330 | 320 | 320 |  | 320 | 320 | 320 | 315 | 310 | 310 | 310 | 7949376
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 91 | 91 | 91 | 90 | 91 | 91 | 90 | 88 | 89 | 91 | 90 | 91 | 91 | 91 | 91 | 90 | 91 | 91 |  | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 2157818
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 209 | 210 | 220 | 253 | 280 | 280 | 280 |  | 280 | 280 | 280 | 260 | 260 | 230 | 230 | 6347800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 170 | 140 | 130 | 130 | 130 | 130 | 130 | 160 | 170 | 170 | 180 | 200 | 200 | 170 | 170 | 140 |  | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 4254782
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 345 | 387 | 396 | 378 | 338 | 350 | 328 | 212 | 352 | 386 | 398 | 398 | 398 | 383 | 422 | 415 | 323 | 355 |  | 402 | 401 | 400 | 397 | 375 | 399 | 380 | 9124727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 18 | 18 | 18 | 17 | 17 | 17 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 410160
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 7 | 230724
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 212980
165 | Amnura 50 MW PP(Sinha) | [12 empty] | 3 | 18 | 18 | 35 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 |  |  | 391000
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [7 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 70 |  | 94 | 100 | 100 | 25 |  |  |  | 788304
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 0 |  | 35 | 35 | 35 |  |  |  |  | 95808
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 35 | 0 |  |  |  |  | 70 | 70 | 70 | 70 | 80 | 109 | 50 | 90 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1728768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [8 empty] | 17 | 17 | 17 | 15 | 15 | 15 | 13 | [11 empty] | 115000
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 34 |  | 73 | 70 | 72 | 69 |  |  |  | 262080
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.3 | 2.8 | 4.9 | 5.6 | 6.2 | 5.5 | 1.9 | 4.9 | 2.8 | 1.3 | 0.1 | [8 empty] | 37869
178
178