## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-05 | Thursday
|  | Date (day): | 2020-03-05 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11954.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14575 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-04 | 2020-03-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 0 | 0 |  | 85 | Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 166 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 370 | 336 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 363 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 326 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 84 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 150 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 67 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 50 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 33 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 20 | 96 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 85 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 10 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 56 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 86 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 31 | 101 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2210 | 2739 | 3532 | 4134 | 991 | 660
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 68 | 68 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 224 | 204 | 210 | 210
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 145 | 104 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 20 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 22 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 191 | 232 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 786.4 | 949 | 1484 | 1621 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 142 | 183 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 265 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 265 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 35 |  | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 30 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 81 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 124 | 102 | 113
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 22 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1158 | 1179 | 1592 | 2267 | 590 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 130 | 130 | 160 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 49 | 91 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.7 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 40 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 295.7 | 396 | 493.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 86 | 88 | 85 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 32 | 22 | 22 |  | 58 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 126 | 133 | 150 | 150 |  | 180 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 82 | 80 | 82
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 127 | 158 | 220 | 220
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 275 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 236 | 235 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1386 | 1335 | 1522 | 1527 | 0 | 403
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 642 | 885 | 647 | 895
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 66 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 260 | 360 | 300 | 110 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 32 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 942 | 1243 | 1292 | 2030 | 110 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 7 | 21 | 21 | 22 |  | 11 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 121 | 130 | 135 |  | 59 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 52 | 95 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 189 | 285 | 310 | 392 | 0 | 70
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 32 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 170 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 421 | 379 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 10 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 17 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 816 | 789 | 1238 | 1505 | 611 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 90 | 88 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 32 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.5 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 411.5 | 400 | 491 | 517 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 8194.6 | 9315 | 11954.6 | 14575 | 2764 | 1399
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7862.0655 | 8937 | 11469.4858 | 13983.5507
A. |  | 2020-03-04 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9315 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 6045 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9315 | MW
3 | Day peak Generation : |  |  | 8194.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8937 | MW
4 | Evening peak Generation : |  |  | 9315 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 184.0573 | MKWHr | By Solar | 0.19593 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 140.3445 | MKWHr |  | By Oil: | 17.6426 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.4866 | MKWHr |  | By Hydro: | 1.5445 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2764 | MW | Dhaka | 3490 | 3490 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1399 | MW | Chittagong | 1038 | 1038 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4163 | MW | Khulna | 1027 | 1027 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1103.5 | MMCFD |  |  | Rajshahi | 652 | 652 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129394188.736 | ii) Oil : | Taka | 126460958.66 | Comilla | 773 | 773 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 39584436.65 | Total | Taka | 295439584.046 | Mymensingh | 727 | 727 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.042 | MKWHr. | Sylhet | 347 | 347 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 24 | MW (E to W) at | 19:00 | hrs | Barisal | 217 | 217 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -386 | MW at | 1:00 | hrs | Rangpur | 666 | 666 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30° C |  |  | Total | 8937 | 8937 |  | 0
B. |  | 2020-03-05 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14575 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8100 | MW
4 | Reserve(Generation end) |  |  |  | 5075 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 187.7127 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5894 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.5295 | MKWHr. | ii) HVDC Flow at Peak Time |  | 885 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3136 | MKWHr. | iii) Maximum HVDC Flow : |  | 887 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.23 |  | (b) Today: | 89.09 |  | (c) Rule Curve: |  | 92.36
.

## YesterdayGen
2020-03-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 0 | 151 | 0 | 297 | 0 | 0 | 351 | 352 |  | 0 | 400 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 19 | 40 | 0 | 80 | 0 | 280 | 270 | 198 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 90 | 147 | 64 | 20 | 0 | 87 | 22 | 53 | 48 | 163 | 131 | 65 | 78 | 0 | 118 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 |  | 198 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 5 | 92 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 |  | 5310 | 1616 | 6926 | 3912 | 198 | 1949 | 387 | 322 | 68 | 0 | 90 | 0 | 0 | 89.28
2:00 | 37 | 0 | 150 | 0 | 304 | 0 | 0 | 343 | 363 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 80 | 0 | 290 | 275 | 198 | 8 | 90 | 5 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 84 | 157 | 8 | 20 | 0 | 87 | 22 | 53 | 48 | 163 | 133 | 45 | 10 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 5 | 92 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4912 | 1595 | 6507 | 3840 | 199 | 1866 | 128 | 322 | 68 | 0 | 84 | 0 | 0 | 89.27
3:00 | 37 | 0 | 100 | 0 | 298 | 0 | 0 | 342 | 364 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 202 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 280 | 270 | 198 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 21 | 84 | 161 | 8 | 20 | 0 | 87 | 22 | 5 | 5 | 163 | 125 | 45 | 10 | 0 | 67 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 5 | 91 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4611 | 1574 | 6185 | 3696 | 198 | 1690 | 128 | 321 | 68 | 0 | 84 | 0 | 0 | 89.26
4:00 | 37 | 0 | 99 | 0 | 300 | 0 | 0 | 339 | 325 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 280 | 270 | 197 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 18 | 80 | 161 | 8 | 20 | 0 | 87 | 22 | 5 | 5 | 130 | 124 | 45 | 10 | 0 | 68 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 5 | 90 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4487 | 1558 | 6045 | 3688 | 199 | 1562 | 128 | 320 | 68 | 0 | 80 | 0 | 0 | 89.25
5:00 | 37 | 0 | 100 | 0 | 317 | 0 | 0 | 349 | 285 |  | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 208 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 80 | 0 | 295 | 285 | 202 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 18 | 82 | 161 | 8 | 20 | 0 | 87 | 22 | 5 | 5 | 130 | 126 | 45 | 10 | 0 | 68 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 5 | 90 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4550 | 1558 | 6108 | 3759 | 198 | 1553 | 128 | 320 | 68 | 0 | 82 | 0 | 0 | 89.24
6:00 | 37 | 0 | 200 | 0 | 330 | 0 | 0 | 364 | 317 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 206 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 13 | 0 | 80 | 0 | 305 | 325 | 197 | 8 | 90 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 18 | 84 | 161 | 8 | 20 | 0 | 87 | 22 | 5 | 10 | 130 | 126 | 56 | 10 | 0 | 67 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 5 | 89 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4817 | 1671 | 6488 | 3989 | 198 | 1672 | 158 | 319 | 68 | 0 | 84 | 0 | 0 | 89.23
7:00 | 37 | 0 | 200 | 0 | 340 | 0 | 0 | 345 | 317 |  | 0 | 380 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 212 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 80 | 0 | 305 | 325 | 196 | 8 | 90 | 29 | 5 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 8 | 18 | 82 | 161 | 22 | 20 | 0.1 | 87 | 22 | 5 | 48 | 130 | 126 | 65 | 10 | 0 | 67 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.8 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 |  | 608 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 2 | 5 | 90 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 |  | 4962.2 | 2125.2 | 7087.4 | 4046 | 608 | 1738 | 223 | 320 | 68 | 0 | 82 | 2.4 | 0 | 89.22
8:00 | 37 | 0 | 200 | 0 | 325 | 0 | 0 | 348 | 367 |  | 0 | 420 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 80 | 0 | 320 | 300 | 192 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 84 | 160 | 82 | 20 | 0.6 | 87 | 22 | 50 | 48 | 110 | 126 | 65 | 50 | 0 | 68 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6.5 | 0 | 0 | 0 | 233 | 36 | 0 | 0 | 1.7 | 33 | 0 | 0 | 0 | 0 |  | 641 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 90 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 0 | 9 | 0 | 0.8 | 50 | 0 |  | 5319.8 | 2194.8 | 7514.6 | 4044 | 641 | 1901 | 447 | 320 | 68 | 0 | 84 | 9.6 | 0 | 89.21
9:00 | 37 | 0 | 200 | 0 | 325 | 0 | 0 | 353 | 365 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 10 | 25 | 30 | 25 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 203 | 0 | 135 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 80 | 0 | 315 | 360 | 169 | 8 | 90 | 33 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 86 | 160 | 90 | 0 | 1.2 | 89 | 22 | 50 | 48 | 163 | 131 | 64 | 50 | 0 | 68 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12.5 | 0 | 0 | 0 | 233 | 91 | 0 | 0 | 2.9 | 66 | 0 | 0 | 0 | 0 |  | 640 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 90 | 0 | 230 | 0 | 0 | 195 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 40 | 0 | 3.6 | 109 | 0 |  | 5584.6 | 2278.6 | 7863.2 | 4102 | 640 | 1971 | 657 | 320 | 67 | 0 | 86 | 20.2 | 0 | 89.2
10:00 | 37 | 0 | 200 | 0 | 383 | 0 | 0 | 345 | 360 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 133 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 80 | 0 | 315 | 295 | 170 | 8 | 90 | 33 | 5 | 0 | 43 | 0 | 0 | 0 | 6 | 0 | 33 | 18 | 88 | 130 | 64 | 0 | 1.8 | 88 | 22 | 48 | 48 | 163 | 132 | 65 | 50 | 0 | 67 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 3.9 | 120 | 0 | 0 | 0 | 0 |  | 640 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 4 | 11 | 89 | 0 | 270 | 0 | 0 | 220 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 109 | 0 |  | 5607.7 | 2295 | 7902.7 | 4073 | 640 | 1906 | 748 | 359 | 67 | 0 | 88 | 21.7 | 0 | 89.19
11:00 | 37 | 0 | 200 | 0 | 345 | 0 | 0 | 355 | 354 |  | 0 | 420 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 228 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 80 | 0 | 310 | 285 | 135 | 8 | 90 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 18 | 96 | 130 | 49 | 0 | 1.8 | 89 | 20 | 48 | 48 | 130 | 131 | 45 | 50 | 0 | 128 | 19 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 18.3 | 0 | 0 | 0 | 234 | 115 | 0 | 0 | 4.7 | 106 | 0 | 0 | 0 | 0 |  | 642 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 40 | 0 | 6.2 | 109 | 0 |  | 5544.8 | 2352.2 | 7897 | 4098 | 642 | 1886 | 707 | 370 | 67 | 0 | 96 | 31 | 0 | 89.18
12:00 | 37 | 0 | 200 | 0 | 370 | 0 | 0 | 378 | 347 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 224 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 80 | 0 | 320 | 290 | 142 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 18 | 92 | 130 | 49 | 0 | 1.7 | 86 | 20 | 48 | 48 | 163 | 126 | 59 | 79 | 0 | 127 | 19 | 0 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 18.8 | 0 | 0 | 0 | 236 | 115 | 0 | 0 | 5.6 | 191 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 35 | 0 | 6.5 | 109 | 0 |  | 5836.1 | 2358.5 | 8194.6 | 4130 | 642 | 2042 | 818 | 370 | 68 | 0 | 92 | 32.6 | 0 | 89.18
13:00 | 37 | 0 | 192 | 0 | 325 | 0 | 0 | 389 | 338 |  | 0 | 450 | 150 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 64 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 207 | 0 | 133 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4 | 22 | 6 | 0 | 80 | 0 | 270 | 285 | 158 | 8 | 80 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 100 | 131 | 49 | 0 | 2 | 85 | 20 | 48 | 48 | 163 | 131 | 61 | 79 | 0 | 147 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 17.9 | 36 | 0 | 0 | 236 | 115 | 0 | 0 | 1.2 | 231 | 0 | 0 | 0 | 0 |  | 642 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 50 | 0 | 6.5 | 90 | 0 |  | 5984.1 | 2338.5 | 8322.6 | 4021 | 642 | 2002 | 1092 | 370 | 68 | 0 | 100 | 27.6 | 0 | 89.17
14:00 | 37 | 0 | 172 | 0 | 326 | 0 | 0 | 340 | 313 |  | 0 | 450 | 150 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 65 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 2 | 0 | 80 | 0 | 310 | 260 | 179 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 106 | 113 | 49 | 0 | 1.3 | 86 | 32 | 50 | 48 | 130 | 135 | 60 | 79 | 0 | 97 | 19 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15.5 | 10 | 0 | 0 | 235 | 115 | 0 | 0 | 3.9 | 143 | 0 | 0 | 0 | 0 |  | 642 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 88 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 45 | 0 | 6.1 | 109 | 0 |  | 5759.7 | 2291.1 | 8050.8 | 3868 | 642 | 1920 | 1052 | 368 | 68 | 0 | 106 | 26.8 | 0 | 89.17
15:00 | 37 | 0 | 170 | 0 | 352 | 0 | 0 | 378 | 320 |  | 0 | 450 | 150 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 70 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 213 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 22 | 2 | 0 | 80 | 0 | 290 | 280 | 156 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 21 | 104 | 111 | 49 | 0 | 1.4 | 86 | 32 | 50 | 48 | 163 | 133 | 60 | 82 | 0 | 28 | 19 | 0 | 10 | 325 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 11.1 | 45 | 0 | 0 | 234 | 115 | 0 | 0 | 3.1 | 202 | 0 | 0 | 0 | 0 |  | 642 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 35 | 0 | 4.6 | 109 | 0 |  | 5860.6 | 2296.6 | 8157.2 | 3884 | 642 | 2015 | 1055 | 369 | 68 | 0 | 104 | 20.2 | 0 | 89.16
16:00 | 37 | 0 | 171 | 0 | 326 | 0 | 0 | 342 | 320 |  | 0 | 450 | 150 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 80 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 28 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 206 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 2 | 0 | 80 | 0 | 265 | 265 | 188 | 8 | 86 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 5 | 33 | 21 | 88 | 111 | 49 | 0 | 0.7 | 87 | 32 | 53 | 48 | 130 | 132 | 45 | 82 | 0 | 18 | 19 | 0 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6.5 | 30 | 0 | 0 | 235 | 115 | 0 | 0 | 1.8 | 214 | 0 | 0 | 0 | 0 |  | 642 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 35 | 0 | 3.4 | 109 | 0 |  | 5735 | 2289.4 | 8024.4 | 3748 | 642 | 1958 | 1139 | 369 | 68 | 0 | 88 | 12.4 | 0 | 89.16
17:00 | 37 | 0 | 170 | 0 | 340 | 0 | 0 | 349 | 320 |  | 0 | 450 | 150 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 25 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 208 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 8 | 0 | 80 | 0 | 280 | 280 | 177 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 22 | 84 | 128 | 49 | 0 | 0.1 | 87 | 32 | 25 | 48 | 100 | 133 | 45 | 50 | 0 | 18 | 19 | 0 | 10 | 270 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1.8 | 10 | 0 | 0 | 235 | 75 | 0 | 0 | 0.619 | 180 | 0 | 0 | 0 | 0 |  | 642 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 89 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 109 | 0 |  | 5479.519 | 2261.4 | 7740.919 | 3839 | 642 | 1866 | 869 | 369 | 68 | 0 | 84 | 3.919 | 0 | 89.15
18:00 | 37 | 0 | 170 | 0 | 343 | 0 | 0 | 347 | 320 |  | 0 | 400 | 150 | 25 | 1 | 4 | 0 | 0 | 0 | 0 | 96 | 32 | 0 | 5 | 0 | 0 | 1 | 53 | 17 | 0 | 0 | 25 | 16 | 33 | 16 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 217 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 7 | 19 | 22 | 13 | 0 | 80 | 0 | 285 | 285 | 193 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 22 | 116 | 127 | 76 | 0 | 0 | 86 | 32 | 23 | 50 | 100 | 132 | 45 | 50 | 0 | 139 | 19 | 0 | 10 | 300 | 23 | 11 | 0 | 6 | 0 | 0 | 7 | 0 | 35 | 0 | 10 | 0 | 5 | 233 | 80 | 17 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 641 | 0 | 260 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 14 | 32 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 423 | 0 | 0 | 2 | 15 | 0 | 0 | 0.1 | 109 | 0 |  | 5681 | 2333.1 | 8014.1 | 3944 | 641 | 1842 | 1019 | 370 | 68 | 14 | 116 | 0.1 | 0 | 89.15
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 0 | 166 | 0 | 336 | 0 | 0 | 363 | 326 |  | 0 | 450 | 150 | 84 | 67 | 50 | 0 | 0 | 0 | 0 | 96 | 85 | 48 | 33 | 0 | 0 | 10 | 53 | 55 | 0 | 22 | 25 | 31 | 33 | 32 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 44 | 46 | 19 | 22 | 0 | 80 | 0 | 265 | 265 | 183 | 8 | 81 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 124 | 130 | 91 | 20 | 0 | 88 | 32 | 53 | 50 | 100 | 133 | 65 | 82 | 0 | 158 | 19 | 0 | 10 | 275 | 24 | 11 | 0 | 86 | 0 | 0 | 40 | 0 | 101 | 0 | 100 | 0 | 30 | 235 | 115 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 |  | 885 | 0 | 260 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 88 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 32 | 32 | 0 | 0 | 109 | 0 |  | 6598 | 2717 | 9315 | 3917 | 885 | 1948 | 1940 | 368 | 68 | 65 | 124 | 0 | 0 | 89.14
19:30 | 37 | 0 | 170 | 0 | 332 | 0 | 0 | 337 | 326 |  | 0 | 450 | 150 | 100 | 50 | 55 | 0 | 0 | 0 | 0 | 96 | 85 | 48 | 0 | 0 | 0 | 40 | 53 | 55 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 87 | 50 | 19 | 28 | 0 | 80 | 0 | 265 | 265 | 183 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 124 | 130 | 91 | 0 | 0 | 88 | 32 | 53 | 50 | 100 | 134 | 63 | 82 | 0 | 158 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 17 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 0 | 50 | 235 | 85 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 |  | 886 | 0 | 260 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 88 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 32 | 74 | 0 | 0 | 109 | 0 |  | 6535 | 2680 | 9215 | 3851 | 886 | 1974 | 1896 | 368 | 68 | 48 | 124 | 0 | 0 | 0
20:00 | 37 | 0 | 170 | 0 | 341 | 0 | 0 | 340 | 318 |  | 0 | 450 | 130 | 100 | 15 | 30 | 0 | 0 | 0 | 0 | 96 | 85 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 209 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 96 | 50 | 19 | 28 | 0 | 80 | 0 | 280 | 280 | 197 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 120 | 130 | 91 | 0 | 0 | 88 | 32 | 53 | 50 | 100 | 132 | 63 | 82 | 0 | 158 | 19 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 0 | 10 | 235 | 55 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 |  | 886 | 0 | 260 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 15 | 74 | 0 | 0 | 109 | 0 |  | 6360 | 2712 | 9072 | 3934 | 886 | 1980 | 1667 | 369 | 68 | 48 | 120 | 0 | 0 | 89.14
21:00 | 37 | 0 | 170 | 0 | 339 | 0 | 0 | 340 | 295 |  | 0 | 450 | 130 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 45 | 50 | 19 | 30 | 0 | 80 | 0 | 265 | 265 | 218 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 120 | 131 | 58 | 0 | 0 | 87 | 32 | 53 | 50 | 100 | 134 | 45 | 82 | 0 | 160 | 19 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 50 | 0 | 0 | 235 | 7 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 |  | 886 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 50 | 0 |  | 5850 | 2512 | 8362 | 3895 | 886 | 1862 | 1161 | 370 | 68 | 0 | 120 | 0 | 0 | 89.13
22:00 | 37 | 0 | 169 | 0 | 325 | 0 | 0 | 356 | 290 |  | 0 | 400 | 125 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 23 | 19 | 33 | 0 | 80 | 0 | 265 | 265 | 199 | 8 | 87 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 112 | 135 | 24 | 22 | 0 | 87 | 32 | 53 | 50 | 130 | 134 | 55 | 50 | 0 | 159 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 |  | 887 | 0 | 275 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 14 | 11 | 5 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 |  | 5254 | 2451 | 7705 | 3831 | 887 | 1861 | 579 | 369 | 66 | 0 | 112 | 0 | 0 | 89.13
23:00 | 37 | 0 | 174 | 0 | 325 | 0 | 0 | 340 | 343 |  | 0 | 400 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 0 | 8 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 80 | 0 | 265 | 270 | 193 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 72 | 133 | 8 | 22 | 0 | 88 | 32 | 53 | 50 | 163 | 130 | 45 | 81 | 0 | 158 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 788 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 5 | 89 | 0 | 281 | 0 | 0 | 150 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5033 | 2229 | 7262 | 3722 | 788 | 2038 | 206 | 370 | 66 | 0 | 72 | 0 | 0 | 89.12
24:00 | 37 | 0 | 170 | 0 | 348 | 0 | 0 | 355 | 353 |  | 0 | 400 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 22 | 25 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 80 | 0 | 280 | 290 | 202 | 8 | 91 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 13 | 94 | 134 | 0 | 22 | 0 | 87 | 32 | 53 | 50 | 163 | 126 | 55 | 81 | 0 | 158 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 433 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5192 | 1883 | 7075 | 3872 | 433 | 2043 | 198 | 369 | 66 | 0 | 94 | 0 | 0 | 89.12
KWH | 878000 | 0 | 4033000 | 0 | 8008418 | 0 | 0 | 8599700 | 7906000 |  | 0 | 9666500 | 3293935 | 645120 | 146400 | 103036 | 0 | 0 | 0 | 0 | 1026048 | 670896 | 117600 | 48252 | 0 | 0 | 43392 | 889200 | 302496 | 0 | 244260 | 600000 | 635040 | 592200 | 661300 | 0 | 0 | 576540 | 968000 | 2600000 | 0 | 0 | 4943612 | 0 | 2914743 | 0 |  | 0 | 0 | 0 | 0 | 201600 | 279360 | 455856 | 442080 | 0 | 1988895 | 0 | 7284000 | 6992500 | 4470000 | 200727 | 2103410 | 308016 | 133920 | 0 | 1026344 | 0 | 0 | 0 | 442872 | 91980 | 638800 | 488240 | 2313600 | 3249200 | 1156800 | 224640 | 12500 | 2045000 | 630120 | 952800 | 1033128 | 3453136 | 2971000 | 1307424 | 1373760 | 0 | 2543260 | 307000 | 0 | 169920 | 7622500 | 386520 | 181144 | 0 | 125454 | 0 | 0 | 62400 | 0 | 871200 | 119745 | 407040 | 0 | 83636 | 5618000 | 1352400 | 19764 | 0 | 25800 | 2536691 | 0 | 0 | 0 | 0 |  | 13529455 | 0 | 7437312 | 0 | 292800 | 0 | 0 | 0 | 0 | 0 | 0 | 3119000 | 331100 | 186912 | 0 | 0 | 0 | 0 | 0 | 24540 | 527780 | 0 | 0 | 0 | 0 | 357840 | 172332 | 163458 | 2137745 | 0 | 6348900 | 0 | 0 | 4624627 | 0 | 0 | 0 | 921431 | 0 | 0 | 0 | 9798418 | 0 | 0 | 46176 | 69120 | 508800 | 0 | 37887 | 1603776 | 0 |  | 131817870 | 52239409 | 184057279 | 94782547 | 13529455 | 45561936 | 17500484 | 8486645 | 1544540 | 142140 | 2313600 | 195932 | 0
Fuel Cost | 983360 | 0 | 4315310 | 0 | 5926229.32 | 0 | 0 | 6191784 | 6008560 |  | 0 | 7733200 | 2964541.5 | 6580224 | 1585512 | 1057149.36 | 0 | 0 | 0 | 0 | 11389132.8 | 6816303.36 | 1165416 | 505680.96 | 0 | 0 | 406149.12 | 8527428 | 2885811.84 | 0 | 183195 | 450000 | 0 | 0 | 0 | 0 | 0 | 149900.4 | 251680 | 3978000 | 0 | 0 | 5190792.6 | 0 | 3701723.61 | 0 |  | 0 | 0 | 0 | 0 | 1917216 | 2614809.6 | 419387.52 | 1228982.4 | 0 | 2088339.75 | 0 | 5390160 | 5873700 | 4112400 | 196712.46 | 2797535.3 | 252573.12 | 137937.6 | 0 | 1467671.92 | 0 | 0 | 0 | 451729.44 | 68985 | 1207332 | 366180 | 15963840 | 2664344 | 11001168 | 229132.8 | 205000 | 2781200 | 856963.2 | 1295808 | 1291410 | 4281888.64 | 2733320 | 1948061.76 | 2417817.6 | 0 | 3865755.2 | 488130 | 0 | 399312 | 5411975 | 289890 | 137669.44 | 0 | 1313503.38 | 0 | 0 | 600288 | 0 | 8790408 | 1381857.3 | 3793612.8 | 0 | 783669.32 | 5280920 | 11860548 | 176097.24 | 0 | 0 | 23388291.02 | 0 | 0 | 0 | 0 |  | 36529528.5 | 0 | 5801103.36 | 0 | 2822592 | 0 | 0 | 0 | 0 | 0 | 0 | 2495200 | 513205 | 2007434.88 | 0 | 0 | 0 | 0 | 0 | 242946 | 5473078.6 | 0 | 0 | 0 | 0 | 393624 | 284347.8 | 123737.706 | 13617435.65 | 0 | 25967001 | 0 | 0 | 4069671.76 | 0 | 0 | 0 | 1465075.29 | 0 | 0 | 0 | 7152845.14 | 0 | 0 | 423895.68 | 615859.2 | 4752192 | 0 | 0 | 0 | 0 |  | 235170616.68 | 114750773.566 | 349921390.246 | 87713815.886 | 36529528.5 | 41680372.85 | 125052596.66 | 39584436.65 | 401580.4 | 1408362 | 15963840 | 1586857.3 | 0
Yesterday Day Peak | 37 | 0 | 200 | 0 | 370 | 0 | 0 | 378 | 347 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 224 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 80 | 0 | 320 | 290 | 142 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 5 | 33 | 18 | 92 | 130 | 49 | 0 | 1.7 | 86 | 20 | 48 | 48 | 163 | 126 | 59 | 79 | 0 | 127 | 19 | 0 | 10 | 330 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 18.8 | 0 | 0 | 0 | 236 | 115 | 0 | 0 | 5.6 | 191 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 35 | 0 | 6.5 | 109 | 0 |  | 8194.6 | DayPeak
Yesterday Evening Peak | 37 | 0 | 166 | 0 | 336 | 0 | 0 | 363 | 326 | 0 | 0 | 450 | 150 | 84 | 67 | 50 | 0 | 0 | 0 | 0 | 96 | 85 | 48 | 33 | 0 | 0 | 10 | 53 | 55 | 0 | 22 | 25 | 31 | 33 | 32 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 46 | 19 | 22 | 0 | 80 | 0 | 265 | 265 | 183 | 8 | 81 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 124 | 130 | 91 | 20 | 0 | 88 | 32 | 53 | 50 | 100 | 133 | 65 | 82 | 0 | 158 | 19 | 0 | 10 | 275 | 24 | 11 | 0 | 86 | 0 | 0 | 40 | 0 | 101 | 0 | 100 | 0 | 30 | 235 | 115 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 |  | 885 | 0 | 260 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 88 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 32 | 32 | 0 | 0 | 109 | 0 |  | 9315 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 20 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 113 | 150 | 95 | 22 | 0 | 88 | 22 | 51 | 44 | 163 | 150 | 66 | 82 | 0 | 220 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 895 | 40 | 300 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 135 | 22 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 11 | 11 | 90 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 0 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 20 | 10 | 0 | 80 | 0 | 360 | 360 | 225 | 8 | 90 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 102 | 160 | 95 | 22 | 1.6 | 85 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 220 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 647 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 130 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 90 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 0 | 0 | 100 | 0 | 276 | 0 | 0 | 338 | 366 | 0 | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 0 | 80 | 0 | 265 | 270 | 190 | 8 | 91 | 39 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 0 | 14 | 80 | 162 | 95 | 22 | 0.5 | 86 | 32 | 45 | 51 | 130 | 125 | 65 | 81 | 0 | 158 | 20 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6.4 | 0 | 0 | 0 | 233 | 16 | 0 | 0 | 1.8 | 50 | 0 | 0 | 0 | 0 | 0 | 642 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 12 | 0 | 1.4 | 70 | 0 | 0
199
| Minimum Generation |  | 6045 | 4:00
| Highest Generation |  | 9315 | 19:00
| Day Peak Generation |  | 8194.6 | 12:00
| Evening Peak Generation |  | 9315 | 19:00
| HVDC Max Flow |  | 887 | 22:00
| HVDC EvPeak Flow |  | 885 | 19:00
| Load factor L.F |  | 82.33%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8194.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5894 | MW
Evening Peak Generation : |  | 9315 | MW Hour : | 19:00 | Available Max Generation : |  | 14575 | MW
E.P. Demand (at gen end) : |  | 9315 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 9315 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5075 | MW
Total Gen. (MKWH) : |  | 184.0573 | System Load Factor : | 82.33% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -386 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-05
Actual : | 89.09 | Ft.(MSL) , | Rule curve : | 92.36 | Ft.( MSL )
Gas Consumed : | Total = | 1103.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 129394188.736
: |  | Coal : | 39584436.65 | Oil : | 126460958.66 | Total : | 295439584.046
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3400.5419 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1152.4038 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1031.8084 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 932.0749 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 842.441 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 679.8101 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 385.2234 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 175.168 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 524.2788 |  |  | 0 | 0%
Total | 0 |  | 9123.7502 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Bhola 225 MW STG
3) Ghorasal Unit-1,2,3 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) B.Baria 132/33 kV T-1 transformer was under shut down from 08:20 to 12:20 for C/M.
b) Aminbazar-Savar 132 kV Ckt-2 was under shut down from 09:42 to 21:07 for D/W.
c) Kishorganj 132/33 kV T-3 transformer was under shut down from 10:06 to 10:36 for A/M.
d) Ashuganj-Kishorganj 132 kV Ckt-1 was under shut down from 10:47 to 11:28 for D/W.
e) Kishorganj 132/33 kV T-2 transformer was under shut down from 08:53 to 09:44 for D/W.
f) Kishorganj-Mymensing 132 kV Ckt-2 was under shut down from 09:56 to 10:45 for D/W.
g) Kishorganj-Ashuganj 132 kV Ckt-2 was under shut down from 09:30 to 10:52 for D/W.
h) Mymensing 132/33 kV T-1 transformer was under shut down from 11:56 to 15:47 for A/M.
i) Dohazari-Cox'sbazar 132 kV Ckt-1 was under shut down from 12:20 to 17:38 for D/W.
j) Ghorasal-Ishurdi 230 kV Ckt-1 tripped at 12:32 showing PD-3,PTAW at Ghorasal end & dist.protection
,DT,Z2 at Ishurdi end and was switched on at 17:09.
k) Madaripur 132 kV Bus-A was under shut down from 11:07 to 12:15 for D/W.
l) B.Baria 132/33 kV T-2 transformer was under shut down from 12:36 to 13:18 for A/M.
m) Mymensing 132/33 kV T-2 transformer was under shut down from 15:50 to 17:29 for tan delta test.
n) Shahjibazar 132/33 kV T-2 transformer tripped at 15:13 showing Buchholz relay and was switched |  |  |  |  | About 33 MW power interruption occurred under Shahjibazar S/S areas
on at 15:56. |  |  |  |  | from 15:13 to 15:56.
o) Tangail-Kaliakoir 132 kV Ckt-2 tripped at 19:30 showing dist.differential at Tangail end & dist.Z1,Z2,
Z3,Z5 at Kaliakoir end and was switched on at 20:12.
p) Mymensing-Valuka 132 kV Ckt-1 & 2 tripped at 20:11 showing dist.Z3,3-phase and were switched |  |  |  |  | About 80 MW power interruption occurred under Valuka S/S areas
on at 20:31. |  |  |  |  | from 20:11 to 20:31.
q) Ullon-Siddirganj 132 kV Ckt tripped at 20:51 showing Z1,BN,dist,trip-1,trip-2 and was switched |  |  |  |  | About 105 MW power interruption occurred under Dhanmondi S/S areas
on at 20:59. |  |  |  |  | from 20:51 to 20:59.
r) Ullon-Haripur 132 kV Ckt tripped at 20:51 showing Y-phase,Z2 and was switched on at 20:59.
s) Sylhet-225 MW ST was synchronized at 17:23.
t) Jhenaidah-Chuadanga 132 kV Ckt is under shut down since 07:21(5/3/20) for D/W.
u) Kodda-Gazipur-100 MW P/S 132 kV Ckt is under shut down since 06:54(5/3/20) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 878000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 166 | 4033000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 336 | 8008418
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 363 | 8599700 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7906000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9666500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 84 | 645120 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 150 | 3293935 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 67 | 146400 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 50 | 103036
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 33 | 48252 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 244260
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 96 | 1026048
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 670896 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 10 | 43392 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 889200
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 117600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 302496
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1235040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 592200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 661300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 86 | 125454 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 101 | 871200 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 19764 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2739 | 50127211
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 119745
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 279360
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 68 | 1544540 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4943612
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2914743 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 407040
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 455856
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 442080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 201600 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 232 | 2536691 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 949 | 16471067
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1988895 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4470000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 7284000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6992500 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 308016 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 133920 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1026344 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 83636 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 81 | 2103410
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 442872
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 91980 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2313600
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 638800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 488240
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1179 | 28566940
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 130 | 3249200 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 224640
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 1156800
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12500
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 62400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1352400
| Mymensingh Area Total |  |  |  | 637 | 396 | 6057940
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2045000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 630120
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3453136 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 133 | 2971000 | FGMO & GT-1 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 952800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1033128
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 181144
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1307424 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1373760
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 158 | 2543260
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 307000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 386520
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7622500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 235 | 5618000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 169920
| Sylhet Area Total |  |  |  | 1949 | 1335 | 30594712
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 885 | 13529455
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 66 | 292800 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7437312 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 32 | 69120 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1243 | 21328687
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 186912 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 331100 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 121 | 3119000 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 921431 | Gas shortage.
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | Machine problem
| Barisal Area Total |  |  |  | 462 | 285 | 4558443
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 527780
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4624627 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 379 | 9798418 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 357840 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 172332
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 163458 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 17 | 24540 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 46176 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1603776
| Rajshahi Area Total |  |  |  | 2183 | 789 | 17318947
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 88 | 2137745
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6348900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 32 | 508800 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37887
| Rangpur Area Total |  |  |  | 605 | 400 | 9033332
| Total |  |  |  | 19107 | 9315 | 184057279
| Eastern Grid Total |  |  |  | 13543 | 6598 | 131817870
| Western Grid Total |  |  |  | 5564 | 2717 | 52239409
| National Grid Total |  |  |  | 19107 | 9315 | 184057279
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-04
(a) ENTIRE EASTERN GRID : |  | 6375 | MW | (b) ENTIRE WESTERN GRID : |  | 2562 | MW
i) Dhaka area |  | 3490 | MW | i) Khulna area |  | 1027 | MW
ii) Chittagong area |  | 1038 | MW | ii) Rajshahi area |  | 652 | MW
iii) Comilla area |  | 773 | MW | iii) Barisal area |  | 217 | MW
iv) Mymensingh area |  | 727 | MW | iv) Rangpur area |  | 666 | MW
v) Sylhet area |  | 347 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8937 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 12:00 | Sherpur | 92 | 18:30 | Benapol | 32 | 19:30
Munsiganj | 88 | 19:00 | Srimongal | 31 | 18:30 | Jhenida | 83 | 19:00
Sonargaon | 72 | 19:00 | Shahjibazar | 77 | 18:30 | Bottail | 80 | 12:00
Shyampur | 184 | 13:00 | Fenchuganj | 29 | 18:30 | G.K Project | 32 | 19:30
Bhulta | 164 | 1:00 | Kulawara | 28 | 18:30 | Faridpur | 120 | 18:00
Madanganj | 55 | 15:00 | Sylhet | 105 | 18:30 | Madaripur | 61 | 20:00
Shitalakhya | 107 | 10:00 | Chatak | 18 | 19:30 | Sariatpur | 40 | 19:30
Rahim steel | 23 | 11:00 | Sunamganj | 28 | 19:00 | Gopalganj | 68 | 19:00
Matuail | 92 | 12:00 | Biani Bazar | 34 | 19:00 | Bagerhat | 74 | 19:00
Ghorasal | 68 | 19:30 | Comilla (S) | 124 | 19:00 | Mongla | 36 | 8:00
Narsingdi | 122 | 19:30 | Comilla(N) | 89 | 18:30 | Satkhira | 74 | 19:00
Haripur (SBU) | 98 | 9:00 | Chandpur | 61 | 19:00 | Gallamari | 39 | 19:00
Ullon | 60 | 20:00 | Feni | 80 | 19:00 | Magura | 36 | 18:30
Hasnabad | 138 | 20:00 | Chowmuhani | 112 | 19:00 | Norail | 30 | 18:30
Magbazar | 91 | 15:00 | Ashuganj | 46 | 21:00 | Chuadanga | 53 | 19:30
Maniknagar | 90 | 18:00 | Daudkandi | 100 | 20:00 | Barisal(N) | 28 | 21:00
Bangabhaban | 28 | 13:00 | B.Baria | 104 | 19:00 | Barisal (S) | 74 | 19:00
Narinda | 84 | 16:00 | Ramganj | 72 | 19:00 | Patuakhali | 75 | 21:00
Dhanmondi | 124 | 12:00 | Chaddagram | 20 | 13:00 | Bhandaria | 40 | 19:00
Lalbag | 53 | 13:00 | PHP | 3 | 17:00 | Borhan Uddin | 27 | 19:30
Madartek | 52 | 20:00 | Madunaghat | 43 | 18:30 | Ishurdi | 37 | 20:00
Dhaka University |  |  | Hathazari | 76 | 21:00 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 86 | 19:00 | Khulshi | 156 | 16:00 | Natore | 81 | 8:00
Kalyanpur | 78 | 19:00 | Halishahar | 107 | 19:30 | Bogra | 129 | 18:30
Gulshan | 98 | 19:00 | Baraulia | 148 | 0:00 | Noagaon | 94 | 9:00
Uttara | 62 | 13:00 | Sikalbaha | 20 | 12:00 | Rajshahi | 95 | 20:00
Uttara New | 37 | 19:00 | Dohazari | 70 | 22:00 | Rajshahi New | 8 | 19:00
Kamrangirchar | 91 | 19:00 | Cox'sbazar | 83 | 19:30 | C.Nawabganj | 57 | 7:00
Savar | 110 | 19:00 | Chandraghona | 24 | 19:00 | Amnura | 24 | 19:00
Bhasantec | 116 | 19:00 | Kaptai | 3.8 | 19:00 | Pabna | 76 | 13:00
Agargaon | 42 | 13:00 | A. Khaer Stl. | 22 | 7:00 | Shahjadpur | 88 | 8:00
Satmosjid | 74 | 19:00 | Bakulia | 85 | 18:30 | Serajganj | 85 | 7:00
Tongi | 91 | 11:00 | Julda | 21 | 12:00 | Niyamatpur | 77 | 10:00
Kabirpur | 166 | 11:00 | TK chemical | 11 | 19:00 | Joypurhat | 54 | 8:00
Basundhara | 116 | 18:30 | Modern Steel | 16 | 11:00 | Sherpur(Bogura) | 36 | 7:00
Manikganj | 82 | 19:00 | Shahmirpur | 26 | 18:30 | Mohastangor | 39 | 19:30
Joydevpur | 137 | 18:00 | Khagrachhari | 18 | 20:00 | Rangpur | 121 | 19:00
New Tongi | 89 | 16:00 | Matarbari | 25 | 18:30 | Lalmonirhat | 45 | 19:30
Korda | 176 | 19:30 | Baroiar Hat | 26 | 19:00 | Saidpur | 96 | 19:00
Dhamrai | 54 | 15:00 | Rangamati | 10 | 19:00 | Purbasadipur | 96 | 19:00
Rajendrapur | 74 | 18:30 | Abul Khair 230 | 124 | 8:00 | Thakurgaon | 65 | 19:30
Valuka | 92 | 19:00 | BSRM | 105 | 8:00 | Palashbari | 100 | 19:00
Tangail | 171 | 7:00 | GPH Ispat | 57 | 16:00 | Barapukuria | 46 | 13:00
Mymensing | 169 | 18:30 | Goalpara | 26 | 13:00 | Panchagar | 35 | 18:30
Kishorganj | 92 | 20:00 | Central s/s | 66 | 19:00 | Joldhaka | 23 | 19:30
Netrokona | 96 | 19:00 | Noapara | 49 | 18:30 | Kurigram | 47 | 0.79167
Jamalpur | 92 | 18:30 | Jessore | 96 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-04 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.16667 | 395 | 0.5 | Kaliakoir | 386 | 0.125 | 372 | 0.70833
Bheramara | 405 | 0.125 | 391 | 0.79167 | Bhulta | 395 | 0.20833 | 381 | 0.5
Ashuganj(N) | 402 | 0.25 | 387 | 0.5 | Gopalganj | 417 | 0.125 | 378 | 0.77083
Payra | 421 | 0.20833 | 389 | 0.875
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 236 | 0.875 | 235 | 0.041667 | Hathazari | 223 | 0.125 | 217 | 0.45833
Ishurdi | 239 | 0.16667 | 228 | 0.29167 | Megnaghat | 234 | 0.041667 | 228 | 0.625
Ashuganj | 242 | 0.79167 | 235 | 0.5 | Fenchuganj | 242 | 0.54167 | 238 | 0.375
Serajganj | 233 | 0.16667 | 227 | 0.33333 | Siddhirganj | 234 | 0.125 | 225 | 0.45833
Baghabari | 245 | 0.125 | 238 | 0.29167 | Maniknagar | 232 | 0.125 | 223 | 0.5
Barapukuria | 237 | 0.041667 | 230 | 0.33333 | Old Airport | 232 | 0.125 | 221 | 0.5
Bogra | 230 | 0.75 | 216 | 0.29167 | Barisal | 249 | 0.20833 | 240 | 0.77083
Khulna South | 237 | 0.20833 | 218 | 0.77083 | AKSML | 220 | 0.16667 | 214 | 0.95833
Rampura | 231 | 0.041667 | 225 | 0.5 | BSRM | 225 | 0.16667 | 218 | 0.66667
Haripur | 231 | 0.041667 | 223 | 0.5 | Bibiyana | 240 | 0.16667 | 235 | 0.54167
Hasnabad | 230 | 0.041667 | 222 | 0.5 | Bhulta | 234 | 0.125 | 225 | 0.5
Shyampur | 230 | 0.16667 | 220 | 0.5 | Ashuganj (S) | 239 | 0.083333 | 232 | 0.41667
Aminbazar | 233 | 0.16667 | 222 | 0.5 | Kaliakoir | 233 | 0.16667 | 221 | 0.5
Tongi | 229 | 0.16667 | 220 | 0.45833 | GPH | 220 | 0.8125 | 215 | 0.5
Comilla (N) | 2323 | 0.41667 | 231 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.79167 | 127 | 0.5 | Hathazari | 133 | 0.16667 | 129 | 0.45833
Munsiganj | 135 | 0.75 | 127 | 0.5 | Khulshi | 130 | 0.8125 | 125 | 0.45833
Sonargaon | 130 | 0.041667 | 123 | 0.5 | Halishahar | 133 | 0.8125 | 127 | 0.33333
Shyampur | 134 | 0.125 | 127 | 0.5 | Baraulia | 131 | 0.79167 | 127 | 0.45833
Bhulta | 128 | 0.16667 | 123 | 0.45833 | Sikalbaha | 132 | 0.79167 | 127 | 0.5
Madanganj | 135 | 0.79167 | 125 | 0.45833 | Dohazari | 129 | 0.33333 | 126 | 0.5
Shitalakhya | 137 | 0.79167 | 125 | 0.5 | Cox'sbazar | 125 | 0.41667 | 118 | 0.54167
Rahim steal | 133 | 1:00 | 128 | 0.5 | Chandraghona | 132 | 0.79167 | 129 | 0.5
Matuail | 133 | 0.79167 | 126 | 0.5 | Kaptai | 132 | 0.041667 | 130 | 0.375
Ghorasal | 140 | 0.041667 | 136 | 0.625 | A. Khaer Stl. | 130 | 0.041667 | 126 | 0.41667
Narsinghdi | 131 | 0.16667 | 127 | 0.75 | Bakulia | 130 | 0.83333 | 126 | 0.33333
Haripur (SBU) | 134 | 0.8125 | 128 | 0.5 | Julda | 131 | 0.79167 | 127 | 0.33333
Ullon | 130 | 0.25 | 123 | 0.5 | TK Chemical | 131 | 0.16667 | 128 | 0.33333
Hasnabad | 133 | 0.25 | 127 | 0.5 | Modern Steel | 131 | 0.83333 | 126 | 0.45833
Magbazar | 132 | 0.25 | 124 | 0.5 | Shahmirpur | 131 | 0.79167 | 127 | 0.41667
Maniknagar | 135 | 0.25 | 130 | 0.5 | Khagrachhari | 131 | 0.8125 | 128 | 0.5
Bangabhaban | 135 | 0.29167 | 130 | 0.54167 | Matarbari | 129 | 0.54167 | 120 | 0.75
Narinda | 135 | 0.33333 | 130 | 0.58333 | Baroiar Hat | 132 | 0.041667 | 130 | 10:00
Dhanmondi | 130 | 0.25 | 123 | 0.5 | Rangamati | 131 | 0.79167 | 129 | 8:00
Lalbag | 134 | 0.25 | 121 | 0.5 | Goalpara | 135 | 0.66667 | 124 | 0.33333
Madartek | 131 | 0.20833 | 123 | 0.5 | Central s/s | 134 | 0.083333 | 124 | 0.77083
Dhaka University |  |  |  |  | Noapara | 133 | 0.66667 | 123 | 0.29167
Mirpur | 137 | 0.25 | 128 | 0.70833 | Jessore | 132 | 0.66667 | 119 | 0.33333
Kalyanpur | 135 | 0.25 | 128 | 0.70833 | Benapol | 134 | 0.16667 | 122 | 0.33333
Gulshan | 130 | 0.25 | 124 | 0.70833 | Jhenida | 133 | 0.95833 | 122 | 0.33333
Uttara | 135 | 0.25 | 127 | 0.70833 | Bottail | 135 | 0.16667 | 128 | 0.33333
Uttara New | 135 | 0.25 | 128 | 0.70833 | G.K Project | 140 | 0.16667 | 134 | 0.29167
Kamrangirchar | 132 | 0.25 | 124 | 0.70833 | Faridpur | 140 | 0.20833 | 126 | 0.77083
Savar | 134 | 0.25 | 127 | 0.70833 | Madaripur | 140 | 0.20833 | 127 | 0.77083
Bhasantec | 133 | 0.25 | 127 | 0.70833 | Sariatpur | 142 | 0.20833 | 129 | 0.77083
Agargaon | 135 | 0.25 | 128 | 0.70833 | Gopalganj | 146 | 0.16667 | 135 | 0.77083
Satmosjid | 136 | 0.25 | 127 | 0.70833 | Bagerhat | 133 | 0.125 | 120 | 0.77083
Tongi | 137 | 0.16667 | 130 | 0.45833 | Mongla | 132 | 0.125 | 121 | 0.33333
Kabirpur | 133 | 0.875 | 125 | 0.375 | Satkhira | 133 | 0.125 | 122 | 0.77083
Basundhara | 130 | 8:00 | 123 | 0.70833 | Gallamari | 134 | 0.16667 | 124 | 0.33333
Manikganj | 138 | 0.79167 | 130 | 0.66667 | Magura | 133 | 0.16667 | 120 | 0.33333
Joydevpur | 140 | 0.8125 | 134 | 0.75 | Norail | 131 | 0.125 | 120 | 0.79167
New Tongi | 136 | 0.875 | 128 | 0.70833 | Chuadanga | 131 | 0.75 | 118 | 0.29167
Kodda | 135 | 0.83333 | 122 | 0.5 | Barisal(N) | 142 | 0.20833 | 134 | 0.77083
Dhamrai | 133 | 0.83333 | 125 | 0.125 | Barisal (S) | 139 | 0.66667 | 131 | 0.77083
Rajendrapur | 138 | 0.875 | 130 | 0.54167 | Patuakhali | 138 | 0.25 | 128 | 0.77083
Valuka | 134 | 0.91667 | 118 | 0.375 | Bhandaria | 136 | 0.16667 | 125 | 0.77083
Tangail | 134 | 0.875 | 122 | 0.375 | Ishurdi | 137 | 0.75 | 130 | 0.33333
Mymensing | 135 | 0.91667 | 121 | 0.375 | Ruppur Paromanobik | 136 | 0.125 | 130 | 0.29167
Kishorganj | 134 | 0.91667 | 124 | 0.375 | Natore | 137 | 0.75 | 125 | 0.29167
Netrokona | 134 | 0.91667 | 119 | 0.75 | Bogra | 137 | 0.75 | 127 | 0.33333
Jamalpur | 139 | 0.79167 | 122 | 0.95833 | Noagaon | 133 | 0.75 | 119 | 0.33333
Sherpur | 137 | 0.79167 | 122 | 0.95833 | Rajshahi | 135 | 0.70833 | 122 | 0.29167
Srimongal | 138 | 0.041667 | 136 | 0.54167 | Rajshahi New | 134 | 0.66667 | 120 | 0.29167
Shahjibazar | 136 | 0.041667 | 133 | 18:00 | C.Nawabganj | 133 | 0.66667 | 119 | 0.33333
Fenchuganj | 138 | 0.375 | 135 | 0.5 | Amnura | 136 | 0.66667 | 119 | 0.29167
Khulawara | 137 | 0.20833 | 134 | 0.77083 | Pabna | 135 | 0.125 | 125 | 0.29167
Sylhet | 136 | 0.041667 | 133 | 0.77083 | Shahjadpur | 137 | 0.79167 | 125 | 0.29167
Chatak | 135 | 0.041667 | 132 | 0.70833 | Serajganj | 135 | 0.041667 | 125 | 0.29167
Sunamganj | 135 | 0.083333 | 132 | 0.70833 | Niyamatpur | 133 | 0.70833 | 115 | 0.29167
Biani Bazar | 136 | 0.041667 | 133 | 0.66667 | Joypurhat | 133 | 0.70833 | 116 | 0.33333
Comilla(s) | 133 | 0.95833 | 125 | 0.375 | Sherpur(Bogura) | 136 | 0.75 | 125 | 0.29167
Comilla(n) | 138 | 0.29167 | 136 | 0.45833 | Mohastangor | 135 | 0.083333 | 125 | 0.29167
Chandpur | 135 | 0.29167 | 131 | 0.875 | Rangpur | 130 | 0.75 | 116 | 0.29167
Feni | 132 | 0.29167 | 129 | 0.79167 | Lalmonirhat | 128 | 0.125 | 120 | 0.77083
Chowmuhani | 130 | 0.29167 | 126 | 0.91667 | Saidpur | 131 | 0.125 | 122 | 0.33333
Ashuganj | 137 | 0.25 | 134 | 0.75 | Purbasadipur | 130 | 0.125 | 115 | 0.33333
Daudkandi | 133 | 0.29167 | 128 | 0.5 | Thakurgaon | 128 | 0.125 | 115 | 0.33333
B.Baria | 133 | 0.91667 | 129 | 0.75 | Palashbari | 133 | 0.125 | 123 | 0.5
Ramganj | 128 | 0.75 | 124 | 0.8125 | Barapukuria | 137 | 0.041667 | 130 | 0.33333
Chaddagram | 134 | 0.083333 | 131 | 0.41667 | Panchagar | 126 | 0.083333 | 117 | 0.29167
PHP | 132 | 0.20833 | 128 | 0.66667 | Joldhaka | 131 | 0.083333 | 117 | 0.29167
Madanhat | 133 | 0.79167 | 130 | 0.375 | Kurigram | 133 | 0.20833 | 119 | 0.33333

## L-Curve
Date | 2020-03-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 138 | 5192 | 1883 | 7075 |  |  |  | QF-LDC-12
0:30 | 262 | 5251 | 1749.5 | 7000.5 | Date: | 2020-03-04
1:00 | 386 | 5310 | 1616 | 6926
1:30 | 349.5 | 5111 | 1605.5 | 6716.5
2:00 | 313 | 4912 | 1595 | 6507
2:30 | 281.5 | 4761.5 | 1584.5 | 6346 | [5 empty] | Gen. at Eve. Peak | 9315 | 9315 MW (19:00 )
3:00 | 250 | 4611 | 1574 | 6185 | [6 empty] | 19:00
3:30 | 234 | 4549 | 1566 | 6115 | [5 empty] | Gen. at Day Peak | 8194.6 | 8194.6 MW (12:00 )
4:00 | 218 | 4487 | 1558 | 6045 | [6 empty] | 12:00
4:30 | 205.5 | 4518.5 | 1558 | 6076.5 | [5 empty] | Highest Generation | 9315
5:00 | 193 | 4550 | 1558 | 6108 | [6 empty] | 19:00
5:30 | 214 | 4683.5 | 1614.5 | 6298
6:00 | 235 | 4817 | 1671 | 6488
6:30 | 204 | 4889.6 | 1898.1 | 6787.7
7:00 | 173 | 4962.2 | 2125.2 | 7087.4
7:30 | 195.5 | 5141 | 2160 | 7301
8:00 | 218 | 5319.8 | 2194.8 | 7514.6
8:30 | 131 | 5452.2 | 2236.7 | 7688.9
9:00 | 44 | 5584.6 | 2278.6 | 7863.2
9:30 | 57.5 | 5596.15 | 2286.8 | 7882.95
10:00 | 71 | 5607.7 | 2295 | 7902.7
10:30 | 85.5 | 5576.25 | 2323.6 | 7899.85
11:00 | 100 | 5544.8 | 2352.2 | 7897
11:30 | 78 | 5690.45 | 2355.35 | 8045.8
12:00 | 56 | 5836.1 | 2358.5 | 8194.6
12:30 | 58 | 5910.1 | 2348.5 | 8258.6
13:00 | 60 | 5984.1 | 2338.5 | 8322.6
13:30 | 70 | 5871.9 | 2314.8 | 8186.7
14:00 | 80 | 5759.7 | 2291.1 | 8050.8
14:30 | 115 | 5810.15 | 2293.85 | 8104
15:00 | 150 | 5860.6 | 2296.6 | 8157.2
15:30 | 195 | 5797.8 | 2293 | 8090.8
16:00 | 240 | 5735 | 2289.4 | 8024.4
16:30 | 255 | 5607.2595 | 2275.4 | 7882.6595
17:00 | 270 | 5479.519 | 2261.4 | 7740.919
17:30 | 277.5 | 5580.2595 | 2297.25 | 7877.5095
18:00 | 285 | 5681 | 2333.1 | 8014.1
18:30 | 154.5 | 6139.5 | 2525.05 | 8664.55
19:00 | 24 | 6598 | 2717 | 9315
19:30 | 100 | 6535 | 2680 | 9215
20:00 | 116 | 6360 | 2712 | 9072 |  |  |  | Executive Engineer
20:30 | 171 | 6105 | 2612 | 8717 |  |  |  | Network Operation Division
21:00 | 226 | 5850 | 2512 | 8362
21:30 | 153 | 5552 | 2481.5 | 8033.5
22:00 | 80 | 5254 | 2451 | 7705 |  |  |  |  | Page 6 of 7
22:30 | 73.5 | 5143.5 | 2340 | 7483.5
23:00 | 67 | 5033 | 2229 | 7262
23:30 | 102.5 | 5112.5 | 2056 | 7168.5
24:00 | 138 | 5192 | 1883 | 7075
9315 MW (19:00 )
8194.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-04 |  | Energy | 184057279
[10 empty] | 2020-03-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3872 | 433 | 2043 | 206 | 369 | 66 | 0 | 0 | 94
0:30 | 3892 | 315.5 | 1996 | 296.5 | 345.5 | 67 | 0 | 0 | 92 | Date: | 2020-03-04
1:00 | 3912 | 198 | 1949 | 387 | 322 | 68 | 0 | 0 | 90
1:30 | 3876 | 198.5 | 1907.5 | 257.5 | 322 | 68 | 0 | 0 | 87 | [7 empty] | Total Energy | 184.0573 | Total Energy Gen 184.057 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.057 MKWHr
2:00 | 3840 | 199 | 1866 | 128 | 322 | 68 | 0 | 0 | 84 | [7 empty] | Energy not Served | 0
2:30 | 3768 | 198.5 | 1778 | 128 | 321.5 | 68 | 0 | 0 | 84 | [7 empty] | Energy Requirement | 184.0573
3:00 | 3696 | 198 | 1690 | 128 | 321 | 68 | 0 | 0 | 84
3:30 | 3692 | 198.5 | 1626 | 128 | 320.5 | 68 | 0 | 0 | 82 | [6 empty] | Shortage
4:00 | 3688 | 199 | 1562 | 128 | 320 | 68 | 0 | 0 | 80
4:30 | 3723.5 | 198.5 | 1557.5 | 128 | 320 | 68 | 0 | 0 | 81
5:00 | 3759 | 198 | 1553 | 128 | 320 | 68 | 0 | 0 | 82
5:30 | 3874 | 198 | 1612.5 | 143 | 319.5 | 68 | 0 | 0 | 83
6:00 | 3989 | 198 | 1672 | 158 | 319 | 68 | 0 | 0 | 84
6:30 | 4017.5 | 403 | 1705 | 190.5 | 319.5 | 68 | 0 | 0 | 83 |  |  |  |  | Coal
7:00 | 4046 | 608 | 1738 | 223 | 320 | 68 | 0 | 0 | 82
7:30 | 4045 | 624.5 | 1819.5 | 335 | 320 | 68 | 0 | 0 | 83 |  |  |  | Oil |  |  |  | ,
8:00 | 4044 | 641 | 1901 | 447 | 320 | 68 | 0 | 0 | 84
8:30 | 4073 | 640.5 | 1936 | 552 | 320 | 67.5 | 0 | 0 | 85
9:00 | 4102 | 640 | 1971 | 657 | 320 | 67 | 0 | 0 | 86
9:30 | 4087.5 | 640 | 1938.5 | 702.5 | 339.5 | 67 | 0 | 0 | 87
10:00 | 4073 | 640 | 1906 | 748 | 359 | 67 | 0 | 0 | 88
10:30 | 4085.5 | 641 | 1896 | 727.5 | 364.5 | 67 | 0 | 0 | 92
11:00 | 4098 | 642 | 1886 | 707 | 370 | 67 | 0 | 0 | 96
11:30 | 4114 | 642 | 1964 | 762.5 | 370 | 67.5 | 0 | 0 | 94
12:00 | 4130 | 642 | 2042 | 818 | 370 | 68 | 0 | 0 | 92
12:30 | 4075.5 | 642 | 2022 | 955 | 370 | 68 | 0 | 0 | 96
13:00 | 4021 | 642 | 2002 | 1092 | 370 | 68 | 0 | 0 | 100
13:30 | 4021 | 642 | 2002 | 1092 | 370 | 68 | 0 | 0 | 100
14:00 | 4021 | 642 | 2002 | 1092 | 370 | 68 | 0 | 0 | 100
14:30 | 3952.5 | 642 | 2008.5 | 1073.5 | 369.5 | 68 | 0 | 0 | 102
15:00 | 3884 | 642 | 2015 | 1055 | 369 | 68 | 0 | 0 | 104
15:30 | 3816 | 642 | 1986.5 | 1097 | 369 | 68 | 0 | 0 | 96
16:00 | 3748 | 642 | 1958 | 1139 | 369 | 68 | 0 | 0 | 88
16:30 | 3793.5 | 642 | 1912 | 1004 | 369 | 68 | 0 | 0 | 86
17:00 | 3839 | 642 | 1866 | 869 | 369 | 68 | 0 | 0 | 84
17:30 | 3891.5 | 641.5 | 1854 | 944 | 369.5 | 68 | 7 | 0 | 100
18:00 | 3944 | 641 | 1842 | 1019 | 370 | 68 | 14 | 0 | 116
18:30 | 3930.5 | 763 | 1895 | 1479.5 | 369 | 68 | 39.5 | 0 | 120
19:00 | 3917 | 885 | 1948 | 1940 | 368 | 68 | 65 | 0 | 124
19:30 | 3851 | 886 | 1974 | 1896 | 368 | 68 | 48 | 0 | 124
20:00 | 3934 | 886 | 1980 | 1667 | 369 | 68 | 48 | 0 | 120
20:30 | 3914.5 | 886 | 1921 | 1414 | 369.5 | 68 | 24 | 0 | 120
21:00 | 3895 | 886 | 1862 | 1161 | 370 | 68 | 0 | 0 | 120
21:30 | 3863 | 886.5 | 1861.5 | 870 | 369.5 | 67 | 0 | 0 | 116
22:00 | 3831 | 887 | 1861 | 579 | 369 | 66 | 0 | 0 | 112
22:30 | 3776.5 | 837.5 | 1949.5 | 392.5 | 369.5 | 66 | 0 | 0 | 92
23:00 | 3722 | 788 | 2038 | 206 | 370 | 66 | 0 | 0 | 72
23:30 | 3797 | 610.5 | 2040.5 | 206 | 369.5 | 66 | 0 | 0 | 83 | Max Temp. in Dhaka |  | 30° C
24:00 | 3872 | 433 | 2043 | 206 | 369 | 66 | 0 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.057 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.057 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 576540
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.8 | 6.5 | 12.5 | 16 | 18.3 | 18.8 | 17.9 | 15.5 | 11.1 | 6.5 | 1.8 | [9 empty] | 119745
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 202 | 202 | 203 | 208 | 206 | 212 | 205 | 203 | 204 | 228 | 224 | 207 | 205 | 213 | 206 | 208 | 217 |  | 204 | 203 | 209 | 204 | 204 | 203 | 218 | 4943612
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 106 | 104 | 105 | 104 | 105 | 105 | 134 | 135 | 135 | 133 | 144 | 145 | 133 | 106 | 140 | 138 | 140 | 140 |  | 104 | 104 | 104 | 104 | 104 | 139 | 139 | 2914743
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 6 |  | 86 | 17 | [5 empty] | 125454
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 878000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 151 | 150 | 100 | 99 | 100 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 172 | 170 | 171 | 170 | 170 |  | 166 | 170 | 170 | 170 | 169 | 174 | 170 | 4033000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 297 | 304 | 298 | 300 | 317 | 330 | 340 | 325 | 325 | 383 | 345 | 370 | 325 | 326 | 352 | 326 | 340 | 343 |  | 336 | 332 | 341 | 339 | 325 | 325 | 348 | 8008418
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1988895
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 29 | 33 | 33 | 33 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 308016
33 | Ashuganj 225 MW CCPP | 198 | 198 | 198 | 197 | 202 | 197 | 196 | 192 | 169 | 170 | 135 | 142 | 158 | 179 | 156 | 188 | 177 | 193 |  | 183 | 183 | 197 | 218 | 199 | 193 | 202 | 4470000
34 | Ashuganj 450 MW CCPP(South) | 270 | 275 | 270 | 270 | 285 | 325 | 325 | 300 | 360 | 295 | 285 | 290 | 285 | 260 | 280 | 265 | 280 | 285 |  | 265 | 265 | 280 | 265 | 265 | 270 | 290 | 6992500
| Ashuganj 450 MW CCPP(North) | 280 | 290 | 280 | 280 | 295 | 305 | 305 | 320 | 315 | 315 | 310 | 320 | 270 | 310 | 290 | 265 | 280 | 285 |  | 265 | 265 | 280 | 265 | 265 | 265 | 280 | 7284000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 133920
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 91 | 86 | 91 | 91 |  | 81 | 90 | 90 | 90 | 87 | 90 | 91 | 2103410
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 343 | 342 | 339 | 349 | 364 | 345 | 348 | 353 | 345 | 355 | 378 | 389 | 340 | 378 | 342 | 349 | 347 |  | 363 | 337 | 340 | 340 | 356 | 340 | 355 | 8599700
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 370 | 370 | 380 | 380 | 420 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 9666500
41 | Haripur 360MW CCPP(HPL) | 352 | 363 | 364 | 325 | 285 | 317 | 317 | 367 | 365 | 360 | 354 | 347 | 338 | 313 | 320 | 320 | 320 | 320 |  | 326 | 326 | 318 | 295 | 290 | 343 | 353 | 7906000
42 | RPCL 210MW CCPP | 147 | 157 | 161 | 161 | 161 | 161 | 161 | 160 | 160 | 130 | 130 | 130 | 131 | 113 | 111 | 111 | 128 | 127 |  | 130 | 130 | 130 | 131 | 135 | 133 | 134 | 3249200
43
44 | Fenchugonj CCPP Phase-1 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 89 | 88 | 89 | 86 | 85 | 86 | 86 | 87 | 87 | 86 |  | 88 | 88 | 88 | 87 | 87 | 88 | 87 | 2045000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 630120
46 | Shajibazar 330 MW CCPP | 131 | 133 | 125 | 124 | 126 | 126 | 126 | 126 | 131 | 132 | 131 | 126 | 131 | 135 | 133 | 132 | 133 | 132 |  | 133 | 134 | 132 | 134 | 134 | 130 | 126 | 2971000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 45 | 45 | 45 | 45 | 56 | 65 | 65 | 64 | 65 | 45 | 59 | 61 | 60 | 60 | 45 | 45 | 45 |  | 65 | 63 | 63 | 45 | 55 | 45 | 55 | 1307424
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 79 | 79 | 79 | 82 | 82 | 50 | 50 |  | 82 | 82 | 82 | 82 | 50 | 81 | 81 | 1373760
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 118 | 120 | 67 | 68 | 68 | 67 | 67 | 68 | 68 | 67 | 128 | 127 | 147 | 97 | 28 | 18 | 18 | 139 |  | 158 | 158 | 158 | 160 | 159 | 158 | 158 | 2543260
51 | Sylhet 20 MW GTPP | 19 | [7 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 |  |  | 307000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 |  | 0 | 169920
54 | Hobiganj 11MW PP Cofidence-E | 11 | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 181144
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 48 | 48 | 48 | 48 | 50 | 50 | 53 | 25 | 23 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 952800
56 | Shahjahanulla 25 MW PP | 24 | [6 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 23 |  | 24 | 24 | 24 | 24 | 24 |  | 0 | 386520
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 290 | 320 | 320 | 310 | 300 | 310 | 290 | 280 | 330 | 300 | 280 | 325 | 300 | 270 | 300 |  | 275 | 295 | 270 | 270 | 320 | 310 | 320 | 7622500
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 455856
61 | Narshingdi 22 MW PP (Doreen) | 22 | [7 empty] | 10 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 22 | 22 | 22 | 22 | 22 |  | 0 | 244260
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [11 empty] | 20 |  |  |  | 22 | 22 | 22 | 224640
63 | Impoprt (Tripura) | 90 | 84 | 84 | 80 | 82 | 84 | 82 | 84 | 86 | 88 | 96 | 92 | 100 | 106 | 104 | 88 | 84 | 116 |  | 124 | 124 | 120 | 120 | 112 | 72 | 94 | 2313600
64 | Malancha, Ctg. EPZ (United) | 40 | 16 | 5 | 5 | 5 | 13 | 10 | 10 | 2 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 8 | 13 |  | 22 | 28 | 28 | 30 | 33 | 38 | 38 | 442080
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 6 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 442872
66 | Feni 11 MW PP (Doreen) | 8 | [9 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 |  |  | 91980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  | 0 | 638800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 |  | 13 | 488240
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 28 | 31 | 16 |  | 31 | 31 | 31 | 31 | 0 | 24 | 10 | 635040
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 |  |  | 22 | 592200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 16 |  | 32 | 33 | 33 | 33 | 0 | 8 | 25 | 661300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [25 empty] | 0 | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | [7 empty] | 4 | 16 | 16 | 20 | 85 | 96 | 95 | 94 | 95 | 96 |  | 96 | 96 | 96 | 94 | 16 |  | 0 | 1026048
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [19 empty] | 48 | 48 | 48 |  |  |  | 0 | 117600
80 | Jamalpur 95 MW PP(Powerpac) | 64 | 8 | 8 | 8 | 8 | 8 | 22 | 82 | 90 | 64 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 76 |  | 91 | 91 | 91 | 58 | 24 | 8 | 0 | 1156800
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 17 | [7 empty] | 0 | 19764
| Kaptai 7 MW Solar PP | [6 empty] | 0.3 | 1.7 | 2.9 | 3.9 | 4.7 | 5.6 | 1.2 | 3.9 | 3.1 | 1.8 | 0.619 | [9 empty] | 25800
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 1 |  | 67 | 50 | 15 |  |  |  | 0 | 146400
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 5 |  | 33 | [5 empty] | 0 | 48252
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 120 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 130 | 130 | 125 | 130 | 130 | 3293935
87 | Meghnaghat 100 MW(IEL) | 7 | [11 empty] | 61 | 78 | 51 | 75 | 35 | 25 |  | 84 | 100 | 100 | 75 | 7 |  | 0 | 645120
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 5 | 5 | 5 | 10 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1033128
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 5 | 5 | 5 | 5 | 35 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 1026344
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [7 empty] | 7 | 16 | 16 | 16 | 64 | 65 | 70 | 80 | 24 | 32 |  | 85 | 85 | 85 | 32 |  |  | 0 | 670896
95 | Patenga 50MW PP (Baraka) | 5 | [11 empty] | 4 | 18 | 6 | 24 | 25 | 19 |  | 46 | 50 | 50 | 50 | 23 |  | 0 | 279360
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 7 |  | 44 | 87 | 96 | 45 |  |  | 0 | 201600
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 1 |  | 10 | 40 |  |  |  |  | 0 | 43392
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 4 |  | 50 | 55 | 30 |  |  |  | 0 | 103036
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 17 |  |  | 0 | 302496
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 110 | 163 | 163 | 130 | 163 | 163 | 130 | 163 | 130 | 100 | 100 |  | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 3453136
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.6 | 1.2 | 1.8 | 1.8 | 1.7 | 2 | 1.3 | 1.4 | 0.7 | 0.1 | [9 empty] | 12500
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | [5 empty] | 17 | 40 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 889200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [17 empty] | 7 |  | 40 | [5 empty] | 0 | 62400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 2 | 15 | 15 | 16 | 34 | 31 | 55 | 80 | 34 | 70 | 35 | 35 |  | 101 | 149 | 149 | 123 | 30 |  | 0 | 871200
115 | Juldah 100 MW PP Unit-3 (Acorn) | [12 empty] | 36 | 10 | 45 | 30 | 10 | 10 |  | 100 | 100 | 100 | 50 |  |  | 0 | 407040
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 5 |  | 30 | 50 | 10 |  |  |  | 0 | 83636
118 | Bibiyana-III 400 MW CCPP | 234 | 234 | 233 | 234 | 234 | 233 | 232 | 233 | 233 | 234 | 234 | 236 | 236 | 235 | 234 | 235 | 235 | 233 |  | 235 | 235 | 235 | 235 | 233 | 234 | 232 | 5618000
| Jamalpur 115 MW PP (United) | [7 empty] | 36 | 91 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 75 | 80 |  | 115 | 85 | 55 | 7 |  |  | 0 | 1352400
| Anwara 300 MW PP (United) | 31 | [6 empty] | 33 | 66 | 120 | 106 | 191 | 231 | 143 | 202 | 214 | 180 | 180 |  | 232 | 196 | 196 | 166 | 161 | 51 | 51 | 2536691
120 | Eastern Zone Total | 5310 | 4912 | 4611 | 4487 | 4550 | 4817 | 4962.2 | 5319.8 | 5584.6 | 5607.7 | 5544.8 | 5836.1 | 5984.1 | 5759.7 | 5860.6 | 5735 | 5479.519 | 5681 |  | 6598 | 6535 | 6360 | 5850 | 5254 | 5033 | 5192 | 131817870
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 19 |  | 66 | 74 | 76 | 80 | 60 |  | 0 | 292800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 48 | 48 | 48 | 48 | 32 |  | 0 | 186912
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 13 | 13 | 12 | 11 | 13 | 13 | 13 | 13 | 13 | 54 | 52 | 53 | 53 | 54 | 53 | 52 | 52 |  | 95 | 96 | 70 | 18 | 18 | 96 | 95 | 921431
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 134 | 134 | 133 | 134 | 133 | 134 |  | 121 | 113 | 136 | 122 | 128 | 120 | 120 | 3119000
140 | Bhola 33 MW PP (Venture) | 14 | 16 | 14 | 15 | 15 | 15 | 14 | 13 | 12 | 7 | 6 | 7 | 7 | 8 | 10 | 12 | 13 | 16 |  | 21 | 21 | 21 | 22 | 21 | 20 | 19 | 331100
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 32 | 32 | 15 |  |  |  | 0 | 69120
146 | Bheramara HVDC | 198 | 199 | 198 | 199 | 198 | 198 | 608 | 641 | 640 | 640 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 641 |  | 885 | 886 | 886 | 886 | 887 | 788 | 433 | 13529455
147 | Bheramara 410 MW CCPP | 310 | 320 | 330 | 330 | 330 | 380 | 380 | 370 | 350 | 325 | 310 | 300 | 285 | 270 | 270 | 265 | 265 | 260 |  | 260 | 260 | 260 | 260 | 275 | 260 | 285 | 7437312
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 92 | 92 | 91 | 90 | 90 | 89 | 90 | 90 | 90 | 89 | 90 | 90 | 90 | 88 | 89 | 89 | 89 | 90 |  | 88 | 88 | 89 | 90 | 89 | 89 | 89 | 2137745
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 281 | 280 | 6348900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 195 | 220 | 214 | 214 | 214 | 180 | 190 | 190 | 190 | 190 |  | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 4624627
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 384 | 400 | 386 | 370 | 372 | 434 | 433 | 426 | 414 | 387 | 399 | 421 | 415 | 412 | 416 | 413 | 435 | 423 |  | 379 | 370 | 435 | 389 | 397 | 395 | 396 | 9798418
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 5 | 5 | 5 | 5 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 14 | 14 |  | 357840
163 | Bogura 20 MW PP (Energyprima) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 172332
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 5 | 5 | 5 | 5 | 163458
165 | Amnura 50 MW PP(Sinha) | [6 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 12 | 32 |  | 50 | 50 | 34 | 34 | 34 |  |  | 527780
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 14 |  | 17 | [6 empty] | 24540
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 2 |  | 35 | [5 empty] | 0 | 46176
172 | Confidence Power Bogura Unit-1 113 MW | 50 | [6 empty] | 50 | 109 | 109 | 109 | 109 | 90 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 50 | 50 |  | 0 | 1603776
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 9 | 40 | 40 | 40 | 35 | 50 | 45 | 35 | 35 |  |  |  | 32 | 74 | 74 | 49 |  |  | 0 | 508800
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 0.8 | 3.6 |  | 6.2 | 6.5 | 6.5 | 6.1 | 4.6 | 3.4 | 1.4 | 0.1 | [8 empty] | 37887
178
178