## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-06 | Friday
|  | Date (day): | 2020-03-06 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11635.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14491 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-05 | 2020-03-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 150 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 320 | 325 | 325
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 342 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 357 | 314 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 370 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 86 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 120 | 120 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 55 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 40 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 50 | 100 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 30 | 90 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 30 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 37 | 139 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2057 | 2502 | 3582 | 4234 | 991 | 660
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 8 | 48 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 66 | 67 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 204 | 210 | 210
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 104 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 26 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 20 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 30 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 40 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.8 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 193 | 215 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 784.6 | 957 | 1504 | 1641 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 150 | 150 | 150 | 49
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 221 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 295 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 155 | 155 | 0 | 0 |  |  | Under Maint.
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 46 | 36 | 46 | 35 |  | Gas shortage
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 83 | 195 | 195 | 0
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 80 | 90 | 90 |  | 73 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 116 | 102 | 113
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 22 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1119 | 1359 | 1515 | 2200 | 403 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 156 | 210 | 210 | -8
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 49 | 91 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 2 | 40 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 54 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 274.1 | 424 | 543.6 | 642 | -8 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 89 | 86 | 85 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 32 | 32 | 22 | 22 |  | 58 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 126 | 125 | 150 | 150 |  | 180 | Gas shortage.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 51 | 51 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 80 | 82
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 229 | 229 | 220 | 220
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 234 | 234 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1439 | 1440 | 1522 | 1527 | 0 | 403
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 642 | 888 | 312 | 665
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 380 | 320 | 330 | 330 | 110 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1054 | 1323 | 927 | 1830 | 110 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 9 | 21 | 22 |  | 11 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 137 | 124 | 130 | 135 |  | 59 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 73 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 240 | 222 | 310 | 392 | 0 | 70
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 24 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 170 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 429 | 360 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 38
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 10 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 68 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 27 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 109 | 108 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 758 | 812 | 1238 | 1505 | 611 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 90 | 90 | 93 | 93
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 72 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 411.8 | 442 | 494 | 520 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 8137.5 | 9481 | 11635.6 | 14491 | 2517 | 1399
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7800.1899 | 9088 | 11153.289 | 13890.3289
A. |  | 2020-03-05 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 9481 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5894 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9481 | MW
3 | Day peak Generation : |  |  | 8137.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9088 | MW
4 | Evening peak Generation : |  |  | 9481 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 184.1494 | MKWHr | By Solar | 0.18809 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 140.2911 | MKWHr |  | By Oil: | 17.8798 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.1258 | MKWHr |  | By Hydro: | 1.5465 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2517 | MW | Dhaka | 3487 | 3487 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1399 | MW | Chittagong | 1013 | 1013 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3916 | MW | Khulna | 1009 | 1009 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1140.89 | MMCFD |  |  | Rajshahi | 942 | 942 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 131197687.39 | ii) Oil : | Taka | 132326926.59 | Comilla | 796 | 796 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 38131391.34 | Total | Taka | 301656005.32 | Mymensingh | 767 | 767 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.602 | MKWHr. | Sylhet | 345 | 345 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -58 | MW (E to W) at | 19:00 | hrs | Barisal | 85 | 85 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -330 | MW at | 1:00 | hrs | Rangpur | 644 | 644 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.1° C |  |  | Total | 9088 | 9088 |  | 0
B. |  | 2020-03-06 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 29.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14491 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 5691 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 170.9224 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6470 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.6749 | MKWHr. | ii) HVDC Flow at Peak Time |  | 888 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4432 | MKWHr. | iii) Maximum HVDC Flow : |  | 890 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.09 |  | (b) Today: | 88.89 |  | (c) Rule Curve: |  | 92.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-03-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 0 | 167 | 0 | 325 | 0 | 0 | 341 | 363 |  | 0 | 400 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 10 | 33 | 25 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 80 | 0 | 250 | 265 | 182 | 8 | 82 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 0 | 12 | 94 | 148 | 0 | 22 | 0 | 86 | 32 | 5 | 5 | 163 | 126 | 65 | 50 | 0 | 159 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 |  | 210 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4935 | 1593 | 6528 | 3778 | 210 | 1822 | 189 | 369 | 66 | 0 | 94 | 0 | 0 | 89.11
2:00 | 37 | 0 | 96 | 0 | 283 | 0 | 0 | 335 | 337 |  | 0 | 370 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 30 | 16 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 80 | 0 | 265 | 275 | 194 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 88 | 149 | 0 | 0 | 0 | 86 | 32 | 5 | 5 | 163 | 126 | 54 | 5 | 0 | 157 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 210 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 89 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4528 | 1567 | 6095 | 3578 | 210 | 1654 | 130 | 369 | 66 | 0 | 88 | 0 | 0 | 89.1
3:00 | 37 | 0 | 94 | 0 | 275 | 0 | 0 | 337 | 307 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 80 | 0 | 255 | 265 | 183 | 8 | 81 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 161 | 0 | 0 | 0 | 86 | 32 | 5 | 5 | 163 | 126 | 54 | 5 | 0 | 157 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 210 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4417 | 1530 | 5947 | 3564 | 210 | 1531 | 120 | 370 | 66 | 0 | 86 | 0 | 0 | 89.1
4:00 | 37 | 0 | 100 | 0 | 295 | 0 | 0 | 286 | 277 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 205 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 80 | 0 | 270 | 285 | 177 | 8 | 91 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 84 | 161 | 0 | 0 | 0 | 86 | 32 | 5 | 5 | 130 | 126 | 45 | 5 | 0 | 158 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 210 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4367 | 1575 | 5942 | 3599 | 210 | 1493 | 120 | 370 | 66 | 0 | 84 | 0 | 0 | 89.1
5:00 | 0 | 0 | 100 | 0 | 295 | 0 | 0 | 280 | 277 |  | 0 | 330 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 25 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 80 | 0 | 255 | 265 | 163 | 8 | 88 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 82 | 161 | 0 | 0 | 0 | 87 | 32 | 5 | 5 | 130 | 126 | 45 | 5 | 0 | 156 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 209 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 90 | 0 | 279 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4288 | 1606 | 5894 | 3532 | 209 | 1516 | 120 | 369 | 66 | 0 | 82 | 0 | 0 | 89.09
6:00 | 0 | 0 | 100 | 0 | 295 | 0 | 0 | 333 | 276 |  | 0 | 330 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 28 | 25 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 218 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 80 | 0 | 265 | 295 | 202 | 8 | 90 | 15 | 5 | 0 | 9 | 0 | 0 | 0 | 3 | 0 | 0 | 12 | 80 | 161 | 2 | 22 | 0 | 86 | 32 | 17 | 8 | 130 | 126 | 56 | 81 | 0 | 158 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 206 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 5 | 89 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4602 | 1554 | 6156 | 3667 | 206 | 1626 | 142 | 369 | 66 | 0 | 80 | 0 | 0 | 89.09
7:00 | 0 | 0 | 100 | 0 | 275 | 0 | 0 | 339 | 275 |  | 0 | 330 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 10 | 25 | 28 | 25 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 206 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 36 | 0 | 80 | 0 | 265 | 270 | 190 | 8 | 91 | 39 | 5 | 0 | 44 | 0 | 0 | 0 | 19 | 5 | 0 | 12 | 82 | 161 | 48 | 22 | 0.1 | 87 | 32 | 48 | 47 | 130 | 126 | 66 | 81 | 0 | 157 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.64 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0.5 | 10 | 0 | 0 | 0 | 0 |  | 642 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 5 | 0 |  | 4845.24 | 2056.4 | 6901.64 | 3725 | 642 | 1761 | 252 | 370 | 67 | 0 | 82 | 2.64 | 0 | 89.08
8:00 | 0 | 0 | 100 | 0 | 276 | 0 | 0 | 338 | 366 |  | 0 | 360 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 0 | 80 | 0 | 265 | 270 | 190 | 8 | 91 | 39 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 0 | 14 | 80 | 162 | 95 | 22 | 0.5 | 86 | 32 | 45 | 51 | 130 | 125 | 65 | 81 | 0 | 158 | 20 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6.4 | 0 | 0 | 0 | 233 | 16 | 0 | 0 | 1.8 | 50 | 0 | 0 | 0 | 0 |  | 642 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 12 | 0 | 1.4 | 70 | 0 |  | 5165.7 | 2252.4 | 7418.1 | 3874 | 642 | 1893 | 482 | 370 | 67 | 0 | 80 | 10.1 | 0 | 89.08
9:00 | 0 | 0 | 198 | 0 | 275 | 0 | 0 | 336 | 365 |  | 0 | 360 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 25 | 8 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 80 | 0 | 265 | 265 | 225 | 8 | 81 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 0 | 15 | 86 | 160 | 82 | 22 | 1.4 | 86 | 32 | 22 | 51 | 163 | 125 | 65 | 81 | 0 | 221 | 20 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 11.5 | 0 | 0 | 0 | 235 | 29 | 0 | 0 | 3 | 86 | 0 | 0 | 0 | 0 |  | 642 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 89 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 39 | 0 | 3.5 | 109 | 0 |  | 5401.9 | 2285.5 | 7687.4 | 4054 | 642 | 1853 | 597 | 369 | 67 | 0 | 86 | 19.4 | 0 | 89.07
10:00 | 0 | 0 | 200 | 0 | 300 | 0 | 0 | 346 | 360 |  | 0 | 360 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 29 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 207 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 80 | 0 | 300 | 160 | 202 | 8 | 90 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 0 | 15 | 94 | 159 | 49 | 22 | 2 | 89 | 32 | 22 | 51 | 130 | 132 | 63 | 78 | 0 | 229 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 0 | 0 | 0 | 232 | 32 | 0 | 0 | 3.2 | 121 | 0 | 0 | 0 | 0 |  | 642 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 433 | 0 | 0 | 0 | 0 | 35 | 0 | 4.9 | 109 | 0 |  | 5391.2 | 2333.9 | 7725.1 | 4048 | 642 | 1868 | 611 | 370 | 66 | 0 | 94 | 26.1 | 0 | 89.07
11:00 | 0 | 0 | 200 | 0 | 303 | 0 | 0 | 359 | 359 |  | 0 | 360 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 216 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1 | 0 | 100 | 0 | 310 | 160 | 201 | 26 | 90 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 25 | 20 | 100 | 145 | 49 | 22 | 1.4 | 89 | 32 | 22 | 51 | 130 | 126 | 62 | 81 | 0 | 229 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 18.5 | 0 | 0 | 0 | 232 | 45 | 0 | 0 | 4.7 | 123 | 0 | 0 | 0 | 0 |  | 642 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 90 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 36 | 0 | 6.2 | 109 | 0 |  | 5544.6 | 2344.2 | 7888.8 | 4130 | 642 | 1900 | 650 | 370 | 66 | 0 | 100 | 30.8 | 0 | 89.06
12:00 | 0 | 0 | 200 | 0 | 300 | 0 | 0 | 368 | 357 |  | 0 | 390 | 120 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 2 | 0 | 100 | 0 | 280 | 155 | 187 | 26 | 91 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 104 | 145 | 49 | 22 | 2.1 | 89 | 32 | 22 | 51 | 130 | 126 | 61 | 81 | 0 | 229 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 2 | 0 | 37 | 18.8 | 20 | 0 | 0 | 234 | 54 | 0 | 0 | 4.8 | 193 | 0 | 0 | 0 | 0 |  | 642 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 429 | 0 | 0 | 0 | 0 | 35 | 0 | 6.8 | 109 | 0 |  | 5673.7 | 2463.8 | 8137.5 | 4089 | 642 | 2003 | 831 | 370 | 66 | 0 | 104 | 32.5 | 0 | 89.06
13:00 | 0 | 0 | 200 | 0 | 340 | 0 | 0 | 351 | 358 |  | 0 | 390 | 130 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 19 | 8 | 0 | 100 | 0 | 335 | 155 | 192 | 26 | 91 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 25 | 21 | 100 | 130 | 49 | 22 | 1.2 | 89 | 32 | 25 | 51 | 163 | 127 | 60 | 81 | 0 | 229 | 19 | 0 | 9 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 60 | 0 | 10 | 0 | 0 | 233 | 115 | 0 | 0 | 4.6 | 160 | 0 | 0 | 0 | 0 |  | 642 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 195 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 30 | 0 | 6.8 | 70 | 0 |  | 5904.8 | 2423.8 | 8328.6 | 4162 | 642 | 2025 | 951 | 370 | 66 | 0 | 100 | 12.6 | 0 | 89.05
14:00 | 0 | 0 | 200 | 0 | 300 | 0 | 0 | 350 | 333 |  | 0 | 450 | 125 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 207 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 2 | 0 | 100 | 0 | 330 | 155 | 195 | 26 | 91 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 5 | 25 | 21 | 100 | 132 | 49 | 20 | 2.1 | 89 | 32 | 25 | 51 | 130 | 126 | 60 | 81 | 0 | 227 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 35 | 10.7 | 10 | 0 | 0 | 233 | 115 | 0 | 0 | 3.8 | 160 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 0 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 5763.6 | 2168 | 7931.6 | 4008 | 642 | 1990 | 829 | 280 | 66 | 0 | 100 | 16.6 | 0 | 89.05
15:00 | 0 | 0 | 200 | 0 | 350 | 0 | 0 | 356 | 335 |  | 0 | 450 | 120 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 206 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 2 | 0 | 150 | 0 | 290 | 155 | 183 | 55 | 90 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 20 | 5 | 25 | 21 | 98 | 129 | 49 | 22 | 1.4 | 85 | 32 | 24 | 51 | 130 | 126 | 61 | 81 | 0 | 228 | 19 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 9 | 10 | 0 | 0 | 230 | 115 | 0 | 0 | 3 | 160 | 0 | 0 | 0 | 0 |  | 642 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 5836.4 | 2330 | 8166.4 | 4114 | 642 | 2058 | 804 | 370 | 67 | 0 | 98 | 13.4 | 0 | 89.04
16:00 | 0 | 0 | 150 | 0 | 350 | 0 | 0 | 340 | 314 |  | 0 | 400 | 125 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 215 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 2 | 0 | 150 | 0 | 290 | 155 | 182 | 55 | 91 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 25 | 21 | 100 | 131 | 49 | 22 | 0.6 | 85 | 32 | 22 | 10 | 130 | 129 | 61 | 81 | 0 | 226 | 19 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 40 | 4.2 | 10 | 0 | 0 | 234 | 115 | 0 | 0 | 1.5 | 106 | 0 | 0 | 0 | 0 |  | 642 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 6 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 35 | 0 |  | 5617.3 | 2257 | 7874.3 | 4028 | 642 | 1921 | 730 | 370 | 68 | 6 | 100 | 9.3 | 0 | 89.03
17:00 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 353 | 314 |  | 0 | 370 | 120 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 0 | 1 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 10 | 0 | 150 | 0 | 265 | 160 | 164 | 55 | 84 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 25 | 21 | 96 | 132 | 49 | 22 | 0.2 | 85 | 32 | 22 | 10 | 130 | 127 | 61 | 30 | 0 | 228 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 2 | 0 | 0 | 7 | 0 | 47 | 1.2 | 10 | 0 | 2 | 234 | 115 | 0 | 0 | 0.6 | 106 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 6 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 35 | 0 | 1.2 | 35 | 0 |  | 5488 | 2220.2 | 7708.2 | 3948 | 642 | 1802 | 772 | 371 | 68 | 6 | 96 | 3.2 | 0 | 89.02
18:00 | 0 | 0 | 150 | 0 | 321 | 0 | 0 | 353 | 284 |  | 0 | 340 | 120 | 18 | 12 | 18 | 0 | 0 | 0 | 0 | 60 | 58 | 0 | 16 | 0 | 0 | 3 | 53 | 17 | 0 | 22 | 25 | 24 | 25 | 33 | 0 | 0 | 28 | 40 | 110 | 0 | 0 | 205 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 15 | 26 | 19 | 11 | 0 | 150 | 0 | 270 | 155 | 175 | 55 | 80 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 5 | 25 | 21 | 116 | 145 | 56 | 20 | 0 | 86 | 32 | 25 | 15 | 130 | 127 | 63 | 30 | 0 | 229 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 17 | 0 | 0 | 10 | 0 | 50 | 0 | 27 | 0 | 8 | 234 | 115 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 7 | 62 | 0 | 0.1 | 50 | 0 |  | 5589 | 2395.1 | 7984.1 | 3930 | 642 | 1732 | 1093 | 371 | 68 | 32 | 116 | 0.1 | 0 | 89.01
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 342 | 314 |  | 0 | 370 | 120 | 86 | 55 | 55 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 40 | 0 | 0 | 30 | 53 | 55 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 40 | 48 | 19 | 24 | 0 | 150 | 0 | 295 | 155 | 221 | 83 | 80 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 22 | 116 | 156 | 91 | 22 | 0 | 86 | 32 | 53 | 51 | 130 | 125 | 65 | 81 | 0 | 229 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 40 | 0 | 139 | 0 | 100 | 0 | 80 | 234 | 115 | 0 | 26 | 0 | 215 | 0 | 0 | 0 | 0 |  | 888 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 360 | 0 | 0 | 27 | 0 | 72 | 0 | 0 | 108 | 0 |  | 6682 | 2799 | 9481 | 4026 | 888 | 1933 | 2013 | 370 | 67 | 68 | 116 | 0 | 0 | 89
19:30 | 0 | 0 | 180 | 0 | 320 | 0 | 0 | 338 | 314 |  | 0 | 370 | 125 | 100 | 55 | 55 | 0 | 0 | 0 | 0 | 98 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 50 | 50 | 19 | 24 | 0 | 150 | 0 | 295 | 155 | 222 | 83 | 80 | 46 | 30 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 118 | 158 | 91 | 22 | 0 | 85 | 32 | 53 | 51 | 130 | 126 | 65 | 81 | 0 | 229 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 0 | 80 | 234 | 75 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 888 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 70 | 0 | 0 | 109 | 0 |  | 6641 | 2809 | 9450 | 4069 | 888 | 1970 | 1900 | 370 | 67 | 68 | 118 | 0 | 0 | 0
20:00 | 0 | 0 | 180 | 0 | 320 | 0 | 0 | 341 | 316 |  | 0 | 400 | 130 | 100 | 55 | 30 | 0 | 0 | 0 | 0 | 98 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 50 | 50 | 19 | 24 | 0 | 150 | 0 | 305 | 155 | 220 | 83 | 90 | 46 | 40 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 122 | 157 | 91 | 22 | 0 | 85 | 32 | 53 | 51 | 130 | 125 | 63 | 81 | 0 | 230 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 0 | 30 | 234 | 64 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 889 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 89 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 108 | 0 |  | 6575 | 2745 | 9320 | 4043 | 889 | 2043 | 1753 | 369 | 67 | 34 | 122 | 0 | 0 | 88.99
21:00 | 0 | 0 | 180 | 0 | 320 | 0 | 0 | 353 | 330 |  | 0 | 400 | 130 | 100 | 15 | 15 | 0 | 0 | 0 | 0 | 98 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 17 | 0 | 22 | 25 | 31 | 28 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 165 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 12 | 50 | 19 | 32 | 0 | 150 | 0 | 295 | 195 | 221 | 83 | 85 | 46 | 48 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 118 | 157 | 95 | 20 | 0 | 85 | 32 | 53 | 51 | 130 | 126 | 63 | 81 | 0 | 230 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 50 | 0 | 0 | 234 | 64 | 0 | 34 | 0 | 215 | 0 | 0 | 0 | 0 |  | 889 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 91 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 0 |  | 6445 | 2747 | 9192 | 4084 | 889 | 2087 | 1542 | 371 | 67 | 34 | 118 | 0 | 0 | 88.98
22:00 | 0 | 0 | 57 | 0 | 325 | 0 | 0 | 346 | 360 |  | 0 | 450 | 130 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 65 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 36 | 0 | 150 | 0 | 325 | 0 | 220 | 102 | 91 | 46 | 47 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 114 | 158 | 95 | 20 | 0 | 85 | 32 | 50 | 51 | 130 | 124 | 63 | 81 | 0 | 230 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 232 | 32 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 0 |  | 890 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 175 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5891 | 2612 | 8503 | 3783 | 890 | 2223 | 1056 | 370 | 67 | 0 | 114 | 0 | 0 | 88.97
23:00 | 0 | 0 | 202 | 0 | 325 | 0 | 0 | 340 | 364 |  | 0 | 450 | 120 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 10 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 164 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 315 | 0 | 222 | 185 | 91 | 46 | 49 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 108 | 159 | 95 | 22 | 0 | 88 | 32 | 51 | 51 | 163 | 126 | 63 | 81 | 0 | 230 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 |  | 789 | 0 | 285 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 93 | 0 | 281 | 0 | 0 | 200 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5879 | 2437 | 8316 | 3888 | 789 | 2322 | 768 | 374 | 67 | 0 | 108 | 0 | 0 | 88.96
24:00 | 0 | 0 | 200 | 0 | 329 | 0 | 0 | 356 | 363 |  | 0 | 450 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 168 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 0 | 150 | 0 | 315 | 0 | 222 | 192 | 87 | 46 | 49 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 22 | 92 | 157 | 95 | 22 | 0 | 88 | 32 | 51 | 47 | 163 | 126 | 64 | 81 | 0 | 230 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 |  | 398 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 92 | 0 | 280 | 0 | 0 | 205 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5781 | 2079 | 7860 | 3937 | 398 | 2375 | 619 | 372 | 67 | 0 | 92 | 0 | 0 | 88.95
KWH | 158000 | 0 | 3661000 | 0 | 7463618 | 0 | 0 | 8314730 | 7839000 |  | 0 | 9011250 | 2990167 | 576000 | 156600 | 145829 | 0 | 0 | 0 | 0 | 1106880 | 642096 | 0 | 68859 | 0 | 0 | 92160 | 966600 | 300226 | 0 | 290448 | 600000 | 596160 | 723300 | 633700 | 0 | 0 | 574500 | 972000 | 2600000 | 0 | 0 | 4736833 | 0 | 2854980 | 0 |  | 0 | 0 | 0 | 0 | 127680 | 331680 | 354672 | 538080 | 0 | 2661755 | 0 | 7111800 | 4688000 | 4755000 | 1070545 | 2095990 | 803376 | 348000 | 0 | 1046644 | 0 | 0 | 0 | 375660 | 112500 | 383500 | 469840 | 2443200 | 3498880 | 1252800 | 395964 | 12250 | 2053000 | 776400 | 717000 | 930600 | 3566045 | 2878000 | 1432800 | 1509120 | 0 | 4959120 | 301000 | 0 | 181620 | 7627550 | 374088 | 198021 | 0 | 72764 | 0 | 0 | 110400 | 0 | 1025280 | 111510 | 350400 | 0 | 153890 | 5595000 | 1242000 | 0 | 112909 | 30000 | 2639564 | 0 | 0 | 0 | 0 |  | 13674909 | 0 | 8352576 | 0 | 582720 | 0 | 0 | 0 | 0 | 7680 | 0 | 2847000 | 326200 | 90336 | 0 | 0 | 0 | 0 | 0 | 166568 | 547660 | 0 | 0 | 0 | 0 | 309840 | 184464 | 0 | 2147782 | 0 | 5978000 | 0 | 0 | 4282964 | 0 | 0 | 0 | 1052204 | 0 | 0 | 0 | 9643273 | 0 | 0 | 51936 | 7920 | 435840 | 0 | 34326 | 1524384 | 0 |  | 131900833 | 52248582 | 184149415 | 94389675 | 13674909 | 45901435 | 17705580 | 8125782 | 1546500 | 174248 | 2443200 | 188086 | 0
Fuel Cost | 176960 | 0 | 3917270 | 0 | 5523077.32 | 0 | 0 | 5986605.6 | 5957640 |  | 0 | 7209000 | 2691150.3 | 5875200 | 1695978 | 1496205.54 | 0 | 0 | 0 | 0 | 12286368 | 6523695.36 | 0 | 721642.32 | 0 | 0 | 862617.6 | 9269694 | 2864156.04 | 0 | 217836 | 450000 | 0 | 0 | 0 | 0 | 0 | 149370 | 252720 | 3978000 | 0 | 0 | 4973674.65 | 0 | 3625824.6 | 0 |  | 0 | 0 | 0 | 0 | 1214236.8 | 3104524.8 | 326298.24 | 1495862.4 | 0 | 2794842.75 | 0 | 5262732 | 3937920 | 4374600 | 1049134.1 | 2787666.7 | 658768.32 | 358440 | 0 | 1496700.92 | 0 | 0 | 0 | 383173.2 | 84375 | 724815 | 352380 | 16858080 | 2869081.6 | 11914128 | 403883.28 | 200900 | 2792080 | 1055904 | 975120 | 1163250 | 4421895.8 | 2647760 | 2134872 | 2656051.2 | 0 | 7537862.4 | 478590 | 0 | 426807 | 5415560.5 | 280566 | 150495.96 | 0 | 761839.08 | 0 | 0 | 1062048 | 0 | 10345075.2 | 1286825.4 | 3265728 | 0 | 1441949.3 | 5259300 | 10892340 | 0 | 1066990.05 | 0 | 24336780.08 | 0 | 0 | 0 | 0 |  | 36922254.3 | 0 | 6515009.28 | 0 | 5617420.8 | 0 | 0 | 0 | 0 | 100608 | 0 | 2277600 | 505610 | 970208.64 | 0 | 0 | 0 | 0 | 0 | 1649023.2 | 5679234.2 | 0 | 0 | 0 | 0 | 340824 | 304365.6 | 0 | 13681371.34 | 0 | 24450020 | 0 | 0 | 3769008.32 | 0 | 0 | 0 | 1673004.36 | 0 | 0 | 0 | 7039589.29 | 0 | 0 | 476772.48 | 70567.2 | 4070745.6 | 0 | 0 | 0 | 0 |  | 241212918.41 | 116113236.61 | 357326155.02 | 88708832.22 | 36922254.3 | 42488855.17 | 130577295.39 | 38131391.34 | 402090 | 1749631.2 | 16858080 | 1487725.4 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 300 | 0 | 0 | 368 | 357 |  | 0 | 390 | 120 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 32 | 25 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 19 | 2 | 0 | 100 | 0 | 280 | 155 | 187 | 26 | 91 | 43 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 5 | 33 | 20 | 104 | 145 | 49 | 22 | 2.1 | 89 | 32 | 22 | 51 | 130 | 126 | 61 | 81 | 0 | 229 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 2 | 0 | 37 | 18.8 | 20 | 0 | 0 | 234 | 54 | 0 | 0 | 4.8 | 193 | 0 | 0 | 0 | 0 |  | 642 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 429 | 0 | 0 | 0 | 0 | 35 | 0 | 6.8 | 109 | 0 |  | 8137.5 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 342 | 314 | 0 | 0 | 370 | 120 | 86 | 55 | 55 | 0 | 0 | 0 | 0 | 90 | 102 | 0 | 40 | 0 | 0 | 30 | 53 | 55 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 48 | 19 | 24 | 0 | 150 | 0 | 295 | 155 | 221 | 83 | 80 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 22 | 116 | 156 | 91 | 22 | 0 | 86 | 32 | 53 | 51 | 130 | 125 | 65 | 81 | 0 | 229 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 45 | 0 | 0 | 40 | 0 | 139 | 0 | 100 | 0 | 80 | 234 | 115 | 0 | 26 | 0 | 215 | 0 | 0 | 0 | 0 |  | 888 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 68 | 50 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 360 | 0 | 0 | 27 | 0 | 72 | 0 | 0 | 108 | 0 |  | 9481 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 40 | 0 | 150 | 0 | 360 | 0 | 225 | 195 | 90 | 46 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 113 | 210 | 95 | 22 | 0 | 88 | 22 | 51 | 44 | 163 | 150 | 66 | 82 | 0 | 220 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 665 | 40 | 330 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 135 | 22 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 38 | 22 | 11 | 11 | 93 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 0 | 0 | 200 | 0 | 325 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 50 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 210 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 20 | 30 | 0 | 150 | 0 | 360 | 0 | 225 | 195 | 90 | 36 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 102 | 210 | 95 | 22 | 1.6 | 85 | 22 | 51 | 44 | 163 | 150 | 66 | 80 | 0 | 220 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 312 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 130 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 22 | 10 | 11 | 93 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 275 | 0 | 0 | 338 | 300 | 0 | 0 | 370 | 120 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 24 | 33 | 33 | 0 | 0 | 27 | 40 | 100 | 0 | 0 | 165 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 0 | 150 | 0 | 315 | 0 | 184 | 197 | 81 | 36 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 8 | 22 | 76 | 215 | 95 | 22 | 0.5 | 87 | 32 | 11 | 10 | 130 | 120 | 45 | 20 | 0 | 230 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 3 | 0 | 15 | 1 | 0 | 0 | 0 | 234 | 85 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 93 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0
199
| Minimum Generation |  | 5894 | 5:00
| Highest Generation |  | 9481 | 19:00
| Day Peak Generation |  | 8137.5 | 12:00
| Evening Peak Generation |  | 9481 | 19:00
| HVDC Max Flow |  | 890 | 22:00
| HVDC EvPeak Flow |  | 888 | 19:00
| Load factor L.F |  | 80.93%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8137.5 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 6470 | MW
Evening Peak Generation : |  | 9481 | MW Hour : | 19:00 | Available Max Generation : |  | 14491 | MW
E.P. Demand (at gen end) : |  | 9481 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8800 | MW
Maximum Generation : |  | 9481 | MW Hour : | 19:00 | Reserve(Generation end) |  | 5691 | MW
Total Gen. (MKWH) : |  | 184.1494 | System Load Factor : | 80.93% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -330 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-06
Actual : | 88.89 | Ft.(MSL) , | Rule curve : | 92.2 | Ft.( MSL )
Gas Consumed : | Total = | 1140.89 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 131197687.39
: |  | Coal : | 38131391.34 | Oil : | 132326926.59 | Total : | 301656005.32
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3151.0602 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1065.7574 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 953.8539 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 861.5219 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 778.7465 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 628.4063 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 358.8085 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 161.9945 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 484.6225 |  |  | 0 | 0%
Total | 0 |  | 8444.7716 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Bhola 225 MW STG
3) Ghorasal Unit-1,2,3 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Siddhirganj 210 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) B.Baria 132/33 kV T-2 transformer was under shut down from 09:45 to 22:46 for D/W.
b) Aminbazar-Savar 132 kV Ckt-2 was under shut down from 09:45 to 22:46 for D/W.
c) Chaddogram 132/33 kV T-2 transformer was under shut down from 09:10 to 11:13 for A/M. |  |  |  |  | About 15 MW power interruption occurred under Chaddogram S/S areas
from 09:10 to 11:13.
d) B.Baria 132/33 kV T-3 transformer was under shut down from 09:20 to 12:35 for D/W.
e) Mymensing-Kishorganj 132 kV Ckt-1 & 2 were under shut down from 08:02 to 16:05 for D/W.
f) Mymensing 132/33 kV T-3 transformer was under shut down from 09:09 to 12:11 for tan delta test.
g) Sikalbaha-Bakulia 132 kV Ckt-1 was under shut down from 10:28 to 18:01 due to CT ratio changing
at Sikalbaha end.
h) Shahjadpur-Sirajganj 132 kV Ckt-1 was under shut down from 15:06 to 15:58 for D/W.
i) Daudkandi-Sonargaon 132 kV Ckt-1 tripped at 16:04 showing Dist, ABC, Z1 relays at Daudkandi end
& GT, Dist, R,Y-phase, Z1 relays at Sonargaon end and was switched on at 16:17.
j) Barishal(N) 132/33 T1 & T2 transformers tripped at 18:40 showing E/F relay at 33 kV end and was
switched on at 18:57.
k) Ashuganj(S) 450 MW CCPP tripped at 21:38 due to flame failure.
l) Hasnabad 33 kV Full Bus tripped at 03:47(06/03/2020) due to Jinjira-1 33 kV feeder fault and was |  |  |  |  | About 104 MW power interruption occurred under Hasnabad S/S areas
switched on at 04:13(06/03/2020). |  |  |  |  | from 03:47(06/03/2020) to 04:13(06/03/2020).
m) Kishorganj 132 kV Full Bus along with outgoing 132 kV Ckt were shut down at 07:08(06/03/2020) |  |  |  |  | About 60 MW power interruption occurred under Kishoreganj S/S areas
for D/W. |  |  |  |  | from 07:08(06/03/2020) to till.
n) Rangpur 132 kV Full Bus along with outgoing 132 kV Ckt were shut down at 06:35(06/03/2020) |  |  |  |  | About 130 MW power interruption occurred under Rangpur S/S areas
for D/W. |  |  |  |  | from 06:35(06/03/2020) to till.
o) B.Baria 132/33 kV T-3 transformer was shut down at 07:09(06/03/2020) for D/W.
p) Ghorashal 230/132 kV T-1 transformer was shut down at 07:39(06/03/2020) for C/M.
q) Hasnabad 132/33 kV T-3 transformer was shut down at 07:12(06/03/2020) for C/M.
r) Ishwardi-Bheramara 132 kV Ckt-1 & 2 were shut down since 06:28(6/3/2020) for D/W.
s) Barishal-Patuakhali 132 kV Ckt was shut down since 07:16(06/03/2020) for D/W. |  |  |  |  | About 31 MW power interruption occurred under Barishal S/S areas
from 07:16(06/03/2020) to till.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 158000 | Unit-1,2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3661000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 7463618
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8314730 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 314 | 7839000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 9011250 | Gas shortage.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 86 | 576000 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 2990167 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 55 | 156600 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 145829
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 40 | 68859 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 290448
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1106880
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 642096
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 30 | 92160 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 966600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 300226
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Reserve
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1196160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 723300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 633700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 72764 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 139 | 1025280 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2502 | 47434667
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 111510
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 331680
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 67 | 1546500 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4736833
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2854980 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 26 | 112909 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 350400
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 354672
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 538080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 40 | 127680 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30000
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 215 | 2639564 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 957 | 16334808
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 2661755 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 221 | 4755000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7111800 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 155 | 4688000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 803376 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 348000 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 83 | 1070545 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1046644
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 153890 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2095990
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 375660
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 112500 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 116 | 2443200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 383500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 469840
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1359 | 28519700
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3498880 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 395964
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 91 | 1252800
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12250
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 110400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1242000
| Mymensingh Area Total |  |  |  | 637 | 424 | 6512294
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2053000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 32 | 776400
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3566045 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 125 | 2878000 | FGMO & GT-2 Under S/D.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 717000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 930600
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 198021
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1432800 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1509120
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 229 | 4959120
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 301000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 374088
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7627550 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 234 | 5595000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 181620
| Sylhet Area Total |  |  |  | 1949 | 1440 | 33099364
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 888 | 13674909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 582720
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 7680 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8352576 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 7920 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1323 | 22625805
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 90336 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 9 | 326200 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 124 | 2847000 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 73 | 1052204 | Gas shortage.
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | Machine problem
| Barisal Area Total |  |  |  | 462 | 222 | 4315740
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 547660
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4282964 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 360 | 9643273 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 309840 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 184464
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 68 | 166568 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 27 | 51936 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 108 | 1524384
| Rajshahi Area Total |  |  |  | 2183 | 812 | 16711089
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 90 | 2147782
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 5978000
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 72 | 435840 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34326
| Rangpur Area Total |  |  |  | 605 | 442 | 8595948
| Total |  |  |  | 19107 | 9481 | 184149415
| Eastern Grid Total |  |  |  | 13543 | 6682 | 131900833
| Western Grid Total |  |  |  | 5564 | 2799 | 52248582
| National Grid Total |  |  |  | 19107 | 9481 | 184149415
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-05
(a) ENTIRE EASTERN GRID : |  | 6408 | MW | (b) ENTIRE WESTERN GRID : |  | 2680 | MW
i) Dhaka area |  | 3487 | MW | i) Khulna area |  | 1009 | MW
ii) Chittagong area |  | 1013 | MW | ii) Rajshahi area |  | 942 | MW
iii) Comilla area |  | 796 | MW | iii) Barisal area |  | 85 | MW
iv) Mymensingh area |  | 767 | MW | iv) Rangpur area |  | 644 | MW
v) Sylhet area |  | 345 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9088 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 11:00 | Sherpur | 86 | 19:00 | Benapol | 32 | 19:00
Munsiganj | 88 | 21:00 | Srimongal | 26 | 18:00 | Jhenida | 80 | 19:00
Sonargaon | 71 | 20:00 | Shahjibazar | 84 | 18:30 | Bottail | 92 | 19:00
Shyampur | 184 | 11:00 | Fenchuganj | 28 | 18:30 | G.K Project | 39 | 19:00
Bhulta | 173 | 12:00 | Kulawara | 29 | 19:00 | Faridpur | 126 | 19:00
Madanganj | 62 | 16:00 | Sylhet | 109 | 18:30 | Madaripur | 57 | 22:00
Shitalakhya | 105 | 16:00 | Chatak | 18 | 18:30 | Sariatpur | 42 | 19:30
Rahim steel | 20 | 7:00 | Sunamganj | 29 | 19:30 | Gopalganj | 60 | 20:00
Matuail | 98 | 12:00 | Biani Bazar | 33 | 19:00 | Bagerhat | 58 | 20:00
Ghorasal | 64 | 19:00 | Comilla (S) | 122 | 20:00 | Mongla | 40 | 12:00
Narsingdi | 125 | 19:30 | Comilla(N) | 97 | 19:00 | Satkhira | 66 | 19:30
Haripur (SBU) | 96 | 12:00 | Chandpur | 75 | 20:00 | Gallamari | 38 | 13:00
Ullon | 57 | 14:00 | Feni | 81 | 19:00 | Magura | 37 | 19:30
Hasnabad | 144 | 21:00 | Chowmuhani | 110 | 18:30 | Norail | 28 | 18:30
Magbazar | 87 | 15:00 | Ashuganj | 44 | 19:00 | Chuadanga | 63 | 19:30
Maniknagar | 90 | 12:00 | Daudkandi | 100 | 22:00 | Barisal(N) | 26 | 21:00
Bangabhaban | 26 | 12:00 | B.Baria | 105 | 21:00 | Barisal (S) | 70 | 13:00
Narinda | 84 | 16:00 | Ramganj | 64 | 18:30 | Patuakhali | 60 | 23:00
Dhanmondi | 123 | 13:00 | Chaddagram | 30 | 13:00 | Bhandaria | 26 | 1:00
Lalbag | 54 | 13:00 | PHP | 2 | 8:00 | Borhan Uddin | 24 | 1:00
Madartek | 53 | 21:00 | Madunaghat | 53 | 18:30 | Ishurdi | 48 | 18:30
Dhaka University |  |  | Hathazari | 64 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Mirpur | 83 | 19:00 | Khulshi | 169 | 12:00 | Natore | 84 | 19:00
Kalyanpur | 75 | 19:00 | Halishahar | 106 | 19:30 | Bogra | 136 | 20:00
Gulshan | 103 | 13:00 | Baraulia | 148 | 12:00 | Noagaon | 90 | 8:00
Uttara | 55 | 18:30 | Sikalbaha | 20 | 18:00 | Rajshahi | 94 | 19:00
Uttara New | 30 | 15:00 | Dohazari | 66 | 18:30 | Rajshahi New | 8 | 19:00
Kamrangirchar | 90 | 19:00 | Cox'sbazar | 84 | 18:30 | C.Nawabganj | 58 | 19:30
Savar | 120 | 18:30 | Chandraghona | 24 | 18:30 | Amnura | 26 | 19:00
Bhasantec | 114 | 18:30 | Kaptai | 3.5 | 18:30 | Pabna | 82 | 19:30
Agargaon | 40 | 19:00 | A. Khaer Stl. | 23 | 9:00 | Shahjadpur | 77 | 19:00
Satmosjid | 72 | 19:00 | Bakulia | 86 | 18:30 | Serajganj | 73 | 20:00
Tongi | 124 | 15:00 | Julda | 19 | 18:00 | Niyamatpur | 66 | 8:00
Kabirpur | 208 | 15:00 | TK chemical | 10.9 | 19:00 | Joypurhat | 53 | 19:00
Basundhara | 120 | 15:00 | Modern Steel | 17 | 8:00 | Sherpur(Bogura) | 34 | 18:30
Manikganj | 72 | 19:30 | Shahmirpur | 26 | 18:30 | Mohastangor | 38 | 19:00
Joydevpur | 134 | 18:30 | Khagrachhari | 18 | 18:00 | Rangpur | 113 | 19:00
New Tongi | 89 | 18:30 | Matarbari | 23.5 | 18:30 | Lalmonirhat | 46 | 18:00
Korda | 191 | 15:00 | Baroiar Hat | 26 | 19:00 | Saidpur | 100 | 9:00
Dhamrai | 46 | 18:30 | Rangamati | 10 | 18:30 | Purbasadipur | 98 | 9:00
Rajendrapur | 70 | 18:30 | Abul Khair 230 | 130 | 13:00 | Thakurgaon | 65 | 19:00
Valuka | 82 | 16:00 | BSRM | 140 | 0:00 | Palashbari | 94 | 19:30
Tangail | 161 | 18:30 | GPH Ispat | 69 | 10:00 | Barapukuria | 45 | 19:00
Mymensing | 172 | 18:30 | Goalpara | 26 | 12:00 | Panchagar | 37 | 19:00
Kishorganj | 92 | 19:00 | Central s/s | 63 | 19:00 | Joldhaka | 24 | 19:00
Netrokona | 94 | 18:30 | Noapara | 47 | 19:00 | Kurigram | 46 | 0.8125
Jamalpur | 98 | 18:30 | Jessore | 86 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-05 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.083333 | 392 | 0.625 | Kaliakoir | 386 | 0.041667 | 369 | 0.625
Bheramara | 405 | 0.041667 | 389 | 0.79167 | Bhulta | 394 | 0.125 | 378 | 0.5
Ashuganj(N) | 400 | 0.125 | 385 | 0.5 | Gopalganj | 422 | 0.041667 | 381 | 0.91667
Payra | 425 | 0.20833 | 384 | 0.91667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 230 | 0.33333 | Hathazari | 221 | 0.25 | 216 | 0.45833
Ishurdi | 240 | 0.125 | 228 | 0.83333 | Megnaghat | 234 | 0.041667 | 222 | 0.625
Ashuganj | 242 | 0.041667 | 234 | 0.91667 | Fenchuganj | 242 | 0.041667 | 237 | 0.5
Serajganj | 238 | 0.83333 | 227 | 0.33333 | Siddhirganj | 234 | 0.083333 | 224 | 0.45833
Baghabari | 245 | 0.041667 | 238 | 0.33333 | Maniknagar | 232 | 0.083333 | 222 | 0.45833
Barapukuria | 237 | 0.041667 | 230 | 0.33333 | Old Airport | 233 | 0.125 | 219 | 0.625
Bogra | 226 | 0.041667 | 218 | 0.33333 | Barisal | 250 | 0.75 | 238 | 0.91667
Khulna South | 239 | 0.16667 | 222 | 0.91667 | AKSML | 221 | 0.125 | 214 | 0.45833
Rampura | 231 | 0.041667 | 223 | 0.41667 | BSRM | 224 | 0.125 | 218 | 0.41667
Haripur | 231 | 0.20833 | 221 | 0.5 | Bibiyana | 240 | 0.125 | 233 | 0.45833
Hasnabad | 230 | 0.041667 | 220 | 0.625 | Bhulta | 234 | 0.125 | 224 | 0.45833
Shyampur | 230 | 0.125 | 219 | 0.45833 | Ashuganj (S) | 239 | 0.125 | 230 | 0.625
Aminbazar | 223 | 0.54167 | 221 | 0.45833 | Kaliakoir | 234 | 0.125 | 220 | 0.625
Tongi | 228 | 0.041667 | 216 | 0.5 | GPH | 220 | 0.125 | 215 | 0.41667
Comilla (N) | 236 | 0.25 | 229 | 0.625
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 133 | 0.25 | 127 | 0.45833 | Hathazari | 132 | 0.8125 | 129 | 0.41667
Munsiganj | 135 | 0.77083 | 127 | 0.5 | Khulshi | 130 | 0.83333 | 125 | 0.41667
Sonargaon | 132 | 0.77083 | 126 | 0.29167 | Halishahar | 132 | 0.83333 | 126 | 0.45833
Shyampur | 135 | 0.16667 | 127 | 0.45833 | Baraulia | 131 | 0.083333 | 127 | 0.45833
Bhulta | 125 | 0.041667 | 120 | 0.5 | Sikalbaha | 131 | 0.79167 | 127 | 0.45833
Madanganj | 136 | 0.77083 | 125 | 0.5 | Dohazari | 128 | 0.041667 | 126 | 0.125
Shitalakhya | 137 | 0.79167 | 125 | 0.41667 | Cox'sbazar | 124 | 0.58333 | 117 | 0.77083
Rahim steal | 132 | 1:00 | 127 | 0.66667 | Chandraghona | 132 | 0.83333 | 128 | 0.45833
Matuail | 132 | 0.083333 | 126 | 0.41667 | Kaptai | 132 | 0.29167 | 128 | 0.5
Ghorasal | 138 | 0.041667 | 135 | 0.45833 | A. Khaer Stl. | 130 | 0.8125 | 126 | 0.41667
Narsinghdi | 132 | 0.16667 | 127 | 0.70833 | Bakulia | 130 | 0.8125 | 126 | 0.45833
Haripur (SBU) | 132 | 0.25 | 128 | 0.41667 | Julda | 130 | 0.77083 | 126 | 0.375
Ullon | 130 | 0.125 | 123 | 0.66667 | TK Chemical | 132 | 0.79167 | 127 | 0.45833
Hasnabad | 134 | 0.125 | 124 | 0.66667 | Modern Steel | 131 | 0.83333 | 127 | 0.041667
Magbazar | 132 | 0.20833 | 122 | 0.66667 | Shahmirpur | 131 | 0.83333 | 127 | 0.45833
Maniknagar | 135 | 0.125 | 128 | 0.66667 | Khagrachhari | 131 | 0.83333 | 128 | 0.5
Bangabhaban | 135 | 0.125 | 128 | 0.66667 | Matarbari | 126 | 0.375 | 120 | 0.75
Narinda | 135 | 0.125 | 128 | 0.66667 | Baroiar Hat | 131 | 0.041667 | 127 | 15:00
Dhanmondi | 130 | 0.125 | 123 | 0.66667 | Rangamati | 131 | 0.83333 | 128 | 11:00
Lalbag | 135 | 0.125 | 124 | 0.66667 | Goalpara | 137 | 0.75 | 127 | 0.91667
Madartek | 131 | 0.125 | 123 | 0.66667 | Central s/s | 136 | 0.125 | 125 | 0.29167
Dhaka University |  | 0 |  |  | Noapara | 135 | 0.083333 | 124 | 0.29167
Mirpur | 133 | 0.041667 | 125 | 0.625 | Jessore | 132 | 0.75 | 122 | 0.83333
Kalyanpur | 135 | 0.16667 | 126 | 0.5 | Benapol | 133 | 0.16667 | 123 | 0.83333
Gulshan | 131 | 0.16667 | 122 | 0.625 | Jhenida | 133 | 0.041667 | 122 | 0.83333
Uttara | 136 | 0.16667 | 123 | 0.625 | Bottail | 136 | 0.20833 | 128 | 0.83333
Uttara New | 135 | 0.25 | 124 | 0.625 | G.K Project | 139 | 0.125 | 134 | 0.83333
Kamrangirchar | 131 | 0.25 | 122 | 0.66667 | Faridpur | 140 | 0.041667 | 128 | 0.83333
Savar | 134 | 0.25 | 124 | 0.625 | Madaripur | 141 | 0.041667 | 128 | 0.91667
Bhasantec | 134 | 0.20833 | 124 | 0.625 | Sariatpur | 144 | 0.083333 | 128 | 0.91667
Agargaon | 135 | 0.20833 | 126 | 0.625 | Gopalganj | 147 | 0.041667 | 132 | 0.91667
Satmosjid | 134 | 0.20833 | 126 | 0.625 | Bagerhat | 136 | 0.75 | 125 | 0.875
Tongi | 136 | 0.041667 | 127 | 0.625 | Mongla | 133 | 0.75 | 122 | 0.91667
Kabirpur | 134 | 0.125 | 123 | 0.625 | Satkhira | 135 | 0.20833 | 125 | 0.83333
Basundhara | 130 | 2:00 | 122 | 0.58333 | Gallamari | 137 | 0.75 | 126 | 0.91667
Manikganj | 138 | 0.20833 | 124 | 0.625 | Magura | 133 | 0.125 | 116 | 0.8125
Joydevpur | 141 | 0.083333 | 132 | 0.625 | Norail | 132 | 0.083333 | 118 | 0.83333
New Tongi | 135 | 0.16667 | 124 | 0.625 | Chuadanga | 130 | 0.041667 | 116 | 0.83333
Kodda | 134 | 0.875 | 116 | 0.625 | Barisal(N) | 142 | 0.75 | 132 | 0.91667
Dhamrai | 134 | 0.125 | 125 | 0.625 | Barisal (S) | 140 | 0.75 | 134 | 0.875
Rajendrapur | 139 | 0.125 | 128 | 0.625 | Patuakhali | 137 | 0.125 | 128 | 0.91667
Valuka | 131 | 0.041667 | 117 | 0.83333 | Bhandaria | 142 | 0.75 | 130 | 0.45833
Tangail | 135 | 0.16667 | 126 | 0.66667 | Ishurdi | 137 | 0.125 | 131 | 0.54167
Mymensing | 132 | 0.041667 | 119 | 0.83333 | Ruppur Paromanobik | 137 | 0.125 | 131 | 0.29167
Kishorganj | 133 | 0.125 | 123 | 0.83333 | Natore | 135 | 0.75 | 128 | 0.54167
Netrokona | 131 | 0.083333 | 117 | 0.83333 | Bogra | 135 | 0.75 | 129 | 0.33333
Jamalpur | 136 | 0.75 | 122 | 0.83333 | Noagaon | 132 | 0.125 | 122 | 0.33333
Sherpur | 136 | 0.75 | 122 | 0.83333 | Rajshahi | 132 | 0.75 | 123 | 0.33333
Srimongal | 140 | 0.25 | 135 | 0.66667 | Rajshahi New | 133 | 0.75 | 123 | 0.29167
Shahjibazar | 136 | 0.16667 | 133 | 12:00 | C.Nawabganj | 130 | 0.77083 | 123 | 0.29167
Fenchuganj | 138 | 0.125 | 135 | 0.5 | Amnura | 132 | 0.75 | 121 | 0.33333
Khulawara | 137 | 0.20833 | 134 | 0.5 | Pabna | 136 | 0.083333 | 128 | 0.83333
Sylhet | 135 | 0.041667 | 133 | 0.625 | Shahjadpur | 135 | 0.041667 | 129 | 0.33333
Chatak | 135 | 0.041667 | 133 | 0.45833 | Serajganj | 135 | 0.041667 | 128 | 0.29167
Sunamganj | 136 | 0.125 | 132 | 0.77083 | Niyamatpur | 128 | 0.16667 | 118 | 0.75
Biani Bazar | 137 | 0.083333 | 133 | 0.75 | Joypurhat | 132 | 0.25069 | 121 | 0.29167
Comilla(s) | 133 | 0.083333 | 127 | 0.45833 | Sherpur(Bogura) | 137 | 0.125 | 128 | 0.33333
Comilla(n) | 138 | 0.375 | 134 | 0.625 | Mohastangor | 135 | 0.16667 | 126 | 0.29167
Chandpur | 132 | 0.33333 | 130 | 19:0 | Rangpur | 133 | 0.16667 | 122 | 0.29167
Feni | 132 | 0.29167 | 128 | 0.66667 | Lalmonirhat | 128 | 0.125 | 115 | 0.29167
Chowmuhani | 128 | 0.375 | 123 | 0.8125 | Saidpur | 133 | 0.16667 | 117 | 0.33333
Ashuganj | 138 | 0.25 | 134 | 0.79167 | Purbasadipur | 130 | 0.125 | 117 | 0.33333
Daudkandi | 133 | 0.29167 | 128 | 0.45833 | Thakurgaon | 127 | 0.16667 | 118 | 0.29167
B.Baria | 134 | 0.29167 | 129 | 0.8125 | Palashbari | 130 | 0.77083 | 118 | 0.29167
Ramganj | 130 | 0.41667 | 125 | 0.91667 | Barapukuria | 137 | 0.041667 | 130 | 0.33333
Chaddagram | 134 | 0.29167 | 129 | 0.625 | Panchagar | 125 | 0.125 | 113 | 0.29167
PHP | 130 | 0.33333 | 127 | 0.625 | Joldhaka | 132 | 0.125 | 121 | 0.375
Madanhat | 132 | 0.20833 | 129 | 0.45833 | Kurigram | 133 | 0.20833 | 120 | 0.33333

## L-Curve
Date | 2020-03-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 201 | 5781 | 2079 | 7860 |  |  |  | QF-LDC-12
0:30 | 265.5 | 5358 | 1836 | 7194 | Date: | 2020-03-05
1:00 | 330 | 4935 | 1593 | 6528
1:30 | 294 | 4731.5 | 1580 | 6311.5
2:00 | 258 | 4528 | 1567 | 6095
2:30 | 224 | 4472.5 | 1548.5 | 6021 | [5 empty] | Gen. at Eve. Peak | 9481 | 9481 MW (19:00 )
3:00 | 190 | 4417 | 1530 | 5947 | [6 empty] | 19:00
3:30 | 167 | 4392 | 1552.5 | 5944.5 | [5 empty] | Gen. at Day Peak | 8137.5 | 8137.5 MW (12:00 )
4:00 | 144 | 4367 | 1575 | 5942 | [6 empty] | 12:00
4:30 | 146 | 4327.5 | 1590.5 | 5918 | [5 empty] | Highest Generation | 9481
5:00 | 148 | 4288 | 1606 | 5894 | [6 empty] | 19:00
5:30 | 228 | 4445 | 1580 | 6025
6:00 | 308 | 4602 | 1554 | 6156
6:30 | 229 | 4723.62 | 1805.2 | 6528.82
7:00 | 150 | 4845.24 | 2056.4 | 6901.64
7:30 | 136.5 | 5005.47 | 2154.4 | 7159.87
8:00 | 123 | 5165.7 | 2252.4 | 7418.1
8:30 | 92 | 5283.8 | 2268.95 | 7552.75
9:00 | 61 | 5401.9 | 2285.5 | 7687.4
9:30 | 102 | 5396.55 | 2309.7 | 7706.25
10:00 | 143 | 5391.2 | 2333.9 | 7725.1
10:30 | 164 | 5467.9 | 2339.05 | 7806.95
11:00 | 185 | 5544.6 | 2344.2 | 7888.8
11:30 | 168.5 | 5609.15 | 2404 | 8013.15
12:00 | 152 | 5673.7 | 2463.8 | 8137.5
12:30 | 90.5 | 5789.25 | 2443.8 | 8233.05
13:00 | 29 | 5904.8 | 2423.8 | 8328.6
13:30 | 40.5 | 5834.2 | 2295.9 | 8130.1
14:00 | 52 | 5763.6 | 2168 | 7931.6
14:30 | 119 | 5800 | 2249 | 8049
15:00 | 186 | 5836.4 | 2330 | 8166.4
15:30 | 187 | 5726.85 | 2293.5 | 8020.35
16:00 | 188 | 5617.3 | 2257 | 7874.3
16:30 | 189 | 5552.65 | 2238.6 | 7791.25
17:00 | 190 | 5488 | 2220.2 | 7708.2
17:30 | 186 | 5538.5 | 2307.65 | 7846.15
18:00 | 182 | 5589 | 2395.1 | 7984.1
18:30 | 120 | 6135.5 | 2597.05 | 8732.55
19:00 | 58 | 6682 | 2799 | 9481
19:30 | 91 | 6641 | 2809 | 9450
20:00 | 153 | 6575 | 2745 | 9320 |  |  |  | Executive Engineer
20:30 | 150 | 6510 | 2746 | 9256 |  |  |  | Network Operation Division
21:00 | 147 | 6445 | 2747 | 9192
21:30 | 76.5 | 6168 | 2679.5 | 8847.5
22:00 | 6 | 5891 | 2612 | 8503 |  |  |  |  | Page 6 of 7
22:30 | 20 | 5885 | 2524.5 | 8409.5
23:00 | 34 | 5879 | 2437 | 8316
23:30 | 117.5 | 5830 | 2258 | 8088
24:00 | 201 | 5781 | 2079 | 7860
9481 MW (19:00 )
8137.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-05 |  | Energy | 184149415
[10 empty] | 2020-03-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3937 | 398 | 2375 | 768 | 372 | 67 | 0 | 0 | 92
0:30 | 3857.5 | 304 | 2098.5 | 478.5 | 370.5 | 66.5 | 0 | 0 | 93 | Date: | 2020-03-05
1:00 | 3778 | 210 | 1822 | 189 | 369 | 66 | 0 | 0 | 94
1:30 | 3678 | 210 | 1738 | 159.5 | 369 | 66 | 0 | 0 | 91 | [7 empty] | Total Energy | 184.1494 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3578 | 210 | 1654 | 130 | 369 | 66 | 0 | 0 | 88 | [7 empty] | Energy not Served | 0
2:30 | 3571 | 210 | 1592.5 | 125 | 369.5 | 66 | 0 | 0 | 87 | [7 empty] | Energy Requirement | 184.1494
3:00 | 3564 | 210 | 1531 | 120 | 370 | 66 | 0 | 0 | 86
3:30 | 3581.5 | 210 | 1512 | 120 | 370 | 66 | 0 | 0 | 85 | [6 empty] | Shortage
4:00 | 3599 | 210 | 1493 | 120 | 370 | 66 | 0 | 0 | 84
4:30 | 3565.5 | 209.5 | 1504.5 | 120 | 369.5 | 66 | 0 | 0 | 83
5:00 | 3532 | 209 | 1516 | 120 | 369 | 66 | 0 | 0 | 82
5:30 | 3599.5 | 207.5 | 1571 | 131 | 369 | 66 | 0 | 0 | 81
6:00 | 3667 | 206 | 1626 | 142 | 369 | 66 | 0 | 0 | 80
6:30 | 3696 | 424 | 1693.5 | 197 | 369.5 | 66.5 | 0 | 0 | 81 |  |  |  |  | Coal
7:00 | 3725 | 642 | 1761 | 252 | 370 | 67 | 0 | 0 | 82
7:30 | 3799.5 | 642 | 1827 | 367 | 370 | 67 | 0 | 0 | 81 |  |  |  | Oil |  |  |  | ,
8:00 | 3874 | 642 | 1893 | 482 | 370 | 67 | 0 | 0 | 80
8:30 | 3964 | 642 | 1873 | 539.5 | 369.5 | 67 | 0 | 0 | 83
9:00 | 4054 | 642 | 1853 | 597 | 369 | 67 | 0 | 0 | 86
9:30 | 4051 | 642 | 1860.5 | 604 | 369.5 | 66.5 | 0 | 0 | 90
10:00 | 4048 | 642 | 1868 | 611 | 370 | 66 | 0 | 0 | 94
10:30 | 4089 | 642 | 1884 | 630.5 | 370 | 66 | 0 | 0 | 97
11:00 | 4130 | 642 | 1900 | 650 | 370 | 66 | 0 | 0 | 100
11:30 | 4109.5 | 642 | 1951.5 | 740.5 | 370 | 66 | 0 | 0 | 102
12:00 | 4089 | 642 | 2003 | 831 | 370 | 66 | 0 | 0 | 104
12:30 | 4125.5 | 642 | 2014 | 891 | 370 | 66 | 0 | 0 | 102
13:00 | 4162 | 642 | 2025 | 951 | 370 | 66 | 0 | 0 | 100
13:30 | 4162 | 642 | 2025 | 951 | 370 | 66 | 0 | 0 | 100
14:00 | 4162 | 642 | 2025 | 951 | 370 | 66 | 0 | 0 | 100
14:30 | 4138 | 642 | 2041.5 | 877.5 | 370 | 66.5 | 0 | 0 | 99
15:00 | 4114 | 642 | 2058 | 804 | 370 | 67 | 0 | 0 | 98
15:30 | 4071 | 642 | 1989.5 | 767 | 370 | 67.5 | 3 | 0 | 99
16:00 | 4028 | 642 | 1921 | 730 | 370 | 68 | 6 | 0 | 100
16:30 | 3988 | 642 | 1861.5 | 751 | 370.5 | 68 | 6 | 0 | 98
17:00 | 3948 | 642 | 1802 | 772 | 371 | 68 | 6 | 0 | 96
17:30 | 3939 | 642 | 1767 | 932.5 | 371 | 68 | 19 | 0 | 106
18:00 | 3930 | 642 | 1732 | 1093 | 371 | 68 | 32 | 0 | 116
18:30 | 3978 | 765 | 1832.5 | 1553 | 370.5 | 67.5 | 50 | 0 | 116
19:00 | 4026 | 888 | 1933 | 2013 | 370 | 67 | 68 | 0 | 116
19:30 | 4069 | 888 | 1970 | 1900 | 370 | 67 | 68 | 0 | 118
20:00 | 4043 | 889 | 2043 | 1753 | 369 | 67 | 34 | 0 | 122
20:30 | 4063.5 | 889 | 2065 | 1647.5 | 370 | 67 | 34 | 0 | 120
21:00 | 4084 | 889 | 2087 | 1542 | 371 | 67 | 34 | 0 | 118
21:30 | 3933.5 | 889.5 | 2155 | 1299 | 370.5 | 67 | 17 | 0 | 116
22:00 | 3783 | 890 | 2223 | 1056 | 370 | 67 | 0 | 0 | 114
22:30 | 3835.5 | 839.5 | 2272.5 | 912 | 372 | 67 | 0 | 0 | 111
23:00 | 3888 | 789 | 2322 | 768 | 374 | 67 | 0 | 0 | 108
23:30 | 3912.5 | 593.5 | 2348.5 | 768 | 373 | 67 | 0 | 0 | 100 | Max Temp. in Dhaka |  | 30.1° C
24:00 | 3937 | 398 | 2375 | 768 | 372 | 67 | 0 | 0 | 92
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 26 | 26 | 26 | 26 | 26 | 27 | 28 | 28 | 28 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 574500
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2 | [19 empty] | 0
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1.64 | 6.4 | 11.5 | 16 | 18.5 | 18.8 | 0 | 10.7 | 9 | 4.2 | 1.2 | [9 empty] | 111510
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 205 | 203 | 218 | 206 | 204 | 204 | 207 | 216 | 204 | 204 | 207 | 206 | 215 | 204 | 205 |  | 204 | 205 | 164 | 165 | 164 | 164 | 168 | 4736833
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 105 | 105 | 105 | 105 | 105 | 105 | 140 | 140 | 140 | 145 | 139 | 145 | 104 | 139 | 139 | 139 | 104 |  | 104 | 100 | 100 | 100 | 100 | 100 | 100 | 2854980
10 | Sikalbaha 150MW GTPP(Oil) | [19 empty] | 0
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 0 | [6 empty] | 0
12 | Hathazari 100 MW peaking PP | [19 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 26 | 34 | 34 | 34 |  |  |  | 112909
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 0
15 | 210 MW Siddhirgonj TPP | [19 empty] | 0
16 | Siddhirgonj 2*120 MW GTPP | [19 empty] | 0
17 | Siddhirganj 335 MW CCPP | [19 empty] | 0
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 2 | 17 |  | 45 | [6 empty] | 72764
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 55 | 55 | 55 | 55 |  | 83 | 83 | 83 | 83 | 102 | 185 | 192 | 1070545
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | [22 empty] | 158000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 167 | 96 | 94 | 100 | 100 | 100 | 100 | 100 | 198 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 |  | 150 | 180 | 180 | 180 | 57 | 202 | 200 | 3661000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 325 | 283 | 275 | 295 | 295 | 295 | 275 | 276 | 275 | 300 | 303 | 300 | 340 | 300 | 350 | 350 | 320 | 321 |  | 320 | 320 | 320 | 320 | 325 | 325 | 329 | 7463618
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2661755
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 15 | 39 | 39 | 43 | 43 | 43 | 43 | 46 | 46 | 46 | 42 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 803376
33 | Ashuganj 225 MW CCPP | 182 | 194 | 183 | 177 | 163 | 202 | 190 | 190 | 225 | 202 | 201 | 187 | 192 | 195 | 183 | 182 | 164 | 175 |  | 221 | 222 | 220 | 221 | 220 | 222 | 222 | 4755000
34 | Ashuganj 450 MW CCPP(South) | 265 | 275 | 265 | 285 | 265 | 295 | 270 | 270 | 265 | 160 | 160 | 155 | 155 | 155 | 155 | 155 | 160 | 155 |  | 155 | 155 | 155 | 195 |  |  |  | 4688000
| Ashuganj 450 MW CCPP(North) | 250 | 265 | 255 | 270 | 255 | 265 | 265 | 265 | 265 | 300 | 310 | 280 | 335 | 330 | 290 | 290 | 265 | 270 |  | 295 | 295 | 305 | 295 | 325 | 315 | 315 | 7111800
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 30 | 40 | 48 | 47 | 49 | 49 | 348000
36 | Chandpur 150 MW CCPP | 82 | 90 | 81 | 91 | 88 | 90 | 91 | 91 | 81 | 90 | 90 | 91 | 91 | 91 | 90 | 91 | 84 | 80 |  | 80 | 80 | 90 | 85 | 91 | 91 | 87 | 2095990
37 | Tongi 80 MW GTPP | [19 empty] | 0
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 341 | 335 | 337 | 286 | 280 | 333 | 339 | 338 | 336 | 346 | 359 | 368 | 351 | 350 | 356 | 340 | 353 | 353 |  | 342 | 338 | 341 | 353 | 346 | 340 | 356 | 8314730
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 370 | 330 | 330 | 330 | 330 | 330 | 360 | 360 | 360 | 360 | 390 | 390 | 450 | 450 | 400 | 370 | 340 |  | 370 | 370 | 400 | 400 | 450 | 450 | 450 | 9011250
41 | Haripur 360MW CCPP(HPL) | 363 | 337 | 307 | 277 | 277 | 276 | 275 | 366 | 365 | 360 | 359 | 357 | 358 | 333 | 335 | 314 | 314 | 284 |  | 314 | 314 | 316 | 330 | 360 | 364 | 363 | 7839000
42 | RPCL 210MW CCPP | 148 | 149 | 161 | 161 | 161 | 161 | 161 | 162 | 160 | 159 | 145 | 145 | 130 | 132 | 129 | 131 | 132 | 145 |  | 156 | 158 | 157 | 157 | 158 | 159 | 157 | 3498880
43
44 | Fenchugonj CCPP Phase-1 | 86 | 86 | 86 | 86 | 87 | 86 | 87 | 86 | 86 | 89 | 89 | 89 | 89 | 89 | 85 | 85 | 85 | 86 |  | 86 | 85 | 85 | 85 | 85 | 88 | 88 | 2053000
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 776400
46 | Shajibazar 330 MW CCPP | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 125 | 125 | 132 | 126 | 126 | 127 | 126 | 126 | 129 | 127 | 127 |  | 125 | 126 | 125 | 126 | 124 | 126 | 126 | 2878000
47 | Shahjibazar GTPP Unit- 8 & 9 | 65 | 54 | 54 | 45 | 45 | 56 | 66 | 65 | 65 | 63 | 62 | 61 | 60 | 60 | 61 | 61 | 61 | 63 |  | 65 | 65 | 63 | 63 | 63 | 63 | 64 | 1432800
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 5 | 5 | 5 | 5 | 81 | 81 | 81 | 81 | 78 | 81 | 81 | 81 | 81 | 81 | 81 | 30 | 30 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1509120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 159 | 157 | 157 | 158 | 156 | 158 | 157 | 158 | 221 | 229 | 229 | 229 | 229 | 227 | 228 | 226 | 228 | 229 |  | 229 | 229 | 230 | 230 | 230 | 230 | 230 | 4959120
51 | Sylhet 20 MW GTPP | [7 empty] | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 301000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 181620
54 | Hobiganj 11MW PP Cofidence-E | [6 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198021
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 17 | 48 | 45 | 22 | 22 | 22 | 22 | 25 | 25 | 24 | 22 | 22 | 25 |  | 53 | 53 | 53 | 53 | 50 | 51 | 51 | 717000
56 | Shahjahanulla 25 MW PP | [6 empty] | 24 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 374088
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 290 | 310 | 320 | 310 | 300 | 300 | 310 | 325 | 320 | 300 | 310 | 310 | 300 | 305 | 300 |  | 290 | 305 | 300 | 310 | 310 | 300 | 305 | 7627550
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | [5 empty] | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 354672
61 | Narshingdi 22 MW PP (Doreen) | [6 empty] | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 |  |  | 22 | 290448
62 | Tangail 22 MW PP (Doreen) | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 20 |  | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 395964
63 | Impoprt (Tripura) | 94 | 88 | 86 | 84 | 82 | 80 | 82 | 80 | 86 | 94 | 100 | 104 | 100 | 100 | 98 | 100 | 96 | 116 |  | 116 | 118 | 122 | 118 | 114 | 108 | 92 | 2443200
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 36 | 11 | 8 | 2 | 1 | 2 | 8 | 2 | 2 | 2 | 10 | 11 |  | 24 | 24 | 24 | 32 | 36 | 38 | 38 | 538080
65 | Feni 22MW PP (Doreen) | 22 |  |  |  |  | 3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 375660
66 | Feni 11 MW PP (Doreen) | [6 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 112500
67 | Jangalia 33MW PP (Summit) | [10 empty] | 25 | 33 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 383500
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 15 | 15 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 469840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 10 | 0 | 10 | 28 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 31 | 31 | 31 | 24 |  | 31 | 31 | 31 | 31 | 31 | 10 | 10 | 596160
71 | Maona 33 MW PP(Summit) | 33 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 28 | 25 | 28 | 33 | 33 | 33 | 723300
72 | Rupganj 33 MW PP(Summit) | 25 | 16 | 17 | 17 | 17 | 17 | 17 | 25 | 8 | 29 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 633700
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [26 empty] | 0
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 0 | 30 | 30 | 16 | 16 | 30 | 90 | 70 | 60 | 60 | 60 | 60 |  | 90 | 98 | 98 | 98 | 98 | 96 | 60 | 1106880
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) |  |  |  | 0 | 0 | 2 | 48 | 95 | 82 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 56 |  | 91 | 91 | 91 | 95 | 95 | 95 | 95 | 1252800
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [6 empty] | 0.5 | 1.8 | 3 | 3.2 | 4.7 | 4.8 | 4.6 | 3.8 | 3 | 1.5 | 0.6 | [9 empty] | 30000
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [17 empty] | 12 |  | 55 | 55 | 55 | 15 |  |  |  | 156600
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 1 | 16 |  | 40 | [6 empty] | 68859
86 | Meghnaghat CCPP(Summit) | 120 | 130 | 120 | 120 | 120 | 130 | 130 | 120 | 115 | 125 | 127 | 120 | 130 | 125 | 120 | 125 | 120 | 120 |  | 120 | 125 | 130 | 130 | 130 | 120 | 125 | 2990167
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 16 | 40 | 21 | 16 | 16 | 16 | 18 |  | 86 | 100 | 100 | 100 | 74 | 57 |  | 576000
88 | Ghorashal 78.5 MW PP(MAX) | [26 empty] | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 8 | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 15 |  | 51 | 51 | 51 | 51 | 51 | 51 | 47 | 930600
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 9 | 44 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1046644
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 16 | 32 | 40 | 32 | 32 | 32 | 32 | 58 |  | 102 | 102 | 102 | 102 | 65 |  |  | 642096
95 | Patenga 50MW PP (Baraka) | [11 empty] | 8 | 24 | 25 | 25 | 25 | 25 | 26 |  | 48 | 50 | 50 | 50 |  |  |  | 331680
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 15 |  | 40 | 50 | 50 | 12 |  |  |  | 127680
97 | Katpotti 52 MW PP (Sinha) | [17 empty] | 3 |  | 30 | 18 | 18 | 18 |  |  |  | 92160
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 18 |  | 55 | 55 | 30 | 15 |  |  |  | 145829
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 17 |  |  |  | 300226
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 3566045
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.1 | 0.5 | 1.4 | 2 | 1.4 | 2.1 | 1.2 | 2.1 | 1.4 | 0.6 | 0.2 | [9 empty] | 12250
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 |  |  |  |  | 10 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 966600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 2 | 7 | 7 | 7 | 7 | 7 | 10 |  | 40 | [6 empty] | 110400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 12 | 30 | 30 | 35 | 37 | 60 | 35 | 30 | 40 | 47 | 50 |  | 139 | 149 | 149 | 149 | 112 | 55 | 15 | 1025280
115 | Juldah 100 MW PP Unit-3 (Acorn) | [11 empty] | 20 | 10 | 10 | 10 | 10 | 10 | 27 |  | 100 | 100 | 100 | 50 |  |  |  | 350400
116 | Chandpur 200MW (Desh energy) | [26 empty] | 0
117 | Ashuganj 150MW PP (Midland) | [16 empty] | 2 | 8 |  | 80 | 80 | 30 |  |  |  |  | 153890
118 | Bibiyana-III 400 MW CCPP | 232 | 233 | 234 | 233 | 234 | 233 | 233 | 233 | 235 | 232 | 232 | 234 | 233 | 233 | 230 | 234 | 234 | 234 |  | 234 | 234 | 234 | 234 | 232 | 232 | 232 | 5595000
| Jamalpur 115 MW PP (United) | [7 empty] | 16 | 29 | 32 | 45 | 54 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 75 | 64 | 64 | 32 |  |  | 1242000
| Anwara 300 MW PP (United) | 52 | [5 empty] | 10 | 50 | 86 | 121 | 123 | 193 | 160 | 160 | 160 | 106 | 106 | 120 |  | 215 | 215 | 215 | 215 | 215 | 162 | 162 | 2639564
120 | Eastern Zone Total | 4935 | 4528 | 4417 | 4367 | 4288 | 4602 | 4845.24 | 5165.7 | 5401.9 | 5391.2 | 5544.6 | 5673.7 | 5904.8 | 5763.6 | 5836.4 | 5617.3 | 5488 | 5589 |  | 6682 | 6641 | 6575 | 6445 | 5891 | 5879 | 5781 | 131900833
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [11 empty] | 32 | 32 | 16 | 16 | 16 | 16 | 57 |  | 115 | 115 | 115 | 115 | 49 | 9 |  | 582720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 48 |  | 16 | 16 | 16 | 16 |  |  |  | 90336
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | [6 empty] | 11 | 11 | 11 | 12 | 90 | 92 | 95 | 95 | 85 | 53 | 54 |  | 73 | 72 | 71 | 72 | 61 | 72 | 95 | 1052204
| Bhola 225 MW CCPP | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 142 | 139 | 138 | 138 | 137 | 136 | 130 | 134 | 130 | 130 | 130 |  | 124 | 130 | 130 | 130 | 130 | 130 | 130 | 2847000
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 14 | 15 | 15 | 15 | 14 | 13 | 11 | 11 | 11 | 13 | 13 | 12 | 13 | 13 | 13 | 16 |  | 9 | 7 | 6 | 12 | 20 | 18 | 16 | 326200
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 6 | 6 | [9 empty] | 7680
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [17 empty] | 7 | [8 empty] | 7920
146 | Bheramara HVDC | 210 | 210 | 210 | 210 | 209 | 206 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 |  | 888 | 888 | 889 | 889 | 890 | 789 | 398 | 13674909
147 | Bheramara 410 MW CCPP | 315 | 340 | 355 | 375 | 405 | 350 | 350 | 365 | 380 | 390 | 390 | 380 | 360 | 300 | 330 | 320 | 300 | 300 |  | 320 | 320 | 320 | 320 | 320 | 285 | 290 | 8352576
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 89 | 89 | 90 | 90 | 90 | 89 | 90 | 90 | 89 | 90 | 90 | 90 | 90 | 0 | 90 | 90 | 91 | 91 |  | 90 | 90 | 89 | 91 | 90 | 93 | 92 | 2147782
151 | Barapukuria TPP Unit-2 | [19 empty] | 0
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 279 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 281 | 280 | 5978000
153 | Baghabari 71 MW GTPP | [19 empty] | 0
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 0 | [6 empty] | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 150 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 150 | 170 | 195 | 190 | 190 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 175 | 200 | 205 | 4282964
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 382 | 396 | 346 | 380 | 383 | 382 | 394 | 422 | 389 | 433 | 430 | 429 | 424 | 380 | 417 | 414 | 395 | 377 |  | 360 | 360 | 398 | 395 | 435 | 410 | 435 | 9643273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) |  |  | 0 | 0 | 0 | 3 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 309840
163 | Bogura 20 MW PP (Energyprima) | 11 |  |  |  |  | 4 | 11 | 11 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184464
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11
165 | Amnura 50 MW PP(Sinha) | [6 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 50 |  | 50 | 50 | 50 | 50 | 24 | 12 |  | 547660
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 32 |  | 68 | 68 | 34 | 34 |  |  |  | 166568
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 0
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 27 | 35 | [5 empty] | 51936
172 | Confidence Power Bogura Unit-1 113 MW | [6 empty] | 5 | 70 | 109 | 109 | 109 | 109 | 70 | 70 | 70 | 35 | 35 | 50 |  | 108 | 109 | 108 | 109 | 109 | 109 | 109 | 1524384
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 12 | 39 | 35 | 36 | 35 | 30 |  |  |  | 35 | 62 |  | 72 | 70 | 40 | 35 |  |  |  | 435840
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 1.4 | 3.5 | 4.9 | 6.2 | 6.8 | 6.8 | 0 | 0 | 3 | 1.2 | 0.1 | [8 empty] | 34326
178
178