## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-10 | Tuesday
|  | Date (day): | 2020-03-10 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11655.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14455 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-09 | 2020-03-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 230 | 100 | 100 | 150
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 275 | 275 | 275
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 335 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 355 | 362 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 370 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 120 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 64 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 52 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 56 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 110 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 16 | 137 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2085 | 2493 | 3419 | 4071 | 991 | 623
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 67 | 66 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 105 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 13 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 45 | 214 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 572 | 930 | 1499 | 1631 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 202 | 182 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 265 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 42 | 42 | 36 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 50 | 10 | 10 | 45 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 89 | 90 | 94 |  | 69 | Engine problem
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 124 | 96 | 122
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 19 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1306 | 1312 | 1637 | 2337 | 530 | 69
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 82 | 126 | 150 | 150
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.6 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 112 | 93 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 250.6 | 451 | 483.6 | 582 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 87 | 86 | 87 | 87
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 117 | 273 | 147 | 150 | 180 |  | GT-1 under maintenance.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 51 | 51 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 63 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 80 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 234 | 120 | 0 | 0
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 15 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 234 | 234 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1463 | 1466 | 1309 | 1313 | 180 | 225
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 642 | 932 | 660 | 954
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 10 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 320 | 330 | 330 | 80 |  | Gas shortage
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 32 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 952 | 1439 | 1275 | 2119 | 80 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 12 | 18 | 18 | 21 |  | 12 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 55 | 130 | 130 |  | 64 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 97 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 168 | 250 | 307 | 386 | 0 | 76
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 180 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 421 | 340 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 18 | 18
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 43 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 722 | 767 | 1235 | 1499 | 611 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 87 | 88 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 37 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 407.2 | 481 | 491 | 517 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 7925.8 | 9589 | 11655.6 | 14455 | 2802 | 1186
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7566.2502 | 9154 | 11126.8498 | 13799.2564
A. |  | 2020-03-09 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 9589 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6272 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9589 | MW
3 | Day peak Generation : |  |  | 7925.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9154 | MW
4 | Evening peak Generation : |  |  | 9589 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 185.9207 | MKWHr | By Solar | 0.22701 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 142.8598 | MKWHr |  | By Oil: | 16.3268 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.6946 | MKWHr |  | By Hydro: | 1.5144 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2802 | MW | Dhaka | 3375 | 3375 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1186 | MW | Chittagong | 969 | 969 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3988 | MW | Khulna | 1103 | 1103 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1146.22 | MMCFD |  |  | Rajshahi | 958 | 958 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 133731392.132 | ii) Oil : | Taka | 118109184.74 | Comilla | 792 | 792 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 40435156.65 | Total | Taka | 292275733.522 | Mymensingh | 748 | 748 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.1505 | MKWHr. | Sylhet | 333 | 333 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -205 | MW (E to W) at | 19:30 | hrs | Barisal | 239 | 239 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -306 | MW at | 6:00 | hrs | Rangpur | 637 | 637 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.4° C |  |  | Total | 9154 | 9154 |  | 0
B. |  | 2020-03-10 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 30.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14455 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 4655 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 190.0118 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6266 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.9767 | MKWHr. | ii) HVDC Flow at Peak Time |  | 932 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3213 | MKWHr. | iii) Maximum HVDC Flow : |  | 942 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.27 |  | (b) Today: | 88.09 |  | (c) Rule Curve: |  | 91.56
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-03-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 0 | 200 | 0 | 282 | 0 | 0 | 352 | 310 |  | 0 | 390 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 32 | 28 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 140 | 0 | 335 | 0 | 196 | 92 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 90 | 167 | 43 | 22 | 0 | 86 | 30 | 53 | 48 | 130 | 117 | 63 | 81 | 0 | 224 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 |  | 5209 | 1860 | 7069 | 3977 | 251 | 2087 | 228 | 370 | 66 | 0 | 90 | 0 | 0 | 88.32
2:00 | 37 | 0 | 170 | 0 | 293 | 0 | 0 | 352 | 310 |  | 0 | 390 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 28 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 140 | 0 | 325 | 80 | 191 | 92 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 20 | 21 | 90 | 168 | 8 | 22 | 0 | 87 | 30 | 53 | 48 | 130 | 118 | 63 | 20 | 0 | 224 | 19 | 0 | 10 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5118 | 1746 | 6864 | 3892 | 251 | 2036 | 160 | 370 | 65 | 0 | 90 | 0 | 0 | 88.31
3:00 | 37 | 0 | 170 | 0 | 272 | 0 | 0 | 352 | 310 |  | 0 | 390 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 28 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 140 | 0 | 325 | 75 | 183 | 92 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 8 | 21 | 88 | 188 | 0 | 22 | 0 | 87 | 30 | 5 | 5 | 130 | 118 | 63 | 20 | 0 | 224 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 252 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4843 | 1668 | 6511 | 3780 | 252 | 1821 | 135 | 370 | 65 | 0 | 88 | 0 | 0 | 88.3
4:00 | 37 | 0 | 170 | 0 | 293 | 0 | 0 | 355 | 309 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 28 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 100 | 0 | 340 | 75 | 198 | 25 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 8 | 21 | 88 | 189 | 0 | 22 | 0 | 87 | 30 | 5 | 5 | 130 | 117 | 45 | 10 | 0 | 227 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 5 | 91 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4724 | 1654 | 6378 | 3769 | 255 | 1690 | 140 | 371 | 65 | 0 | 88 | 0 | 0 | 88.29
5:00 | 37 | 0 | 170 | 0 | 285 | 0 | 0 | 351 | 311 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 214 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 100 | 0 | 340 | 10 | 195 | 25 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 8 | 21 | 86 | 189 | 0 | 22 | 0 | 87 | 30 | 5 | 5 | 130 | 116 | 45 | 10 | 0 | 226 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 5 | 90 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4649 | 1623 | 6272 | 3693 | 255 | 1692 | 140 | 340 | 66 | 0 | 86 | 0 | 0 | 88.28
6:00 | 37 | 0 | 220 | 0 | 296 | 0 | 0 | 371 | 338 |  | 0 | 380 | 135 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 207 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 16 | 0 | 100 | 0 | 345 | 75 | 178 | 8 | 96 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 0 | 28 | 21 | 82 | 204 | 0 | 22 | 0 | 87 | 30 | 15 | 10 | 130 | 118 | 64 | 77 | 0 | 226 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 10 | 5 | 90 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4981 | 1670 | 6651 | 3876 | 255 | 1865 | 167 | 340 | 66 | 0 | 82 | 0 | 0 | 88.27
7:00 | 37 | 0 | 230 | 0 | 283 | 0 | 0 | 341 | 339 |  | 0 | 380 | 130 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 100 | 0 | 330 | 95 | 178 | 8 | 96 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 84 | 205 | 0 | 22 | 0.2 | 87 | 30 | 53 | 48 | 130 | 116 | 65 | 78 | 0 | 226 | 0 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 2.4 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 |  | 521 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 20 | 10 | 11 | 90 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 6 | 0 |  | 5166.1 | 1981.2 | 7147.3 | 3905 | 521 | 1978 | 250 | 340 | 66 | 0 | 84 | 3.3 | 0 | 88.26
8:00 | 37 | 0 | 230 | 0 | 275 | 0 | 0 | 337 | 311 |  | 0 | 380 | 125 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 100 | 0 | 320 | 105 | 165 | 8 | 94 | 0 | 10 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 76 | 0 | 0 | 22 | 0 | 87 | 30 | 53 | 48 | 110 | 118 | 63 | 81 | 0 | 225 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7.5 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 |  | 642 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 9 | 11 | 90 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 32 | 0 | 1.9 | 35 | 0 |  | 4836.3 | 2167.9 | 7004.2 | 3712 | 642 | 1844 | 313 | 340 | 66 | 0 | 76 | 11.2 | 0 | 88.25
9:00 | 37 | 0 | 230 | 0 | 314 | 0 | 0 | 340 | 316 |  | 0 | 350 | 135 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 100 | 0 | 320 | 250 | 184 | 8 | 90 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 84 | 88 | 0 | 22 | 1.6 | 86 | 30 | 53 | 48 | 110 | 118 | 62 | 81 | 0 | 227 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 52 | 0 | 16 | 13.5 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 |  | 640 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 9 | 11 | 90 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 38 | 0 | 3.4 | 35 | 0 |  | 5216.3 | 2207.4 | 7423.7 | 4018 | 640 | 1857 | 397 | 340 | 66 | 0 | 84 | 21.7 | 0 | 88.24
10:00 | 37 | 0 | 230 | 0 | 300 | 0 | 0 | 348 | 316 |  | 0 | 380 | 135 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 32 | 0 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 202 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 100 | 0 | 315 | 360 | 178 | 8 | 85 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 16 | 8 | 33 | 21 | 88 | 84 | 5 | 22 | 2.1 | 87 | 30 | 50 | 51 | 110 | 119 | 61 | 81 | 0 | 227 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 112 | 0 | 30 | 17.2 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 4.3 | 10 | 0 | 0 | 0 | 0 |  | 641 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 10 | 11 | 91 | 0 | 250 | 0 | 0 | 160 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 35 | 0 | 4.9 | 35 | 0 |  | 5413.6 | 2173.9 | 7587.5 | 4037 | 641 | 1898 | 488 | 341 | 66 | 0 | 88 | 28.5 | 0 | 88.23
11:00 | 37 | 0 | 230 | 0 | 300 | 0 | 0 | 340 | 316 |  | 0 | 380 | 135 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 0 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 315 | 310 | 182 | 8 | 96 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 90 | 83 | 32 | 22 | 2.5 | 87 | 30 | 50 | 51 | 110 | 116 | 60 | 79 | 0 | 234 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 112 | 0 | 18 | 19.2 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 5.1 | 16 | 0 | 0 | 0 | 0 |  | 641 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 92 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 35 | 0 |  | 5407.8 | 2225 | 7632.8 | 4023 | 641 | 1902 | 509 | 372 | 66 | 0 | 90 | 29.8 | 0 | 88.22
12:00 | 37 | 0 | 230 | 0 | 320 | 0 | 0 | 367 | 355 |  | 0 | 400 | 140 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 29 | 0 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 335 | 330 | 202 | 8 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 90 | 82 | 32 | 22 | 2.6 | 87 | 30 | 50 | 51 | 130 | 117 | 60 | 81 | 0 | 234 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 112 | 0 | 16 | 19.8 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 5.2 | 45 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 87 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 37 | 0 | 3.2 | 50 | 0 |  | 5676.6 | 2249.2 | 7925.8 | 4095 | 642 | 2019 | 615 | 367 | 67 | 0 | 90 | 30.8 | 0 | 88.21
13:00 | 37 | 0 | 230 | 0 | 300 | 0 | 0 | 348 | 355 |  | 0 | 400 | 120 | 7 | 75 | 0 | 0 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 202 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 6 | 0 | 100 | 0 | 310 | 310 | 185 | 8 | 85 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 94 | 86 | 32 | 22 | 2.5 | 87 | 30 | 50 | 51 | 130 | 119 | 60 | 81 | 0 | 233 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 8 | 0 | 0 | 112 | 0 | 15 | 18.7 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 5 | 45 | 0 | 0 | 0 | 0 |  | 642 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 9 | 92 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 36 | 0 | 3 | 100 | 0 |  | 5664.2 | 2333 | 7997.2 | 4054 | 642 | 2014 | 726 | 372 | 66 | 0 | 94 | 29.2 | 0 | 88.2
14:00 | 37 | 0 | 230 | 0 | 300 | 0 | 0 | 340 | 245 |  | 0 | 370 | 130 | 7 | 78 | 0 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 285 | 280 | 183 | 8 | 97 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 100 | 66 | 32 | 0 | 2.4 | 89 | 30 | 47 | 51 | 130 | 146 | 60 | 81 | 0 | 234 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 15 | 0 | 0 | 100 | 0 | 16 | 17.1 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 4.3 | 52 | 0 | 0 | 0 | 0 |  | 643 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 9 | 90 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 35 | 0 | 2.2 | 109 | 0 |  | 5482.8 | 2264.2 | 7747 | 3970 | 643 | 1817 | 755 | 370 | 66 | 0 | 100 | 26 | 0 | 88.19
15:00 | 37 | 0 | 228 | 0 | 300 | 0 | 0 | 352 | 255 |  | 0 | 370 | 130 | 7 | 79 | 0 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 116 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 315 | 280 | 182 | 8 | 90 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 18 | 96 | 128 | 32 | 22 | 1.8 | 87 | 30 | 53 | 51 | 163 | 272 | 60 | 81 | 0 | 134 | 19 | 0 | 10 | 310 | 15 | 11 | 0 | 15 | 0 | 0 | 101 | 0 | 15 | 13.4 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 3.3 | 51 | 0 | 0 | 0 | 0 |  | 641 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 9 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 35 | 0 | 2.7 | 109 | 0 |  | 5669.5 | 2250.7 | 7920.2 | 4091 | 641 | 1879 | 755 | 371 | 66 | 0 | 96 | 21.2 | 0 | 88.19
16:00 | 37 | 0 | 130 | 0 | 277 | 0 | 0 | 344 | 292 |  | 0 | 350 | 130 | 7 | 79 | 0 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 115 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 315 | 285 | 173 | 8 | 96 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 18 | 88 | 144 | 32 | 22 | 1 | 89 | 30 | 50 | 51 | 163 | 274 | 45 | 81 | 0 | 103 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 101 | 0 | 15 | 8.5 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 2 | 105 | 0 | 0 | 0 | 0 |  | 641 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 12 | 9 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 70 | 0 |  | 5545.5 | 2102.5 | 7648 | 3893 | 641 | 1882 | 692 | 370 | 66 | 2 | 88 | 14 | 0 | 88.18
17:00 | 37 | 0 | 100 | 0 | 293 | 0 | 0 | 344 | 279 |  | 0 | 320 | 140 | 7 | 85 | 0 | 0 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 32 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 211 | 0 | 70 | 0 |  | 0 | 9 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 100 | 0 | 275 | 280 | 183 | 8 | 95 | 42 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 0 | 18 | 92 | 157 | 32 | 22 | 0.3 | 89 | 30 | 11 | 10 | 100 | 280 | 45 | 20 | 0 | 145 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 15 | 3.3 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0.8 | 108 | 0 | 0 | 0 | 0 |  | 642 | 0 | 260 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 19 | 12 | 9 | 90 | 0 | 281 | 0 | 0 | 140 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 70 | 0 |  | 5308.4 | 2007.9 | 7316.3 | 3871 | 642 | 1507 | 752 | 371 | 66 | 9 | 92 | 6.3 | 0 | 88.18
18:00 | 37 | 0 | 100 | 0 | 313 | 0 | 0 | 372 | 277 |  | 0 | 340 | 150 | 8 | 96 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 0 | 45 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 15 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 214 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 0 | 100 | 0 | 310 | 310 | 203 | 8 | 96 | 42 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 13 | 19 | 116 | 144 | 40 | 22 | 0 | 87 | 30 | 11 | 10 | 130 | 286 | 61 | 20 | 0 | 146 | 19 | 0 | 10 | 310 | 15 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 16 | 0 | 5 | 0 | 0 | 233 | 9 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 642 | 0 | 295 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 12 | 9 | 89 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 86 | 0 |  | 5659 | 2155.2 | 7814.2 | 4051 | 642 | 1626 | 944 | 369 | 66 | 0 | 116 | 0.2 | 0 | 88.17
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 351 | 359 |  | 0 | 370 | 130 | 65 | 86 | 28 | 0 | 0 | 0 | 0 | 85 | 85 | 0 | 0 | 50 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 214 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 83 | 38 | 19 | 13 | 0 | 100 | 0 | 295 | 265 | 220 | 8 | 85 | 42 | 40 | 0 | 30 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 124 | 145 | 95 | 22 | 0 | 86 | 30 | 53 | 51 | 163 | 271 | 63 | 81 | 0 | 146 | 19 | 0 | 10 | 300 | 15 | 11 | 0 | 56 | 0 | 0 | 93 | 0 | 100 | 0 | 100 | 0 | 28 | 233 | 63 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 |  | 932 | 0 | 315 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 32 | 65 | 21 | 58 | 0 | 0 | 0 | 0 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 20 | 12 | 11 | 89 | 0 | 280 | 0 | 0 | 145 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 32 | 80 | 0 | 0 | 109 | 0 |  | 6636 | 2892 | 9528 | 4022 | 932 | 2028 | 1945 | 369 | 66 | 42 | 124 | 0 | 0 | 88.17
19:30 | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 335 | 362 |  | 0 | 370 | 120 | 100 | 64 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 52 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 50 | 50 | 19 | 13 | 0 | 100 | 0 | 315 | 265 | 182 | 8 | 89 | 42 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 124 | 126 | 95 | 22 | 0 | 86 | 30 | 53 | 51 | 130 | 273 | 63 | 81 | 0 | 120 | 19 | 0 | 10 | 290 | 15 | 11 | 0 | 110 | 0 | 0 | 93 | 0 | 137 | 0 | 100 | 0 | 10 | 234 | 115 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 |  | 932 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 55 | 18 | 80 | 0 | 0 | 0 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 88 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 32 | 113 | 0 | 0 | 109 | 0 |  | 6652 | 2937 | 9589 | 3970 | 932 | 1950 | 2136 | 368 | 66 | 43 | 124 | 0 | 0 | 0
20:00 | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 338 | 361 |  | 0 | 370 | 125 | 100 | 74 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 56 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 27 | 0 | 100 | 0 | 315 | 265 | 183 | 8 | 90 | 46 | 49 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 126 | 126 | 95 | 22 | 0 | 88 | 30 | 53 | 51 | 130 | 271 | 63 | 81 | 0 | 120 | 19 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 110 | 0 | 134 | 0 | 20 | 0 | 0 | 233 | 35 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 18 | 80 | 0 | 0 | 0 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 89 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 32 | 113 | 0 | 0 | 109 | 0 |  | 6506 | 2988 | 9494 | 4022 | 932 | 1967 | 1969 | 369 | 66 | 43 | 126 | 0 | 0 | 88.16
21:00 | 37 | 0 | 146 | 0 | 320 | 0 | 0 | 344 | 362 |  | 0 | 400 | 130 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 65 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 34 | 0 | 100 | 0 | 310 | 300 | 184 | 8 | 86 | 46 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 116 | 126 | 95 | 22 | 0 | 87 | 30 | 53 | 51 | 130 | 270 | 64 | 81 | 0 | 146 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 95 | 0 | 0 | 110 | 0 | 35 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 |  | 940 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 80 | 22 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 89 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 0 |  | 6406 | 2980 | 9386 | 4191 | 940 | 2081 | 1623 | 369 | 66 | 0 | 116 | 0 | 0 | 88.16
22:00 | 37 | 0 | 150 | 0 | 319 | 0 | 0 | 337 | 363 |  | 0 | 400 | 125 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 19 | 39 | 0 | 100 | 0 | 315 | 305 | 182 | 8 | 96 | 46 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 114 | 127 | 11 | 22 | 0 | 87 | 30 | 53 | 51 | 163 | 282 | 64 | 81 | 0 | 143 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 16 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 |  | 942 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 88 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 |  | 6055 | 2622 | 8677 | 4263 | 942 | 2097 | 827 | 368 | 66 | 0 | 114 | 0 | 0 | 88.15
23:00 | 37 | 0 | 150 | 0 | 343 | 0 | 0 | 360 | 365 |  | 0 | 420 | 140 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 213 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 100 | 0 | 335 | 320 | 199 | 8 | 96 | 46 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 108 | 127 | 0 | 22 | 0 | 87 | 30 | 51 | 51 | 163 | 108 | 63 | 81 | 0 | 144 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 |  | 799 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 89 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 |  | 5737 | 2383 | 8120 | 4181 | 799 | 2124 | 473 | 369 | 66 | 0 | 108 | 0 | 0 | 88.15
24:00 | 37 | 0 | 120 | 0 | 320 | 0 | 0 | 350 | 364 |  | 0 | 420 | 135 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 25 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 80 | 0 | 315 | 305 | 185 | 8 | 95 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 100 | 150 | 0 | 22 | 0 | 88 | 30 | 51 | 51 | 163 | 149 | 63 | 81 | 0 | 130 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 |  | 410 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 8 | 89 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5543 | 2000 | 7543 | 4134 | 410 | 2065 | 399 | 369 | 66 | 0 | 100 | 0 | 0 | 88.15
KWH | 908000 | 0 | 4285000 | 0 | 7236364 | 0 | 0 | 8516630 | 7657000 |  | 0 | 8923750 | 3314676 | 292800 | 1262760 | 58978 | 0 | 0 | 0 | 0 | 704640 | 548928 | 0 | 0 | 398400 | 0 | 0 | 785160 | 45098 | 0 | 304668 | 600000 | 694800 | 743300 | 818300 | 0 | 0 | 550440 | 964000 | 2600000 | 0 | 0 | 4906013 | 0 | 2159826 | 0 |  | 0 | 27816 | 0 | 0 | 119040 | 178080 | 441744 | 445440 | 0 | 2552910 | 0 | 7986500 | 5280000 | 4584000 | 518545 | 2215470 | 971280 | 459840 | 0 | 1007856 | 0 | 0 | 0 | 455076 | 191700 | 492500 | 486790 | 2321280 | 3138160 | 745920 | 472680 | 17000 | 2065000 | 728160 | 971400 | 983088 | 3394800 | 3895000 | 1393248 | 1583040 | 0 | 4676050 | 341000 | 0 | 197460 | 7606500 | 376680 | 213081 | 0 | 348764 | 0 | 0 | 1651200 | 0 | 514080 | 141345 | 146880 | 0 | 56872 | 5618000 | 174000 | 0 | 0 | 35040 | 1648472 | 0 | 0 | 0 | 0 |  | 13976727 | 0 | 7786944 | 0 | 463680 | 0 | 0 | 0 | 0 | 0 | 105750 | 1771000 | 336700 | 27744 | 0 | 0 | 0 | 0 | 0 | 96144 | 603880 | 0 | 0 | 0 | 0 | 398880 | 258948 | 212076 | 2137745 | 0 | 6556900 | 0 | 0 | 4348973 | 0 | 0 | 0 | 1751680 | 0 | 0 | 0 | 9897945 | 0 | 0 | 0 | 89280 | 590400 | 0 | 33620 | 1327392 | 0 |  | 133148318 | 52772408 | 185920726 | 96466923 | 13976727 | 46392872 | 16202874 | 8694645 | 1514440 | 123960 | 2321280 | 227005 | 0
Fuel Cost | 1016960 | 0 | 4584950 | 0 | 5354909.36 | 0 | 0 | 6131973.6 | 5819320 |  | 0 | 7139000 | 2983208.4 | 2986560 | 13675690.8 | 605114.28 | 0 | 0 | 0 | 0 | 7821504 | 5577108.48 | 0 | 0 | 3625440 | 0 | 0 | 7529684.4 | 430234.92 | 0 | 228501 | 450000 | 0 | 0 | 0 | 0 | 0 | 143114.4 | 250640 | 3978000 | 0 | 0 | 5151313.65 | 0 | 2742979.02 | 0 |  | 0 | 294571.44 | 0 | 0 | 1132070.4 | 1666828.8 | 406404.48 | 1238323.2 | 0 | 2680555.5 | 0 | 5910010 | 4435200 | 4217280 | 508174.1 | 2946575.1 | 796449.6 | 473635.2 | 0 | 1441234.08 | 0 | 0 | 0 | 464177.52 | 143775 | 930825 | 365092.5 | 16016832 | 2573291.2 | 7093699.2 | 482133.6 | 278800 | 2808400 | 990297.6 | 1321104 | 1228860 | 4209552 | 3583400 | 2075939.52 | 2786150.4 | 0 | 7107596 | 542190 | 0 | 464031 | 5400615 | 282510 | 161941.56 | 0 | 3651559.08 | 0 | 0 | 15884544 | 0 | 5187067.2 | 1631121.3 | 1368921.6 | 0 | 532890.64 | 5280920 | 1525980 | 0 | 0 | 0 | 15198911.84 | 0 | 0 | 0 | 0 |  | 37737162.9 | 0 | 6073816.32 | 0 | 4469875.2 | 0 | 0 | 0 | 0 | 0 | 1045867.5 | 1416800 | 521885 | 297970.56 | 0 | 0 | 0 | 0 | 0 | 951825.6 | 6262235.6 | 0 | 0 | 0 | 0 | 438768 | 427264.2 | 160541.532 | 13617435.65 | 0 | 26817721 | 0 | 0 | 3827096.24 | 0 | 0 | 0 | 2785171.2 | 0 | 0 | 0 | 7225499.85 | 0 | 0 | 0 | 795484.8 | 5514336 | 0 | 0 | 0 | 0 |  | 227946646.97 | 120386757.152 | 348333404.122 | 90302804.902 | 37737162.9 | 43428587.23 | 116862787.7 | 40435156.65 | 393754.4 | 1246397.04 | 16016832 | 1909921.3 | 0
Yesterday Day Peak | 37 | 0 | 230 | 0 | 320 | 0 | 0 | 367 | 355 |  | 0 | 400 | 140 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 25 | 29 | 0 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 100 | 0 | 335 | 330 | 202 | 8 | 95 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 90 | 82 | 32 | 22 | 2.6 | 87 | 30 | 50 | 51 | 130 | 117 | 60 | 81 | 0 | 234 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 112 | 0 | 16 | 19.8 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 5.2 | 45 | 0 | 0 | 0 | 0 |  | 642 | 0 | 300 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 87 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 37 | 0 | 3.2 | 50 | 0 |  | 7925.8 | DayPeak
Yesterday Evening Peak | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 335 | 362 | 0 | 0 | 370 | 120 | 100 | 64 | 15 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 52 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 19 | 13 | 0 | 100 | 0 | 315 | 265 | 182 | 8 | 89 | 42 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 124 | 126 | 95 | 22 | 0 | 86 | 30 | 53 | 51 | 130 | 273 | 63 | 81 | 0 | 120 | 19 | 0 | 10 | 290 | 15 | 11 | 0 | 110 | 0 | 0 | 93 | 0 | 137 | 0 | 100 | 0 | 10 | 234 | 115 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 |  | 932 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 55 | 18 | 80 | 0 | 0 | 0 | 0 | 0 | 43 | 50 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 88 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 32 | 113 | 0 | 0 | 109 | 0 |  | 9589 | EvPeak
Forecast for Evening | 37 | 0 | 150 | 0 | 275 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 94 | 42 | 10 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 122 | 150 | 95 | 22 | 0 | 87 | 30 | 51 | 44 | 163 | 150 | 66 | 81 | 0 | 0 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 954 | 40 | 330 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 130 | 21 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 18 | 11 | 11 | 90 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 20 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 36 | 10 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 96 | 150 | 95 | 22 | 1.6 | 87 | 30 | 51 | 44 | 163 | 147 | 66 | 80 | 0 | 0 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 660 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 130 | 18 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 37 | 0 | 100 | 0 | 275 | 0 | 0 | 342 | 368 | 0 | 0 | 340 | 130 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 35 | 0 | 22 | 25 | 31 | 25 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12 | 0 | 80 | 0 | 315 | 265 | 182 | 8 | 30 | 42 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 19 | 80 | 151 | 49 | 22 | 0.9 | 86 | 30 | 51 | 51 | 163 | 147 | 64 | 78 | 0 | 0 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 112 | 0 | 11 | 7.3 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 653 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 88 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 25 | 0 | 1.8 | 60 | 0 | 0
199
| Minimum Generation |  | 6272 | 5:00
| Highest Generation |  | 9589 | 19:30
| Day Peak Generation |  | 7925.8 | 12:00
| Evening Peak Generation |  | 9589 | 19:30
| HVDC Max Flow |  | 942 | 22:00
| HVDC EvPeak Flow |  | 932 | 19:30
| Load factor L.F |  | 80.79%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-10
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7925.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6266 | MW
Evening Peak Generation : |  | 9589 | MW Hour : | 19:30 | Available Max Generation : |  | 14455 | MW
E.P. Demand (at gen end) : |  | 9589 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 9589 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4655 | MW
Total Gen. (MKWH) : |  | 185.9207 | System Load Factor : | 80.79% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -306 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-10
Actual : | 88.09 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 1146.22 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 133731392.132
: |  | Coal : | 40435156.65 | Oil : | 118109184.74 | Total : | 292275733.522
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3489.501 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1183.2998 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1059.6051 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 957.2323 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 865.153 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 698.1394 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 394.6423 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 179.8653 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 538.4193 |  |  | 0 | 0%
Total | 0 |  | 9365.8575 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2.
2) Siddhirganj 210 MW
3) Ghorasal Unit-2,3 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Bhola CCPP STG
| Additional Information of Machines, lines, Interruption / Forced Load shed etc. |  | a
|  | Description |  |  | Comments on Power Interruption
a) After maintenance Ashuganj 230/132 kV OA12 was switched on at 11:50.
b) Aminbazar-Manikganj 162 MW Ckt-1 was under shut down from 08:57 to 17:53 for C/M.
c) Bibiyana south dia-6 was under shut down since 09:15 for D/W.
d) Joydevpur 132/33 kV T-3,T-4 transformer tripped at 09:54 showing O/C relay due to 33 kV BOF |  |  |  |  | About 40 MW power interruption occurred under Joydevpur S/S
feeder fault and were switched on at 10:49 & 11:19 respectively |  |  |  |  | area from 09:54 to 11:19.
e) After maintenance Siddhirganj 335 MW Ckt was switched on at 11:38.
f) Kishoreganj 132/33 kV T2 transformer was shut down from 09:17 to 12:33 for D/W.
g) After maintenance Bhola 225 MW CCPP GT-1 was synchronized at 20:55.
h) Barisal-Patuakhali 132 kV Ckt is under shut down since 06:57 for D/W..
i) Saver 132/33 kV T2 transformer is under shut down since 07:28 due to CT oil leakage.
j) Sylhet 150 MW CCPP is under shut down since 05:15 due to air filter change.
k) Shahjibazar 330 MW CCPP GT-1 was under shut down since at 22:36 for maintenance work.
l) Ashuganj-Kishoreganj 132 kV Ckt-2 is under shut down since 07:24 for D/W.
m) Barapukuria 132/33 kV T-3 transformer is under shut down since 07:24 for D/W.
n) B.Baria 132/33 kV T-1 transformer is under shut down since 07:16 for D/W. |  |  |  |  | About 40 MW power interruption has been occurring under B.Baria S/S
area from 07:16 to till now.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 37 | 908000 | #1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 4285000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 275 | 7236364 | Transformer overload
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8516630 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 362 | 7657000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8923750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 292800
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3314676 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 1262760 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 58978 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 304668
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 704640
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 548928
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 785160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 45098 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 52 | 398400 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1294800 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 743300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 818300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 110 | 348764 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 137 | 514080
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2493 | 48962096
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 141345
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 178080
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 66 | 1514440 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4906013
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 105 | 2159826 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 27816 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 146880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 441744
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 445440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 119040 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35040
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 214 | 1648472 | Transformer overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 930 | 14364136
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2552910
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4584000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7986500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 5280000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 971280
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 459840
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 518545 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1007856 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 56872 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2215470
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 455076
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 191700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2321280
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 492500
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 486790 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1312 | 29580619
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3138160 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 472680
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 745920
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 17000
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 93 | 1651200 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 174000
| Mymensingh Area Total |  |  |  | 637 | 451 | 6198960
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 86 | 2065000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 728160
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3394800 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 273 | 3895000 | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 971400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 983088
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 213081
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1393248 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1583040
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 120 | 4676050
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 341000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 15 | 376680 | Low demand
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7606500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 234 | 5618000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 197460
| Sylhet Area Total |  |  |  | 1949 | 1466 | 34042507
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 932 | 13976727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 463680
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 7786944 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 105750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 32 | 89280 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1439 | 22422381
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 27744 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 18 | 336700 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 55 | 1771000 | GT-1 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1751680
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | Machine problem
| Barisal Area Total |  |  |  | 462 | 250 | 3887124
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 603880
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4348973 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 340 | 9897945 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 398880
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 258948
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212076
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 96144 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1327392
| Rajshahi Area Total |  |  |  | 2183 | 767 | 17144238
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 88 | 2137745
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6556900
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 590400
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33620
| Rangpur Area Total |  |  |  | 605 | 481 | 9318665
| Total |  |  |  | 19107 | 9589 | 185920726
| Eastern Grid Total |  |  |  | 13543 | 6652 | 133148318
| Western Grid Total |  |  |  | 5564 | 2937 | 52772408
| National Grid Total |  |  |  | 19107 | 9589 | 185920726
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-09
(a) ENTIRE EASTERN GRID : |  | 6217 | MW | (b) ENTIRE WESTERN GRID : |  | 2937 | MW
i) Dhaka area |  | 3375 | MW | i) Khulna area |  | 1103 | MW
ii) Chittagong area |  | 969 | MW | ii) Rajshahi area |  | 958 | MW
iii) Comilla area |  | 792 | MW | iii) Barisal area |  | 239 | MW
iv) Mymensingh area |  | 748 | MW | iv) Rangpur area |  | 637 | MW
v) Sylhet area |  | 333 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9154 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 18:30 | Sherpur | 86 | 19:00 | Benapol | 34 | 19:00
Munsiganj | 90 | 20:00 | Srimongal | 32 | 18:30 | Jhenida | 87 | 19:00
Sonargaon | 69 | 21:00 | Shahjibazar | 75 | 18:30 | Bottail | 96 | 19:00
Shyampur | 200 | 11:00 | Fenchuganj | 26 | 19:00 | G.K Project | 36 | 19:00
Bhulta | 175 | 1:00 | Kulawara | 33 | 19:00 | Faridpur | 130 | 19:00
Madanganj | 59 | 20:00 | Sylhet | 98 | 19:00 | Madaripur | 61 | 20:00
Shitalakhya | 108 | 16:00 | Chatak | 18 | 18:30 | Sariatpur | 40 | 19:30
Rahim steel | 20 | 20:00 | Sunamganj | 28 | 19:30 | Gopalganj | 67 | 19:30
Matuail | 93 | 12:00 | Biani Bazar | 32 | 19:00 | Bagerhat | 66 | 21:00
Ghorasal | 62 | 19:30 | Comilla (S) | 126 | 18:30 | Mongla | 42 | 8:00
Narsingdi | 111 | 20:00 | Comilla(N) | 81 | 20:00 | Satkhira | 75 | 19:00
Haripur (SBU) | 96 | 19:30 | Chandpur | 78 | 19:30 | Gallamari | 40 | 20:00
Ullon | 60 | 20:00 | Feni | 92 | 18:30 | Magura | 40 | 19:30
Hasnabad | 104 | 14:00 | Chowmuhani | 114 | 20:00 | Norail | 28 | 19:00
Magbazar | 89 | 15:00 | Ashuganj | 42 | 22:00 | Chuadanga | 66 | 19:00
Maniknagar | 84 | 19:00 | Daudkandi | 112 | 18:30 | Barisal(N) | 28 | 19:30
Bangabhaban | 28 | 13:00 | B.Baria | 103 | 19:30 | Barisal (S) | 78 | 19:00
Narinda | 84 | 13:00 | Ramganj | 54 | 19:30 | Patuakhali | 86 | 19:00
Dhanmondi | 119 | 12:00 | Chaddagram | 30 | 13:00 | Bhandaria | 38 | 21:00
Lalbag | 67 | 13:00 | PHP | 3 | 14:00 | Borhan Uddin | 27 | 21:00
Madartek | 45 | 13:00 | Madunaghat | 53 | 19:30 | Ishurdi | 45 | 18:30
Dhaka University |  |  | Hathazari | 66 | 19:00 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 79 | 19:00 | Khulshi | 165 | 16:00 | Natore | 100 | 19:00
Kalyanpur | 70 | 18:00 | Halishahar | 107 | 18:30 | Bogra | 134 | 19:00
Gulshan | 96 | 12:00 | Baraulia | 145 | 6:00 | Noagaon | 100 | 19:00
Uttara | 59 | 19:00 | Sikalbaha | 23 | 18:30 | Rajshahi | 94 | 20:00
Uttara New | 22 | 19:00 | Dohazari | 72 | 18:30 | Rajshahi New | 8 | 18:30
Kamrangirchar | 67 | 13:00 | Cox'sbazar | 91 | 19:00 | C.Nawabganj | 58 | 20:00
Savar | 106 | 18:30 | Chandraghona | 24 | 18:30 | Amnura | 28 | 19:30
Bhasantec | 106 | 14:00 | Kaptai | 3.8 | 19:00 | Pabna | 78 | 19:00
Agargaon | 43 | 13:00 | A. Khaer Stl. | 22 | 3:00 | Shahjadpur | 78 | 8:00
Satmosjid | 84 | 19:30 | Bakulia | 88 | 18:30 | Serajganj | 82 | 19:00
Tongi | 110 | 18:00 | Julda | 21 | 10:00 | Niyamatpur | 65 | 18:30
Kabirpur | 172 | 10:00 | TK chemical | 10.5 | 19:00 | Joypurhat | 43 | 19:30
Basundhara | 117 | 18:30 | Modern Steel | 15 | 18:00 | Sherpur(Bogura) | 38 | 18:30
Manikganj | 72 | 21:00 | Shahmirpur | 18.5 | 12:00 | Mohastangor | 36 | 19:00
Joydevpur | 155 | 18:30 | Khagrachhari | 18 | 18:30 | Rangpur | 117 | 19:00
New Tongi | 89 | 15:00 | Matarbari | 24.5 | 19:00 | Lalmonirhat | 47 | 19:00
Korda | 173 | 9:00 | Baroiar Hat | 20 | 18:30 | Saidpur | 92 | 19:00
Dhamrai | 56 | 13:00 | Rangamati | 10 | 18:30 | Purbasadipur | 88 | 19:30
Rajendrapur | 62 | 21:00 | Abul Khair 230 | 124 | 14:00 | Thakurgaon | 65 | 19:30
Valuka | 90 | 15:00 | BSRM | 57 | 20:00 | Palashbari | 96 | 19:00
Tangail | 160 | 19:30 | GPH Ispat | 60 | 13:00 | Barapukuria | 44 | 19:00
Mymensing | 165 | 18:30 | Goalpara | 22 | 13:00 | Panchagar | 35 | 18:30
Kishorganj | 94 | 19:00 | Central s/s | 66 | 19:00 | Joldhaka | 23 | 18:30
Netrokona | 89 | 19:00 | Noapara | 44 | 19:30 | Kurigram | 44 | 0.77083
Jamalpur | 100 | 19:00 | Jessore | 100 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-09 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 402 | 24:00 | 393 | 0.45833 | Kaliakoir | 384 | 0.125 | 369 | 0.5
Bheramara | 403 | 0.041667 | 390 | 0.79167 | Bhulta | 394 | 0.16667 | 381 | 0.5
Ashuganj(N) | 399 | 0.125 | 388 | 0.5 | Gopalganj | 410 | 0.083333 | 370 | 0.79167
Payra | 413 | 0.375 | 372 | 0.79167
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 238 | 0.041667 | Hathazari | 223 | 0.77083 | 217 | 0.5
Ishurdi | 238 | 0.083333 | 226 | 0.79167 | Megnaghat | 235 | 0.16667 | 226 | 0.5
Ashuganj | 242 | 0.041667 | 236 | 0.5 | Fenchuganj | 241 | 0.79167 | 235 | 0.375
Serajganj | 235 | 0.125 | 229 | 0.29167 | Siddhirganj | 234 | 0.16667 | 224 | 0.5
Baghabari | 246 | 0.083333 | 238 | 0.375 | Maniknagar | 231 | 0.125 | 222 | 0.5
Barapukuria | 232 | 0.041667 | 226 | 0.29167 | Old Airport | 231 | 0.20833 | 219 | 0.5
Bogra | 229 | 0.041667 | 218 | 0.29167 | Barisal | 253 | 0.083333 | 238 | 0.79167
Khulna South | 237 | 0.125 | 220 | 0.79167 | AKSML | 221 | 0.125 | 214 | 0.45833
Rampura | 230 | 0.041667 | 225 | 0.5 | BSRM | 225 | 0.125 | 219 | 0.5
Haripur | 230 | 0.041667 | 222 | 0.5 | Bibiyana | 239 | 0.8125 | 233 | 0.5
Hasnabad | 230 | 0.041667 | 220 | 0.5 | Bhulta | 233 | 0.083333 | 225 | 0.5
Shyampur | 228 | 0.125 | 219 | 0.5 | Ashuganj (S) | 238 | 0.083333 | 232 | 0.5
Aminbazar | 231 | 0.083333 | 221 | 0.5 | Kaliakoir | 234 | 0.125 | 224 | 0.5
Tongi | 230 | 0.8125 | 220 | 0.45833 | GPH | 221 | 0.125 | 215 | 0.45833
Comilla (N) | 237 | 0.29167 | 230 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 0.16667 | 127 | 0.45833 | Hathazari | 133 | 0.25 | 130 | 0.29167
Munsiganj | 134 | 0.77083 | 128 | 0.41667 | Khulshi | 130 | 0.125 | 125 | 0.5
Sonargaon | 130 | 0.041667 | 123 | 0.625 | Halishahar | 132 | 0.8125 | 125 | 0.45833
Shyampur | 135 | 0.125 | 127 | 0.5 | Baraulia | 131 | 0.79167 | 126 | 0.625
Bhulta | 126 | 0.77083 | 120 | 0.41667 | Sikalbaha | 132 | 0.79167 | 128 | 0.41667
Madanganj | 131 | 0.125 | 125 | 0.45833 | Dohazari | 129 | 0.8125 | 126 | 0.58333
Shitalakhya | 136 | 0.8125 | 123 | 0.5 | Cox'sbazar | 123 | 0.083333 | 118 | 0.77083
Rahim steal | 132 | 1:00 | 128 | 0.41667 | Chandraghona | 132 | 0.79167 | 129 | 0.375
Matuail | 132 | 0.83333 | 126 | 0.45833 | Kaptai | 133 | 0.041667 | 126 | 0.54167
Ghorasal | 140 | 0.041667 | 136 | 0.41667 | A. Khaer Stl. | 130 | 0.083333 | 126 | 0.41667
Narsinghdi | 134 | 0.29167 | 128 | 0.54167 | Bakulia | 131 | 0.8125 | 126 | 0.375
Haripur (SBU) | 133 | 0.83333 | 127 | 0.5 | Julda | 131 | 0.79167 | 126 | 0.375
Ullon | 130 | 0.25 | 124 | 0.5 | TK Chemical | 132 | 0.79167 | 126 | 0.45833
Hasnabad | 134 | 0.25 | 125 | 0.5 | Modern Steel | 131 | 0.8125 | 126 | 0.375
Magbazar | 131 | 0.20833 | 124 | 0.5 | Shahmirpur | 131 | 0.79167 | 127 | 0.41667
Maniknagar | 135 | 0.29167 | 128 | 0.5 | Khagrachhari | 131 | 0.125 | 127 | 0.54167
Bangabhaban | 135 | 0.29167 | 128 | 0.5 | Matarbari | 125 | 0.375 | 120 | 0.77083
Narinda | 135 | 0.29167 | 128 | 0.5 | Baroiar Hat | 132 | 0.041667 | 128 | 13:00
Dhanmondi | 130 | 0.25 | 124 | 0.5 | Rangamati | 131 | 0.083333 | 128 | 10:00
Lalbag | 133 | 0.25 | 122 | 0.5 | Goalpara | 137 | 0.125 | 127 | 0.33333
Madartek | 130 | 0.25 | 123 | 0.5 | Central s/s | 134 | 0.25 | 127 | 0.33333
Dhaka University |  |  |  |  | Noapara | 135 | 0.125 | 125 | 0.29167
Mirpur | 135 | 0.25 | 127 | 0.54167 | Jessore | 132 | 0.083333 | 120 | 0.79167
Kalyanpur | 133 | 0.25 | 128 | 0.70833 | Benapol | 135 | 0.125 | 123 | 0.79167
Gulshan | 130 | 0.25 | 124 | 0.5 | Jhenida | 133 | 0.16667 | 117 | 0.79167
Uttara | 132 | 0.25 | 125 | 0.54167 | Bottail | 135 | 0.16667 | 125 | 0.79167
Uttara New | 133 | 0.25 | 126 | 0.66667 | G.K Project | 139 | 0.16667 | 132 | 0.79167
Kamrangirchar | 132 | 0.25 | 125 | 0.75 | Faridpur | 137 | 0.375 | 127 | 0.79167
Savar | 132 | 0.25 | 123 | 0.5 | Madaripur | 140 | 0.375 | 128 | 0.79167
Bhasantec | 133 | 0.25 | 126 | 0.625 | Sariatpur | 142 | 0.083333 | 128 | 0.79167
Agargaon | 133 | 0.25 | 127 | 0.66667 | Gopalganj | 144 | 0.16667 | 132 | 0.79167
Satmosjid | 133 | 0.25 | 127 | 0.66667 | Bagerhat | 135 | 0.125 | 121 | 0.79167
Tongi | 138 | 0.875 | 131 | 0.625 | Mongla | 131 | 0.041667 | 120 | 0.79167
Kabirpur | 132 | 0.041667 | 125 | 0.375 | Satkhira | 134 | 0.083333 | 126 | 0.33333
Basundhara | 130 | 2:00 | 123 | 0.66667 | Gallamari | 136 | 0.125 | 126 | 0.79167
Manikganj | 138 | 0.79167 | 130 | 0.375 | Magura | 135 | 0.125 | 116 | 0.77083
Joydevpur | 140 | 0.41667 | 134 | 0.5 | Norail | 132 | 0.16667 | 114 | 0.79167
New Tongi | 137 | 0.8125 | 129 | 0.5 | Chuadanga | 129 | 0.16667 | 111 | 0.79167
Kodda | 136 | 0.79167 | 123 | 0.375 | Barisal(N) | 142 | 0.083333 | 132 | 0.79167
Dhamrai | 132 | 0.125 | 123 | 0.5 | Barisal (S) | 140 | 0.125 | 133 | 0.70833
Rajendrapur | 138 | 0.125 | 132 | 0.58333 | Patuakhali | 137 | 0.041667 | 124 | 0.79167
Valuka | 130 | 0.16667 | 114 | 0.5 | Bhandaria | 135 | 0.041667 | 125 | 0.79167
Tangail | 133 | 0.125 | 124 | 0.41667 | Ishurdi | 136 | 0.125 | 130 | 0.79167
Mymensing | 132 | 0.20833 | 117 | 0.5 | Ruppur Paromanobik | 136 | 0.041667 | 129 | 0.79167
Kishorganj | 133 | 0.125 | 123 | 0.41667 | Natore | 134 | 0.20833 | 127 | 0.29167
Netrokona | 131 | 0.20833 | 114 | 0.5 | Bogra | 137 | 0.041667 | 129 | 0.33333
Jamalpur | 138 | 0.8125 | 118 | 0.5 | Noagaon | 134 | 0.125 | 122 | 0.33333
Sherpur | 136 | 0.79167 | 117 | 0.5 | Rajshahi | 131 | 0.75 | 125 | 0.33333
Srimongal | 138 | 0.16667 | 136 | 0.75 | Rajshahi New | 130 | 0.25 | 121 | 0.29167
Shahjibazar | 136 | 0.16667 | 133 | 13:00 | C.Nawabganj | 130 | 0.75 | 119 | 0.29167
Fenchuganj | 137 | 0.54167 | 135 | 0.083333 | Amnura | 131 | 0.75 | 120 | 0.29167
Khulawara | 137 | 0.33333 | 135 | 0.79167 | Pabna | 135 | 0.083333 | 127 | 0.33333
Sylhet | 136 | 0.041667 | 134 | 0.70833 | Shahjadpur | 136 | 0.041667 | 127 | 0.375
Chatak | 135 | 0.041667 | 133 | 0.70833 | Serajganj | 134 | 0.041667 | 125 | 0.8125
Sunamganj | 136 | 0.25 | 132 | 0.77083 | Niyamatpur | 131 | 0.041667 | 119 | 0.33333
Biani Bazar |  |  |  |  | Joypurhat | 134 | 0.041667 | 121 | 0.33333
Comilla(s) | 132 | 0 | 127 | 0.41667 | Sherpur(Bogura) | 137 | 0.20833 | 127 | 0.29167
Comilla(n) | 138 | 0.29167 | 135 | 0.8125 | Mohastangor | 135 | 0.125 | 126 | 0.29167
Chandpur | 135 | 0.29167 | 130 | 0.77083 | Rangpur | 131 | 0.083333 | 120 | 0.33333
Feni | 132 | 0.41667 | 128 | 0.79167 | Lalmonirhat | 128 | 0.25 | 115 | 0.33333
Chowmuhani | 132 | 0.29167 | 125 | 0.77083 | Saidpur | 130 | 0.125 | 120 | 0.33333
Ashuganj | 138 | 0.20833 | 135 | 0.375 | Purbasadipur | 128 | 0.16667 | 116 | 0.33333
Daudkandi | 132 | 0.29167 | 127 | 0.5 | Thakurgaon | 125 | 0.16667 | 112 | 0.33333
B.Baria | 135 | 0.33333 | 131 | 0.58333 | Palashbari | 131 | 0.625 | 117 | 0.33333
Ramganj | 128 | 0.45833 | 123 | 0.875 | Barapukuria | 132 | 0.041667 | 126 | 0.29167
Chaddagram | 133 | 0.375 | 128 | 0.5 | Panchagar | 124 | 0.20833 | 112 | 0.29167
PHP | 131 | 0.875 | 127 | 0.625 | Joldhaka | 131 | 0.20833 | 118 | 0.33333
Madanhat | 134 | 0.79167 | 129 | 0.45833 | Kurigram | 128 | 0.041667 | 118 | 0.33333

## L-Curve
Date | 2020-03-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 254 | 5543 | 2000 | 7543 |  |  |  | QF-LDC-12
0:30 | 254 | 5376 | 1930 | 7306 | Date: | 2020-03-09
1:00 | 254 | 5209 | 1860 | 7069
1:30 | 257 | 5163.5 | 1803 | 6966.5
2:00 | 260 | 5118 | 1746 | 6864
2:30 | 237.5 | 4980.5 | 1707 | 6687.5 | [5 empty] | Gen. at Eve. Peak | 9589 | 9589 MW (19:30 )
3:00 | 215 | 4843 | 1668 | 6511 | [6 empty] | 19:30
3:30 | 203.5 | 4783.5 | 1661 | 6444.5 | [5 empty] | Gen. at Day Peak | 7925.8 | 7925.8 MW (12:00 )
4:00 | 192 | 4724 | 1654 | 6378 | [6 empty] | 12:00
4:30 | 209.5 | 4686.5 | 1638.5 | 6325 | [5 empty] | Highest Generation | 9589
5:00 | 227 | 4649 | 1623 | 6272 | [6 empty] | 19:30
5:30 | 266.5 | 4815 | 1646.5 | 6461.5
6:00 | 306 | 4981 | 1670 | 6651
6:30 | 301 | 5073.55 | 1825.6 | 6899.15
7:00 | 296 | 5166.1 | 1981.2 | 7147.3
7:30 | 262 | 5001.2 | 2074.55 | 7075.75
8:00 | 228 | 4836.3 | 2167.9 | 7004.2
8:30 | 130.5 | 5026.3 | 2187.65 | 7213.95
9:00 | 33 | 5216.3 | 2207.4 | 7423.7
9:30 | 18.5 | 5314.95 | 2190.65 | 7505.6
10:00 | 4 | 5413.6 | 2173.9 | 7587.5
10:30 | 19 | 5410.7 | 2199.45 | 7610.15
11:00 | 34 | 5407.8 | 2225 | 7632.8
11:30 | 69 | 5542.2 | 2237.1 | 7779.3
12:00 | 104 | 5676.6 | 2249.2 | 7925.8
12:30 | 92 | 5670.4 | 2291.1 | 7961.5
13:00 | 80 | 5664.2 | 2333 | 7997.2
13:30 | 85 | 5573.5 | 2298.6 | 7872.1
14:00 | 90 | 5482.8 | 2264.2 | 7747
14:30 | 144 | 5576.15 | 2257.45 | 7833.6
15:00 | 198 | 5669.5 | 2250.7 | 7920.2
15:30 | 140 | 5607.5 | 2176.6 | 7784.1
16:00 | 82 | 5545.5 | 2102.5 | 7648
16:30 | 76 | 5426.95 | 2055.2 | 7482.15
17:00 | 70 | 5308.4 | 2007.9 | 7316.3
17:30 | 60 | 5483.7 | 2081.55 | 7565.25
18:00 | 50 | 5659 | 2155.2 | 7814.2
18:30 | 145 | 6147.5 | 2523.6 | 8671.1
19:00 | 240 | 6636 | 2892 | 9528
19:30 | 205 | 6652 | 2937 | 9589
20:00 | 152 | 6506 | 2988 | 9494 |  |  |  | Executive Engineer
20:30 | 120 | 6456 | 2984 | 9440 |  |  |  | Network Operation Division
21:00 | 88 | 6406 | 2980 | 9386
21:30 | 91 | 6230.5 | 2801 | 9031.5
22:00 | 94 | 6055 | 2622 | 8677 |  |  |  |  | Page 6 of 7
22:30 | 88 | 5896 | 2502.5 | 8398.5
23:00 | 82 | 5737 | 2383 | 8120
23:30 | 168 | 5640 | 2191.5 | 7831.5
24:00 | 254 | 5543 | 2000 | 7543
9589 MW (19:30 )
7925.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-09 |  | Energy | 185920726
[10 empty] | 2020-03-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4134 | 410 | 2065 | 473 | 369 | 66 | 0 | 0 | 100
0:30 | 4055.5 | 330.5 | 2076 | 350.5 | 369.5 | 66 | 0 | 0 | 95 | Date: | 2020-03-09
1:00 | 3977 | 251 | 2087 | 228 | 370 | 66 | 0 | 0 | 90
1:30 | 3934.5 | 251 | 2061.5 | 194 | 370 | 65.5 | 0 | 0 | 90 | [7 empty] | Total Energy | 185.9207 | Total Energy Gen 185.921 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.921 MKWHr
2:00 | 3892 | 251 | 2036 | 160 | 370 | 65 | 0 | 0 | 90 | [7 empty] | Energy not Served | 0
2:30 | 3836 | 251.5 | 1928.5 | 147.5 | 370 | 65 | 0 | 0 | 89 | [7 empty] | Energy Requirement | 185.9207
3:00 | 3780 | 252 | 1821 | 135 | 370 | 65 | 0 | 0 | 88
3:30 | 3774.5 | 253.5 | 1755.5 | 137.5 | 370.5 | 65 | 0 | 0 | 88 | [6 empty] | Shortage
4:00 | 3769 | 255 | 1690 | 140 | 371 | 65 | 0 | 0 | 88
4:30 | 3731 | 255 | 1691 | 140 | 355.5 | 65.5 | 0 | 0 | 87
5:00 | 3693 | 255 | 1692 | 140 | 340 | 66 | 0 | 0 | 86
5:30 | 3784.5 | 255 | 1778.5 | 153.5 | 340 | 66 | 0 | 0 | 84
6:00 | 3876 | 255 | 1865 | 167 | 340 | 66 | 0 | 0 | 82
6:30 | 3890.5 | 388 | 1921.5 | 208.5 | 340 | 66 | 0 | 0 | 83 |  |  |  |  | Coal
7:00 | 3905 | 521 | 1978 | 250 | 340 | 66 | 0 | 0 | 84
7:30 | 3808.5 | 581.5 | 1911 | 281.5 | 340 | 66 | 0 | 0 | 80 |  |  |  | Oil |  |  |  | ,
8:00 | 3712 | 642 | 1844 | 313 | 340 | 66 | 0 | 0 | 76
8:30 | 3865 | 641 | 1850.5 | 355 | 340 | 66 | 0 | 0 | 80
9:00 | 4018 | 640 | 1857 | 397 | 340 | 66 | 0 | 0 | 84
9:30 | 4027.5 | 640.5 | 1877.5 | 442.5 | 340.5 | 66 | 0 | 0 | 86
10:00 | 4037 | 641 | 1898 | 488 | 341 | 66 | 0 | 0 | 88
10:30 | 4030 | 641 | 1900 | 498.5 | 356.5 | 66 | 0 | 0 | 89
11:00 | 4023 | 641 | 1902 | 509 | 372 | 66 | 0 | 0 | 90
11:30 | 4059 | 641.5 | 1960.5 | 562 | 369.5 | 66.5 | 0 | 0 | 90
12:00 | 4095 | 642 | 2019 | 615 | 367 | 67 | 0 | 0 | 90
12:30 | 4074.5 | 642 | 2016.5 | 670.5 | 369.5 | 66.5 | 0 | 0 | 92
13:00 | 4054 | 642 | 2014 | 726 | 372 | 66 | 0 | 0 | 94
13:30 | 4054 | 642 | 2014 | 726 | 372 | 66 | 0 | 0 | 94
14:00 | 4054 | 642 | 2014 | 726 | 372 | 66 | 0 | 0 | 94
14:30 | 4072.5 | 641.5 | 1946.5 | 740.5 | 371.5 | 66 | 0 | 0 | 95
15:00 | 4091 | 641 | 1879 | 755 | 371 | 66 | 0 | 0 | 96
15:30 | 3992 | 641 | 1880.5 | 723.5 | 370.5 | 66 | 1 | 0 | 92
16:00 | 3893 | 641 | 1882 | 692 | 370 | 66 | 2 | 0 | 88
16:30 | 3882 | 641.5 | 1694.5 | 722 | 370.5 | 66 | 5.5 | 0 | 90
17:00 | 3871 | 642 | 1507 | 752 | 371 | 66 | 9 | 0 | 92
17:30 | 3961 | 642 | 1566.5 | 848 | 370 | 66 | 4.5 | 0 | 104
18:00 | 4051 | 642 | 1626 | 944 | 369 | 66 | 0 | 0 | 116
18:30 | 4036.5 | 787 | 1827 | 1444.5 | 369 | 66 | 21 | 0 | 120
19:00 | 4022 | 932 | 2028 | 1945 | 369 | 66 | 42 | 0 | 124
19:30 | 3970 | 932 | 1950 | 2136 | 368 | 66 | 43 | 0 | 124
20:00 | 4022 | 932 | 1967 | 1969 | 369 | 66 | 43 | 0 | 126
20:30 | 4106.5 | 936 | 2024 | 1796 | 369 | 66 | 21.5 | 0 | 121
21:00 | 4191 | 940 | 2081 | 1623 | 369 | 66 | 0 | 0 | 116
21:30 | 4227 | 941 | 2089 | 1225 | 368.5 | 66 | 0 | 0 | 115
22:00 | 4263 | 942 | 2097 | 827 | 368 | 66 | 0 | 0 | 114
22:30 | 4222 | 870.5 | 2110.5 | 650 | 368.5 | 66 | 0 | 0 | 111
23:00 | 4181 | 799 | 2124 | 473 | 369 | 66 | 0 | 0 | 108
23:30 | 4157.5 | 604.5 | 2094.5 | 473 | 369 | 66 | 0 | 0 | 104 | Max Temp. in Dhaka |  | 29.4° C
24:00 | 4134 | 410 | 2065 | 473 | 369 | 66 | 0 | 0 | 100
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 185.921 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 185.921 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 26 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 550440
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 964000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2.4 | 7.5 | 13.5 | 17.2 | 19.2 | 19.8 | 18.7 | 17.1 | 13.4 | 8.5 | 3.3 | [9 empty] | 141345
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 204 | 203 | 204 | 214 | 207 | 202 | 203 | 204 | 202 | 204 | 204 | 202 | 203 | 204 | 204 | 211 | 214 |  | 214 | 203 | 204 | 204 | 203 | 213 | 204 | 4906013
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 80 | 80 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 110 | 105 | 116 | 115 | 70 | 70 |  | 104 | 105 | 104 | 104 | 104 | 104 | 104 | 2159826
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP | [15 empty] | 2 | 9 | 0 |  | 0 | [6 empty] | 27816
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 8 | 15 | 15 |  |  |  |  | 56 | 110 | 145 | 95 |  |  | 0 | 348764
19 | Ashuganj 195MW PP (APSCL-United) | 92 | 92 | 92 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 518545
20 | Ghorasal TPP (Unit-1&2) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 908000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 170 | 170 | 170 | 170 | 220 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 228 | 130 | 100 | 100 |  | 100 | 100 | 100 | 146 | 150 | 150 | 120 | 4285000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 282 | 293 | 272 | 293 | 285 | 296 | 283 | 275 | 314 | 300 | 300 | 320 | 300 | 300 | 300 | 277 | 293 | 313 |  | 275 | 275 | 275 | 320 | 319 | 343 | 320 | 7236364
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 140 | 140 | 140 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 2552910
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 0 | 46 | 46 | 42 | 42 | 46 | 42 | 46 | 46 | 42 | 42 |  | 42 | 42 | 46 | 46 | 46 | 46 | 46 | 971280
33 | Ashuganj 225 MW CCPP | 196 | 191 | 183 | 198 | 195 | 178 | 178 | 165 | 184 | 178 | 182 | 202 | 185 | 183 | 182 | 173 | 183 | 203 |  | 220 | 182 | 183 | 184 | 182 | 199 | 185 | 4584000
34 | Ashuganj 450 MW CCPP(South) | 0 | 80 | 75 | 75 | 10 | 75 | 95 | 105 | 250 | 360 | 310 | 330 | 310 | 280 | 280 | 285 | 280 | 310 |  | 265 | 265 | 265 | 300 | 305 | 320 | 305 | 5280000
| Ashuganj 450 MW CCPP(North) | 335 | 325 | 325 | 340 | 340 | 345 | 330 | 320 | 320 | 315 | 315 | 335 | 310 | 285 | 315 | 315 | 275 | 310 |  | 295 | 315 | 315 | 310 | 315 | 335 | 315 | 7986500
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 50 | 49 | 50 | 51 | 51 | 10 | 459840
36 | Chandpur 150 MW CCPP | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 94 | 90 | 85 | 96 | 95 | 85 | 97 | 90 | 96 | 95 | 96 |  | 85 | 89 | 90 | 86 | 96 | 96 | 95 | 2215470
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 352 | 352 | 352 | 355 | 351 | 371 | 341 | 337 | 340 | 348 | 340 | 367 | 348 | 340 | 352 | 344 | 344 | 372 |  | 351 | 335 | 338 | 344 | 337 | 360 | 350 | 8516630
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 350 | 350 | 380 | 380 | 380 | 350 | 380 | 380 | 400 | 400 | 370 | 370 | 350 | 320 | 340 |  | 370 | 370 | 370 | 400 | 400 | 420 | 420 | 8923750
41 | Haripur 360MW CCPP(HPL) | 310 | 310 | 310 | 309 | 311 | 338 | 339 | 311 | 316 | 316 | 316 | 355 | 355 | 245 | 255 | 292 | 279 | 277 |  | 359 | 362 | 361 | 362 | 363 | 365 | 364 | 7657000
42 | RPCL 210MW CCPP | 167 | 168 | 188 | 189 | 189 | 204 | 205 |  | 88 | 84 | 83 | 82 | 86 | 66 | 128 | 144 | 157 | 144 |  | 145 | 126 | 126 | 126 | 127 | 127 | 150 | 3138160
43
44 | Fenchugonj CCPP Phase-1 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 87 | 87 | 87 | 87 | 89 | 87 | 89 | 89 | 87 |  | 86 | 86 | 88 | 87 | 87 | 87 | 88 | 2065000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728160
46 | Shajibazar 330 MW CCPP | 117 | 118 | 118 | 117 | 116 | 118 | 116 | 118 | 118 | 119 | 116 | 117 | 119 | 146 | 272 | 274 | 280 | 286 |  | 271 | 273 | 271 | 270 | 282 | 108 | 149 | 3895000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 45 | 45 | 64 | 65 | 63 | 62 | 61 | 60 | 60 | 60 | 60 | 60 | 45 | 45 | 61 |  | 63 | 63 | 63 | 64 | 64 | 63 | 63 | 1393248
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 20 | 20 | 10 | 10 | 77 | 78 | 81 | 81 | 81 | 79 | 81 | 81 | 81 | 81 | 81 | 20 | 20 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1583040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 224 | 224 | 224 | 227 | 226 | 226 | 226 | 225 | 227 | 227 | 234 | 234 | 233 | 234 | 134 | 103 | 145 | 146 |  | 146 | 120 | 120 | 146 | 143 | 144 | 130 | 4676050
51 | Sylhet 20 MW GTPP | 19 | 19 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 341000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 197460
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 213081
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 5 | 5 | 5 | 15 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 47 | 53 | 50 | 11 | 11 |  | 53 | 53 | 53 | 53 | 53 | 51 | 51 | 971400
56 | Shahjahanulla 25 MW PP | 24 | 23 |  |  |  |  | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 15 | 15 | 15 | 15 |  | 15 | 15 | 24 | 24 | 24 | 24 | 24 | 376680
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 305 | 310 | 310 | 320 | 305 | 295 | 300 | 310 | 300 | 325 | 310 | 305 | 310 | 300 | 300 | 310 |  | 300 | 290 | 280 | 300 | 290 | 310 | 305 | 7606500
58 | Nababganj 55 MW PP (Southern power )
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 441744
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | [5 empty] | 22 |  |  | 19 |  |  | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 304668
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 472680
63 | Impoprt (Tripura) | 90 | 90 | 88 | 88 | 86 | 82 | 84 | 76 | 84 | 88 | 90 | 90 | 94 | 100 | 96 | 88 | 92 | 116 |  | 124 | 124 | 126 | 116 | 114 | 108 | 100 | 2321280
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 10 | 10 | 10 | 16 | 38 | 9 | 3 | 3 | 2 | 2 | 6 | 2 | 2 | 2 | 8 | 7 |  | 13 | 13 | 27 | 34 | 39 | 40 | 40 | 445440
65 | Feni 22MW PP (Doreen) | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 455076
66 | Feni 11 MW PP (Doreen) | 8 | 8 |  |  |  |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 191700
67 | Jangalia 33MW PP (Summit) | 33 | 20 | 8 | 8 | 8 | 28 | 33 | 33 | 33 | 33 | 33 | [6 empty] | 13 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 492500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 486790
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 28 | 28 | 32 | 32 | 28 | 32 | 31 | 29 | 31 | 30 | 30 | 30 | 32 | 15 |  | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 694800
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 743300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
Chowmuhani 113 MW
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 2 | 16 | 16 | 16 | 16 | 35 | 40 | 40 | 40 | 40 | 40 |  | 85 | 100 | 100 | 100 | 50 |  | 0 | 704640
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | 43 | 8 | [7 empty] | 5 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 |  | 95 | 95 | 95 | 95 | 11 | 0 | 0 | 745920
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [6 empty] | 0.5 | 1.8 | 3.2 | 4.3 | 5.1 | 5.2 | 5 | 4.3 | 3.3 | 2 | 0.8 | [9 empty] | 35040
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [5 empty] | 1 | 32 | 48 | 48 | 48 | 46 | 48 | 75 | 78 | 79 | 79 | 85 | 96 |  | 86 | 64 | 74 | 81 | 94 | 48 | 48 | 1262760
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 135 | 135 | 135 | 140 | 140 | 135 | 130 | 125 | 135 | 135 | 135 | 140 | 120 | 130 | 130 | 130 | 140 | 150 |  | 130 | 120 | 125 | 130 | 125 | 140 | 135 | 3314676
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 7 | 7 | 7 | 7 | 7 | 8 |  | 65 | 100 | 100 |  |  |  | 0 | 292800
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 5 | 5 | 5 | 10 | 48 | 48 | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 983088
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 |  | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 1007856
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 5 | 7 | 16 | 32 | 32 | 32 | 32 | 32 | 40 |  | 85 | 102 | 102 | 102 |  |  | 0 | 548928
95 | Patenga 50MW PP (Baraka) | [19 empty] | 38 | 50 | 50 | 50 | 36 |  | 0 | 178080
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 83 | 50 |  |  |  |  | 0 | 119040
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [16 empty] | 32 | 45 |  | 50 | 52 | 56 | 65 | 72 | 72 | 72 | 398400
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 28 | 15 | 15 |  |  |  | 0 | 58978
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 35 | 17 |  |  |  |  | 0 | 45098
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 163 | 163 | 100 | 130 |  | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 3394800
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.2 | 0 | 1.6 | 2.1 | 2.5 | 2.6 | 2.5 | 2.4 | 1.8 | 1 | 0.3 | [9 empty] | 17000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 |  | 0 | 785160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [5 empty] | 2 | 53 |  | 52 | 112 | 112 | 112 | 112 | 100 | 101 | 101 | 110 | 110 |  | 93 | 93 | 110 | 110 | 110 | 40 | 40 | 1651200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 14 | 16 | 30 | 18 | 16 | 15 | 16 | 15 | 15 | 15 | 16 |  | 100 | 137 | 134 | 35 | 16 | 16 | 0 | 514080
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 5 |  | 100 | 100 | 20 |  |  |  | 0 | 146880
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [19 empty] | 28 | 10 |  |  |  |  | 0 | 56872
118 | Bibiyana-III 400 MW CCPP | 234 | 234 | 234 | 233 | 233 | 232 | 232 | 234 | 234 | 234 | 234 | 234 | 234 | 235 | 233 | 233 | 233 | 233 |  | 233 | 234 | 233 | 233 | 234 | 233 | 234 | 5618000
| Jamalpur 115 MW PP (United) | [17 empty] | 9 |  | 63 | 115 | 35 |  |  |  | 0 | 174000
| Anwara 300 MW PP (United) | [9 empty] | 10 | 16 | 45 | 45 | 52 | 51 | 105 | 108 | 180 |  | 209 | 214 | 216 | 216 | 162 | 126 | 104 | 1648472
120 | Eastern Zone Total | 5209 | 5118 | 4843 | 4724 | 4649 | 4981 | 5166.1 | 4836.3 | 5216.3 | 5413.6 | 5407.8 | 5676.6 | 5664.2 | 5482.8 | 5669.5 | 5545.5 | 5308.4 | 5659 |  | 6636 | 6652 | 6506 | 6406 | 6055 | 5737 | 5543 | 133148318
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [11 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 16 |  | 102 | 115 | 115 | 115 | 16 |  | 0 | 463680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [19 empty] | 58 | 80 | 80 | 80 |  | 16 | 0 | 27744
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 98 | 98 | 52 | 21 | 20 | 41 | 61 | 96 | 94 | 93 | 90 | 91 | 91 | 94 | 93 | 51 | 22 | 83 |  | 97 | 97 | 97 | 98 | 98 | 43 | 43 | 1751680
| Bhola 225 MW CCPP | 154 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 65 | 65 | 65 |  | 65 | 55 | 65 | 80 | 128 | 115 | 130 | 1771000
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 16 | 14 | 15 | 15 | 11 | 5 | 5 | 11 | 12 | 12 | 14 | 13 | 13 | 12 | 12 | 18 |  | 21 | 18 | 18 | 22 | 21 | 20 | 17 | 336700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 32 | 40 | 40 | 40 |  |  |  | 105750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [19 empty] | 32 | 32 | 32 |  |  | 15 | 0 | 89280
146 | Bheramara HVDC | 251 | 251 | 252 | 255 | 255 | 255 | 521 | 642 | 640 | 641 | 641 | 642 | 642 | 643 | 641 | 641 | 642 | 642 |  | 932 | 932 | 932 | 940 | 942 | 799 | 410 | 13976727
147 | Bheramara 410 MW CCPP | 315 | 315 | 315 | 315 | 315 | 315 | 330 | 355 | 350 | 315 | 320 | 300 | 290 | 280 | 260 | 255 | 260 | 295 |  | 315 | 320 | 345 | 350 | 350 | 350 | 350 | 7786944
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 90 | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 91 | 92 | 87 | 92 | 90 | 91 | 90 | 90 | 89 |  | 89 | 88 | 89 | 89 | 88 | 89 | 89 | 2137745
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 280 | 280 | 281 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6556900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 200 | 180 | 180 | 140 | 140 | 140 |  | 145 | 180 | 180 | 180 | 180 | 180 | 214 | 4348973
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 434 | 434 | 418 | 435 | 435 | 437 | 434 | 356 | 397 | 392 | 411 | 421 | 425 | 378 | 387 | 430 | 356 | 350 |  | 400 | 340 | 355 | 405 | 392 | 434 | 425 | 9897945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 19 | 19 | 3 | 3 | 3 | 15 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 17 | 19 | 20 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 398880
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 258948
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 212076
165 | Amnura 50 MW PP(Sinha) | [5 empty] | 12 | 12 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 12 | 50 |  | 50 | 50 | 50 | 50 | 12 |  |  | 603880
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 42 | 43 | 43 |  |  |  | 0 | 96144
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | 15 | [5 empty] | 6 | 35 | 35 | 35 | 35 | 50 | 100 | 109 | 109 | 70 | 70 | 86 |  | 109 | 109 | 109 | 109 | 70 |  | 0 | 1327392
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 32 | 38 | 35 | 35 | 37 | 36 | 35 | 35 |  |  |  |  | 80 | 113 | 113 | 97 |  |  | 0 | 590400
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1.9 | 3.4 | 4.9 | 3 | 3.2 | 3 | 2.2 | 2.7 | 2.5 | 1.9 | 0.2 | [8 empty] | 33620
178
178