## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-03-12 | Thursday
|  | Date (day): | 2020-03-12 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11852.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14606 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-11 | 2020-03-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 341 | 320 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 371 | 338 | 412 | 412 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 352 | 360 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 130 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 30 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 93 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 6 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 50 | 72 | 70 | 70 |  | 38 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 53 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 16 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 150 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 15 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2195 | 2862 | 3552 | 4154 | 991 | 660
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15.1 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 67 | 65 | 70 | 70 | 160 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 114 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 19 | 20 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 23 | 10 | 15
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 60 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 65 | 178 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 632.2 | 922 | 1499 | 1631 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 110 | 110 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 310 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 265 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 20 | 46 | 46
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 20 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 86 | 90 | 94 |  | 69 | STG Under S/D
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 130 | 87 | 122
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1340 | 1322 | 1640 | 2343 | 520 | 69
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 159 | 163 | 163 | 39 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 154 | 100 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 381.3 | 545 | 496.6 | 595 | 39 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 87 | 88 | 87 | 87
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 154 | 147 | 147 | 150 |  | 180 | GT-1 under maintenance.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 51 | 48 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 62 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 80 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 295 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 233 | 235 | 235 | 235 |  | 165 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1239 | 1200 | 1279 | 1283 | 0 | 435
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 650 | 940 | 658 | 953
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 330 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 50 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1052 | 1475 | 1353 | 2198 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 22 | 18 | 21 |  | 12 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 126 | 130 | 130 |  | 64 | ST under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 51 | 95 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 194 | 291 | 307 | 386 | 0 | 76
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 214 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 390 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 18 | 18
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 12 | 12 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 51 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 0 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 795 | 852 | 1235 | 1499 | 611 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 92 | 91 | 90 | 90
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 114 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.1 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 429.1 | 485 | 491 | 517 | 0 | 85
| Total |  |  |  |  | 19630 | 19107 | 8257.6 | 9954 | 11852.6 | 14606 | 2571 | 1433
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7860.2331 | 9475 | 11282.2368 | 13903.1394
A. |  | 2020-03-11 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 9954 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6407 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9954 | MW
3 | Day peak Generation : |  |  | 8257.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9475 | MW
4 | Evening peak Generation : |  |  | 9954 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 192.7532 | MKWHr | By Solar | 0.2155 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 143.3602 | MKWHr |  | By Oil: | 22.2351 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.8242 | MKWHr |  | By Hydro: | 1.4867 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2571 | MW | Dhaka | 3477 | 3477 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1433 | MW | Chittagong | 980 | 980 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4004 | MW | Khulna | 1134 | 1134 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1136.35 | MMCFD |  |  | Rajshahi | 998 | 998 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 130489104.562 | ii) Oil : | Taka | 172190280.76 | Comilla | 839 | 839 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 41033503.35 | Total | Taka | 343712888.672 | Mymensingh | 782 | 782 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.623 | MKWHr. | Sylhet | 334 | 334 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -170 | MW (E to W) at | 19:30 | hrs | Barisal | 270 | 270 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -320 | MW at | 1:00 | hrs | Rangpur | 661 | 661 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0° C |  |  | Total | 9475 | 9475 |  | 0
B. |  | 2020-03-12 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14606 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8600 | MW
4 | Reserve(Generation end) |  |  |  | 4306 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 199.4533 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6769 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.2393 | MKWHr. | ii) HVDC Flow at Peak Time |  | 940 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3923 | MKWHr. | iii) Maximum HVDC Flow : |  | 940 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.09 |  | (b) Today: | 87.73 |  | (c) Rule Curve: |  | 91.24
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-03-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 180 | 0 | 314 | 0 | 0 | 339 | 310 |  | 0 | 400 | 130 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 72 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 120 | 0 | 295 | 295 | 223 | 8 | 50 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 92 | 151 | 0 | 22 | 0 | 86 | 0 | 53 | 51 | 163 | 147 | 54 | 81 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 |  | 262 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 5 | 92 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5440 | 1837 | 7277 | 3882 | 262 | 2037 | 565 | 372 | 67 | 0 | 92 | 0 | 0 | 88.14
2:00 | 0 | 0 | 180 | 0 | 316 | 0 | 0 | 336 | 308 |  | 0 | 400 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 206 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 110 | 0 | 300 | 305 | 219 | 8 | 50 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 88 | 151 | 0 | 22 | 0 | 86 | 0 | 53 | 51 | 163 | 152 | 54 | 81 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 263 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 5 | 91 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5086 | 1834 | 6920 | 3886 | 263 | 2020 | 226 | 371 | 66 | 0 | 88 | 0 | 0 | 88.13
3:00 | 0 | 0 | 180 | 0 | 314 | 0 | 0 | 337 | 309 |  | 0 | 400 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 212 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 110 | 0 | 295 | 295 | 225 | 8 | 50 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 8 | 19 | 88 | 151 | 0 | 22 | 0 | 86 | 0 | 11 | 5 | 163 | 150 | 45 | 40 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 262 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4849 | 1767 | 6616 | 3847 | 262 | 1829 | 154 | 370 | 66 | 0 | 88 | 0 | 0 | 88.12
4:00 | 0 | 0 | 150 | 0 | 321 | 0 | 0 | 346 | 309 |  | 0 | 360 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 110 | 0 | 305 | 305 | 225 | 8 | 50 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 19 | 86 | 164 | 0 | 22 | 0 | 86 | 0 | 11 | 5 | 163 | 151 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 262 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4769 | 1713 | 6482 | 3828 | 262 | 1707 | 164 | 370 | 65 | 0 | 86 | 0 | 0 | 88.11
5:00 | 0 | 0 | 150 | 0 | 314 | 0 | 0 | 338 | 310 |  | 0 | 360 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 24 | 40 | 110 | 0 | 0 | 203 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 110 | 0 | 290 | 295 | 224 | 8 | 50 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 84 | 164 | 0 | 22 | 0 | 86 | 0 | 11 | 5 | 163 | 149 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 262 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4722 | 1685 | 6407 | 3778 | 262 | 1685 | 164 | 370 | 64 | 0 | 84 | 0 | 0 | 88.1
6:00 | 0 | 0 | 150 | 0 | 350 | 0 | 0 | 360 | 309 |  | 0 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 216 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 42 | 0 | 110 | 0 | 360 | 345 | 225 | 8 | 50 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 84 | 164 | 0 | 22 | 0 | 86 | 0 | 11 | 5 | 163 | 156 | 45 | 10 | 0 | 0 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 262 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 5 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4934 | 1782 | 6716 | 4022 | 262 | 1738 | 174 | 370 | 66 | 0 | 84 | 0 | 0 | 88.09
7:00 | 0 | 0 | 200 | 0 | 334 | 0 | 0 | 375 | 365 |  | 0 | 400 | 140 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 215 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 110 | 0 | 335 | 325 | 224 | 8 | 51 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 0 | 21 | 84 | 164 | 2 | 22 | 0.2 | 86 | 0 | 11 | 9 | 163 | 156 | 63 | 10 | 0 | 0 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 2 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 |  | 650 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 5 | 12 | 8 | 90 | 0 | 280 | 0 | 0 | 140 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 |  | 5093.1 | 2201.4 | 7294.5 | 4015 | 650 | 1848 | 257 | 370 | 67 | 0 | 84 | 3.5 | 0 | 88.26
8:00 | 0 | 0 | 200 | 0 | 312 | 0 | 0 | 351 | 363 |  | 0 | 400 | 130 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 202 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 0 | 110 | 0 | 300 | 305 | 183 | 8 | 95 | 10 | 10 | 0 | 34 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 80 | 164 | 32 | 22 | 0.8 | 86 | 0 | 45 | 44 | 163 | 146 | 63 | 78 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 7.6 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 1.9 | 16 | 0 | 0 | 0 | 0 |  | 650 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 93 | 0 | 280 | 0 | 0 | 155 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 20 | 0 | 1.6 | 33 | 0 |  | 5306.3 | 2325.6 | 7631.9 | 3915 | 650 | 2018 | 517 | 373 | 67 | 0 | 80 | 11.9 | 0 | 87.87
9:00 | 0 | 0 | 200 | 0 | 312 | 0 | 0 | 337 | 363 |  | 0 | 400 | 130 | 7 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 203 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 110 | 0 | 305 | 300 | 184 | 8 | 88 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 84 | 162 | 32 | 22 | 1.4 | 89 | 0 | 45 | 48 | 163 | 147 | 61 | 78 | 0 | 0 | 19 | 0 | 8 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 168 | 0 | 8 | 12.9 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 3.3 | 16 | 0 | 0 | 0 | 0 |  | 650 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 92 | 0 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 44 | 0 | 3.5 | 70 | 0 |  | 5360.6 | 2405.5 | 7766.1 | 3909 | 650 | 2004 | 659 | 372 | 67 | 0 | 84 | 21.1 | 0 | 87.86
10:00 | 0 | 0 | 200 | 0 | 314 | 0 | 0 | 340 | 330 |  | 0 | 370 | 140 | 7 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 106 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 110 | 0 | 305 | 305 | 185 | 8 | 92 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 21 | 88 | 160 | 32 | 22 | 1.9 | 88 | 0 | 45 | 48 | 130 | 147 | 61 | 75 | 0 | 0 | 0 | 0 | 8 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 14 | 17 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 4.2 | 50 | 0 | 0 | 0 | 0 |  | 650 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 70 | 0 | 4.9 | 70 | 0 |  | 5334.1 | 2424.9 | 7759 | 3903 | 650 | 1918 | 754 | 351 | 67 | 0 | 88 | 28 | 0 | 87.85
11:00 | 0 | 0 | 200 | 0 | 326 | 0 | 0 | 350 | 270 |  | 0 | 340 | 140 | 7 | 30 | 45 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 207 | 0 | 136 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 110 | 0 | 330 | 330 | 216 | 8 | 95 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 92 | 157 | 32 | 22 | 2.1 | 87 | 0 | 48 | 51 | 110 | 154 | 59 | 75 | 0 | 0 | 0 | 0 | 8 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 15 | 19 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 9.1 | 48 | 0 | 0 | 0 | 0 |  | 650 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 6.2 | 70 | 0 |  | 5438.2 | 2444.2 | 7882.4 | 4105 | 650 | 1783 | 798 | 351 | 67 | 0 | 92 | 36.4 | 0 | 87.84
12:00 | 0 | 0 | 200 | 0 | 341 | 0 | 0 | 371 | 352 |  | 0 | 420 | 140 | 7 | 30 | 55 | 0 | 0 | 0 | 0 | 30 | 7 | 0 | 0 | 50 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 217 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 110 | 0 | 340 | 335 | 205 | 8 | 95 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 155 | 32 | 22 | 2.3 | 87 | 0 | 48 | 51 | 163 | 154 | 58 | 75 | 0 | 0 | 0 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 15 | 15.1 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 5.1 | 65 | 0 | 0 | 0 | 0 |  | 650 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 7.1 | 80 | 0 |  | 5787.5 | 2470.1 | 8257.6 | 4160 | 650 | 2014 | 885 | 352 | 67 | 0 | 100 | 29.6 | 0 | 87.83
13:00 | 0 | 0 | 200 | 0 | 314 | 0 | 0 | 355 | 352 |  | 0 | 420 | 135 | 20 | 64 | 55 | 0 | 0 | 0 | 0 | 98 | 24 | 0 | 0 | 65 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 204 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 0 | 110 | 0 | 310 | 305 | 184 | 8 | 95 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 157 | 32 | 22 | 2.3 | 89 | 0 | 48 | 51 | 163 | 153 | 60 | 78 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 15 | 17.3 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 5 | 103 | 0 | 0 | 0 | 0 |  | 650 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 70 | 0 | 7.1 | 100 | 0 |  | 5872.6 | 2426.1 | 8298.7 | 4013 | 650 | 1986 | 1103 | 352 | 67 | 0 | 96 | 31.7 | 0 | 87.82
14:00 | 0 | 0 | 200 | 0 | 335 | 0 | 0 | 348 | 290 |  | 0 | 360 | 140 | 0 | 78 | 55 | 0 | 0 | 0 | 0 | 84 | 7 | 0 | 0 | 72 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 211 | 0 | 134 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 110 | 0 | 335 | 300 | 194 | 8 | 96 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 155 | 8 | 22 | 2.1 | 89 | 0 | 50 | 51 | 130 | 160 | 58 | 20 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 16.8 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 4.4 | 69 | 0 | 0 | 0 | 0 |  | 650 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 44 | 0 | 6.2 | 109 | 0 |  | 5612.3 | 2406.2 | 8018.5 | 4059 | 650 | 1791 | 971 | 352 | 66 | 0 | 100 | 29.5 | 0 | 87.81
15:00 | 0 | 0 | 200 | 0 | 335 | 0 | 0 | 379 | 347 |  | 0 | 420 | 140 | 0 | 96 | 55 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 72 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 214 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 110 | 0 | 330 | 285 | 186 | 8 | 95 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 155 | 8 | 22 | 1.6 | 89 | 0 | 50 | 51 | 130 | 153 | 58 | 20 | 0 | 0 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 3.6 | 69 | 0 | 0 | 0 | 0 |  | 648 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 35 | 0 | 4.8 | 109 | 0 |  | 5703.2 | 2372.8 | 8076 | 4027 | 648 | 1926 | 947 | 352 | 66 | 0 | 100 | 10 | 0 | 87.8
16:00 | 0 | 0 | 200 | 0 | 333 | 0 | 0 | 373 | 350 |  | 0 | 420 | 140 | 0 | 96 | 55 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 72 | 0 | 0 | 53 | 17 | 0 | 19 | 25 | 28 | 33 | 17 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 0 | 110 | 0 | 320 | 270 | 179 | 8 | 96 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 154 | 8 | 22 | 0.5 | 88 | 0 | 50 | 51 | 163 | 152 | 58 | 78 | 0 | 0 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 7.9 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 2 | 87 | 0 | 0 | 0 | 0 |  | 648 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 109 | 0 |  | 5742.4 | 2412 | 8154.4 | 3995 | 648 | 2010 | 955 | 372 | 65 | 0 | 96 | 13.4 | 0 | 87.79
17:00 | 0 | 0 | 200 | 0 | 320 | 0 | 0 | 344 | 320 |  | 0 | 370 | 130 | 0 | 80 | 55 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 72 | 0 | 0 | 53 | 17 | 0 | 16 | 25 | 28 | 33 | 33 | 0 | 0 | 24 | 40 | 110 | 0 | 0 | 204 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 110 | 0 | 320 | 265 | 184 | 8 | 87 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 154 | 13 | 22 | 0.3 | 88 | 0 | 53 | 51 | 130 | 149 | 60 | 78 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 2.9 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0.7 | 121 | 0 | 0 | 0 | 0 |  | 648 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 35 | 0 | 1.3 | 109 | 0 |  | 5568.9 | 2379.3 | 7948.2 | 3968 | 648 | 1873 | 922 | 372 | 64 | 0 | 96 | 5.2 | 0 | 87.79
18:00 | 0 | 0 | 200 | 0 | 364 | 0 | 0 | 360 | 300 |  | 0 | 300 | 145 | 3 | 80 | 55 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 3 | 72 | 0 | 0 | 53 | 17 | 0 | 16 | 25 | 24 | 33 | 33 | 0 | 0 | 24 | 40 | 110 | 0 | 0 | 217 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 2 | 1 | 19 | 12 | 0 | 110 | 0 | 360 | 305 | 203 | 8 | 95 | 30 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 120 | 154 | 16 | 22 | 0 | 88 | 0 | 53 | 48 | 110 | 164 | 45 | 20 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 173 | 0 | 4 | 0 | 35 | 0 | 0 | 233 | 4 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 |  | 746 | 0 | 390 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 35 | 0 | 0.2 | 109 | 0 |  | 5670 | 2500.2 | 8170.2 | 4138 | 746 | 1676 | 1055 | 371 | 64 | 0 | 120 | 0.2 | 0 | 87.78
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 320 | 0 | 0 | 370 | 358 |  | 0 | 450 | 130 | 80 | 91 | 55 | 0 | 0 | 0 | 0 | 100 | 72 | 0 | 24 | 72 | 0 | 20 | 53 | 35 | 0 | 19 | 25 | 20 | 33 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 204 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 37 | 38 | 19 | 20 | 0 | 110 | 0 | 315 | 265 | 183 | 8 | 86 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 132 | 158 | 75 | 22 | 0 | 88 | 0 | 53 | 48 | 163 | 146 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 99 | 0 | 0 | 154 | 0 | 116 | 0 | 100 | 0 | 40 | 235 | 66 | 34 | 0 | 0 | 224 | 0 | 0 | 0 | 0 |  | 939 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 125 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 50 | 71 | 0 | 0 | 109 | 0 |  | 6750 | 3035 | 9785 | 3960 | 939 | 2069 | 2198 | 371 | 65 | 51 | 132 | 0 | 0 | 87.78
19:30 | 0 | 0 | 200 | 0 | 320 | 0 | 0 | 338 | 360 |  | 0 | 450 | 130 | 100 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 72 | 0 | 6 | 53 | 35 | 0 | 19 | 25 | 28 | 33 | 33 | 16 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 60 | 50 | 19 | 23 | 0 | 110 | 0 | 310 | 265 | 184 | 8 | 86 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 130 | 159 | 95 | 22 | 0 | 88 | 0 | 53 | 48 | 130 | 147 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 150 | 0 | 0 | 154 | 0 | 149 | 0 | 100 | 0 | 70 | 235 | 115 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 |  | 940 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 126 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 50 | 114 | 0 | 0 | 109 | 0 |  | 6851 | 3103 | 9954 | 3948 | 940 | 2045 | 2404 | 371 | 65 | 51 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 336 | 0 | 0 | 338 | 300 |  | 0 | 450 | 140 | 100 | 97 | 25 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 72 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 28 | 33 | 33 | 34 | 0 | 25 | 40 | 110 | 0 | 0 | 202 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 48 | 50 | 19 | 28 | 0 | 110 | 0 | 315 | 265 | 184 | 8 | 95 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 130 | 159 | 95 | 22 | 0 | 87 | 0 | 53 | 48 | 130 | 148 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 149 | 0 | 0 | 154 | 0 | 150 | 0 | 70 | 0 | 35 | 233 | 115 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 |  | 939 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 130 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 90 | 0 | 280 | 0 | 0 | 220 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 50 | 114 | 0 | 0 | 109 | 0 |  | 6743 | 3143 | 9886 | 3986 | 939 | 2017 | 2328 | 370 | 65 | 51 | 130 | 0 | 0 | 87.77
21:00 | 0 | 0 | 200 | 0 | 345 | 0 | 0 | 364 | 298 |  | 0 | 450 | 140 | 100 | 97 | 0 | 0 | 0 | 0 | 0 | 100 | 102 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 48 | 0 | 24 | 40 | 110 | 0 | 0 | 208 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 48 | 19 | 34 | 0 | 110 | 0 | 350 | 295 | 185 | 8 | 95 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 122 | 159 | 95 | 0 | 0 | 88 | 0 | 53 | 48 | 130 | 155 | 61 | 78 | 0 | 0 | 19 | 0 | 10 | 305 | 24 | 11 | 0 | 89 | 0 | 0 | 154 | 0 | 84 | 0 | 0 | 0 | 0 | 233 | 115 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 |  | 939 | 0 | 365 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 130 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 90 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 50 | 114 | 0 | 0 | 109 | 0 |  | 6521 | 3178 | 9699 | 4109 | 939 | 2042 | 2002 | 370 | 64 | 51 | 122 | 0 | 0 | 87.77
22:00 | 0 | 0 | 200 | 0 | 320 | 0 | 0 | 348 | 307 |  | 0 | 450 | 140 | 70 | 97 | 0 | 0 | 0 | 0 | 0 | 100 | 58 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 40 | 110 | 0 | 0 | 203 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 37 | 0 | 95 | 0 | 295 | 260 | 221 | 8 | 95 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 120 | 160 | 95 | 22 | 0 | 87 | 0 | 53 | 45 | 130 | 150 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 154 | 0 | 20 | 0 | 0 | 0 | 0 | 233 | 85 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 |  | 940 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 130 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 437 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 109 | 0 |  | 6139 | 2995 | 9134 | 3963 | 940 | 2070 | 1606 | 371 | 64 | 0 | 120 | 0 | 0 | 87.77
23:00 | 0 | 0 | 200 | 0 | 328 | 0 | 0 | 340 | 358 |  | 0 | 400 | 140 | 50 | 97 | 0 | 0 | 0 | 0 | 0 | 100 | 58 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 203 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 80 | 0 | 290 | 265 | 221 | 8 | 95 | 46 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 22 | 116 | 161 | 48 | 22 | 0 | 85 | 0 | 53 | 45 | 163 | 153 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 |  | 794 | 0 | 340 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5979 | 2558 | 8537 | 3986 | 794 | 2090 | 1114 | 371 | 66 | 0 | 116 | 0 | 0 | 87.76
24:00 | 0 | 0 | 200 | 0 | 336 | 0 | 0 | 358 | 359 |  | 0 | 400 | 140 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 40 | 110 | 0 | 0 | 212 | 0 | 114 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 28 | 0 | 80 | 0 | 300 | 275 | 222 | 8 | 95 | 46 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 108 | 161 | 0 | 22 | 0 | 85 | 0 | 53 | 45 | 163 | 155 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 |  | 407 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 200 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 |  | 5811 | 2158 | 7969 | 4056 | 407 | 2110 | 851 | 371 | 66 | 0 | 108 | 0 | 0 | 87.76
KWH | 0 | 0 | 4571000 | 0 | 7842973 | 0 | 0 | 8586240 | 7803000 |  | 0 | 9304250 | 3322705 | 503040 | 1401816 | 569141 | 0 | 0 | 0 | 0 | 1210560 | 531792 | 0 | 33053 | 1016640 | 0 | 39840 | 803160 | 229828 | 0 | 434340 | 600000 | 676080 | 838400 | 667200 | 137580 | 0 | 554700 | 932000 | 2600000 | 0 | 0 | 4930868 | 0 | 2760655 | 0 |  | 0 | 0 | 0 | 0 | 85440 | 151680 | 448368 | 511680 | 0 | 2572700 | 0 | 7956500 | 7264000 | 4959000 | 200727 | 1895880 | 390168 | 279840 | 0 | 903856 | 0 | 0 | 0 | 489492 | 249120 | 685300 | 541180 | 2392320 | 3698080 | 710400 | 483300 | 15100 | 2041000 | 0 | 1005000 | 1011240 | 3752345 | 3522000 | 1368000 | 1380480 | 0 | 0 | 395000 | 0 | 242640 | 7706500 | 575655 | 264000 | 0 | 358799 | 0 | 0 | 3100800 | 0 | 470880 | 119340 | 196800 | 0 | 120436 | 5610000 | 444000 | 29952 | 0 | 35520 | 1866764 | 0 | 0 | 0 | 0 |  | 14239273 | 0 | 8683200 | 0 | 877440 | 0 | 0 | 0 | 0 | 0 | 143625 | 3118000 | 372946 | 211200 | 0 | 0 | 0 | 0 | 0 | 168516 | 708310 | 0 | 0 | 0 | 0 | 360000 | 281736 | 180396 | 2167855 | 0 | 6656300 | 0 | 0 | 4774855 | 0 | 0 | 0 | 1566033 | 7680 | 0 | 0 | 10005000 | 0 | 0 | 0 | 151344 | 934080 | 0 | 45540 | 1697760 | 0 |  | 135402143 | 57351089 | 192753232 | 96672950 | 14239273 | 46687273 | 22066545 | 8824155 | 1486700 | 168516 | 2392320 | 215500 | 0
Fuel Cost | 0 | 0 | 4890970 | 0 | 5803800.02 | 0 | 0 | 6182092.8 | 5930280 |  | 0 | 7443400 | 2990434.5 | 5131008 | 15181667.28 | 5839386.66 | 0 | 0 | 0 | 0 | 13437216 | 5403006.72 | 0 | 346395.44 | 9251424 | 0 | 372902.4 | 7702304.4 | 2192559.12 | 0 | 325755 | 450000 | 0 | 0 | 0 | 1318016.4 | 0 | 144222 | 242320 | 3978000 | 0 | 0 | 5177411.4 | 0 | 3506031.85 | 0 |  | 0 | 0 | 0 | 0 | 812534.4 | 1419724.8 | 412498.56 | 1422470.4 | 0 | 2701335 | 0 | 5887810 | 6101760 | 4562280 | 196712.46 | 2521520.4 | 319937.76 | 288235.2 | 0 | 1292514.08 | 0 | 0 | 0 | 499281.84 | 186840 | 1295217 | 405885 | 16507008 | 3032425.6 | 6755904 | 492966 | 247640 | 2775760 | 0 | 1366800 | 1264050 | 4652907.8 | 3240240 | 2038320 | 2429644.8 | 0 | 0 | 628050 | 0 | 570204 | 5471615 | 431741.25 | 200640 | 0 | 3756625.53 | 0 | 0 | 29829696 | 0 | 4751179.2 | 1377183.6 | 1834176 | 0 | 1128485.32 | 5273400 | 3893880 | 266872.32 | 0 | 0 | 17211564.08 | 0 | 0 | 0 | 0 |  | 38446037.1 | 0 | 6772896 | 0 | 8458521.6 | 0 | 0 | 0 | 0 | 0 | 1420451.25 | 2494400 | 578066.3 | 2268288 | 0 | 0 | 0 | 0 | 0 | 1668308.4 | 7345174.7 | 0 | 0 | 0 | 0 | 396000 | 464864.4 | 136559.772 | 13809236.35 | 0 | 27224267 | 0 | 0 | 4201872.4 | 0 | 0 | 0 | 2489992.47 | 129792 | 0 | 0 | 7303650 | 0 | 0 | 0 | 1348475.04 | 8724307.2 | 0 | 0 | 0 | 0 |  | 264996139.39 | 135681159.982 | 400677299.372 | 86927697.652 | 38446037.1 | 43561406.91 | 170521972.36 | 41033503.35 | 386542 | 1668308.4 | 16507008 | 1624823.6 | 0
Yesterday Day Peak | 0 | 0 | 200 | 0 | 341 | 0 | 0 | 371 | 352 |  | 0 | 420 | 140 | 7 | 30 | 55 | 0 | 0 | 0 | 0 | 30 | 7 | 0 | 0 | 50 | 0 | 0 | 35 | 17 | 0 | 19 | 25 | 31 | 33 | 17 | 0 | 0 | 27 | 40 | 110 | 0 | 0 | 217 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 110 | 0 | 340 | 335 | 205 | 8 | 95 | 10 | 10 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 100 | 155 | 32 | 22 | 2.3 | 87 | 0 | 48 | 51 | 163 | 154 | 58 | 75 | 0 | 0 | 0 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 15 | 15.1 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 5.1 | 65 | 0 | 0 | 0 | 0 |  | 650 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 12 | 8 | 92 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 7.1 | 80 | 0 |  | 8257.6 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 320 | 0 | 0 | 338 | 360 | 0 | 0 | 450 | 130 | 100 | 97 | 55 | 0 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 72 | 0 | 6 | 53 | 35 | 0 | 19 | 25 | 28 | 33 | 33 | 16 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 19 | 23 | 0 | 110 | 0 | 310 | 265 | 184 | 8 | 86 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 130 | 159 | 95 | 22 | 0 | 88 | 0 | 53 | 48 | 130 | 147 | 62 | 78 | 0 | 0 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 150 | 0 | 0 | 154 | 0 | 149 | 0 | 100 | 0 | 70 | 235 | 115 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 |  | 940 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 126 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 91 | 0 | 280 | 0 | 0 | 214 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 50 | 114 | 0 | 0 | 109 | 0 |  | 9954 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 94 | 46 | 20 | 0 | 43 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 122 | 163 | 95 | 22 | 0 | 87 | 0 | 51 | 44 | 163 | 150 | 66 | 81 | 0 | 0 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 235 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 |  | 953 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 130 | 21 | 110 | 30 | 0 | 0 | 50 | 45 | 100 | 50 | 40 | 40 | 52 | 36 | 18 | 11 | 11 | 90 | 0 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 0 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 0 | 0 | 180 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 70 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 30 | 40 | 110 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 20 | 10 | 0 | 100 | 0 | 360 | 360 | 225 | 8 | 90 | 46 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 87 | 163 | 95 | 22 | 1.6 | 87 | 0 | 51 | 44 | 163 | 147 | 66 | 80 | 0 | 0 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 0 | 100 | 235 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 |  | 658 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 130 | 18 | 70 | 0 | 0 | 0 | 0 | 0 | 80 | 50 | 40 | 40 | 52 | 0 | 18 | 11 | 11 | 90 | 0 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 0 | 0 | 410 | 50 | 100 | 0 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 0 | 0 | 120 | 0 | 320 | 0 | 0 | 337 | 363 | 0 | 0 | 420 | 135 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 0 | 0 | 72 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 25 | 40 | 110 | 0 | 0 | 203 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 22 | 5 | 0 | 80 | 0 | 300 | 275 | 186 | 8 | 95 | 46 | 20 | 0 | 43 | 0 | 0 | 0 | 0 | 11 | 33 | 21 | 94 | 163 | 5 | 22 | 0.8 | 85 | 0 | 45 | 45 | 163 | 149 | 45 | 78 | 0 | 0 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 173 | 0 | 4 | 7.44 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 1.9 | 16 | 0 | 0 | 0 | 0 | 0 | 653 | 0 | 330 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 92 | 0 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 423 | 0 | 0 | 0 | 0 | 37 | 0 | 1.1 | 106 | 0 | 0
199
| Minimum Generation |  | 6407 | 5:00
| Highest Generation |  | 9954 | 19:30
| Day Peak Generation |  | 8257.6 | 12:00
| Evening Peak Generation |  | 9954 | 19:30
| HVDC Max Flow |  | 940 | 19:30
| HVDC EvPeak Flow |  | 940 | 19:30
| Load factor L.F |  | 80.68%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-03-12
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8257.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6769 | MW
Evening Peak Generation : |  | 9954 | MW Hour : | 19:30 | Available Max Generation : |  | 14606 | MW
E.P. Demand (at gen end) : |  | 9954 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10300 | MW
Maximum Generation : |  | 9954 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4306 | MW
Total Gen. (MKWH) : |  | 192.7532 | System Load Factor : | 80.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -320 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-03-12
Actual : | 87.73 | Ft.(MSL) , | Rule curve : | 91.24 | Ft.( MSL )
Gas Consumed : | Total = | 1136.35 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 130489104.562
: |  | Coal : | 41033503.35 | Oil : | 172190280.76 | Total : | 343712888.672
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3654.6881 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1240.6701 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1111.2205 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1003.9469 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 907.3265 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 732.175 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 412.1322 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 188.5878 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 564.6766 |  |  | 0 | 0%
Total | 0 |  | 9815.4237 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 10) Chandpur 150 MW CCPP STG
2) Siddhirganj 210 MW
3) Ghorasal Unit-2,3 & 5.
4) Baghabari 100 MW & 71 MW
5) Ashuganj unit-3,5
6) Sirajganj unit-2,3
7) Siddhirganj 335 MW
8) Kaptai-2,3,5
9) Bhola CCPP STG
| Additional Information of Machines, lines, Interruption / Forced Load shed etc. |  | a
|  | Description |  |  | Comments on Power Interruption
a) Siddhirganj-EGCB P/S 132 kV Ckt-1 tripped at 11:26 from Siddhirganj end showing master trip and
was switched on at 12:02.
b) Siddhirganj-Maniknagar 230 kV Ckt-2 tripped at 11:28 from both ends showing differential trip, distance
Z-1 B phase both end and was switched on at 12:31.
c) Barisal(N) 132/33 kV T4 & T5 transformer were shut down from 08:57 to 17:10 for D/W. |  |  |  |  | About 17 MW power interruption occurred under Barisal(N) S/S
area from 08:57 to 17:10.
d) Aminbazar-Manikganj P/P 132 kV Ckt-2 was under shut down from 09:03 to 17:47 for C/M.
e) Jessore 132/33 kV T3 transformer was under shut down from 09:23 to 15:57 for C/M.
f) Madaripur-Gopalganj (N) 132 kV Ckt-3 was under shut down from 13:05 to 14:30 for D/W.
g) Madaripur 132/33 kV T1 transformer was shut down from 13:08 to 14:27 for D/W.
h) Barisal(S)-Patuakhali 132 kV Ckt was under shut down from 06:55 to 18:50 for D/W. |  |  |  |  | About 40 MW power interruption occurred under Patuakhali S/S
area from 06:55 to 18:50.
i) After maintenance Uttara 132/33 kV GT-2 transformer was switched on at 14:43.
j) Madaripur-Barisal (N) 132 kV Ckt-2 was under shut down from 14:37 to 16:59 for D/W.
k) Madaripur 132/33 kV T2 transformer was shut down from 14:40 to 16:30 for D/W.
l) Madaripur-Gopalganj 132 kV Ckt-1,2,3 are tripped at 17:44 from Gopalganj end showing main |  |  |  |  | About 33 MW power interruption occurred under Madaripur S/S
protection trip ,SOTF relay at Gopalganj end and were switched on at 17:58,17:59 & 18:02 respectively. |  |  |  |  | area from 17:44 to 18:58.
m) Barisal(N)-Madaripur 132 kV Ckt-1 &2 are tripped at 17:45 from both end showing dist relay at
Barisal end and was switched on at 18:01 &18:02 respectively.
n) Joypurhat 132/33 kV T-2 transformer was shut down from 15:20 to 20:43 due to ten delta test.
o) Sonargaon-Meghnaghat IEL 132 kV Ckt is under shut down since 03:58 for safety as a tower # 2 was
accidental damage by a construction crane of Meghnaghat new economic zone.
p) Madunaghat- Sikalbaha 132 kV Ckt-1 is under shut down since 07:08 for D/W.
q) Daudkandi 132/33 kV T1 transformer is under shut down since at 07:05 for C/M.
r) Madaripur-Barisal (N) 132 kV Ckt-2 is under shut down 07:36 for D/W.
s) Sikalbaha-Tk chemical 132 kV Ckt-1 is under shut down since 07:11 for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4571000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 320 | 7842973
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8586240 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 360 | 7803000 | Gas shortage.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9304250 | Gas shortage.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 503040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 130 | 3322705 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1401816
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 569141
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 33053 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 434340
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1210560
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 531792
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 6 | 39840 | Low demand
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 803160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 229828 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1016640 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1276080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 838400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 667200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 16 | 137580 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 150 | 358799 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 470880
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 29952 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2862 | 51982269
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2600000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 119340
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 151680
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 65 | 1486700 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4930868
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 114 | 2760655 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 196800
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448368
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 511680
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 85440 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35520
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 178 | 1866764 | Transformer overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Chattogram area Total |  |  |  | 2166 | 922 | 15193815
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 110 | 2572700 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4959000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7956500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 7264000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 390168 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 279840 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 903856 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 120436 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 1895880
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489492
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 2392320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 685300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 541180 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1322 | 30900519
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3698080 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 483300
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 710400
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15100
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 154 | 3100800 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 444000
| Mymensingh Area Total |  |  |  | 637 | 545 | 8451680
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 2041000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3752345 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 147 | 3522000 | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1005000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 1011240
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1368000 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1380480
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 0 | 0 | Machine problem
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 395000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 575655
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7706500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 235 | 5610000 | Engine problem
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 242640
| Sylhet Area Total |  |  |  | 1949 | 1200 | 28873860
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 940 | 14239273
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 877440
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8683200 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 143625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 7680 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 50 | 151344 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1475 | 24102562
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 211200 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 372946 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 3118000 | ST Under S/D.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 95 | 1566033
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  | 462 | 291 | 5268179
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 708310
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4774855 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 10005000 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 360000
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 12 | 281736
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 180396
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 168516 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1697760
| Rajshahi Area Total |  |  |  | 2183 | 852 | 18176573
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 91 | 2167855
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6656300
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 114 | 934080
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45540
| Rangpur Area Total |  |  |  | 605 | 485 | 9803775
| Total |  |  |  | 19107 | 9954 | 192753232
| Eastern Grid Total |  |  |  | 13543 | 6851 | 135402143
| Western Grid Total |  |  |  | 5564 | 3103 | 57351089
| National Grid Total |  |  |  | 19107 | 9954 | 192753232
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-11
(a) ENTIRE EASTERN GRID : |  | 6412 | MW | (b) ENTIRE WESTERN GRID : |  | 3063 | MW
i) Dhaka area |  | 3477 | MW | i) Khulna area |  | 1134 | MW
ii) Chittagong area |  | 980 | MW | ii) Rajshahi area |  | 998 | MW
iii) Comilla area |  | 839 | MW | iii) Barisal area |  | 270 | MW
iv) Mymensingh area |  | 782 | MW | iv) Rangpur area |  | 661 | MW
v) Sylhet area |  | 334 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9475 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 18:00 | Sherpur | 84 | 18:30 | Benapol | 34 | 19:00
Munsiganj | 92 | 21:00 | Srimongal | 30 | 18:30 | Jhenida | 84 | 18:30
Sonargaon | 72 | 19:00 | Shahjibazar | 84 | 19:00 | Bottail | 96 | 19:30
Shyampur | 190 | 11:00 | Fenchuganj | 27 | 18:30 | G.K Project | 36 | 19:00
Bhulta | 163 | 0:00 | Kulawara | 30 | 18:30 | Faridpur | 134 | 20:00
Madanganj | 61 | 20:00 | Sylhet | 101 | 19:30 | Madaripur | 66 | 20:00
Shitalakhya | 103 | 12:00 | Chatak | 18 | 18:30 | Sariatpur | 44 | 21:00
Rahim steel | 21 | 9:00 | Sunamganj | 29 | 21:00 | Gopalganj | 72 | 19:00
Matuail | 90 | 12:00 | Biani Bazar | 32 | 18:30 | Bagerhat | 70 | 19:00
Ghorasal | 62 | 19:30 | Comilla (S) | 132 | 19:00 | Mongla | 36 | 1:00
Narsingdi | 122 | 19:30 | Comilla(N) | 95 | 19:00 | Satkhira | 79 | 20:00
Haripur (SBU) | 98 | 17:00 | Chandpur | 83 | 20:00 | Gallamari | 41 | 19:00
Ullon | 63 | 19:00 | Feni | 93 | 18:30 | Magura | 40 | 19:30
Hasnabad | 156 | 19:00 | Chowmuhani | 122 | 19:00 | Norail | 29 | 19:00
Magbazar | 89 | 18:00 | Ashuganj | 43 | 23:00 | Chuadanga | 63 | 19:00
Maniknagar | 88 | 18:00 | Daudkandi | 116 | 21:00 | Barisal(N) | 39 | 18:30
Bangabhaban | 28 | 16:00 | B.Baria | 120 | 18:30 | Barisal (S) | 84 | 19:00
Narinda | 86 | 17:00 | Ramganj | 54 | 19:00 | Patuakhali | 94 | 20:00
Dhanmondi | 122 | 14:00 | Chaddagram | 32 | 13:00 | Bhandaria | 40 | 19:30
Lalbag | 69 | 19:00 | PHP | 3 | 14:00 | Borhan Uddin | 27 | 20:00
Madartek | 54 | 19:00 | Madunaghat | 42 | 9:00 | Ishurdi | 45 | 18:30
Dhaka University |  |  | Hathazari | 72 | 19:00 | Ruppur Paromanobik | 2 | 1:00
Mirpur | 83 | 19:00 | Khulshi | 160 | 12:00 | Natore | 99 | 19:00
Kalyanpur | 72 | 19:00 | Halishahar | 104 | 19:30 | Bogra | 145 | 19:30
Gulshan | 96 | 19:00 | Baraulia | 150 | 8:00 | Noagaon | 99 | 20:00
Uttara | 57 | 19:00 | Sikalbaha | 19 | 18:30 | Rajshahi | 97 | 20:00
Uttara New | 21 | 19:00 | Dohazari | 76 | 19:00 | Rajshahi New | 10 | 19:30
Kamrangirchar | 77 | 19:00 | Cox'sbazar | 86 | 18:30 | C.Nawabganj | 61 | 19:00
Savar | 118 | 15:00 | Chandraghona | 26 | 18:30 | Amnura | 28 | 19:00
Bhasantec | 118 | 19:00 | Kaptai | 3.5 | 18:30 | Pabna | 79 | 20:00
Agargaon | 44 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 87 | 19:30
Satmosjid | 90 | 13:00 | Bakulia | 87 | 19:00 | Serajganj | 87 | 19:30
Tongi | 122 | 15:00 | Julda | 22 | 19:00 | Niyamatpur | 75 | 19:30
Kabirpur | 197 | 16:00 | TK chemical | 11 | 19:30 | Joypurhat | 46 | 19:00
Basundhara | 110 | 12:00 | Modern Steel | 14 | 2:00 | Sherpur(Bogura) | 36 | 18:30
Manikganj | 76 | 19:00 | Shahmirpur | 27 | 18:30 | Mohastangor | 34 | 7:00
Joydevpur | 140 | 18:30 | Khagrachhari | 20 | 18:30 | Rangpur | 116 | 19:00
New Tongi | 89 | 18:30 | Matarbari | 25 | 19:00 | Lalmonirhat | 47 | 19:00
Korda | 222 | 20:00 | Baroiar Hat | 20 | 18:00 | Saidpur | 97 | 18:30
Dhamrai | 56 | 19:00 | Rangamati | 10 | 18:30 | Purbasadipur | 100 | 8:00
Rajendrapur | 60 | 18:30 | Abul Khair 230 | 117 | 2:00 | Thakurgaon | 66 | 19:00
Valuka | 86 | 9:00 | BSRM | 55 | 4:00 | Palashbari | 103 | 19:00
Tangail | 149 | 19:30 | GPH Ispat | 56 | 18:00 | Barapukuria | 46 | 19:30
Mymensing | 184 | 18:30 | Goalpara | 23 | 13:00 | Panchagar | 36 | 19:30
Kishorganj | 101 | 20:00 | Central s/s | 69 | 19:00 | Joldhaka | 25 | 19:30
Netrokona | 98 | 19:30 | Noapara | 46 | 18:30 | Kurigram | 50 | 0.79167
Jamalpur | 103 | 19:30 | Jessore | 100 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-11 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 401 | 0.041667 | 394 | 0.625 | Kaliakoir | 385 | 0.041667 | 370 | 0.66667
Bheramara | 405 | 0.58333 | 387 | 0.79167 | Bhulta | 392 | 0.041667 | 380 | 0.66667
Ashuganj(N) | 398 | 0.16667 | 387 | 0.66667 | Gopalganj | 408 | 0.041667 | 356 | 0.77083
Payra | 413 | 0.083333 | 359 | 0.77083
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 230 | 0.45833 | Hathazari | 221 | 0.77083 | 216 | 0.5
Ishurdi | 237 | 0.083333 | 228 | 0.29167 | Megnaghat | 234 | 0.041667 | 228 | 0.45833
Ashuganj | 242 | 0.083333 | 235 | 0.41667 | Fenchuganj | 241 | 0.25 | 237 | 0.45833
Serajganj | 233 | 0.083333 | 228 | 0.29167 | Siddhirganj | 233 | 0.16667 | 23 | 0.33333
Baghabari | 245 | 0.083333 | 238 | 0.29167 | Maniknagar | 231 | 0.16667 | 222 | 0.5
Barapukuria | 233 | 0.041667 | 226 | 0.33333 | Old Airport | 231 | 0.041667 | 222 | 0.5
Bogra | 228 | 0.125 | 217 | 0.29167 | Barisal | 251 | 0.083333 | 230 | 0.77083
Khulna South | 238 | 0.083333 | 219 | 0.79167 | AKSML | 219 | 0.33333 | 213 | 0.5
Rampura | 230 | 0.041667 | 225 | 0.45833 | BSRM | 223 | 0.8125 | 215 | 0.66667
Haripur | 230 | 0.041667 | 223 | 0.5 | Bibiyana | 239 | 0.041667 | 234 | 0.375
Hasnabad | 231 | 0.041667 | 224 | 0.5 | Bhulta | 232 | 0.041667 | 225 | 0.625
Shyampur | 229 | 0.125 | 221 | 0.5 | Ashuganj (S) | 237 | 0.041667 | 231 | 0.70833
Aminbazar | 232 | 0.041667 | 224 | 0.45833 | Kaliakoir | 233 | 0.041667 | 222 | 0.66667
Tongi | 235 | 0.95833 | 221 | 0.45833 | GPH | 220 | 0.20833 | 212 | 0.5
Comilla (N) | 236 | 0.16667 | 229 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 0.041667 | 127 | 0.45833 | Hathazari | 132 | 0.83333 | 128 | 0.5
Munsiganj | 135 | 0.041667 | 127 | 0.45833 | Khulshi | 129 | 0.8125 | 124 | 0.5
Sonargaon | 132 | 0.79167 | 128 | 0.45833 | Halishahar | 131 | 0.8125 | 125 | 0.5
Shyampur | 134 | 0.083333 | 129 | 0.45833 | Baraulia | 129 | 0.083333 | 125 | 0.5
Bhulta | 126 | 0.041667 | 120 | 0.45833 | Sikalbaha | 131 | 0.79167 | 127 | 0.41667
Madanganj | 136 | 0.79167 | 128 | 0.41667 | Dohazari | 128 | 0.16667 | 125 | 0.77083
Shitalakhya | 136 | 0.79167 | 127 | 0.41667 | Cox'sbazar | 124 | 0.375 | 115 | 0.77083
Rahim steal | 133 | 19:30 | 128 | 0.5 | Chandraghona | 131 | 0.041667 | 128 | 0.5
Matuail | 133 | 0.25 | 126 | 0.5 | Kaptai | 132 | 0.041667 | 128 | 0.29167
Ghorasal | 140 | 0.29167 | 135 | 0.45833 | A. Khaer Stl. | 130 | 0.083333 | 126 | 0.5
Narsinghdi | 133 | 0.54167 | 127 | 0.79167 | Bakulia | 130 | 0.8125 | 125 | 0.45833
Haripur (SBU) | 133 | 0.041667 | 128 | 0.45833 | Julda | 130 | 0.79167 | 126 | 0.45833
Ullon | 130 | 0.25 | 122 | 0.66667 | TK Chemical | 131 | 0.041667 | 127 | 0.41667
Hasnabad | 134 | 0.125 | 125 | 0.70833 | Modern Steel | 130 | 0.79167 | 125 | 0.5
Magbazar | 130 | 0.25 | 122 | 0.66667 | Shahmirpur | 131 | 0.8125 | 126 | 0.5
Maniknagar | 135 | 0.25 | 131 | 0.77083 | Khagrachhari | 131 | 0.125 | 126 | 0.5
Bangabhaban | 135 | 0.25 | 131 | 0.77083 | Matarbari | 126 | 0.083333 | 119 | 0.75
Narinda | 135 | 0.25 | 131 | 0.77083 | Baroiar Hat | 131 | 0.041667 | 129 | 14:00
Dhanmondi | 130 | 0.25 | 122 | 0.66667 | Rangamati | 131 | 0.041667 | 127 | 12:00
Lalbag | 133 | 0.20833 | 126 | 0.5 | Goalpara | 137 | 0.125 | 126 | 0.79167
Madartek | 129 | 0.25 | 122 | 0.66667 | Central s/s | 134 | 0.41667 | 125 | 0.77083
Dhaka University |  |  |  |  | Noapara | 134 | 0.041667 | 123 | 0.77083
Mirpur | 134 | 0.20833 | 128 | 0.5 | Jessore | 132 | 0.083333 | 118 | 0.77083
Kalyanpur | 135 | 0.20833 | 129 | 0.5 | Benapol | 133 | 0.041667 | 120 | 0.77083
Gulshan | 128 | 0.20833 | 122 | 0.5 | Jhenida | 131 | 0.041667 | 117 | 0.77083
Uttara | 133 | 0.20833 | 128 | 0.5 | Bottail | 135 | 0.20833 | 126 | 0.77083
Uttara New | 134 | 0.20833 | 129 | 0.5 | G.K Project | 140 | 0.16667 | 132 | 0.79167
Kamrangirchar | 132 | 0.20833 | 126 | 0.5 | Faridpur | 138 | 0.33333 | 122 | 0.77083
Savar | 133 | 0.20833 | 127 | 0.5 | Madaripur | 140 | 0.375 | 121 | 0.75
Bhasantec | 133 | 0.20833 | 126 | 0.5 | Sariatpur | 141 | 0.083333 | 122 | 0.77083
Agargaon | 133 | 0.20833 | 127 | 0.5 | Gopalganj | 145 | 0.083333 | 124 | 0.77083
Satmosjid | 133 | 0.20833 | 127 | 0.5 | Bagerhat | 133 | 0.375 | 120 | 0.79167
Tongi | 140 | 0.875 | 129 | 0.625 | Mongla | 131 | 0.16667 | 123 | 0.79167
Kabirpur | 132 | 0.041667 | 125 | 0.41667 | Satkhira | 134 | 0.125 | 122 | 0.77083
Basundhara | 131 | 4:00 | 122 | 0.625 | Gallamari | 135 | 0.083333 | 126 | 0.77083
Manikganj | 141 | 0.79167 | 129 | 0.625 | Magura | 133 | 0.083333 | 115 | 0.79167
Joydevpur | 139 | 0.125 | 133 | 0.625 | Norail | 131 | 0.125 | 115 | 0.79167
New Tongi | 138 | 0.83333 | 128 | 0.66667 | Chuadanga | 128 | 0.041667 | 112 | 0.79167
Kodda | 141 | 0.83333 | 121 | 0.66667 | Barisal(N) | 142 | 0.083333 | 128 | 0.77083
Dhamrai | 132 | 0.041667 | 125 | 0.66667 | Barisal (S) | 140 | 0.375 | 128 | 0.77083
Rajendrapur | 137 | 0.125 | 130 | 0.45833 | Patuakhali | 136 | 0.083333 | 127 | 0.79167
Valuka | 130 | 0.041667 | 122 | 0.375 | Bhandaria | 135 | 0.041667 | 125 | 0.77083
Tangail | 133 | 0.041667 | 126 | 0.66667 | Ishurdi | 136 | 0.083333 | 130 | 0.29167
Mymensing | 131 | 0.041667 | 124 | 0.66667 | Ruppur Paromanobik | 136 | 0.041667 | 129 | 0.79167
Kishorganj | 132 | 0.125 | 127 | 0.77083 | Natore | 133 | 0.125 | 126 | 0.29167
Netrokona | 129 | 0.041667 | 122 | 0.77083 | Bogra | 136 | 0.125 | 128 | 0.29167
Jamalpur | 139 | 0.875 | 124 | 0.25 | Noagaon | 131 | 0.083333 | 120 | 0.29167
Sherpur | 138 | 0.875 | 120 | 0.25 | Rajshahi | 131 | 0.125 | 123 | 0.29167
Srimongal | 138 | 0.041667 | 135 | 0.5 | Rajshahi New | 130 | 0.125 | 123 | 0.29167
Shahjibazar | 136 | 0.125 | 133 | 18:30 | C.Nawabganj | 129 | 0.83333 | 121 | 0.29167
Fenchuganj | 138 | 0.33333 | 133 | 0.625 | Amnura | 131 | 0.83333 | 122 | 0.20833
Khulawara | 136 | 0.125 | 132 | 0.75 | Pabna | 135 | 0.083333 | 126 | 0.79167
Sylhet | 135 | 0.041667 | 130 | 0.75 | Shahjadpur | 134 | 0.041667 | 127 | 0.77083
Chatak | 135 | 0.083333 | 130 | 0.75 | Serajganj | 134 | 0.083333 | 125 | 0.29167
Sunamganj | 134 | 0.083333 | 129 | 0.83333 | Niyamatpur | 130 | 0.041667 | 118 | 0.29167
Biani Bazar | 135 | 0.041667 | 130 | 0.75 | Joypurhat | 133 | 0.125 | 117 | 0.29167
Comilla(s) | 132 | 0.95833 | 125 | 0.75 | Sherpur(Bogura) | 137 | 0.125 | 128 | 0.29167
Comilla(n) | 137 | 0.45833 | 134 | 0.66667 | Mohastangor | 134 | 0.041667 | 124 | 0.29167
Chandpur | 134 | 0.29167 | 130 | 0.79167 | Rangpur | 130 | 0.041667 | 118 | 0.33333
Feni | 132 | 0.29167 | 127 | 0.77083 | Lalmonirhat | 126 | 0.125 | 113 | 0.33333
Chowmuhani | 130 | 0.29167 | 122 | 0.77083 | Saidpur | 130 | 0.16667 | 119 | 0.29167
Ashuganj | 138 | 0.33333 | 135 | 0.75 | Purbasadipur | 127 | 0.083333 | 114 | 0.33333
Daudkandi | 131 | 0.33333 | 128 | 0.5 | Thakurgaon | 125 | 0.083333 | 115 | 0.79167
B.Baria | 134 | 0.375 | 130 | 0.8125 | Palashbari | 131 | 0.125 | 117 | 0.29167
Ramganj | 128 | 0.41667 | 123 | 0.91667 | Barapukuria | 133 | 0.041667 | 126 | 0.33333
Chaddagram | 134 | 0.20833 | 128 | 0.58333 | Panchagar | 126 | 0.083333 | 112 | 0.79167
PHP | 131 | 0.33333 | 126 | 0.875 | Joldhaka | 129 | 0.16667 | 119 | 0.33333
Madanhat | 132 | 0.20833 | 129 | 0.45833 | Kurigram | 130 | 0.16667 | 118 | 0.33333

## L-Curve
Date | 2020-03-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 202 | 5811 | 2158 | 7969 |  |  |  | QF-LDC-12
0:30 | 261 | 5625.5 | 1997.5 | 7623 | Date: | 2020-03-11
1:00 | 320 | 5440 | 1837 | 7277
1:30 | 292 | 5263 | 1835.5 | 7098.5
2:00 | 264 | 5086 | 1834 | 6920
2:30 | 226.5 | 4967.5 | 1800.5 | 6768 | [5 empty] | Gen. at Eve. Peak | 9954 | 9954 MW (19:30 )
3:00 | 189 | 4849 | 1767 | 6616 | [6 empty] | 19:30
3:30 | 175 | 4809 | 1740 | 6549 | [5 empty] | Gen. at Day Peak | 8257.6 | 8257.6 MW (12:00 )
4:00 | 161 | 4769 | 1713 | 6482 | [6 empty] | 12:00
4:30 | 180.5 | 4745.5 | 1699 | 6444.5 | [5 empty] | Highest Generation | 9954
5:00 | 200 | 4722 | 1685 | 6407 | [6 empty] | 19:30
5:30 | 228 | 4828 | 1733.5 | 6561.5
6:00 | 256 | 4934 | 1782 | 6716
6:30 | 249 | 5013.55 | 1991.7 | 7005.25
7:00 | 242 | 5093.1 | 2201.4 | 7294.5
7:30 | 201 | 5199.7 | 2263.5 | 7463.2
8:00 | 160 | 5306.3 | 2325.6 | 7631.9
8:30 | 137.5 | 5333.45 | 2365.55 | 7699
9:00 | 115 | 5360.6 | 2405.5 | 7766.1
9:30 | 143 | 5347.35 | 2415.2 | 7762.55
10:00 | 171 | 5334.1 | 2424.9 | 7759
10:30 | 193 | 5386.15 | 2434.55 | 7820.7
11:00 | 215 | 5438.2 | 2444.2 | 7882.4
11:30 | 166 | 5612.85 | 2457.15 | 8070
12:00 | 117 | 5787.5 | 2470.1 | 8257.6
12:30 | 61 | 5830.05 | 2448.1 | 8278.15
13:00 | 5 | 5872.6 | 2426.1 | 8298.7
13:30 | 66.5 | 5742.45 | 2416.15 | 8158.6
14:00 | 128 | 5612.3 | 2406.2 | 8018.5
14:30 | 159 | 5657.75 | 2389.5 | 8047.25
15:00 | 190 | 5703.2 | 2372.8 | 8076
15:30 | 226.5 | 5722.8 | 2392.4 | 8115.2
16:00 | 263 | 5742.4 | 2412 | 8154.4
16:30 | 259 | 5655.65 | 2395.65 | 8051.3
17:00 | 255 | 5568.9 | 2379.3 | 7948.2
17:30 | 194.5 | 5619.45 | 2439.75 | 8059.2
18:00 | 134 | 5670 | 2500.2 | 8170.2
18:30 | 151 | 6210 | 2767.6 | 8977.6
19:00 | 168 | 6750 | 3035 | 9785
19:30 | 170 | 6851 | 3103 | 9954
20:00 | 107 | 6743 | 3143 | 9886 |  |  |  | Executive Engineer
20:30 | 54 | 6632 | 3160.5 | 9792.5 |  |  |  | Network Operation Division
21:00 | 1 | 6521 | 3178 | 9699
21:30 | 15.5 | 6330 | 3086.5 | 9416.5
22:00 | 30 | 6139 | 2995 | 9134 |  |  |  |  | Page 6 of 7
22:30 | 20 | 6059 | 2776.5 | 8835.5
23:00 | 10 | 5979 | 2558 | 8537
23:30 | 106 | 5895 | 2358 | 8253
24:00 | 202 | 5811 | 2158 | 7969
9954 MW (19:30 )
8257.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-11 |  | Energy | 192753232
[10 empty] | 2020-03-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4056 | 407 | 2110 | 1114 | 371 | 66 | 0 | 0 | 108
0:30 | 3969 | 334.5 | 2073.5 | 839.5 | 371.5 | 66.5 | 0 | 0 | 100 | Date: | 2020-03-11
1:00 | 3882 | 262 | 2037 | 565 | 372 | 67 | 0 | 0 | 92
1:30 | 3884 | 262.5 | 2028.5 | 395.5 | 371.5 | 66.5 | 0 | 0 | 90 | [7 empty] | Total Energy | 192.7532 | Total Energy Gen 192.753 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 192.753 MKWHr
2:00 | 3886 | 263 | 2020 | 226 | 371 | 66 | 0 | 0 | 88 | [7 empty] | Energy not Served | 0
2:30 | 3866.5 | 262.5 | 1924.5 | 190 | 370.5 | 66 | 0 | 0 | 88 | [7 empty] | Energy Requirement | 192.7532
3:00 | 3847 | 262 | 1829 | 154 | 370 | 66 | 0 | 0 | 88
3:30 | 3837.5 | 262 | 1768 | 159 | 370 | 65.5 | 0 | 0 | 87 | [6 empty] | Shortage
4:00 | 3828 | 262 | 1707 | 164 | 370 | 65 | 0 | 0 | 86
4:30 | 3803 | 262 | 1696 | 164 | 370 | 64.5 | 0 | 0 | 85
5:00 | 3778 | 262 | 1685 | 164 | 370 | 64 | 0 | 0 | 84
5:30 | 3900 | 262 | 1711.5 | 169 | 370 | 65 | 0 | 0 | 84
6:00 | 4022 | 262 | 1738 | 174 | 370 | 66 | 0 | 0 | 84
6:30 | 4018.5 | 456 | 1793 | 215.5 | 370 | 66.5 | 0 | 0 | 84 |  |  |  |  | Coal
7:00 | 4015 | 650 | 1848 | 257 | 370 | 67 | 0 | 0 | 84
7:30 | 3965 | 650 | 1933 | 387 | 371.5 | 67 | 0 | 0 | 82 |  |  |  | Oil |  |  |  | ,
8:00 | 3915 | 650 | 2018 | 517 | 373 | 67 | 0 | 0 | 80
8:30 | 3912 | 650 | 2011 | 588 | 372.5 | 67 | 0 | 0 | 82
9:00 | 3909 | 650 | 2004 | 659 | 372 | 67 | 0 | 0 | 84
9:30 | 3906 | 650 | 1961 | 706.5 | 361.5 | 67 | 0 | 0 | 86
10:00 | 3903 | 650 | 1918 | 754 | 351 | 67 | 0 | 0 | 88
10:30 | 4004 | 650 | 1850.5 | 776 | 351 | 67 | 0 | 0 | 90
11:00 | 4105 | 650 | 1783 | 798 | 351 | 67 | 0 | 0 | 92
11:30 | 4132.5 | 650 | 1898.5 | 841.5 | 351.5 | 67 | 0 | 0 | 96
12:00 | 4160 | 650 | 2014 | 885 | 352 | 67 | 0 | 0 | 100
12:30 | 4086.5 | 650 | 2000 | 994 | 352 | 67 | 0 | 0 | 98
13:00 | 4013 | 650 | 1986 | 1103 | 352 | 67 | 0 | 0 | 96
13:30 | 4013 | 650 | 1986 | 1103 | 352 | 67 | 0 | 0 | 96
14:00 | 4013 | 650 | 1986 | 1103 | 352 | 67 | 0 | 0 | 96
14:30 | 4020 | 649 | 1956 | 1025 | 352 | 66.5 | 0 | 0 | 98
15:00 | 4027 | 648 | 1926 | 947 | 352 | 66 | 0 | 0 | 100
15:30 | 4011 | 648 | 1968 | 951 | 362 | 65.5 | 0 | 0 | 98
16:00 | 3995 | 648 | 2010 | 955 | 372 | 65 | 0 | 0 | 96
16:30 | 3981.5 | 648 | 1941.5 | 938.5 | 372 | 64.5 | 0 | 0 | 96
17:00 | 3968 | 648 | 1873 | 922 | 372 | 64 | 0 | 0 | 96
17:30 | 4053 | 697 | 1774.5 | 988.5 | 371.5 | 64 | 0 | 0 | 108
18:00 | 4138 | 746 | 1676 | 1055 | 371 | 64 | 0 | 0 | 120
18:30 | 4049 | 842.5 | 1872.5 | 1626.5 | 371 | 64.5 | 25.5 | 0 | 126
19:00 | 3960 | 939 | 2069 | 2198 | 371 | 65 | 51 | 0 | 132
19:30 | 3948 | 940 | 2045 | 2404 | 371 | 65 | 51 | 0 | 130
20:00 | 3986 | 939 | 2017 | 2328 | 370 | 65 | 51 | 0 | 130
20:30 | 4047.5 | 939 | 2029.5 | 2165 | 370 | 64.5 | 51 | 0 | 126
21:00 | 4109 | 939 | 2042 | 2002 | 370 | 64 | 51 | 0 | 122
21:30 | 4036 | 939.5 | 2056 | 1804 | 370.5 | 64 | 25.5 | 0 | 121
22:00 | 3963 | 940 | 2070 | 1606 | 371 | 64 | 0 | 0 | 120
22:30 | 3974.5 | 867 | 2080 | 1360 | 371 | 65 | 0 | 0 | 118
23:00 | 3986 | 794 | 2090 | 1114 | 371 | 66 | 0 | 0 | 116
23:30 | 4021 | 600.5 | 2100 | 1114 | 371 | 66 | 0 | 0 | 112 | Max Temp. in Dhaka |  | 32.0° C
24:00 | 4056 | 407 | 2110 | 1114 | 371 | 66 | 0 | 0 | 108
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 192.753 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 192.753 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 27 | 26 | 26 | 25 | 24 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 25 | 24 | 24 |  | 25 | 25 | 25 | 24 | 24 | 26 | 26 | 554700
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 932000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7.6 | 12.9 | 17 | 19 | 15.1 | 17.3 | 16.8 |  | 7.9 | 2.9 | [9 empty] | 119340
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 206 | 212 | 203 | 203 | 216 | 215 | 202 | 203 | 204 | 207 | 217 | 204 | 211 | 214 | 203 | 204 | 217 |  | 204 | 203 | 202 | 208 | 203 | 203 | 212 | 4930868
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 104 | 104 | 104 | 107 | 105 | 100 | 100 | 104 | 106 | 106 | 136 | 130 | 134 | 134 | 120 | 120 | 120 | 100 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2760655
10 | Sikalbaha 150MW GTPP(Oil)
Dohazari -Kalaish 100 MW Peaking
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 0 |  | 99 | 150 | 149 | 89 |  |  | 0 | 358799
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 180 | 150 | 150 | 150 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4571000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 314 | 316 | 314 | 321 | 314 | 350 | 334 | 312 | 312 | 314 | 326 | 341 | 314 | 335 | 335 | 333 | 320 | 364 |  | 320 | 320 | 336 | 345 | 320 | 328 | 336 | 7842973
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 120 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 95 | 80 | 80 | 2572700
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 30 |  | 20 | 20 | 20 | 20 | 20 | 46 | 46 | 390168
33 | Ashuganj 225 MW CCPP | 223 | 219 | 225 | 225 | 224 | 225 | 224 | 183 | 184 | 185 | 216 | 205 | 184 | 194 | 186 | 179 | 184 | 203 |  | 183 | 184 | 184 | 185 | 221 | 221 | 222 | 4959000
34 | Ashuganj 450 MW CCPP(South) | 295 | 305 | 295 | 305 | 295 | 345 | 325 | 305 | 300 | 305 | 330 | 335 | 305 | 300 | 285 | 270 | 265 | 305 |  | 265 | 265 | 265 | 295 | 260 | 265 | 275 | 7264000
| Ashuganj 450 MW CCPP(North) | 295 | 300 | 295 | 305 | 290 | 360 | 335 | 300 | 305 | 305 | 330 | 340 | 310 | 335 | 330 | 320 | 320 | 360 |  | 315 | 310 | 315 | 350 | 295 | 290 | 300 | 7956500
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 279840
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 95 | 88 | 92 | 95 | 95 | 95 | 96 | 95 | 96 | 87 | 95 |  | 86 | 86 | 95 | 95 | 95 | 95 | 95 | 1895880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 336 | 337 | 346 | 338 | 360 | 375 | 351 | 337 | 340 | 350 | 371 | 355 | 348 | 379 | 373 | 344 | 360 |  | 370 | 338 | 338 | 364 | 348 | 340 | 358 | 8586240
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 360 | 360 | 360 | 400 | 400 | 400 | 370 | 340 | 420 | 420 | 360 | 420 | 420 | 370 | 300 |  | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 9304250
41 | Haripur 360MW CCPP(HPL) | 310 | 308 | 309 | 309 | 310 | 309 | 365 | 363 | 363 | 330 | 270 | 352 | 352 | 290 | 347 | 350 | 320 | 300 |  | 358 | 360 | 300 | 298 | 307 | 358 | 359 | 7803000
42 | RPCL 210MW CCPP | 151 | 151 | 151 | 164 | 164 | 164 | 164 | 164 | 162 | 160 | 157 | 155 | 157 | 155 | 155 | 154 | 154 | 154 |  | 158 | 159 | 159 | 159 | 160 | 161 | 161 | 3698080
43
44 | Fenchugonj CCPP Phase-1 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 89 | 88 | 87 | 87 | 89 | 89 | 89 | 88 | 88 | 88 |  | 88 | 88 | 87 | 88 | 87 | 85 | 85 | 2041000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 147 | 152 | 150 | 151 | 149 | 156 | 156 | 146 | 147 | 147 | 154 | 154 | 153 | 160 | 153 | 152 | 149 | 164 |  | 146 | 147 | 148 | 155 | 150 | 153 | 155 | 3522000
47 | Shahjibazar GTPP Unit- 8 & 9 | 54 | 54 | 45 | 45 | 45 | 45 | 63 | 63 | 61 | 61 | 59 | 58 | 60 | 58 | 58 | 58 | 60 | 45 |  | 62 | 62 | 62 | 61 | 62 | 62 | 62 | 1368000
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 40 | 10 | 10 | 10 | 10 | 78 | 78 | 75 | 75 | 75 | 78 | 20 | 20 | 78 | 78 | 20 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1380480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 395000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 242640
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 45 | 45 | 45 | 48 | 48 | 48 | 50 | 50 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1005000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 575655
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 300 | 310 | 310 | 315 | 325 | 310 | 300 | 300 | 310 | 325 | 310 | 310 | 325 | 315 | 310 | 300 |  | 300 | 295 | 290 | 305 | 315 | 310 | 320 | 7706500
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448368
61 | Narshingdi 22 MW PP (Doreen) | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 434340
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 483300
63 | Impoprt (Tripura) | 92 | 88 | 88 | 86 | 84 | 84 | 84 | 80 | 84 | 88 | 92 | 100 | 96 | 100 | 100 | 96 | 96 | 120 |  | 132 | 130 | 130 | 122 | 120 | 116 | 108 | 2392320
64 | Malancha, Ctg. EPZ (United) | 40 | 38 | 40 | 40 | 40 | 42 | 34 | 10 | 2 | 2 | 2 | 2 | 10 | 2 | 2 | 5 | 8 | 12 |  | 20 | 23 | 28 | 34 | 37 | 40 | 28 | 511680
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 489492
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 685300
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 541180
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 28 | 28 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 28 | 28 | 24 |  | 20 | 28 | 28 | 30 | 30 | 30 | 30 | 676080
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 838400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 667200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
Chowmuhani 113 MW
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 16 | [6 empty] | 2 | 24 | 24 | 24 | 30 | 98 | 84 | 60 | 60 | 60 | 65 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1210560
78 | Gazipur 52 MW PP | [20 empty] | 16 | 34 | 48 | 51 |  | 0 | 137580
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 2 | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 8 | 13 | 16 |  | 75 | 95 | 95 | 95 | 95 | 48 | 0 | 710400
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [17 empty] | 17 |  | 34 | [5 empty] | 0 | 29952
| Kaptai 7 MW Solar PP | [6 empty] | 0.9 | 1.9 | 3.3 | 4.2 | 9.1 | 5.1 | 5 | 4.4 | 3.6 | 2 | 0.7 | [9 empty] | 35520
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 96 | [5 empty] | 5 | 30 | 30 | 30 | 30 | 30 | 64 | 78 | 96 | 96 | 80 | 80 |  | 91 | 97 | 97 | 97 | 97 | 97 | 97 | 1401816
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 3 |  | 24 | [5 empty] | 0 | 33053
86 | Meghnaghat CCPP(Summit) | 130 | 140 | 130 | 140 | 140 | 150 | 140 | 130 | 130 | 140 | 140 | 140 | 135 | 140 | 140 | 140 | 130 | 145 |  | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 3322705
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 1 | 7 | 7 | 7 | 7 | 20 |  |  |  |  | 3 |  | 80 | 100 | 100 | 100 | 70 | 50 | 0 | 503040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 51 | 51 | 5 | 5 | 5 | 5 | 9 | 44 | 48 | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 48 |  | 48 | 48 | 48 | 48 | 45 | 45 | 45 | 1011240
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 5 | 5 | 5 | 5 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 903856
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 3 | 7 | 7 | 7 | 7 | 24 | 7 | 7 | 7 | 7 | 7 |  | 72 | 93 | 102 | 102 | 58 | 58 | 0 | 531792
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 38 | 50 | 50 | 48 |  |  | 0 | 151680
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 2 |  | 37 | 60 | 48 |  |  |  | 0 | 85440
97 | Katpotti 52 MW PP (Sinha) | [19 empty] | 20 | 6 |  |  |  |  | 0 | 39840
98 | Bosila 108MW PP(CLC) | 72 | [7 empty] | 24 | 24 | 24 | 50 | 65 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1016640
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 25 |  |  |  | 0 | 569141
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 |  |  |  | 0 | 229828
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 163 | 163 | 130 | 130 | 163 | 130 | 110 |  | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 3752345
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.2 | 0.8 | 1.4 | 1.9 | 2.1 | 2.3 | 2.3 | 2.1 | 1.6 | 0.5 | 0.3 | [9 empty] | 15100
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | [7 empty] | 17 | 17 | 17 | 35 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 803160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 165 | 70 | 24 | 24 | 24 | 24 | 65 | 168 | 168 | 170 | 170 | 170 | 170 | 170 | 170 | 160 | 120 | 173 |  | 154 | 154 | 154 | 154 | 154 | 173 | 173 | 3271200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 8 | 14 | 15 | 15 | 15 |  |  |  |  | 4 |  | 116 | 149 | 150 | 84 | 20 |  | 0 | 470880
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 35 |  | 100 | 100 | 70 |  |  |  | 0 | 196800
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 0 |  | 40 | 70 | 35 |  |  |  | 0 | 120436
118 | Bibiyana-III 400 MW CCPP | 234 | 232 | 233 | 233 | 231 | 231 | 233 | 234 | 234 | 234 | 234 | 233 | 233 | 235 | 234 | 234 | 235 | 233 |  | 235 | 235 | 233 | 233 | 233 | 233 | 234 | 5610000
| Jamalpur 115 MW PP (United) | [17 empty] | 4 |  | 66 | 115 | 115 | 115 | 85 |  | 0 | 444000
| Anwara 300 MW PP (United) | 51 | 16 | [5 empty] | 16 | 16 | 50 | 48 | 65 | 103 | 69 | 69 | 87 | 121 | 70 |  | 224 | 178 | 178 | 179 | 179 | 180 | 107 | 1866764
120 | Eastern Zone Total | 5440 | 5086 | 4849 | 4769 | 4722 | 4934 | 5093.1 | 5306.3 | 5360.6 | 5334.1 | 5438.2 | 5787.5 | 5872.6 | 5612.3 | 5703.2 | 5742.4 | 5568.9 | 5670 |  | 6750 | 6851 | 6743 | 6521 | 6139 | 5979 | 5811 | 135572543
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [7 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 55 |  | 115 | 115 | 115 | 115 | 115 | 10 | 0 | 877440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 48 | 48 | 48 | 48 | 48 |  | 0 | 211200
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 98 | 97 | 61 | 22 | 22 | 21 | 32 | 97 | 97 | 97 | 52 | 51 | 51 | 51 | 51 | 51 | 52 | 0 |  | 77 | 95 | 97 | 95 | 95 | 96 | 97 | 1566033
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 125 | 126 | 130 | 130 | 130 | 130 | 130 | 3118000
140 | Bhola 33 MW PP (Venture) | 17 | 16 | 16 | 15 | 15 | 15 | 14 | 13 | 12 | 12 | 12 | 13 | 13 | 13 | 14 | 13 | 13 | 16 |  | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 372946
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 7680
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 40 | 40 | 40 | 40 |  |  | 143625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | [19 empty] | 50 | 50 | 50 | 50 |  |  | 0 | 151344
146 | Bheramara HVDC | 262 | 263 | 262 | 262 | 262 | 262 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 648 | 648 | 648 | 746 |  | 939 | 940 | 939 | 939 | 940 | 794 | 407 | 14239273
147 | Bheramara 410 MW CCPP | 330 | 330 | 330 | 340 | 335 | 385 | 360 | 330 | 330 | 330 | 355 | 370 | 330 | 365 | 350 | 330 | 330 | 390 |  | 330 | 330 | 330 | 365 | 330 | 340 | 350 | 8683200
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1 | 92 | 91 | 90 | 90 | 90 | 90 | 90 | 93 | 92 | 91 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 91 |  | 91 | 91 | 90 | 90 | 91 | 91 | 91 | 2167855
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6656300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 180 | 180 | 180 | 140 | 140 | 140 | 140 | 155 | 180 | 180 | 214 | 214 | 214 | 170 | 170 | 214 | 214 | 160 |  | 200 | 214 | 220 | 214 | 200 | 200 | 200 | 4774855
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 413 | 412 | 396 | 412 | 389 | 437 | 435 | 403 | 397 | 410 | 414 | 414 | 390 | 414 | 416 | 414 | 388 | 416 |  | 399 | 390 | 420 | 428 | 437 | 426 | 437 | 10005000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 5 | 5 | 5 | 5 | 5 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 360000
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 281736
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 180396
165 | Amnura 50 MW PP(Sinha) | [6 empty] | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 33 | 24 | 24 | 18 | 18 |  | 50 | 50 | 50 | 50 | 50 | 24 |  | 708310
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 51 | 51 | 51 | 51 |  |  |  | 168516
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 33 | 70 | 70 | 70 | 80 | 100 | 109 | 109 | 109 | 109 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 1697760
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 20 | 44 | 70 | 70 | 70 | 70 | 44 | 35 | 35 | 35 | 35 |  | 71 | 114 | 114 | 114 | 70 |  | 0 | 934080
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 1.6 | 3.5 | 4.9 | 6.2 | 7.1 | 7.1 | 6.2 | 4.8 | 3 | 1.3 | 0.2 | [8 empty] | 45540
178
178