## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-04-01 | Wednesday
|  | Date (day): | 2020-04-01 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12553.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15256 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-03-31 | 2020-04-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 335 | 250 | 365 | 365
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 364 | 339 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 348 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 52 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 130 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 30 | 80 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 70 | 80 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 200 | 210 | 220 | 220 | 115 |  | ST under S/D.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 |  | 108 | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 35 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 21 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 30 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2051 | 2272 | 3788 | 4408 | 671 | 726
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 76 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 217 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 104 | 145 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 80 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 40 | 40 | 42
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.7 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 65 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 50 | 90 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 639.5 | 766 | 1631 | 1758 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 115 | 100 | 120 | 9 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 180 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 260 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 46 | 46
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 45 | 45 | 150 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 135 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 134 | 116 | 131
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 21 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 65 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1165 | 1414 | 1659 | 2358 | 478 | 0
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 200 | 207 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.5 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 115 | 115 | 120 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 35 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 411.5 | 474 | 563.6 | 642 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 62 | 62 | 62 | 62
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 317 | 281 | 300 | 310 |  | 20 | Engine problem
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 45 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 80 | 86
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 70 | 110 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1026 | 1136 | 1365 | 1381 | 0 | 467
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 351 | 934 | 349 | 745
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 330 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 726 | 1403 | 1084 | 1990 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 22 | 20 | 23 |  | 10 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 177 | 180 | 185 | 185
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 300 | 390 | 0 | 0 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 491 | 592 | 364 | 443 | 0 | 10
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 50 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 60 | 60 | 60 | 40 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel Shortage.
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 40 | 40 |  | 10 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 29 | 37 | 40 | 40
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 150 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 150 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 410 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 12 | 17 | 18 | 18
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 42 | 100 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 18 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 922 | 1147 | 1628 | 1779 | 260 | 10
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 66 | 70 | 70
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 270 | 280 | 280 | 280
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 454.4 | 459 | 471 | 497 | 0 | 0
| Total |  |  |  |  | 19630 | 19107 | 7886.4 | 9663 | 12553.6 | 15256 | 1819 | 1311
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7479.9603 | 9165 | 11906.6278 | 14469.7547
A. |  | 2020-03-31 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 9663 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6673.1 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9663 | MW
3 | Day peak Generation : |  |  | 7886.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9165 | MW
4 | Evening peak Generation : |  |  | 9663 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 190.1744 | MKWHr | By Solar | 0.22069 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 143.5638 | MKWHr |  | By Oil: | 14.3572 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 15.9443 | MKWHr |  | By Hydro: | 1.7661 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1819 | MW | Dhaka | 2625 | 2625 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1311 | MW | Chittagong | 1047 | 1047 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3130 | MW | Khulna | 1221 | 1221 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1179.34 | MMCFD |  |  | Rajshahi | 1124 | 1124 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 165435771.988 | ii) Oil : | Taka | 88724417.14 | Comilla | 958 | 958 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 79246678.97 | Total | Taka | 333406868.098 | Mymensingh | 877 | 877 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.327 | MKWHr. | Sylhet | 350 | 350 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 67 | MW (E to W) at | 19:30 | hrs | Barisal | 249 | 249 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -270 | MW at | 8:00 | hrs | Rangpur | 714 | 714 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36° C |  |  | Total | 9165 | 9165 |  | 0
B. |  | 2020-04-01 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 38.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15256 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 5356 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 194.8387 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6763.1 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.6516 | MKWHr. | ii) HVDC Flow at Peak Time |  | 934 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6707 | MKWHr. | iii) Maximum HVDC Flow : |  | 935 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.51 |  | (b) Today: | 82.19 |  | (c) Rule Curve: |  | 88
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-03-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 120 | 0 | 275 | 0 | 0 | 337 | 273 |  | 0 | 360 | 140 | 0 | 0 | 0 | 183 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 310 | 260 | 161 | 8 | 0 | 44 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 112 | 214 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 130 | 289 | 45 | 10 | 0 | 100 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 |  | 740 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 8 | 0 | 65 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4826 | 2695 | 7521 | 4218 | 740 | 1504 | 220 | 626 | 77 | 24 | 112 | 0 | 0 | 82.66
2:00 | 24 | 0 | 120 | 0 | 276 | 0 | 0 | 348 | 292 |  | 0 | 360 | 150 | 0 | 0 | 0 | 218 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 315 | 265 | 166 | 8 | 0 | 45 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 110 | 214 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 130 | 299 | 45 | 10 | 0 | 100 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 255 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 8 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 |  | 4885 | 2216 | 7101 | 4257 | 255 | 1557 | 194 | 627 | 77 | 24 | 110 | 0 | 0 | 82.63
3:00 | 24 | 0 | 120 | 0 | 275 | 0 | 0 | 340 | 292 |  | 0 | 360 | 140 | 0 | 0 | 0 | 218 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 310 | 260 | 158 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 100 | 214 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 163 | 295 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 255 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 8 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4819 | 2133 | 6952 | 4125 | 255 | 1585 | 184 | 626 | 77 | 0 | 100 | 0 | 0 | 82.6
4:00 | 24 | 0 | 100 | 0 | 276 | 0 | 0 | 337 | 292 |  | 0 | 360 | 140 | 0 | 0 | 0 | 218 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 204 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 280 | 260 | 160 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 100 | 215 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 130 | 291 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 254 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 8 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4702 | 2121 | 6823 | 4061 | 254 | 1522 | 184 | 625 | 77 | 0 | 100 | 0 | 0 | 82.57
5:00 | 24 | 0 | 100 | 0 | 276 | 0 | 0 | 341 | 292 |  | 0 | 320 | 150 | 0 | 0 | 0 | 170 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 208 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 280 | 275 | 175 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 96 | 215 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 130 | 304 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 255 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 8 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4621 | 2166 | 6787 | 4051 | 255 | 1516 | 167 | 625 | 77 | 0 | 96 | 0 | 0 | 82.54
6:00 | 24 | 0 | 100 | 0 | 276 | 0 | 0 | 344 | 262 |  | 0 | 320 | 140 | 0 | 0 | 0 | 150 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 203 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 265 | 260 | 161 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 90 | 216 | 0 | 22 | 0 | 60 | 43 | 5 | 5 | 130 | 291 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 351 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 12 | 11 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 301 |  | 4503 | 2170.1 | 6673.1 | 3902 | 351 | 1437 | 190 | 626 | 77 | 0 | 90 | 0.1 | 0 | 82.51
7:00 | 24 | 0 | 100 | 0 | 276 | 0 | 0 | 338 | 262 |  | 0 | 320 | 145 | 0 | 0 | 0 | 150 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 12 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 204 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 80 | 0 | 280 | 265 | 170 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 5 | 8 | 21 | 90 | 217 | 12 | 20 | 0.4 | 61 | 43 | 5 | 5 | 130 | 296 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 10 |  | 350 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 5 | 12 | 11 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 301 |  | 4581.4 | 2239.8 | 6821.2 | 3906 | 350 | 1483 | 284 | 626 | 77 | 0 | 90 | 5.2 | 0 | 82.49
8:00 | 24 | 0 | 100 | 0 | 289 | 0 | 0 | 348 | 262 |  | 0 | 320 | 150 | 0 | 0 | 0 | 150 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 20 | 17 | 0 | 0 | 37 | 40 | 110 | 0 | 0 | 208 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 300 | 280 | 180 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 5 | 8 | 21 | 82 | 213 | 30 | 20 | 1.1 | 61 | 43 | 5 | 5 | 130 | 300 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 10 |  | 351 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 11 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 42 | 4 | 0 | 0 | 17 | 12 | 11 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 371 | 0 | 0 | 0 | 0 | 30 | 0 | 2.8 | 20 | 301 |  | 4765.5 | 2315.8 | 7081.3 | 4015 | 351 | 1508 | 405 | 626 | 77 | 4 | 82 | 13.3 | 0 | 82.47
9:00 | 24 | 0 | 100 | 0 | 309 | 0 | 0 | 362 | 278 |  | 0 | 320 | 145 | 0 | 4 | 0 | 150 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 17 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 217 | 0 | 108 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 310 | 295 | 181 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 5 | 8 | 21 | 96 | 207 | 40 | 22 | 1.6 | 61 | 43 | 5 | 5 | 130 | 304 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 11 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 10 |  | 351 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 42 | 0 | 0 | 29 | 0 | 0 | 17 | 12 | 11 | 0 | 65 | 260 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 373 | 0 | 0 | 0 | 0 | 40 | 0 | 4.6 | 35 | 301 |  | 4881.5 | 2370.6 | 7252.1 | 4073 | 351 | 1538 | 399 | 626 | 77 | 71 | 96 | 21.1 | 0 | 82.46
10:00 | 24 | 0 | 100 | 0 | 283 | 0 | 0 | 368 | 300 |  | 0 | 320 | 140 | 0 | 15 | 0 | 150 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 17 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 207 | 0 | 103 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 365 | 275 | 170 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 5 | 8 | 21 | 98 | 205 | 50 | 22 | 2 | 61 | 43 | 5 | 5 | 130 | 295 | 45 | 10 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 30 |  | 351 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 42 | 0 | 0 | 29 | 0 | 0 | 17 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 410 | 0 | 0 | 0 | 0 | 64 | 0 | 5.9 | 55 | 300 |  | 4973.2 | 2452.9 | 7426.1 | 4104 | 351 | 1592 | 471 | 635 | 77 | 71 | 98 | 27.1 | 0 | 82.45
11:00 | 24 | 0 | 100 | 0 | 300 | 0 | 0 | 354 | 298 |  | 0 | 320 | 140 | 0 | 22 | 0 | 150 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 17 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 218 | 0 | 105 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 345 | 295 | 182 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 100 | 202 | 64 | 22 | 2.4 | 62 | 43 | 5 | 5 | 130 | 308 | 51 | 10 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 30 |  | 352 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 42 | 0 | 0 | 29 | 0 | 0 | 16 | 11 | 11 | 0 | 64 | 270 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 410 | 0 | 0 | 0 | 0 | 104 | 0 | 6.8 | 70 | 302 |  | 5038.6 | 2505.8 | 7544.4 | 4143 | 352 | 1589 | 546 | 636 | 77 | 71 | 100 | 30.4 | 0 | 82.44
12:00 | 24 | 0 | 100 | 0 | 335 | 0 | 0 | 364 | 343 |  | 0 | 350 | 140 | 0 | 30 | 0 | 200 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 25 | 17 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 219 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 350 | 310 | 183 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 17 | 110 | 200 | 72 | 22 | 2.5 | 62 | 43 | 5 | 5 | 130 | 317 | 58 | 10 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 50 |  | 351 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 42 | 0 | 0 | 29 | 0 | 0 | 12 | 11 | 11 | 0 | 64 | 270 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 402 | 0 | 0 | 0 | 0 | 113 | 0 | 7.4 | 70 | 300 |  | 5293 | 2593.4 | 7886.4 | 4365 | 351 | 1657 | 590 | 634 | 77 | 71 | 110 | 31.4 | 0 | 82.43
13:00 | 24 | 0 | 130 | 0 | 310 | 0 | 0 | 378 | 341 |  | 0 | 420 | 140 | 0 | 30 | 0 | 200 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 218 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 330 | 285 | 195 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 17 | 114 | 189 | 82 | 22 | 2.3 | 62 | 43 | 5 | 5 | 163 | 300 | 58 | 10 | 0 | 128 | 0 | 0 | 0 | 320 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 10 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 70 |  | 350 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 16 | 0 | 0 | 0 | 65 | 0 | 0 | 51 | 0 | 0 | 29 | 0 | 0 | 12 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 405 | 0 | 0 | 0 | 0 | 113 | 0 | 6.7 | 70 | 301 |  | 5559.4 | 2645.7 | 8205.1 | 4521 | 350 | 1768 | 630 | 636 | 77 | 80 | 114 | 29.1 | 0 | 82.42
14:00 | 24 | 0 | 130 | 0 | 304 | 0 | 0 | 353 | 344 |  | 0 | 420 | 120 | 0 | 30 | 0 | 199 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 21 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 226 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 315 | 265 | 184 | 8 | 51 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 21 | 122 | 185 | 82 | 22 | 2.2 | 62 | 43 | 5 | 5 | 163 | 297 | 58 | 81 | 0 | 131 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 15 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 100 |  | 350 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 15 | 0 | 0 | 0 | 65 | 0 | 0 | 51 | 0 | 0 | 33 | 0 | 0 | 12 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 410 | 0 | 0 | 0 | 0 | 113 | 0 | 5.9 | 70 | 302 |  | 5561.5 | 2675.9 | 8237.4 | 4469 | 350 | 1826 | 645 | 637 | 78 | 84 | 122 | 26.4 | 0 | 82.41
15:00 | 24 | 0 | 130 | 0 | 301 | 0 | 0 | 341 | 341 |  | 0 | 420 | 120 | 0 | 47 | 0 | 198 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 227 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 315 | 265 | 181 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 120 | 186 | 82 | 22 | 1.7 | 62 | 43 | 5 | 5 | 163 | 275 | 59 | 81 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 15 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 100 |  | 351 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 19 | 0 | 0 | 50 | 65 | 0 | 0 | 50 | 0 | 0 | 36 | 0 | 0 | 12 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 394 | 0 | 0 | 0 | 0 | 111 | 0 | 4.9 | 70 | 300 |  | 5541.3 | 2708.9 | 8250.2 | 4490 | 351 | 1811 | 660 | 635 | 78 | 86 | 120 | 19.2 | 0 | 82.4
16:00 | 24 | 0 | 131 | 0 | 301 | 0 | 0 | 342 | 340 |  | 0 | 420 | 140 | 0 | 35 | 0 | 198 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 38 | 40 | 100 | 0 | 0 | 225 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 310 | 265 | 181 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 116 | 188 | 16 | 22 | 1 | 62 | 43 | 5 | 5 | 163 | 276 | 59 | 80 | 0 | 139 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 50 |  | 350 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 18 | 0 | 0 | 60 | 65 | 0 | 0 | 50 | 0 | 0 | 37 | 0 | 0 | 12 | 11 | 11 | 0 | 64 | 270 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 402 | 0 | 0 | 0 | 0 | 28 | 0 | 3.6 | 35 | 300 |  | 5336.2 | 2610.6 | 7946.8 | 4455 | 350 | 1806 | 409 | 634 | 78 | 87 | 116 | 11.8 | 0 | 82.39
17:00 | 24 | 0 | 101 | 0 | 301 | 0 | 0 | 341 | 340 |  | 0 | 370 | 130 | 0 | 30 | 0 | 200 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 219 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0 | 80 | 0 | 315 | 265 | 181 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 108 | 200 | 8 | 20 | 0.5 | 62 | 43 | 8 | 5 | 163 | 284 | 60 | 10 | 0 | 100 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 10 |  | 350 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 15 | 0 | 0 | 60 | 50 | 0 | 0 | 50 | 0 | 0 | 37 | 0 | 0 | 13 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 35 | 301 |  | 5057.6 | 2516.8 | 7574.4 | 4330 | 350 | 1663 | 318 | 636 | 77 | 87 | 108 | 5.4 | 0 | 82.38
18:00 | 24 | 0 | 100 | 0 | 275 | 0 | 0 | 341 | 279 |  | 0 | 320 | 135 | 1 | 30 | 0 | 154 | 0 | 86 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 6 | 33 | 21 | 0 | 0 | 36 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 8 | 0 | 10 | 1 | 21 | 40 | 0 | 80 | 0 | 315 | 265 | 180 | 8 | 51 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 21 | 108 | 160 | 8 | 22 | 0 | 62 | 43 | 8 | 5 | 100 | 282 | 62 | 10 | 0 | 70 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0.1 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 8 | 10 |  | 350 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 14 | 0 | 0 | 60 | 50 | 0 | 0 | 50 | 0 | 25 | 37 | 0 | 0 | 15 | 11 | 11 | 0 | 65 | 270 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 35 | 312 |  | 4765.1 | 2494.4 | 7259.5 | 4101 | 350 | 1485 | 397 | 647 | 76 | 95 | 108 | 0.5 | 0 | 82.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 101 | 0 | 250 | 0 | 0 | 353 | 348 |  | 0 | 350 | 120 | 37 | 34 | 15 | 206 | 0 | 108 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 0 | 25 | 6 | 33 | 21 | 0 | 0 | 35 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 59 | 0 | 8 | 28 | 21 | 40 | 0 | 115 | 0 | 315 | 260 | 180 | 8 | 51 | 10 | 5 | 0 | 20 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 134 | 206 | 51 | 22 | 0 | 62 | 43 | 47 | 27 | 100 | 283 | 45 | 81 | 0 | 110 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 55 | 0 | 0 | 112 | 0 | 35 | 0 | 10 | 0 | 45 | 0 | 36 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 58 | 90 |  | 799 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 167 | 23 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 42 | 37 | 8 | 0 | 17 | 11 | 11 | 0 | 65 | 280 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 384 | 0 | 0 | 34 | 0 | 34 | 0 | 0 | 50 | 348 |  | 5902 | 3325 | 9227 | 4306 | 799 | 1731 | 1293 | 693 | 75 | 196 | 134 | 0 | 0 | 82.36
19:30 | 24 | 0 | 100 | 0 | 250 | 0 | 0 | 339 | 348 |  | 0 | 350 | 130 | 52 | 80 | 0 | 210 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 0 | 25 | 10 | 33 | 21 | 0 | 0 | 36 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 0 | 19 | 21 | 40 | 0 | 115 | 0 | 315 | 260 | 180 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 134 | 207 | 95 | 22 | 0 | 62 | 43 | 53 | 50 | 100 | 281 | 45 | 81 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 45 | 0 | 0 | 115 | 0 | 30 | 0 | 0 | 0 | 135 | 0 | 35 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 90 |  | 934 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 22 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 24 | 37 | 0 | 0 | 17 | 11 | 11 | 0 | 66 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 410 | 0 | 0 | 18 | 0 | 113 | 0 | 0 | 109 | 390 |  | 6062 | 3601 | 9663 | 4252 | 934 | 1846 | 1514 | 736 | 76 | 171 | 134 | 0 | 0 | 0
20:00 | 24 | 0 | 101 | 0 | 250 | 0 | 0 | 340 | 333 |  | 0 | 350 | 140 | 0 | 82 | 0 | 213 | 0 | 70 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 10 | 33 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 219 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 40 | 0 | 115 | 0 | 335 | 280 | 196 | 8 | 51 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 134 | 206 | 95 | 22 | 0 | 62 | 43 | 53 | 50 | 100 | 297 | 45 | 81 | 0 | 111 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 25 | 0 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 65 | 90 |  | 935 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 22 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 24 | 40 | 0 | 0 | 17 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 422 | 0 | 0 | 45 | 0 | 113 | 0 | 0 | 109 | 408 |  | 5795 | 3684 | 9479 | 4352 | 935 | 1819 | 1233 | 755 | 77 | 174 | 134 | 0 | 0 | 82.35
21:00 | 24 | 0 | 100 | 0 | 284 | 0 | 0 | 348 | 349 |  | 0 | 420 | 130 | 0 | 48 | 0 | 214 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 10 | 33 | 21 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 218 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 40 | 0 | 120 | 0 | 325 | 275 | 192 | 8 | 50 | 45 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 132 | 207 | 72 | 22 | 0 | 61 | 43 | 53 | 50 | 130 | 294 | 45 | 81 | 0 | 111 | 0 | 0 | 10 | 310 | 0 | 11 | 0 | 0 | 0 | 0 | 124 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 50 |  | 934 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 24 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 24 | 38 | 0 | 0 | 17 | 12 | 11 | 0 | 66 | 280 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 425 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 109 | 452 |  | 5762 | 3653 | 9415 | 4452 | 934 | 1985 | 865 | 798 | 77 | 172 | 132 | 0 | 0 | 82.34
22:00 | 24 | 0 | 100 | 0 | 275 | 0 | 0 | 340 | 352 |  | 0 | 420 | 120 | 0 | 30 | 0 | 218 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 10 | 33 | 21 | 0 | 0 | 33 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 42 | 0 | 120 | 0 | 315 | 260 | 180 | 8 | 50 | 45 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 130 | 212 | 16 | 22 | 0 | 61 | 43 | 5 | 50 | 130 | 281 | 45 | 81 | 0 | 110 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 124 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 30 |  | 935 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 170 | 22 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 24 | 38 | 0 | 0 | 17 | 12 | 11 | 0 | 66 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 388 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 90 | 449 |  | 5471 | 3525 | 8996 | 4345 | 935 | 1863 | 683 | 795 | 73 | 172 | 130 | 0 | 0 | 82.33
23:00 | 24 | 0 | 100 | 0 | 275 | 0 | 0 | 338 | 322 |  | 0 | 390 | 130 | 0 | 30 | 0 | 180 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 10 | 25 | 21 | 0 | 0 | 37 | 40 | 95 | 0 | 0 | 216 | 0 | 104 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 0 | 120 | 0 | 300 | 260 | 180 | 8 | 50 | 43 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 122 | 212 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 100 | 282 | 45 | 5 | 0 | 110 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 |  | 935 | 0 | 335 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 21 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 0 | 10 | 0 | 0 | 18 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 381 |  | 5107 | 3230 | 8337 | 4290 | 935 | 1583 | 458 | 728 | 77 | 144 | 122 | 0 | 0 | 82.32
24:00 | 24 | 0 | 102 | 0 | 275 | 0 | 0 | 338 | 322 |  | 0 | 390 | 130 | 0 | 15 | 0 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 25 | 21 | 0 | 0 | 37 | 40 | 95 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 14 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 0 | 300 | 260 | 159 | 8 | 50 | 43 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 33 | 18 | 114 | 212 | 0 | 22 | 0 | 61 | 43 | 5 | 5 | 100 | 280 | 46 | 5 | 0 | 110 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 30 |  | 935 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 19 | 0 | 0 | 60 | 30 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 11 | 0 | 67 | 280 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4955 | 3024 | 7979 | 4222 | 935 | 1610 | 285 | 647 | 77 | 89 | 114 | 0 | 0 | 82.31
KWH | 524000 | 0 | 2602000 | 0 | 6939518 | 0 | 0 | 8527132 | 7393000 |  | 0 | 8480250 | 3259811 | 85440 | 579816 | 30410 | 4622166 | 0 | 2598000 | 0 | 94080 | 0 | 0 | 0 | 0 | 0 | 0 | 79920 | 61896 | 118964 | 0 | 600000 | 187560 | 718900 | 492400 | 0 | 0 | 810060 | 956000 | 2400000 | 0 | 0 | 5046200 | 0 | 2862537 | 0 |  | 0 | 0 | 213823 | 0 | 23040 | 50400 | 470352 | 1152960 | 0 | 2117530 | 0 | 7669500 | 6624000 | 4322000 | 217454 | 703730 | 490104 | 138240 | 0 | 383868 | 0 | 0 | 0 | 490176 | 201240 | 369800 | 497960 | 2670720 | 4812360 | 874560 | 488016 | 17400 | 1468000 | 1045560 | 287400 | 362736 | 3340227 | 6926000 | 1195296 | 732480 | 0 | 2262270 | 0 | 0 | 16740 | 7275500 | 0 | 264000 | 0 | 125455 | 0 | 0 | 2196000 | 0 | 144000 | 120150 | 15360 | 0 | 165600 | 0 | 87600 | 0 | 0 | 32761 | 138000 | 0 | 0 | 0 | 379680 | 970560 |  | 11651636 | 0 | 8053632 | 0 | 420480 | 0 | 0 | 0 | 0 | 0 | 162000 | 4314677 | 401800 | 0 | 0 | 569000 | 1490000 | 0 | 0 | 1057624 | 0 | 255319 | 474775 | 21600 | 0 | 307680 | 274608 | 244224 | 0 | 1545599 | 6520800 | 0 | 0 | 4250736 | 0 | 0 | 0 | 0 | 0 | 4067600 | 0 | 9270673 | 0 | 0 | 109824 | 0 | 1032960 | 0 | 50383 | 1128192 | 7877900 |  | 124620668 | 65553722 | 190174390 | 103528176 | 11651636 | 40035616 | 12610967 | 15944299 | 1766060 | 1746222 | 2670720 | 220694 | 0
Fuel Cost | 859360 | 0 | 3798920 | 0 | 7702864.98 | 0 | 0 | 8612403.32 | 7614790 |  | 0 | 9243472.5 | 3618390.21 | 648489.6 | 3994932.24 | 257268.6 | 4807052.64 | 0 | 4494540 | 0 | 708422.4 | 0 | 0 | 0 | 0 | 0 | 0 | 583416 | 478456.08 | 1172985.04 | 0 | 450000 | 0 | 0 | 0 | 0 | 0 | 218716.2 | 258120 | 4344000 | 0 | 0 | 5500358 | 0 | 4866312.9 | 0 |  | 0 | 0 | 2074083.1 | 0 | 200448 | 399168 | 592643.52 | 3424291.2 | 0 | 3133944.4 | 0 | 5675430 | 6624000 | 3976240 | 280515.66 | 809289.5 | 553817.52 | 193536 | 0 | 656414.28 | 0 | 0 | 0 | 622523.52 | 150930 | 647150 | 373470 | 20030400 | 5101101.6 | 7941004.8 | 619780.32 | 277356 | 2407520 | 1672896 | 511572 | 565868.16 | 3807858.78 | 7203040 | 2354733.12 | 1399036.8 | 0 | 3913727.1 | 0 | 0 | 34149.6 | 7348255 | 0 | 200640 | 0 | 948439.8 | 0 | 0 | 11419200 | 0 | 1416960 | 1404553.5 | 125184 | 0 | 1167480 | 0 | 798912 | 0 | 0 | 0 | 1043280 | 0 | 0 | 0 | 3253857.6 | 6463929.6 |  | 67113423.36 | 0 | 8456313.6 | 0 | 3304972.8 | 0 | 0 | 0 | 0 | 0 | 1688040 | 4875585.01 | 622790 | 0 | 0 | 1166450 | 3054500 | 0 | 0 | 9359972.4 | 0 | 3451912.88 | 4600569.75 | 209304 | 0 | 590745.6 | 425642.4 | 184877.568 | 0 | 9319961.97 | 35342736 | 0 | 0 | 4973361.12 | 0 | 0 | 0 | 0 | 0 | 4759092 | 0 | 9177966.27 | 0 | 0 | 1042229.76 | 0 | 8015769.6 | 0 | 556732.15 | 8337338.88 | 34583981 |  | 198051901.19 | 225214268.118 | 423266169.308 | 119538867.738 | 67113423.36 | 45896904.25 | 72689791.89 | 79246678.97 | 476836.2 | 16034625.25 | 20030400 | 2238641.65 | 0
Yesterday Day Peak | 24 | 0 | 100 | 0 | 335 | 0 | 0 | 364 | 343 |  | 0 | 350 | 140 | 0 | 30 | 0 | 200 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 25 | 17 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 219 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 80 | 0 | 350 | 310 | 183 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 8 | 17 | 110 | 200 | 72 | 22 | 2.5 | 62 | 43 | 5 | 5 | 130 | 317 | 58 | 10 | 0 | 70 | 0 | 0 | 0 | 315 | 0 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 50 |  | 351 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 65 | 0 | 0 | 42 | 0 | 0 | 29 | 0 | 0 | 12 | 11 | 11 | 0 | 64 | 270 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 402 | 0 | 0 | 0 | 0 | 113 | 0 | 7.4 | 70 | 300 |  | 7886.4 | DayPeak
Yesterday Evening Peak | 24 | 0 | 100 | 0 | 250 | 0 | 0 | 339 | 348 | 0 | 0 | 350 | 130 | 52 | 80 | 0 | 210 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 0 | 25 | 10 | 33 | 21 | 0 | 0 | 36 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 19 | 21 | 40 | 0 | 115 | 0 | 315 | 260 | 180 | 8 | 50 | 10 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 134 | 207 | 95 | 22 | 0 | 62 | 43 | 53 | 50 | 100 | 281 | 45 | 81 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 45 | 0 | 0 | 115 | 0 | 30 | 0 | 0 | 0 | 135 | 0 | 35 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 90 |  | 934 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 22 | 0 | 0 | 60 | 50 | 0 | 0 | 100 | 0 | 24 | 37 | 0 | 0 | 17 | 11 | 11 | 0 | 66 | 280 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 410 | 0 | 0 | 18 | 0 | 113 | 0 | 0 | 109 | 390 |  | 9663 | EvPeak
Forecast for Evening | 24 | 0 | 180 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 220 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 40 | 40 | 100 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 0 | 120 | 0 | 360 | 360 | 225 | 45 | 50 | 46 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 131 | 210 | 95 | 22 | 0 | 62 | 43 | 51 | 44 | 163 | 310 | 66 | 86 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 745 | 40 | 410 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 185 | 23 | 110 | 30 | 60 | 60 | 50 | 45 | 100 | 0 | 40 | 40 | 52 | 36 | 18 | 11 | 11 | 0 | 70 | 280 | 17 | 17 | 210 | 0 | 0 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 0
Forecast for Day | 24 | 0 | 180 | 0 | 365 | 0 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 220 | 0 | 80 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 40 | 40 | 100 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 80 | 100 | 100 | 50 | 22 | 40 | 0 | 100 | 0 | 360 | 360 | 225 | 45 | 50 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 116 | 210 | 95 | 22 | 1.6 | 62 | 43 | 51 | 44 | 163 | 300 | 66 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 120 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 | 100 |  | 349 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 185 | 20 | 70 | 0 | 60 | 60 | 0 | 0 | 80 | 0 | 40 | 40 | 52 | 0 | 18 | 11 | 11 | 0 | 70 | 280 | 0 | 0 | 210 | 0 | 0 |  | 89 | 0 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 0
Generation at 08:00(Today) | 24 | 0 | 99 | 0 | 275 | 0 | 0 | 340 | 266 | 0 | 0 | 320 | 120 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 16 | 0 | 0 | 37 | 40 | 100 | 0 | 0 | 217 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 0 | 280 | 250 | 179 | 8 | 50 | 36 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 5 | 8 | 20 | 88 | 215 | 5 | 22 | 1.1 | 61 | 43 | 5 | 5 | 100 | 282 | 45 | 5 | 0 | 80 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 12 | 0 | 0 | 60 | 40 | 0 | 0 | 42 | 0 | 0 | 0 | 16 | 0 | 18 | 12 | 8 | 0 | 67 | 280 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 354 | 0 | 0 | 0 | 0 | 22 | 0 | 2.5 | 20 | 301 | 0
199
| Minimum Generation |  | 6673.1 | 6:00
| Highest Generation |  | 9663 | 19:30
| Day Peak Generation |  | 7886.4 | 12:00
| Evening Peak Generation |  | 9663 | 19:30
| HVDC Max Flow |  | 935 | 20:00
| HVDC EvPeak Flow |  | 934 | 19:30
| Load factor L.F |  | 82%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-04-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-03-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7886.4 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 6763.1 | MW
Evening Peak Generation : |  | 9663 | MW Hour : | 19:30 | Available Max Generation : |  | 15256 | MW
E.P. Demand (at gen end) : |  | 9663 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9900 | MW
Maximum Generation : |  | 9663 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5356 | MW
Total Gen. (MKWH) : |  | 190.1744 | System Load Factor : | 82% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -270 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-04-01
Actual : | 82.19 | Ft.(MSL) , | Rule curve : | 88 | Ft.( MSL )
Gas Consumed : | Total = | 1179.34 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165435771.988
: |  | Coal : | 79246678.97 | Oil : | 88724417.14 | Total : | 333406868.098
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3502.691 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1187.8807 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1063.7265 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 960.9624 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 868.5204 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 700.8571 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 396.0389 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 180.5618 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 540.5159 |  |  | 0 | 0%
Total | 0 |  | 9401.7547 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1.
2) Siddhirganj 210 MW GT-1
3) Ghorasal Unit-1,3 & 5.
4) Baghabari 100 MW
5) Ashuganj unit-5
6) Sirajganj unit-2
7) Kaptai-2,3,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Siddhirganj-Matuail 132 kV Ckt tripped at 10:51 from Matuail end showing E/F and was switched on at |  |  |  |  | About 35 MW power interruption occurred under Matuail S/S area
10:58. |  |  |  |  | from 10:51 to 10:58.
b) Jhenaidah-Bottail 132 kV Ckt-2 was under shut down from 07:49 to 09:10 for C/M.
c) Chandpur 150 MW CCPP GT was synchronized at 09:54.
d) Rangamati 132/33 kV T2 transformer was under shut down from 22:49 to 22:59 to attend R/H at 33 kV side
isolator.
e) Hasnabad 230/132 kV T01 transformer was shut down at 07:47(01/04/2020) to attend R/H at
B-phase HT Bushing.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-03-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 524000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 2602000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6939518 | Gas shortage.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8527132 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 348 | 7393000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8480250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 52 | 85440 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 130 | 3259811 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 579816 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 30410 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 70 | 2598000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 50 | 94080 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 210 | 4622166
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 79920
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 61896
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 118964 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 787560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 718900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 492400 | Machine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 125455 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 30 | 144000 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2272 | 48264718
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120150
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 50400 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 76 | 1766060 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 217 | 5046200 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 104 | 2862537 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 213823 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 15360 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 470352
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 1152960
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 23040 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32761
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 65 | 138000 | Transformer overload
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 90 | 970560 | On test
| Chattogram area Total |  |  |  | 2166 | 766 | 15262203
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 115 | 2117530
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4322000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7669500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6624000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 490104
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 138240
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 383868
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 165600
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 703730 | Under S/D
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 490176
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 201240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 2670720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 369800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 497960
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 65 | 379680 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1414 | 27441602
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 207 | 4812360
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 488016
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 874560
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 17400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 115 | 2196000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 35 | 87600 | Low demand
| Mymensingh Area Total |  |  |  | 637 | 474 | 8475936
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 62 | 1468000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1045560
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3340227 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 281 | 6926000
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 287400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 362736
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 45 | 1195296 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 732480 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 110 | 2262270
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7275500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 16740
| Sylhet Area Total |  |  |  | 1949 | 1136 | 25176209
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 934 | 11651636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 420480 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8053632 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 162000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1403 | 20287748
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 22 | 401800 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 180 | 4314677
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Payra Test.
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 390 | 7877900 | On test
| Barisal Area Total |  |  |  | 462 | 592 | 12594377
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1490000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 60 | 569000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 255319 | Low demand
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 474775 | Low demand
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 4250736 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4067600 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 9270673 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 307680 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 274608
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244224
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 21600 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1057624
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 18 | 109824 | Low demand
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1128192
| Rajshahi Area Total |  |  |  | 2183 | 1147 | 23521855
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 66 | 1545599 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 280 | 6520800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1032960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50383
| Rangpur Area Total |  |  |  | 605 | 459 | 9149742
| Total |  |  |  | 19107 | 9663 | 190174390
| Eastern Grid Total |  |  |  | 13543 | 6062 | 124620668
| Western Grid Total |  |  |  | 5564 | 3601 | 65553722
| National Grid Total |  |  |  | 19107 | 9663 | 190174390
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-03-31
(a) ENTIRE EASTERN GRID : |  | 5857 | MW | (b) ENTIRE WESTERN GRID : |  | 3308 | MW
i) Dhaka area |  | 2625 | MW | i) Khulna area |  | 1221 | MW
ii) Chittagong area |  | 1047 | MW | ii) Rajshahi area |  | 1124 | MW
iii) Comilla area |  | 958 | MW | iii) Barisal area |  | 249 | MW
iv) Mymensingh area |  | 877 | MW | iv) Rangpur area |  | 714 | MW
v) Sylhet area |  | 350 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9165 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 23:00 | Sherpur | 100 | 19:00 | Benapol | 40 | 19:00
Munsiganj | 102 | 19:30 | Srimongal | 36 | 19:30 | Jhenida | 98 | 19:00
Sonargaon | 43 | 12:00 | Shahjibazar | 72 | 19:30 | Bottail | 92 | 19:00
Shyampur | 142 | 0:00 | Fenchuganj | 25 | 19:30 | G.K Project | 43 | 19:30
Bhulta | 81 | 18:30 | Kulawara | 33 | 18:30 | Faridpur | 144 | 19:30
Madanganj | 45 | 13:00 | Sylhet | 91 | 19:00 | Madaripur | 72 | 19:30
Shitalakhya | 61 | 15:00 | Chatak | 20 | 19:00 | Sariatpur | 44 | 19:00
Rahim steel | 10 | 15:00 | Sunamganj | 32 | 20:00 | Gopalganj | 80 | 19:00
Matuail | 50 | 1:00 | Biani Bazar | 46 | 18:30 | Bagerhat | 74 | 19:00
Ghorasal | 43 | 19:00 | Comilla (S) | 134 | 19:00 | Mongla | 34 | 16:00
Narsingdi | 98 | 19:30 | Comilla(N) | 113 | 19:00 | Satkhira | 89 | 20:00
Haripur (SBU) | 55 | 19:30 | Chandpur | 82 | 19:30 | Gallamari | 39 | 19:00
Ullon | 60 | 19:00 | Feni | 100 | 19:00 | Magura | 44 | 19:00
Hasnabad | 143 | 20:00 | Chowmuhani | 130 | 19:00 | Norail | 32 | 19:30
Magbazar | 70 | 19:00 | Ashuganj | 45 | 19:00 | Chuadanga | 77 | 19:00
Maniknagar | 60 | 20:00 | Daudkandi | 122 | 19:00 | Barisal(N) | 34 | 20:00
Bangabhaban | 16 | 12:00 | B.Baria | 131 | 19:30 | Barisal (S) | 72 | 19:00
Narinda | 52 | 13:00 | Ramganj | 80 | 19:00 | Patuakhali | 80 | 21:00
Dhanmondi | 74 | 13:00 | Chaddagram | 30 | 18:30 | Bhandaria | 40 | 19:00
Lalbag | 22 | 12:00 | PHP | 6 | 11:00 | Borhan Uddin | 29 | 20:00
Madartek | 51 | 14:00 | Madunaghat | 43 | 19:00 | Ishurdi | 45 | 18:30
Dhaka University |  |  | Hathazari | 78 | 19:30 | Ruppur Paromanobik | 2 | 20:00
Mirpur | 75 | 19:30 | Khulshi | 160 | 22:00 | Natore | 118 | 19:00
Kalyanpur | 72 | 19:30 | Halishahar | 99 | 18:30 | Bogra | 144 | 19:00
Gulshan | 68 | 19:30 | Baraulia | 137 | 0:00 | Noagaon | 112 | 19:30
Uttara | 53 | 19:30 | Sikalbaha | 18 | 19:00 | Rajshahi | 105 | 19:00
Uttara New | 15 | 19:00 | Dohazari | 84 | 19:00 | Rajshahi New | 12 | 18:30
Kamrangirchar | 57 | 19:30 | Cox'sbazar | 89 | 19:30 | C.Nawabganj | 75 | 19:30
Savar | 80 | 19:30 | Chandraghona | 26 | 19:00 | Amnura | 52 | 21:00
Bhasantec | 106 | 19:30 | Kaptai | 4.2 | 19:00 | Pabna | 89 | 19:00
Agargaon | 39 | 19:00 | A. Khaer Stl. | 22 | 8:00 | Shahjadpur | 85 | 19:00
Satmosjid | 75 | 19:30 | Bakulia | 76 | 23:00 | Serajganj | 80 | 19:00
Tongi | 87 | 19:00 | Julda | 19 | 18:30 | Niyamatpur | 86 | 19:00
Kabirpur | 87 | 11:00 | TK chemical | 13 | 18:30 | Joypurhat | 63 | 19:00
Basundhara | 95 | 22:00 | Modern Steel | 0.2 | 1:00 | Sherpur(Bogura) | 46 | 19:00
Manikganj | 74 | 19:00 | Shahmirpur | 20.5 | 19:00 | Mohastangor | 44 | 19:30
Joydevpur | 109 | 19:00 | Khagrachhari | 20 | 18:30 | Rangpur | 123 | 20:00
New Tongi | 54 | 19:00 | Matarbari | 26.5 | 19:00 | Lalmonirhat | 56 | 19:00
Kodda | 108 | 19:00 | Baroiar Hat | 30 | 18:30 | Saidpur | 102 | 19:00
Dhamrai | 58 | 19:00 | Rangamati | 10 | 18:30 | Purbasadipur | 99 | 13:00
Rajendrapur | 54 | 19:00 | Abul Khair 230 | 146 | 0:00 | Thakurgaon | 74 | 19:00
Valuka | 54 | 18:30 | BSRM | 156 | 16:00 | Palashbari | 117 | 19:00
Tangail | 186 | 19:00 | GPH Ispat | 6 | 6:00 | Barapukuria | 50 | 19:00
Mymensing | 197 | 18:30 | Goalpara | 23 | 21:00 | Panchagar | 42 | 19:00
Kishorganj | 116 | 19:00 | Central s/s | 63 | 19:30 | Joldhaka | 29 | 19:00
Netrokona | 116 | 19:00 | Noapara | 50 | 19:00 | Kurigram | 52 | 0.79167
Jamalpur | 119 | 19:00 | Jessore | 112 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-03-31 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 402 | 0.16667 | 395 | 0.875 | Kaliakoir | 385 | 0.16667 | 375 | 0.91667
Bheramara | 404 | 0.125 | 382 | 0.83333 | Bhulta | 395 | 0.125 | 386 | 0.91667
Ashuganj(N) | 400 | 0.79167 | 392 | 0.95833 | Gopalganj | 405 | 0.25 | 391 | 0.875
Payra | 411 | 0.16667 | 402 | 0.875
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 234 | 0.58333 | Hathazari | 219 | 0.083333 | 213 | 24:00
Ishurdi | 235 | 0.041667 | 225 | 0.54167 | Megnaghat | 236 | 0.75 | 231 | 0.5
Ashuganj | 242 | 0.041667 | 235 | 0.95833 | Fenchuganj | 243 | 0.25 | 238 | 0.45833
Serajganj | 231 | 0.041667 | 227 | 0.29167 | Siddhirganj | 235 | 0.79167 | 231 | 0.83333
Baghabari | 240 | 0.041667 | 237 | 0.54167 | Maniknagar | 233 | 0.25 | 229 | 0.875
Barapukuria | 236 | 0.041667 | 228 | 0.33333 | Old Airport | 232 | 0.25 | 226 | 0.875
Bogra | 224 | 0.041667 | 215 | 0.29167 | Barisal | 248 | 0.25 | 237 | 0.83333
Khulna South | 225 | 0.77083 | 205 | 0.54167 | AKSML | 218 | 0.79167 | 209 | 0.66667
Rampura | 232 | 0.125 | 229 | 0.91667 | BSRM | 221 | 0.25 | 210 | 24:00
Haripur | 233 | 0.79167 | 229 | 0.91667 | Bibiyana | 240 | 0.125 | 234 | 0.83333
Hasnabad | 232 | 0.16667 | 230 | 0.041667 | Bhulta | 235 | 0.25 | 229 | 24:00
Shyampur | 230 | 0.25 | 225 | 0.95833 | Ashuganj (S) | 237 | 0.125 | 232 | 0.875
Aminbazar | 232 | 0.79167 | 227 | 0.95833 | Kaliakoir | 234 | 0.125 | 228 | 0.875
Tongi | 230 | 0.041667 | 224 | 0.875 | GPH | 218 | 0.29167 | 209 | 24:00
Comilla (N) | 236 | 0.29167 | 230 | 0.625
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.58333 | 132 | 0.041667 | Hathazari | 131 | 0.16667 | 126 | 0
Munsiganj | 136 | 0.8125 | 130 | 0.54167 | Khulshi | 128 | 0.33333 | 123 | 0
Sonargaon | 131 | 0.5 | 130 | 0.041667 | Halishahar | 130 | 0.29167 | 125 | 0.95833
Shyampur | 136 | 0.041667 | 134 | 0.66667 | Baraulia | 131 | 0.16667 | 125 | 0.70833
Bhulta | 130 | 0.77083 | 134 | 0.58333 | Sikalbaha | 131 | 0.79167 | 126 | 0.875
Madanganj | 134 | 0.54167 | 130 | 0.20833 | Dohazari | 127 | 0.083333 | 124 | 0.83333
Shitalakhya | 136 | 0.625 | 131 | 0.625 | Cox'sbazar | 122 | 0.375 | 113 | 0.875
Rahim steal | 135 | 15:00 | 132 | 0.041667 | Chandraghona | 131 | 0.79167 | 127 | 0.95833
Matuail | 135 | 0.041667 | 132 | 0.041667 | Kaptai | 132 | 0.041667 | 127 | 0.5
Ghorasal | 140 | 0.79167 | 138 | 0.041667 | A. Khaer Stl. | 129 | 0.75 | 125 | 0.95833
Narsinghdi | 132 | 0.8125 | 127 | 0.83333 | Bakulia | 129 | 0.79167 | 124 | 0.95833
Haripur (SBU) | 135 | 0.8125 | 131 | 0.16667 | Julda | 129 | 0.77083 | 126 | 0.70833
Ullon | 134 | 0.25 | 132 | 0.5 | TK Chemical | 130 | 0.77083 | 126 | 0.875
Hasnabad | 135 | 0.29167 | 133 | 0.54167 | Modern Steel | 128 | 0.25 | 125 | 0.91667
Magbazar | 135 | 0.25 | 132 | 0.5 | Shahmirpur | 129 | 0.79167 | 125 | 0.875
Maniknagar | 136 | 0.29167 | 133 | 0.83333 | Khagrachhari | 130 | 0.25 | 127 | 0.5
Bangabhaban | 136 | 0.29167 | 133 | 0.83333 | Matarbari | 126 | 0.33333 | 118 | 0.8125
Narinda | 136 | 0.29167 | 133 | 0.83333 | Baroiar Hat | 129 | 0.041667 | 123 | 0:00
Dhanmondi | 134 | 0.25 | 132 | 0.5 | Rangamati | 130 | 0.25 | 126 | 0:00
Lalbag | 136 | 0.29167 | 132 | 0.5 | Goalpara | 138 | 0.75 | 125 | 0.54167
Madartek | 135 | 0.25 | 131 | 0.5 | Central s/s | 136 | 0.75 | 122 | 0.54167
Dhaka University |  |  |  |  | Noapara | 133 | 0.91667 | 123 | 0.5
Mirpur | 134 | 0.25 | 130 | 0.54167 | Jessore | 130 | 0.20833 | 114 | 0.54167
Kalyanpur | 134 | 0.25 | 131 | 0.54167 | Benapol | 131 | 0.125 | 116 | 0.54167
Gulshan | 133 | 0.25 | 131 | 0.54167 | Jhenida | 129 | 0.20833 | 113 | 0.33333
Uttara | 136 | 0.25 | 132 | 0.5 | Bottail | 135 | 0.20833 | 125 | 0.54167
Uttara New | 133 | 0.25 | 130 | 0.54167 | G.K Project | 139 | 0.20833 | 133 | 0.5
Kamrangirchar | 133 | 0.25 | 129 | 0.54167 | Faridpur | 136 | 0.16667 | 130 | 0.79167
Savar | 133 | 0.79167 | 129 | 0.58333 | Madaripur | 141 | 0.25 | 135 | 0.66667
Bhasantec | 133 | 0.25 | 130 | 0.54167 | Sariatpur | 140 | 0.16667 | 132 | 0.8125
Agargaon | 134 | 0.25 | 130 | 0.54167 | Gopalganj | 142 | 0.125 | 134 | 0.79167
Satmosjid | 133 | 0.25 | 130 | 0.54167 | Bagerhat | 133 | 0.91667 | 120 | 0.54167
Tongi | 139 | 0.75 | 135 | 0.875 | Mongla | 131 | 0.91667 | 118 | 0.54167
Kabirpur | 132 | 0.125 | 128 | 0.875 | Satkhira | 136 | 0.75 | 122 | 0.54167
Basundhara | 134 | 4:00 | 131 | 0.91667 | Gallamari | 137 | 0.75 | 125 | 0.54167
Manikganj | 138 | 0.125 | 132 | 0.5 | Magura | 129 | 0.25 | 126 | 0.75
Joydevpur | 142 | 0.083333 | 138 | 0.875 | Norail | 127 | 0.16667 | 110 | 0.33333
New Tongi | 137 | 0.79167 | 133 | 0.875 | Chuadanga | 125 | 0.25 | 107 | 0.8125
Kodda | 133 | 0.79167 | 128 | 0.95833 | Barisal(N) | 140 | 0.25 | 132 | 0.79167
Dhamrai | 132 | 0.16667 | 126 | 0.875 | Barisal (S) | 140 | 0.25 | 132 | 0.79167
Rajendrapur | 132 | 0.125 | 126 | 0.91667 | Patuakhali | 138 | 0.25 | 128 | 0.79167
Valuka | 125 | 0.083333 | 114 | 0.77083 | Bhandaria | 138 | 0.25 | 129 | 0.875
Tangail | 131 | 0.16667 | 123 | 0.77083 | Ishurdi | 135 | 0.041667 | 129 | 0.54167
Mymensing | 127 | 0.125 | 116 | 0.77083 | Ruppur Paromanobik | 134 | 0.75 | 129 | 0.54167
Kishorganj | 129 | 0.20833 | 120 | 0.77083 | Natore | 132 | 0.77083 | 125 | 0.29167
Netrokona | 122 | 0.16667 | 111 | 0.77083 | Bogra | 133 | 0.041667 | 125 | 0.29167
Jamalpur | 130 | 0.8125 | 119 | 0.70833 | Noagaon | 127 | 0.083333 | 115 | 0.33333
Sherpur | 127 | 0.8125 | 117 | 0.66667 | Rajshahi | 131 | 0.75 | 121 | 0.54167
Srimongal | 138 | 0.54167 | 136 | 0.041667 | Rajshahi New | 131 | 0.75 | 120 | 0.5
Shahjibazar | 136 | 0.20833 | 131 | 19:00 | C.Nawabganj | 128 | 0.75 | 117 | 0.5
Fenchuganj | 137 | 0.25 | 135 | 0.375 | Amnura | 127 | 0.77083 | 118 | 0.29167
Khulawara | 137 | 0.20833 | 133 | 0.77083 | Pabna | 133 | 0.125 | 129 | 0.8125
Sylhet | 136 | 0.16667 | 133 | 0.77083 | Shahjadpur | 141 | 0.125 | 136 | 0.29167
Chatak | 135 | 0.125 | 132 | 0.77083 | Serajganj | 133 | 0.041667 | 128 | 0.29167
Sunamganj | 135 | 0.25 | 131 | 0.75 | Niyamatpur | 122 | 0.041667 | 112 | 0.33333
Biani Bazar | 135 | 0.20833 | 131 | 0.79167 | Joypurhat | 125 | 0.083333 | 112 | 0.33333
Comilla(s) | 129 | 0.083333 | 125 | 0.58333 | Sherpur(Bogura) | 134 | 0.16667 | 125 | 0.29167
Comilla(n) | 137 | 0.29167 | 131 | 0.875 | Mohastangor | 134 | 0.125 | 124 | 0.29167
Chandpur | 128 | 0.5 | 125 | 0.70833 | Rangpur | 130 | 0.041667 | 121 | 0.33333
Feni | 130 | 0.29167 | 123 | 0.625 | Lalmonirhat | 126 | 0.083333 | 115 | 0.33333
Chowmuhani | 126 | 0.29167 | 119 | 0.66667 | Saidpur | 131 | 0.125 | 119 | 0.79167
Ashuganj | 137 | 0.20833 | 134 | 0.77083 | Purbasadipur | 130 | 0.083333 | 115 | 0.79167
Daudkandi | 132 | 0.29167 | 127 | 0.625 | Thakurgaon | 128 | 0.125 | 114 | 0.79167
B.Baria | 133 | 0.29167 | 130 | 0.79167 | Palashbari | 130 | 0.125 | 116 | 0.29167
Ramganj | 123 | 0.375 | 115 | 0.66667 | Barapukuria | 136 | 0.041667 | 128 | 0.33333
Chaddagram | 131 | 0.29167 | 124 | 0.70833 | Panchagar | 127 | 0.041667 | 113 | 0.79167
PHP | 129 | 0.33333 | 122 | 0.58333 | Joldhaka | 129 | 0.125 | 117 | 0.33333
Madanhat | 132 | 0.79167 | 128 | 0.66667 | Kurigram | 128 | 0.20833 | 117 | 0.375

## L-Curve
Date | 2020-03-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 458 | 4955 | 3024 | 7979 |  |  |  | QF-LDC-12
0:30 | 356.5 | 4890.5 | 2859.5 | 7750 | Date: | 2020-03-31
1:00 | 255 | 4826 | 2695 | 7521
1:30 | 158 | 4855.5 | 2455.5 | 7311
2:00 | 61 | 4885 | 2216 | 7101
2:30 | 47 | 4852 | 2174.5 | 7026.5 | [5 empty] | Gen. at Eve. Peak | 9663 | 9663 MW (19:30 )
3:00 | 33 | 4819 | 2133 | 6952 | [6 empty] | 19:30
3:30 | 19 | 4760.5 | 2127 | 6887.5 | [5 empty] | Gen. at Day Peak | 7886.4 | 7886.4 MW (12:00 )
4:00 | 5 | 4702 | 2121 | 6823 | [6 empty] | 12:00
4:30 | 14.5 | 4661.5 | 2143.5 | 6805 | [5 empty] | Highest Generation | 9663
5:00 | 24 | 4621 | 2166 | 6787 | [6 empty] | 19:30
5:30 | 59 | 4562 | 2168.05 | 6730.05
6:00 | 94 | 4503 | 2170.1 | 6673.1
6:30 | 169.5 | 4542.2 | 2204.95 | 6747.15
7:00 | 245 | 4581.4 | 2239.8 | 6821.2
7:30 | 257.5 | 4673.45 | 2277.8 | 6951.25
8:00 | 270 | 4765.5 | 2315.8 | 7081.3
8:30 | 223 | 4823.5 | 2343.2 | 7166.7
9:00 | 176 | 4881.5 | 2370.6 | 7252.1
9:30 | 159.5 | 4927.35 | 2411.75 | 7339.1
10:00 | 143 | 4973.2 | 2452.9 | 7426.1
10:30 | 110 | 5005.9 | 2479.35 | 7485.25
11:00 | 77 | 5038.6 | 2505.8 | 7544.4
11:30 | 118.5 | 5165.8 | 2549.6 | 7715.4
12:00 | 160 | 5293 | 2593.4 | 7886.4
12:30 | 170 | 5426.2 | 2619.55 | 8045.75
13:00 | 180 | 5559.4 | 2645.7 | 8205.1
13:30 | 171 | 5560.45 | 2660.8 | 8221.25
14:00 | 162 | 5561.5 | 2675.9 | 8237.4
14:30 | 122 | 5551.4 | 2692.4 | 8243.8
15:00 | 82 | 5541.3 | 2708.9 | 8250.2
15:30 | 62.5 | 5438.75 | 2659.75 | 8098.5
16:00 | 43 | 5336.2 | 2610.6 | 7946.8
16:30 | 24.5 | 5196.9 | 2563.7 | 7760.6
17:00 | 6 | 5057.6 | 2516.8 | 7574.4
17:30 | 6 | 4911.35 | 2505.6 | 7416.95
18:00 | 6 | 4765.1 | 2494.4 | 7259.5
18:30 | 50.5 | 5333.55 | 2909.7 | 8243.25
19:00 | 95 | 5902 | 3325 | 9227
19:30 | 67 | 6062 | 3601 | 9663
20:00 | 189 | 5795 | 3684 | 9479 |  |  |  | Executive Engineer
20:30 | 232.5 | 5778.5 | 3668.5 | 9447 |  |  |  | Network Operation Division
21:00 | 276 | 5762 | 3653 | 9415
21:30 | 343 | 5616.5 | 3589 | 9205.5
22:00 | 410 | 5471 | 3525 | 8996 |  |  |  |  | Page 6 of 7
22:30 | 435 | 5289 | 3377.5 | 8666.5
23:00 | 460 | 5107 | 3230 | 8337
23:30 | 459 | 5031 | 3127 | 8158
24:00 | 458 | 4955 | 3024 | 7979
9663 MW (19:30 )
7886.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-03-31 |  | Energy | 190174390
[10 empty] | 2020-03-31 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4222 | 935 | 1610 | 458 | 647 | 77 | 89 | 0 | 114
0:30 | 4220 | 837.5 | 1557 | 339 | 636.5 | 77 | 56.5 | 0 | 113 | Date: | 2020-03-31
1:00 | 4218 | 740 | 1504 | 220 | 626 | 77 | 24 | 0 | 112
1:30 | 4237.5 | 497.5 | 1530.5 | 207 | 626.5 | 77 | 24 | 0 | 111 | [7 empty] | Total Energy | 190.1744 | Total Energy Gen 190.174 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 190.174 MKWHr
2:00 | 4257 | 255 | 1557 | 194 | 627 | 77 | 24 | 0 | 110 | [7 empty] | Energy not Served | 0
2:30 | 4191 | 255 | 1571 | 189 | 626.5 | 77 | 12 | 0 | 105 | [7 empty] | Energy Requirement | 190.1744
3:00 | 4125 | 255 | 1585 | 184 | 626 | 77 | 0 | 0 | 100
3:30 | 4093 | 254.5 | 1553.5 | 184 | 625.5 | 77 | 0 | 0 | 100 | [6 empty] | Shortage
4:00 | 4061 | 254 | 1522 | 184 | 625 | 77 | 0 | 0 | 100
4:30 | 4056 | 254.5 | 1519 | 175.5 | 625 | 77 | 0 | 0 | 98
5:00 | 4051 | 255 | 1516 | 167 | 625 | 77 | 0 | 0 | 96
5:30 | 3976.5 | 303 | 1476.5 | 178.5 | 625.5 | 77 | 0 | 0 | 93
6:00 | 3902 | 351 | 1437 | 190 | 626 | 77 | 0 | 0 | 90
6:30 | 3904 | 350.5 | 1460 | 237 | 626 | 77 | 0 | 0 | 90 |  |  |  |  | Coal
7:00 | 3906 | 350 | 1483 | 284 | 626 | 77 | 0 | 0 | 90
7:30 | 3960.5 | 350.5 | 1495.5 | 344.5 | 626 | 77 | 2 | 0 | 86 |  |  |  | Oil |  |  |  | ,
8:00 | 4015 | 351 | 1508 | 405 | 626 | 77 | 4 | 0 | 82
8:30 | 4044 | 351 | 1523 | 402 | 626 | 77 | 37.5 | 0 | 89
9:00 | 4073 | 351 | 1538 | 399 | 626 | 77 | 71 | 0 | 96
9:30 | 4088.5 | 351 | 1565 | 435 | 630.5 | 77 | 71 | 0 | 97
10:00 | 4104 | 351 | 1592 | 471 | 635 | 77 | 71 | 0 | 98
10:30 | 4123.5 | 351.5 | 1590.5 | 508.5 | 635.5 | 77 | 71 | 0 | 99
11:00 | 4143 | 352 | 1589 | 546 | 636 | 77 | 71 | 0 | 100
11:30 | 4254 | 351.5 | 1623 | 568 | 635 | 77 | 71 | 0 | 105
12:00 | 4365 | 351 | 1657 | 590 | 634 | 77 | 71 | 0 | 110
12:30 | 4443 | 350.5 | 1712.5 | 610 | 635 | 77 | 75.5 | 0 | 112
13:00 | 4521 | 350 | 1768 | 630 | 636 | 77 | 80 | 0 | 114
13:30 | 4521 | 350 | 1768 | 630 | 636 | 77 | 80 | 0 | 114
14:00 | 4521 | 350 | 1768 | 630 | 636 | 77 | 80 | 0 | 114
14:30 | 4505.5 | 350.5 | 1789.5 | 645 | 635.5 | 77.5 | 83 | 0 | 117
15:00 | 4490 | 351 | 1811 | 660 | 635 | 78 | 86 | 0 | 120
15:30 | 4472.5 | 350.5 | 1808.5 | 534.5 | 634.5 | 78 | 86.5 | 0 | 118
16:00 | 4455 | 350 | 1806 | 409 | 634 | 78 | 87 | 0 | 116
16:30 | 4392.5 | 350 | 1734.5 | 363.5 | 635 | 77.5 | 87 | 0 | 112
17:00 | 4330 | 350 | 1663 | 318 | 636 | 77 | 87 | 0 | 108
17:30 | 4215.5 | 350 | 1574 | 357.5 | 641.5 | 76.5 | 91 | 0 | 108
18:00 | 4101 | 350 | 1485 | 397 | 647 | 76 | 95 | 0 | 108
18:30 | 4203.5 | 574.5 | 1608 | 845 | 670 | 75.5 | 145.5 | 0 | 121
19:00 | 4306 | 799 | 1731 | 1293 | 693 | 75 | 196 | 0 | 134
19:30 | 4252 | 934 | 1846 | 1514 | 736 | 76 | 171 | 0 | 134
20:00 | 4352 | 935 | 1819 | 1233 | 755 | 77 | 174 | 0 | 134
20:30 | 4402 | 934.5 | 1902 | 1049 | 776.5 | 77 | 173 | 0 | 133
21:00 | 4452 | 934 | 1985 | 865 | 798 | 77 | 172 | 0 | 132
21:30 | 4398.5 | 934.5 | 1924 | 774 | 796.5 | 75 | 172 | 0 | 131
22:00 | 4345 | 935 | 1863 | 683 | 795 | 73 | 172 | 0 | 130
22:30 | 4317.5 | 935 | 1723 | 570.5 | 761.5 | 75 | 158 | 0 | 126
23:00 | 4290 | 935 | 1583 | 458 | 728 | 77 | 144 | 0 | 122
23:30 | 4256 | 935 | 1596.5 | 458 | 687.5 | 77 | 116.5 | 0 | 118 | Max Temp. in Dhaka |  | 36° C
24:00 | 4222 | 935 | 1610 | 458 | 647 | 77 | 89 | 0 | 114
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 190.174 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 190.174 MKWHr
Note on W13: Author:

## Generation
g | 2020-03-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 37 | 36 |  | 35 | 36 | 37 | 37 | 33 | 37 | 37 | 810060
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 956000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 3.3 | 7.6 | 12 | 15.1 | 16.8 | 16.8 | 15.5 | 14.4 | 9.7 | 5.4 | 2.4 | 0.1 | [8 empty] | 120150
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 205 | 204 | 208 | 203 | 204 | 208 | 217 | 207 | 218 | 219 | 218 | 226 | 227 | 225 | 219 | 217 |  | 217 | 217 | 219 | 218 | 217 | 216 | 217 | 5046200
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 140 | 104 | 104 | 104 | 104 | 108 | 103 | 105 | 110 | 145 | 141 | 140 | 140 | 140 | 104 |  | 104 | 104 | 104 | 140 | 104 | 104 | 104 | 2862537
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 8 |  | 59 | 34 | 34 | 34 | 34 | 34 | 14 | 213823
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 105 | 105 | 105 | 95 | 103 | 95 | 103 | 103 | 100 | 100 | 95 | 95 | 156 | 155 | 155 | 108 | 85 | 86 |  | 108 | 70 | 70 | 66 | 65 | 65 | 70 | 2598000
17 | Siddhirganj 335 MW CCPP | 183 | 218 | 218 | 218 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 200 | 199 | 198 | 198 | 200 | 154 |  | 206 | 210 | 213 | 214 | 218 | 180 | 180 | 4622166
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 55 | 45 |  |  |  |  | 0 | 125455
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 524000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 131 | 101 | 100 |  | 101 | 100 | 101 | 100 | 100 | 100 | 102 | 2602000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 275 | 276 | 275 | 276 | 276 | 276 | 276 | 289 | 309 | 283 | 300 | 335 | 310 | 304 | 301 | 301 | 301 | 275 |  | 250 | 250 | 250 | 284 | 275 | 275 | 275 | 6939518
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 115 | 115 | 115 | 120 | 120 | 120 | 100 | 2117530
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 45 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 45 | 45 | 43 | 43 | 490104
33 | Ashuganj 225 MW CCPP | 161 | 166 | 158 | 160 | 175 | 161 | 170 | 180 | 181 | 170 | 182 | 183 | 195 | 184 | 181 | 181 | 181 | 180 |  | 180 | 180 | 196 | 192 | 180 | 180 | 159 | 4322000
34 | Ashuganj 450 MW CCPP(South) | 260 | 265 | 260 | 260 | 275 | 260 | 265 | 280 | 295 | 275 | 295 | 310 | 285 | 265 | 265 | 265 | 265 | 265 |  | 260 | 260 | 280 | 275 | 260 | 260 | 260 | 6624000
| Ashuganj 450 MW CCPP(North) | 310 | 315 | 310 | 280 | 280 | 265 | 280 | 300 | 310 | 365 | 345 | 350 | 330 | 315 | 315 | 310 | 315 | 315 |  | 315 | 315 | 335 | 325 | 315 | 300 | 300 | 7669500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 138240
36 | Chandpur 150 MW CCPP | [9 empty] | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 50 | 51 |  | 51 | 50 | 51 | 50 | 50 | 50 | 50 | 703730
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 348 | 340 | 337 | 341 | 344 | 338 | 348 | 362 | 368 | 354 | 364 | 378 | 353 | 341 | 342 | 341 | 341 |  | 353 | 339 | 340 | 348 | 340 | 338 | 338 | 8527132
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 350 | 420 | 420 | 420 | 420 | 370 | 320 |  | 350 | 350 | 350 | 420 | 420 | 390 | 390 | 8480250
41 | Haripur 360MW CCPP(HPL) | 273 | 292 | 292 | 292 | 292 | 262 | 262 | 262 | 278 | 300 | 298 | 343 | 341 | 344 | 341 | 340 | 340 | 279 |  | 348 | 348 | 333 | 349 | 352 | 322 | 322 | 7393000
42 | RPCL 210MW CCPP | 214 | 214 | 214 | 215 | 215 | 216 | 217 | 213 | 207 | 205 | 202 | 200 | 189 | 185 | 186 | 188 | 200 | 160 |  | 206 | 207 | 206 | 207 | 212 | 212 | 212 | 4812360
43
44 | Fenchugonj CCPP Phase-1 | 61 | 61 | 61 | 61 | 61 | 60 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 61 | 61 | 61 | 61 | 1468000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1045560
46 | Shajibazar 330 MW CCPP | 289 | 299 | 295 | 291 | 304 | 291 | 296 | 300 | 304 | 295 | 308 | 317 | 300 | 297 | 275 | 276 | 284 | 282 |  | 283 | 281 | 297 | 294 | 281 | 282 | 280 | 6926000
47 | Shahjibazar GTPP Unit- 8 & 9 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 | 58 | 58 | 58 | 59 | 59 | 60 | 62 |  | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 1195296
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 81 | 81 | 80 | 10 | 10 |  | 81 | 81 | 81 | 81 | 81 | 5 | 5 | 732480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 128 | 131 | 140 | 139 | 100 | 70 |  | 110 | 110 | 111 | 111 | 110 | 110 | 110 | 2262270
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [22 empty] | 10 |  |  | 0 | 16740
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 47 | 53 | 53 | 53 | 5 | 5 | 5 | 287400
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 290 | 305 | 285 | 290 | 280 | 290 | 305 | 315 | 310 | 310 | 315 | 320 | 300 | 300 | 290 | 280 | 275 |  | 270 | 300 | 275 | 310 | 280 | 270 | 290 | 7275500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 118964
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 470352
61 | Narshingdi 22 MW PP (Doreen) | [25 empty] | 0 | 0
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 488016
63 | Impoprt (Tripura) | 112 | 110 | 100 | 100 | 96 | 90 | 90 | 82 | 96 | 98 | 100 | 110 | 114 | 122 | 120 | 116 | 108 | 108 |  | 134 | 134 | 134 | 132 | 130 | 122 | 114 | 2670720
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 40 |  | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 1152960
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 490176
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201240
67 | Jangalia 33MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 369800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 497960
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 3 | 6 | 6 | 8 | 8 | 8 | 6 |  | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 187560
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 718900
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 12 | 17 | 17 | 17 | 17 | 17 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 492400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [17 empty] | 8 |  | 58 | 65 | 65 | 65 | 65 | 60 | 40 | 379680
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 1 |  | 30 | 50 | 40 |  |  |  | 0 | 94080
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [6 empty] | 12 | 30 | 40 | 50 | 64 | 72 | 82 | 82 | 82 | 16 | 8 | 8 |  | 51 | 95 | 95 | 72 | 16 |  | 0 | 874560
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.7 | 1.8 | 2.9 | 4.1 | 4.4 | 4.7 | 4.6 | 3.9 | 2.9 | 1.8 | 0.7 | [9 empty] | 32761
| Jodiac Power | [25 empty] | 0 | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [8 empty] | 4 | 15 | 22 | 30 | 30 | 30 | 47 | 35 | 30 | 30 |  | 34 | 80 | 82 | 48 | 30 | 30 | 15 | 579816
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 140 | 150 | 140 | 140 | 150 | 140 | 145 | 150 | 145 | 140 | 140 | 140 | 140 | 120 | 120 | 140 | 130 | 135 |  | 120 | 130 | 140 | 130 | 120 | 130 | 130 | 3259811
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 1 |  | 37 | 52 |  |  |  |  | 0 | 85440
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 27 | 50 | 50 | 50 | 50 | 5 | 5 | 362736
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 20 | 51 | 51 | 51 | 51 | 5 | 5 | 383868
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 28 | 19 |  |  |  |  | 0 | 50400
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 10 |  | 8 | [5 empty] | 0 | 23040
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 15 | [5 empty] | 0 | 30410
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 12 |  | 35 | 35 |  |  |  |  | 0 | 61896
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 100 |  | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 3340227
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.4 | 1.1 | 1.6 | 2 | 2.4 | 2.5 | 2.3 | 2.2 | 1.7 | 1 | 0.5 | [9 empty] | 17400
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 53 | 53 | 17 |  |  |  | 0 | 79920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 40 | 24 | 24 | 24 | 7 | 32 | 75 | 115 | 117 | 117 | 116 | 115 | 115 | 115 | 115 | 105 | 105 | 105 |  | 112 | 115 | 115 | 124 | 124 | 125 | 70 | 2196000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [12 empty] | 10 | 15 | 15 |  |  | 0 |  | 35 | 30 | 25 | 15 | 14 |  | 0 | 144000
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 10 |  | 10 | [5 empty] | 0 | 15360
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 1 |  | 45 | 135 | 50 |  |  |  | 0 | 165600
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [19 empty] | 36 | 35 | 35 |  |  |  | 0 | 87600
| Anwara 300 MW PP (United) | [17 empty] | 5 |  | 101 | 65 | 32 |  |  |  | 0 | 138000
| Juldah unit-2 | 40 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 50 | 70 | 100 | 100 | 50 | 10 | 10 |  | 90 | 90 | 90 | 50 | 30 | 30 | 30 | 970560
120 | Eastern Zone Total | 4826 | 4885 | 4819 | 4702 | 4621 | 4503 | 4581.4 | 4765.5 | 4881.5 | 4973.2 | 5038.6 | 5293 | 5559.4 | 5561.5 | 5541.3 | 5336.2 | 5057.6 | 4765.1 |  | 5902 | 6062 | 5795 | 5762 | 5471 | 5107 | 4955 | 124620668
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 115 | 99 | 99 | 83 | 83 | 16 | 0 | 420480
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [25 empty] | 0 | 0
| Bhola 225 MW CCPP | 176 | 179 | 179 | 179 | 179 | 179 | 179 | 180 | 179 | 178 | 179 | 177 | 177 | 177 | 174 | 174 | 177 | 169 |  | 167 | 180 | 180 | 180 | 170 | 179 | 168 | 4314677
140 | Bhola 33 MW PP (Venture) | 17 | 17 | 17 | 16 | 16 | 14 | 12 | 11 | 13 | 14 | 14 | 14 | 16 | 15 | 19 | 18 | 15 | 14 |  | 23 | 22 | 22 | 24 | 22 | 21 | 19 | 401800
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [7 empty] | 8 | 8 | [10 empty] | 40 | 40 | 40 | 40 | 40 |  | 0 | 162000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 740 | 255 | 255 | 254 | 255 | 351 | 350 | 351 | 351 | 351 | 352 | 351 | 350 | 350 | 351 | 350 | 350 | 350 |  | 799 | 934 | 935 | 934 | 935 | 935 | 935 | 11651636
147 | Bheramara 410 MW CCPP | 330 | 340 | 330 | 330 | 345 | 280 | 280 | 280 | 280 | 280 | 280 | 375 | 350 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 350 | 345 | 330 | 335 | 335 | 8053632
148 | Payra 1320 MW | 301 | 302 | 301 | 300 | 300 | 301 | 301 | 301 | 301 | 300 | 302 | 300 | 301 | 302 | 300 | 300 | 301 | 312 |  | 348 | 390 | 408 | 452 | 449 | 381 | 300 | 7877900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 64 | 65 | 65 | 65 | 64 | 65 | 65 |  | 65 | 66 | 67 | 66 | 66 | 67 | 67 | 1545599
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6520800
153 | Baghabari 71 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 65 | 65 | 65 | 65 | 65 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 1490000
156 | Baghabari 100 MW GTPP | [14 empty] | 50 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 569000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 160 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 190 | 205 | 205 | 210 | 210 | 160 |  | 170 | 150 | 150 | 165 | 180 | 180 | 180 | 4250736
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 168 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 153 | 180 | 180 | 180 | 140 | 140 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4067600
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 344 | 371 | 351 | 342 | 371 | 334 | 372 | 371 | 373 | 410 | 410 | 402 | 405 | 410 | 394 | 402 | 390 | 390 |  | 384 | 410 | 422 | 425 | 388 | 375 | 384 | 9270673
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 5 | 5 | 5 | 5 | 5 | 5 | 17 | 17 | 17 | 16 | 12 | 12 | 12 | 12 | 12 | 13 | 15 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 307680
163 | Bogura 20 MW PP (Energyprima) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 274608
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244224
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [5 empty] | 8 | 42 | 42 | [9 empty] | 25 |  | 42 | 24 | 24 | 24 | 24 |  |  | 255319
167 | Katakhali 50 MW Peaking PP | [7 empty] | 4 | 29 | 29 | 29 | 29 | 29 | 33 | 36 | 37 | 37 | 37 |  | 37 | 37 | 40 | 38 | 38 | 10 |  | 474775
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [5 empty] | 0 | 21600
170 | Chapainawabganj 100 MW Peaking PP | 24 | 24 | [6 empty] | 42 | 42 | 42 | 42 | 51 | 51 | 50 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 1057624
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 34 | 18 | 45 |  |  |  | 0 | 109824
172 | Confidence Power Bogura Unit-1 113 MW | [7 empty] | 20 | 35 | 55 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 |  | 50 | 109 | 109 | 109 | 90 | 50 | 0 | 1128192
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 30 | 40 | 64 | 104 | 113 | 113 | 113 | 111 | 28 |  |  |  | 34 | 113 | 113 | 88 | 30 |  | 0 | 1032960
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.8 | 2.8 | 4.6 | 5.9 | 6.8 | 7.4 | 6.7 | 5.9 | 4.9 | 3.6 | 1.8 | 0.4 | [8 empty] | 50383
178
178