## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-04-18 | Saturday
|  | Date (day): | 2020-04-18 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13123.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15827 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-04-17 | 2020-04-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 280 | 300 | 300 | 65 |  | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 33 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 266 | 334 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 233 | 303 | 310 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 25 | 225 | 225 | 225 |  | 225 | GT-2 Under maint.
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 135 | 120 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 18 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 110 | 120 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 230 | 218 | 218 |  | 117 | Engine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 15 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 33 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 20 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 25 | 25
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1264 | 1775 | 3441 | 4091 | 543 | 1163
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 5 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 37 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 210 | 223 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 70 | 139 | 140 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 42 | 42
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 32 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 0 | 70 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 448 | 698 | 1608 | 1718 | 450 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 152 | 179 | 200 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 310 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 220 | 260 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 30 | 42 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 20 | 5 | 5 | 50 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 45 | 45 | 150 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 20 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 79 | 90 | 90 |  |  | ST shutdown
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 126 | 116 | 131
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 890 | 1396 | 1670 | 2374 | 463 | 0
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 212 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 70 | 170 | 170 |  | 30 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 150.1 | 310 | 613.6 | 612 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 50 | 55 | 70 | 71
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 22 | 22 |  | 60 | Machine problem.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 255 | 254 | 300 | 300 |  | 30 | Engine problem
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 48 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 28 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 40 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 74 | 81 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 70 | 120 | 30 | 30 |  |  | Engine problem
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 220 | 260 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 805 | 1070 | 1233 | 1234 | 0 | 490
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 353 | 928 | 553 | 947
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 230 | 330 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 583 | 1505 | 1338 | 2192 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 30 | 30
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 155 | 167 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 231 | 361 | 550 | 660 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 405 | 557 | 899 | 1105 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 65 | 65 | 70 | 70 | 30 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 15 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 180 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 145 | 210 | 210 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 178 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 245 | 374 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 2 | 17 | 17 | 17
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 898 | 1242 | 1900 | 2056 | 30 | 17
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 72 | 100 | 100
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 170 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 228.2 | 277 | 421 | 445 | 85 | 0
| Total |  |  |  |  | 19630 | 19107 | 5671.3 | 8830 | 13123.6 | 15827 | 1571 | 1768
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5325.1131 | 8291 | 12322.5105 | 14860.8898
A. |  | 2020-04-17 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8830 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5558.5 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8830 | MW
3 | Day peak Generation : |  |  | 5671.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8291 | MW
4 | Evening peak Generation : |  |  | 8830 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 161.4123 | MKWHr | By Solar | 0.16579 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 126.3356 | MKWHr |  | By Oil: | 7.7907 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.2387 | MKWHr |  | By Hydro: | 0.80208 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1571 | MW | Dhaka | 2412 | 2412 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1768 | MW | Chittagong | 820 | 820 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3339 | MW | Khulna | 1353 | 1353 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1039.16 | MMCFD |  |  | Rajshahi | 989 | 989 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 146175706.812 | ii) Oil : | Taka | 44288802.4 | Comilla | 943 | 943 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 64974661.43 | Total | Taka | 255439170.642 | Mymensingh | 654 | 654 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.204 | MKWHr. | Sylhet | 257 | 257 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 130 | MW (E to W) at | 19:30 | hrs | Barisal | 291 | 291 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -187 | MW at | 13:00 | hrs | Rangpur | 572 | 572 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.5° C |  |  | Total | 8291 | 8291 |  | 0
B. |  | 2020-04-18 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 38.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15827 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 5827 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 182.7999 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5708.7 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.6247 | MKWHr. | ii) HVDC Flow at Peak Time |  | 928 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4547 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.79 |  | (b) Today: | 79.65 |  | (c) Rule Curve: |  | 84.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-04-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 0 | 0 | 210 | 22 | 50 | 335 | 252 |  | 0 | 0 | 135 | 0 | 15 | 0 | 170 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 8 | 0 | 0 | 35 | 0 | 90 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 330 | 280 | 172 | 26 | 90 | 39 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 118 | 209 | 0 | 20 | 0 | 69 | 22 | 11 | 10 | 110 | 289 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 113 | 100 |  | 477 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 27 | 0 | 0 | 50 | 70 | 0 | 0 | 50 | 0 | 0 | 22 | 0 | 0 | 17 | 8 | 8 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 157 | 0 | 24 | 0 | 173 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571 |  | 4544 | 2972 | 7516 | 4276 | 477 | 1258 | 468 | 812 | 35 | 72 | 118 | 0 | 0 | 79.84
2:00 | 24 | 0 | 0 | 0 | 210 | 22 | 50 | 339 | 252 |  | 0 | 0 | 130 | 0 | 15 | 0 | 170 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 320 | 270 | 161 | 26 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 114 | 213 | 0 | 20 | 0 | 69 | 22 | 11 | 10 | 110 | 282 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 100 |  | 205 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 26 | 0 | 0 | 50 | 70 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 162 | 0 | 23 | 0 | 171 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 524 |  | 4443 | 2571 | 7014 | 4221 | 205 | 1292 | 331 | 765 | 36 | 50 | 114 | 0 | 0 | 79.83
3:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 339 | 252 |  | 0 | 0 | 130 | 0 | 15 | 0 | 170 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 330 | 275 | 170 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 116 | 213 | 0 | 0 | 0 | 68 | 22 | 5 | 0 | 110 | 286 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 50 |  | 206 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 25 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 5 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 162 | 0 | 24 | 0 | 171 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 |  | 4221 | 2412 | 6633 | 4208 | 206 | 1171 | 241 | 655 | 36 | 0 | 116 | 0 | 0 | 79.82
4:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 335 | 252 |  | 0 | 0 | 130 | 0 | 15 | 0 | 170 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 320 | 270 | 166 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 112 | 213 | 0 | 0 | 0 | 68 | 22 | 5 | 0 | 110 | 285 | 40 | 5 | 0 | 41 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 50 |  | 205 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 24 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 5 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 161 | 0 | 0 | 0 | 171 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 |  | 4179 | 2262 | 6441 | 4150 | 205 | 1151 | 221 | 566 | 36 | 0 | 112 | 0 | 0 | 79.81
5:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 335 | 252 |  | 0 | 0 | 135 | 0 | 15 | 0 | 170 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 223 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 330 | 275 | 169 | 8 | 90 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 110 | 213 | 0 | 0 | 0 | 68 | 22 | 5 | 0 | 110 | 285 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 30 |  | 205 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 22 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 5 | 72 | 0 | 170 | 0 | 0 | 140 | 0 | 160 | 0 | 0 | 0 | 170 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4175 | 2243 | 6418 | 4176 | 205 | 1143 | 206 | 542 | 36 | 0 | 110 | 0 | 0 | 79.8
6:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 334 | 252 |  | 0 | 0 | 120 | 0 | 15 | 0 | 130 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 37 | 0 | 90 | 0 | 0 | 223 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 250 | 158 | 8 | 80 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 102 | 214 | 0 | 0 | 0 | 70 | 22 | 5 | 0 | 110 | 281 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 26 | 10 |  | 206 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 18 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 7 | 8 | 8 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 145 | 0 | 0 | 0 | 171 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 3928.9 | 2102 | 6030.9 | 3875 | 206 | 1085 | 171 | 541 | 37 | 13 | 102 | 0.9 | 0 | 79.79
7:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 333 | 252 |  | 0 | 0 | 120 | 0 | 15 | 0 | 130 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 17 | 0 | 0 | 37 | 0 | 90 | 0 | 0 | 223 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 250 | 159 | 8 | 80 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 98 | 216 | 0 | 0 | 0 | 68 | 22 | 5 | 0 | 110 | 282 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 26 | 0 |  | 205 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 15 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 7 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 171 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 261 |  | 3846.7 | 2042.1 | 5888.8 | 3811 | 205 | 1040 | 161 | 503 | 37 | 29 | 98 | 4.8 | 0 | 79.78
8:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 323 | 233 |  | 0 | 0 | 120 | 0 | 15 | 0 | 130 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 25 | 20 | 0 | 0 | 38 | 0 | 90 | 0 | 0 | 223 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 275 | 250 | 151 | 8 | 80 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 21 | 100 | 187 | 0 | 0 | 0.7 | 68 | 10 | 5 | 0 | 110 | 279 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 | 0 | 8 | 0 |  | 207 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 15 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 7 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 144 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 230 |  | 3743.1 | 1959.8 | 5702.9 | 3704 | 207 | 997 | 143 | 472 | 38 | 29 | 100 | 12.9 | 0 | 79.77
9:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 289 | 233 |  | 0 | 0 | 125 | 0 | 15 | 0 | 150 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 25 | 8 | 0 | 0 | 37 | 0 | 90 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 17 | 80 | 0 | 0 | 275 | 220 | 150 | 8 | 51 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 86 | 148 | 0 | 0 | 0.9 | 68 | 10 | 5 | 0 | 130 | 280 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 206 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 15 | 0 | 0 | 55 | 60 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 7 | 8 | 11 | 71 | 0 | 170 | 0 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 230 |  | 3619.7 | 1938.8 | 5558.5 | 3572 | 206 | 1004 | 140 | 471 | 37 | 29 | 86 | 13.5 | 0 | 79.76
10:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 268 | 233 |  | 0 | 0 | 135 | 0 | 15 | 0 | 150 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 25 | 8 | 0 | 0 | 37 | 0 | 90 | 0 | 0 | 211 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 310 | 220 | 151 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 70 | 148 | 0 | 0 | 1.1 | 70 | 10 | 5 | 0 | 100 | 264 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 305 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 17 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 35 | 0 | 29 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 231 |  | 3518.6 | 1999.6 | 5518.2 | 3521 | 305 | 897 | 185 | 452 | 37 | 29 | 70 | 22.2 | 0 | 79.75
11:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 266 | 234 |  | 0 | 25 | 135 | 0 | 15 | 0 | 150 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 0 | 8 | 0 | 0 | 37 | 0 | 90 | 0 | 0 | 211 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 295 | 220 | 151 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 70 | 148 | 0 | 0 | 0.3 | 50 | 20 | 5 | 0 | 100 | 261 | 40 | 5 | 0 | 40 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 353 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 18 | 0 | 0 | 65 | 65 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 170 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6 | 0 | 230 |  | 3443.4 | 2100.6 | 5544 | 3525 | 353 | 870 | 200 | 451 | 37 | 15 | 70 | 23 | 0 | 79.74
12:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 266 | 233 |  | 0 | 25 | 135 | 0 | 15 | 0 | 180 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 275 | 220 | 152 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 62 | 148 | 0 | 0 | 2.1 | 50 | 20 | 5 | 0 | 140 | 255 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 353 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 19 | 0 | 0 | 65 | 65 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 180 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0 | 231 |  | 3557.1 | 2114.2 | 5671.3 | 3590 | 353 | 954 | 200 | 452 | 36 | 15 | 62 | 9.3 | 0 | 79.74
13:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 266 | 233 |  | 0 | 150 | 135 | 0 | 15 | 0 | 180 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 35 | 0 | 90 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 275 | 250 | 190 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 66 | 147 | 0 | 0 | 2.3 | 50 | 20 | 5 | 0 | 140 | 253 | 53 | 5 | 0 | 70 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 353 | 0 | 230 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 40 | 155 | 17 | 0 | 0 | 65 | 70 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 200 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 230 |  | 3828.9 | 2214.2 | 6043.1 | 3699 | 353 | 1157 | 250 | 451 | 35 | 15 | 66 | 17.1 | 0 | 79.73
14:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 266 | 233 |  | 0 | 200 | 135 | 0 | 13 | 0 | 180 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 80 | 0 | 0 | 310 | 250 | 180 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 10 | 74 | 148 | 0 | 20 | 1.8 | 51 | 20 | 5 | 0 | 140 | 266 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 353 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 155 | 22 | 0 | 0 | 65 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 214 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 231 |  | 3999 | 2287.9 | 6286.9 | 3830 | 353 | 1275 | 254 | 452 | 35 | 0 | 74 | 13.9 | 0 | 79.73
15:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 290 | 263 |  | 0 | 225 | 135 | 0 | 15 | 0 | 200 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 250 | 161 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 10 | 80 | 146 | 0 | 20 | 1 | 41 | 20 | 5 | 0 | 140 | 253 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 344 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 155 | 20 | 0 | 0 | 65 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 15 | 214 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0 | 231 |  | 3995.4 | 2314.7 | 6310.1 | 3763 | 344 | 1346 | 256 | 452 | 36 | 15 | 80 | 18.1 | 0 | 79.72
16:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 303 | 263 |  | 0 | 225 | 135 | 0 | 15 | 0 | 200 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 20 | 0 | 0 | 36 | 0 | 95 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 250 | 161 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 20 | 88 | 147 | 0 | 20 | 0.6 | 41 | 20 | 5 | 0 | 100 | 255 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 343 | 0 | 265 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 155 | 19 | 0 | 0 | 65 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 2 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 180 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 232 |  | 3977.3 | 2214.2 | 6191.5 | 3745 | 343 | 1261 | 256 | 452 | 36 | 0 | 88 | 10.5 | 0 | 79.72
17:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 286 | 263 |  | 0 | 225 | 135 | 0 | 15 | 0 | 140 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 20 | 0 | 0 | 36 | 0 | 95 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 300 | 250 | 181 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 20 | 88 | 147 | 0 | 20 | 0.4 | 41 | 20 | 5 | 0 | 100 | 262 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 344 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 13 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 71 | 0 | 150 | 0 | 0 | 180 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 230 |  | 3935.1 | 2005.8 | 5940.9 | 3637 | 344 | 1209 | 174 | 451 | 36 | 0 | 88 | 1.9 | 0 | 79.71
18:00 | 24 | 0 | 0 | 0 | 210 | 22 | 0 | 265 | 263 |  | 0 | 160 | 135 | 0 | 15 | 0 | 140 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 17 | 0 | 0 | 37 | 0 | 95 | 0 | 0 | 211 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 330 | 250 | 183 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 20 | 94 | 149 | 0 | 20 | 0 | 46 | 30 | 5 | 0 | 100 | 265 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 |  | 344 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 26 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 72 | 0 | 150 | 0 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 249 |  | 3953 | 1983.2 | 5936.2 | 3623 | 344 | 1189 | 178 | 471 | 37 | 0 | 94 | 0.2 | 0 | 79.71
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 0 | 0 | 280 | 33 | 0 | 295 | 303 |  | 0 | 225 | 120 | 0 | 16 | 0 | 228 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 17 | 0 | 0 | 37 | 0 | 95 | 0 | 1 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 42 | 110 | 0 | 0 | 310 | 260 | 179 | 45 | 82 | 20 | 5 | 0 | 9 | 0 | 0 | 0 | 21 | 5 | 33 | 20 | 126 | 212 | 3 | 20 | 0 | 52 | 30 | 23 | 15 | 100 | 252 | 40 | 74 | 0 | 120 | 19 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 55 | 70 |  | 929 | 0 | 335 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 27 | 0 | 0 | 65 | 70 | 0 | 0 | 100 | 42 | 0 | 0 | 8 | 0 | 17 | 2 | 10 | 72 | 0 | 150 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 19 | 154 | 0 | 390 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 30 | 335 |  | 5049 | 3375 | 8424 | 4422 | 929 | 1620 | 599 | 557 | 37 | 134 | 126 | 0 | 0 | 79.7
19:30 | 24 | 0 | 0 | 0 | 280 | 33 | 0 | 334 | 303 |  | 0 | 225 | 120 | 0 | 18 | 0 | 230 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 25 | 8 | 20 | 20 | 0 | 0 | 37 | 0 | 95 | 0 | 5 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 42 | 135 | 0 | 0 | 310 | 260 | 179 | 45 | 79 | 30 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 5 | 33 | 20 | 126 | 212 | 8 | 20 | 0 | 55 | 30 | 48 | 28 | 100 | 254 | 40 | 74 | 0 | 120 | 19 | 0 | 10 | 260 | 24 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 113 | 70 |  | 928 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 167 | 29 | 0 | 0 | 65 | 70 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 72 | 0 | 170 | 0 | 0 | 180 | 0 | 145 | 0 | 0 | 100 | 178 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 361 |  | 5249 | 3581 | 8830 | 4533 | 928 | 1636 | 833 | 603 | 37 | 134 | 126 | 0 | 0 | 0
20:00 | 24 | 0 | 0 | 0 | 280 | 32 | 0 | 335 | 304 |  | 0 | 225 | 120 | 0 | 30 | 0 | 200 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 11 | 20 | 20 | 0 | 0 | 37 | 0 | 95 | 0 | 9 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 42 | 100 | 0 | 0 | 310 | 260 | 179 | 45 | 84 | 42 | 5 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 128 | 212 | 8 | 20 | 0 | 55 | 30 | 50 | 28 | 100 | 254 | 40 | 78 | 0 | 99 | 19 | 0 | 9 | 280 | 24 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 113 | 50 |  | 928 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 178 | 30 | 0 | 0 | 65 | 70 | 0 | 0 | 65 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 180 | 0 | 145 | 0 | 0 | 98 | 178 | 0 | 396 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 35 | 396 |  | 5160 | 3594 | 8754 | 4462 | 928 | 1674 | 788 | 638 | 37 | 99 | 128 | 0 | 0 | 79.7
21:00 | 24 | 0 | 0 | 0 | 280 | 34 | 0 | 336 | 302 |  | 0 | 225 | 120 | 0 | 30 | 0 | 200 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 11 | 20 | 25 | 0 | 0 | 37 | 0 | 95 | 0 | 16 | 223 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 42 | 100 | 0 | 0 | 310 | 265 | 179 | 45 | 86 | 42 | 5 | 0 | 20 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 122 | 212 | 0 | 20 | 0 | 86 | 30 | 23 | 28 | 100 | 251 | 40 | 78 | 0 | 98 | 19 | 0 | 10 | 290 | 22 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 50 |  | 924 | 0 | 335 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 178 | 31 | 0 | 0 | 65 | 70 | 0 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 180 | 0 | 146 | 0 | 23 | 100 | 178 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 402 |  | 5094 | 3588 | 8682 | 4501 | 924 | 1685 | 710 | 644 | 37 | 59 | 122 | 0 | 0 | 79.69
22:00 | 24 | 0 | 0 | 0 | 280 | 34 | 0 | 335 | 252 |  | 0 | 225 | 120 | 0 | 30 | 0 | 140 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 11 | 20 | 25 | 0 | 0 | 36 | 0 | 95 | 0 | 16 | 223 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 15 | 100 | 0 | 0 | 310 | 265 | 179 | 45 | 82 | 35 | 5 | 0 | 8 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 126 | 213 | 0 | 20 | 0 | 86 | 30 | 5 | 5 | 100 | 256 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 30 |  | 924 | 0 | 330 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 31 | 0 | 0 | 65 | 70 | 0 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 150 | 0 | 145 | 0 | 24 | 0 | 175 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 |  | 4714 | 3322 | 8036 | 4333 | 924 | 1425 | 497 | 644 | 36 | 51 | 126 | 0 | 0 | 79.69
23:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 305 | 252 |  | 0 | 190 | 125 | 0 | 15 | 0 | 140 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 11 | 20 | 25 | 0 | 0 | 36 | 0 | 95 | 0 | 16 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 250 | 140 | 8 | 80 | 5 | 5 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 122 | 216 | 0 | 20 | 0 | 87 | 0 | 5 | 5 | 100 | 253 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 10 |  | 925 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 30 | 0 | 0 | 65 | 40 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 72 | 0 | 170 | 0 | 0 | 150 | 0 | 135 | 0 | 24 | 0 | 130 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 |  | 4222 | 3004 | 7226 | 3884 | 925 | 1355 | 327 | 577 | 36 | 0 | 122 | 0 | 0 | 79.68
24:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 264 | 252 |  | 0 | 190 | 125 | 0 | 15 | 0 | 140 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 8 | 20 | 24 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 230 | 235 | 140 | 8 | 91 | 5 | 5 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 120 | 215 | 0 | 20 | 0 | 86 | 0 | 5 | 5 | 100 | 253 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 10 |  | 829 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 28 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 72 | 0 | 170 | 0 | 0 | 150 | 0 | 141 | 0 | 23 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4118 | 2760 | 6878 | 3789 | 829 | 1291 | 272 | 542 | 35 | 0 | 120 | 0 | 0 | 79.68
KWH | 496000 | 0 | 0 | 0 | 5282209 | 193409 | 109760 | 7425020 | 6093000 |  | 0 | 2228500 | 3024291 | 0 | 438 | 0 | 4233675 | 0 | 2388000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86327 | 93276 | 600000 | 183060 | 651400 | 504500 | 0 | 0 | 802080 | 0 | 2200000 | 0 | 76075 | 5165061 | 0 | 2446394 | 0 |  | 0 | 0 | 108931 | 0 | 0 | 0 | 451152 | 1027680 | 2026630 | 0 | 0 | 7441000 | 6178000 | 4014000 | 368000 | 1677190 | 434376 | 151200 | 0 | 261004 | 0 | 0 | 0 | 464976 | 25740 | 558100 | 431390 | 2454720 | 4338080 | 12480 | 247536 | 9950 | 1492000 | 492000 | 215400 | 150624 | 2903645 | 6091000 | 978048 | 381120 | 0 | 1523830 | 58000 | 0 | 32940 | 6919500 | 68472 | 29000 | 0 | 0 | 0 | 0 | 336000 | 0 | 0 | 98520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16804 | 102873 | 0 | 0 | 0 | 926520 | 616320 |  | 10624727 | 0 | 6914304 | 0 | 555840 | 0 | 0 | 0 | 0 | 0 | 246000 | 3984626 | 510552 | 0 | 0 | 1385000 | 1540000 | 0 | 0 | 346090 | 647070 | 0 | 206748 | 10560 | 0 | 205200 | 120780 | 188316 | 1706181 | 0 | 3940500 | 0 | 11000 | 4200245 | 0 | 3715845 | 0 | 161100 | 279360 | 3935400 | 0 | 7749327 | 0 | 0 | 0 | 0 | 55680 | 0 | 40519 | 142080 | 7592000 |  | 100397226 | 61015050 | 161412276 | 96552851 | 10624727 | 29782741 | 7117914 | 13238681 | 802080 | 672769 | 2454720 | 165793 | 0
Fuel Cost | 813440 | 0 | 0 | 0 | 5863251.99 | 255299.88 | 186592 | 7499270.2 | 6275790 |  | 0 | 2429065 | 3356963.01 | 0 | 3017.82 | 0 | 4403022 | 0 | 4131240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 851184.22 | 69957 | 450000 | 0 | 0 | 0 | 0 | 0 | 216561.6 | 0 | 3982000 | 0 | 706736.75 | 5629916.49 | 0 | 4158869.8 | 0 |  | 0 | 0 | 1056630.7 | 0 | 0 | 0 | 568451.52 | 3052209.6 | 2999412.4 | 0 | 0 | 5506340 | 6178000 | 3692880 | 474720 | 1928768.5 | 490844.88 | 211680 | 0 | 446316.84 | 0 | 0 | 0 | 590519.52 | 19305 | 976675 | 323542.5 | 18410400 | 4598364.8 | 113318.4 | 314370.72 | 158603 | 2446880 | 787200 | 383412 | 234973.44 | 3310155.3 | 6334640 | 1926754.56 | 727939.2 | 0 | 2636225.9 | 127020 | 0 | 67197.6 | 6988695 | 51354 | 22040 | 0 | 0 | 0 | 0 | 1747200 | 0 | 0 | 1151698.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777719.88 | 0 | 0 | 0 | 7940276.4 | 4104691.2 |  | 61198427.52 | 0 | 7260019.2 | 0 | 4368902.4 | 0 | 0 | 0 | 0 | 0 | 2563320 | 4502627.38 | 791355.6 | 0 | 0 | 2839250 | 3157000 | 0 | 0 | 3062896.5 | 4982439 | 0 | 2003388.12 | 102326.4 | 0 | 393984 | 187209 | 142555.212 | 10288271.43 | 0 | 21357510 | 0 | 313830 | 4914286.65 | 0 | 4904915.4 | 0 | 241650 | 4751913.6 | 4604418 | 0 | 7671833.73 | 0 | 0 | 0 | 0 | 432076.8 | 0 | 447734.95 | 1049971.2 | 33328880 |  | 145159604.42 | 191862992.092 | 337022596.512 | 111845628.622 | 61198427.52 | 34330078.19 | 37852057.08 | 64974661.43 | 216561.6 | 6436745.32 | 18410400 | 1758036.75 | 0
Yesterday Day Peak | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 266 | 233 |  | 0 | 25 | 135 | 0 | 15 | 0 | 180 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 20 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 275 | 220 | 152 | 8 | 50 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 62 | 148 | 0 | 0 | 2.1 | 50 | 20 | 5 | 0 | 140 | 255 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 353 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 19 | 0 | 0 | 65 | 65 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 2 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 180 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 0 | 231 |  | 5671.3 | DayPeak
Yesterday Evening Peak | 24 | 0 | 0 | 0 | 280 | 33 | 0 | 334 | 303 | 0 | 0 | 225 | 120 | 0 | 18 | 0 | 230 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 25 | 8 | 20 | 20 | 0 | 0 | 37 | 0 | 95 | 0 | 5 | 223 | 0 | 139 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 42 | 135 | 0 | 0 | 310 | 260 | 179 | 45 | 79 | 30 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 5 | 33 | 20 | 126 | 212 | 8 | 20 | 0 | 55 | 30 | 48 | 28 | 100 | 254 | 40 | 74 | 0 | 120 | 19 | 0 | 10 | 260 | 24 | 8 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 113 | 70 |  | 928 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 167 | 29 | 0 | 0 | 65 | 70 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 72 | 0 | 170 | 0 | 0 | 180 | 0 | 145 | 0 | 0 | 100 | 178 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 361 |  | 8830 | EvPeak
Forecast for Evening | 24 | 0 | 0 | 0 | 300 | 108 | 78 | 412 | 360 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 218 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 25 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 100 | 0 | 0 | 360 | 360 | 225 | 45 | 90 | 42 | 5 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 131 | 210 | 95 | 22 | 0 | 71 | 22 | 51 | 44 | 163 | 300 | 66 | 81 | 0 | 30 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 170 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 947 | 40 | 410 |  | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 180 | 30 | 110 | 30 | 70 | 70 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 100 | 0 | 200 | 17 | 15 | 210 | 0 | 210 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 660
Forecast for Day | 24 | 0 | 0 | 0 | 300 | 108 | 78 | 412 | 310 | 0 | 0 | 225 | 150 | 100 | 100 | 55 | 218 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 25 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 100 | 0 | 0 | 360 | 360 | 200 | 45 | 90 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 116 | 210 | 95 | 22 | 1.6 | 70 | 22 | 51 | 44 | 163 | 300 | 66 | 81 | 0 | 30 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 200 | 0 | 0 | 170 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 0 | 113 | 100 |  | 553 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 180 | 30 | 50 | 0 | 70 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 43 | 0 | 17 | 11 | 11 | 100 | 0 | 200 | 0 | 0 | 210 | 0 | 210 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 550
Generation at 08:00(Today) | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 263 | 242 | 0 | 0 | 190 | 125 | 0 | 2 | 0 | 140 | 0 | 39 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 20 | 25 | 0 | 0 | 37 | 0 | 95 | 0 | 16 | 197 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 250 | 210 | 142 | 8 | 90 | 5 | 5 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 33 | 15 | 94 | 166 | 0 | 0 | 0.4 | 82 | 0 | 5 | 5 | 110 | 245 | 40 | 5 | 0 | 30 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 15 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 72 | 0 | 170 | 0 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 130 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 299 | 0
199
| Minimum Generation |  | 5558.5 | 9:00
| Highest Generation |  | 8830 | 19:30
| Day Peak Generation |  | 5671.3 | 12:00
| Evening Peak Generation |  | 8830 | 19:30
| HVDC Max Flow |  | 929 | 19:00
| HVDC EvPeak Flow |  | 928 | 19:30
| Load factor L.F |  | 76.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-04-18
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-04-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5671.3 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5708.7 | MW
Evening Peak Generation : |  | 8830 | MW Hour : | 19:30 | Available Max Generation : |  | 15827 | MW
E.P. Demand (at gen end) : |  | 8830 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 8830 | MW Hour : | 19:30 | Reserve(Generation end) |  | 5827 | MW
Total Gen. (MKWH) : |  | 161.4123 | System Load Factor : | 76.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -187 | MW at | 13:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-04-18
Actual : | 79.65 | Ft.(MSL) , | Rule curve : | 84.6 | Ft.( MSL )
Gas Consumed : | Total = | 1039.16 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146175706.812
: |  | Coal : | 64974661.43 | Oil : | 44288802.4 | Total : | 255439170.642
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3503.4887 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1188.1578 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1063.9758 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 961.188 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 868.7241 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 701.0215 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 396.1233 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 180.6039 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 540.6427 |  |  | 0 | 0%
Total | 0 |  | 9403.926 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Siddhirganj 210 MW GT-1
3) Ghorasal Unit-1,3,4 & 5.
4) Ashuganj unit-5
5) Siddirganj-335 MW ST
6) Kaptai-2,5
7) Megnaghat-450 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) BSRM-GPH 230 kV Ckt-2 tripped at 12:23 from both ends showing distance Z1, R-phase, 67N at both
ends and was switched on at 13:05.
b) Meghnaghat 450 MW GT-1 was synchronized at 10:43 and STG was synchronized at 12:48.
c) Maniknagar 132/33 kV T-2 transformer was under shut down from 09:33 to 14:00 for DPDC work.
d) Kabirpur 132 kV Reserve Bus was under shut down from 08:58 to 14:56 and 132/33 kV transformer
was under shut down from 08:58 to 15:13 for C/M.
e) Kallyanpur-Lalbagh 132 kV Ckt-1 was charged at 14:32.
f) Barishal-Bhandaria 132 kV Ckt tripped at 17:00 showing O/C relay due to Barguna 33 kV feeder tripped |  |  |  |  | About 35 MW power interruption occurred under Barisal S/S area
showing O/C, E/F relay and was switched on at 17:14. |  |  |  |  | from 17:00 to 17:14.
g) Netrokona 132/33 kV T-3 transformer was under shut down from 20:00 to 20:40 for R/H maintenance |  |  |  |  | About 10 MW power interruption occurred under Barisal S/S area
to attend PBS feeder. |  |  |  |  | from 20:00 to 20:40.
h) Jashore-Jhenaidah 132 kV Ckt-1 tripped at 22:04 from both ends showing U/V relay at Jashore end
trip a-phase,dist. Z1 relay at Jhenaidah end and was switched on at 22:23.
i) Mymensingh-Kishoreganj 132 kV Ckt-1 tripped at 00:00(18/04/2020) from both ends showing Dist. A-B,Z1
relay at Mymensingh end and Dist.B-C, Z1 relay at Kishoreganj end and was switched on at 00:23.
k) Rangpur-Kurigram 132 kV Ckt tripped at 03:14(18/4/2020) from Rangpur end showing Dist. R-Y,Z1 |  |  |  |  | About 10 MW power interruption occurred under Barisal S/S area
relay trial was given at 3:55 tripped again showing O/C,SOTF relay and was switched on at 07:50. |  |  |  |  | from 03:14(18/04/2020) to 07:50.
l) Khulna(s)-Satkhira 132 kV Ckt-2 tripped at 01:38(18/04/2020) from Khulna(s) showing Dist. A-B,Z1 relay
and was switched on at 02:08.
m) Polashbari-Rangpur Confidence 132 kV Ckt-1 tripped at 03:13 from both ends showing dist. Phase-C,O/C
relay at Polashbari end and B-phase, O/C relay at Rangpur Confidence end and was switched on at 04:02.
n) Madunaghat 132/33 kV T-1 transformer was under shut down from 06:28(18/04/2020) to 09:35 for
R/H maintenance at B-phase isolator of 33 kV Bus.
o) Rangpur-Lalmonirhat 132 kV Ckt was under shut down from 06:35(18/04/2020) to 07:45 for repairing
sky wire of Rangpur-Kurigram Ckt.
p) Sylhet 132/33 kV T-2 transformer tripped at 06:43(18/04/2020) due to operating Buchholz relay and
was switched on at 11:30.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-04-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 496000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 5282209 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 109760 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 33 | 193409 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 334 | 7425020 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 303 | 6093000 | Frequency control
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 2228500 | GT-2 under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 120 | 3024291 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 18 | 438 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 93276 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 2388000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 230 | 4233675 | Engine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 15 | 86327 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 783060 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 651400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 504500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1775 | 33592865
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 5 | 76075 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 98520
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 802080 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 223 | 5165061 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2446394 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 108931 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 451152
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1027680
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16804
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 32 | 102873 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 70 | 616320 | Low demand
| Chattogram area Total |  |  |  | 2166 | 698 | 13111890
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2026630 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 179 | 4014000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7441000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6178000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 434376
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 151200 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 368000 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 20 | 261004 | Gas shortage.
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 79 | 1677190 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 464976
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 25740
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2454720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 558100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 431390
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 926520
| Cumilla Area Total |  |  |  | 2980 | 1396 | 27412846
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 212 | 4338080
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 247536
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 12480 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9950
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 70 | 336000 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 310 | 4944046
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 55 | 1492000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 492000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2903645 | Frequency control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 254 | 6091000 | Machine problem
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 215400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 28 | 150624
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 29000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 978048 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 381120
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 120 | 1523830
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 58000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 68472
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6919500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 32940
| Sylhet Area Total |  |  |  | 1949 | 1070 | 21335579
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 928 | 10624727
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 555840
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 6914304 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 246000 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 279360
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1505 | 18620231
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 510552
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 167 | 3984626
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 161100 | For Payra test
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 361 | 7592000 | On test
| Barisal Area Total |  |  |  | 462 | 557 | 12248278
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1540000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 65 | 1385000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 647070
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 206748
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4200245 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 145 | 3715845 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 3935400 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 374 | 7749327 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 205200 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 120780 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 188316 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 10560 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 346090
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 142080 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1242 | 24392661
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1706181
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3940500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 11000 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 55680 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40519
| Rangpur Area Total |  |  |  | 605 | 277 | 5753880
| Total |  |  |  | 19107 | 8830 | 161412276
| Eastern Grid Total |  |  |  | 13543 | 5249 | 100397226
| Western Grid Total |  |  |  | 5564 | 3581 | 61015050
| National Grid Total |  |  |  | 19107 | 8830 | 161412276
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-04-17
(a) ENTIRE EASTERN GRID : |  | 5086 | MW | (b) ENTIRE WESTERN GRID : |  | 3205 | MW
i) Dhaka area |  | 2412 | MW | i) Khulna area |  | 1353 | MW
ii) Chittagong area |  | 820 | MW | ii) Rajshahi area |  | 989 | MW
iii) Comilla area |  | 943 | MW | iii) Barisal area |  | 291 | MW
iv) Mymensingh area |  | 654 | MW | iv) Rangpur area |  | 572 | MW
v) Sylhet area |  | 257 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8291 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 70 | 21:00 | Sherpur | 74 | 19:30 | Benapol | 48 | 21:00
Munsiganj | 102 | 21:00 | Srimongal | 26 | 19:30 | Jhenida | 110 | 19:30
Sonargaon | 39 | 2:00 | Shahjibazar | 54 | 19:00 | Bottail | 94 | 19:30
Shyampur | 132 | 1:00 | Fenchuganj | 20 | 19:30 | G.K Project | 51 | 19:30
Bhulta | 71 | 22:00 | Kulawara | 26 | 21:00 | Faridpur | 164 | 21:00
Madanganj | 44 | 3:00 | Sylhet | 75 | 19:30 | Madaripur | 90 | 21:00
Shitalakhya | 57 | 21:00 | Chatak | 13 | 21:00 | Sariatpur | 56 | 19:30
Rahim steel | 0 | 1:00 | Sunamganj | 24 | 19:30 | Gopalganj | 89 | 19:30
Matuail | 46 | 23:00 | Biani Bazar | 32 | 21:00 | Bagerhat | 80 | 21:00
Ghorasal | 42 | 20:00 | Comilla (S) | 128 | 20:00 | Mongla | 38 | 1:00
Narsingdi | 79 | 20:00 | Comilla(N) | 127 | 18:30 | Satkhira | 106 | 21:00
Haripur (SBU) | 42 | 1:00 | Chandpur | 89 | 20:00 | Gallamari | 44 | 24:00
Ullon | 48 | 14:00 | Feni | 97 | 21:00 | Magura | 50 | 19:00
Hasnabad | 158 | 20:00 | Chowmuhani | 138 | 19:00 | Norail | 38 | 19:00
Magbazar | 68 | 19:00 | Ashuganj | 41 | 22:00 | Chuadanga | 83 | 19:30
Maniknagar | 60 | 20:00 | Daudkandi | 118 | 20:00 | Barisal(N) | 40 | 21:00
Bangabhaban | 12 | 8:00 | B.Baria | 113 | 19:30 | Barisal (S) | 82 | 19:30
Narinda | 58 | 10:00 | Ramganj | 102 | 21:00 | Patuakhali | 97 | 21:00
Dhanmondi | 70 | 18:00 | Chaddagram | 28 | 18:30 | Bhandaria | 48 | 21:00
Lalbag | 34 | 19:00 | PHP | 8 | 20:00 | Borhan Uddin | 36 | 21:00
Madartek | 59 | 21:00 | Madunaghat | 57 | 19:30 | Ishurdi | 50 | 20:00
Dhaka University |  |  | Hathazari | 73 | 1:00 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 73 | 19:30 | Khulshi | 109 | 1:00 | Natore | 101 | 19:30
Kalyanpur | 69 | 19:30 | Halishahar | 101 | 18:30 | Bogra | 109 | 19:30
Gulshan | 70 | 19:30 | Baraulia | 97 | 0:00 | Noagaon | 93 | 19:30
Uttara | 51 | 1:00 | Sikalbaha | 18 | 19:30 | Rajshahi | 122 | 20:00
Uttara New | 16 | 21:00 | Dohazari | 82 | 20:00 | Rajshahi New | 12 | 20:00
Kamrangirchar | 58 | 20:00 | Cox'sbazar | 90 | 19:30 | C.Nawabganj | 74 | 20:00
Savar | 76 | 21:00 | Chandraghona | 24 | 19:30 | Amnura | 48 | 19:00
Bhasantec | 104 | 19:30 | Kaptai | 8 | 22:00 | Pabna | 84 | 20:00
Agargaon | 38 | 19:30 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 76 | 20:00
Satmosjid | 73 | 19:30 | Bakulia | 66 | 1:00 | Serajganj | 67 | 19:00
Tongi | 78 | 19:30 | Julda | 17 | 1:00 | Niyamatpur | 57 | 19:00
Kabirpur | 109 | 3:00 | TK chemical | 12 | 19:00 | Joypurhat | 39 | 20:00
Basundhara | 80 | 19:00 | Modern Steel | 0.2 | 1:00 | Sherpur(Bogura) | 34 | 20:00
Manikganj | 72 | 19:00 | Shahmirpur | 20.5 | 22:00 | Mohastangor | 35 | 19:00
Joydevpur | 77 | 21:00 | Khagrachhari | 18 | 19:00 | Rangpur | 101 | 20:00
New Tongi | 51 | 21:00 | Matarbari | 29.5 | 19:30 | Lalmonirhat | 41 | 19:30
Kodda | 96 | 21:00 | Baroiar Hat | 34 | 19:00 | Saidpur | 75 | 19:00
Dhamrai | 52 | 19:00 | Rangamati | 10 | 19:00 | Purbasadipur | 83 | 19:00
Rajendrapur | 50 | 21:00 | Abul Khair 230 | 15 | 22:00 | Thakurgaon | 58 | 19:30
Valuka | 42 | 19:30 | BSRM | 1 | 1:00 | Palashbari | 82 | 20:00
Tangail | 161 | 19:30 | GPH Ispat | 8 | 16:00 | Barapukuria | 38 | 20:00
Mymensing | 135 | 19:30 | Goalpara | 20 | 20:00 | Panchagar | 37 | 19:30
Kishorganj | 86 | 20:00 | Central s/s | 72 | 19:00 | Joldhaka | 20 | 19:30
Netrokona | 86 | 19:00 | Noapara | 51 | 21:00 | Kurigram | 39 | 0.8125
Jamalpur | 71 | 19:30 | Jessore | 132 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-04-17 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 405 | 0.5 | 395 | 0.041667 | Kaliakoir | 389 | 0.41667 | 379 | 0.041667
Bheramara | 404 | 0.16667 | 385 | 0.83333 | Bhulta | 398 | 0.33333 | 386 | 0.95833
Ashuganj(N) | 400 | 0.375 | 394 | 0.041667 | Gopalganj | 408 | 0.20833 | 386 | 0.041667
Payra | 411 | 0.29167 | 396 | 0.041667
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 0.041667 | 234 | 0.875 | Hathazari | 224 | 0.54167 | 215 | 0.041667
Ishurdi | 235 | 0.041667 | 226 | 0.58333 | Megnaghat | 236 | 0.375 | 230 | 0.041667
Ashuganj | 242 | 0.29167 | 235 | 0.20833 | Fenchuganj | 243 | 0.33333 | 238 | 0.041667
Serajganj | 233 | 0.083333 | 230 | 0.58333 | Siddhirganj | 235 | 0.33333 | 230 | 0.041667
Baghabari | 243 | 0.33333 | 238 | 0.041667 | Maniknagar | 234 | 0.41667 | 229 | 0.041667
Barapukuria | 232 | 0.20833 | 225 | 0.79167 | Old Airport | 233 | 0.375 | 227 | 0.041667
Bogra | 233 | 0.20833 | 225 | 0.79167 | Barisal | 243 | 0.29167 | 232 | 0.83333
Khulna South | 224 | 0.25 | 209 | 0.58333 | AKSML | 222 | 0.54167 | 213 | 0.125
Rampura | 232 | 0.33333 | 228 | 0.041667 | BSRM | 228 | 0.54167 | 218 | 0.041667
Haripur | 232 | 0.29167 | 229 | 0.041667 | Bibiyana | 241 | 0.375 | 236 | 0.79167
Hasnabad | 234 | 0.29167 | 230 | 0.54167 | Bhulta | 236 | 0.29167 | 230 | 0.041667
Shyampur | 231 | 0.33333 | 225 | 0.041667 | Ashuganj (S) | 237 | 0.33333 | 233 | 0.79167
Aminbazar | 235 | 0.375 | 229 | 0.041667 | Kaliakoir | 235 | 0.625 | 227 | 0.041667
Tongi | 234 | 0.33333 | 226 | 0.75 | GPH | 221 | 0.5 | 213 | 0.20833
Comilla (N) | 237 | 0.375 | 231 | 0.041667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 0.33333 | 131 | 0.041667 | Hathazari | 134 | 0.54167 | 128 | 0
Munsiganj | 133 | 0.75 | 129 | 0.041667 | Khulshi | 131 | 0.54167 | 124 | 0.041667
Sonargaon | 133 | 0.41667 | 130 | 0.041667 | Halishahar | 132 | 0.54167 | 125 | 0.041667
Shyampur | 138 | 0.375 | 133 | 0.041667 | Baraulia | 132 | 0.5 | 126 | 0.041667
Bhulta | 129 | 0.29167 | 127 | 0.041667 | Sikalbaha | 132 | 0.54167 | 126 | 0.041667
Madanganj | 134 | 0.375 | 130 | 0.79167 | Dohazari | 130 | 0.58333 | 121 | 0.041667
Shitalakhya | 136 | 0.375 | 131 | 0.041667 | Cox'sbazar | 125 | 0.54167 | 112 | 0.91667
Rahim steal | 134 | 0.29167 | 131 | 0.041667 | Chandraghona | 133 | 0.5 | 126 | 0.041667
Matuail | 134 | 0.375 | 131 | 0.041667 | Kaptai | 134 | 0.54167 | 128 | 0.041667
Ghorasal | 145 | 0.29167 | 142 | 0.041667 | A. Khaer Stl. | 130 | 0.54167 | 125 | 0.125
Narsinghdi | 134 | 0.33333 | 127 | 0.041667 | Bakulia | 130 | 0.5 | 124 | 0
Haripur (SBU) | 134 | 0.33333 | 131 | 0 | Julda | 130 | 0.54167 | 125 | 0.083333
Ullon | 134 | 0.25 | 131 | 0.041667 | TK Chemical | 131 | 0.5 | 126 | 0.16667
Hasnabad | 135 | 7::00 | 130 | 0.041667 | Modern Steel | 130 | 0.58333 | 126 | 0.041667
Magbazar | 137 | 0.29167 | 132 | 0.041667 | Shahmirpur | 130 | 0.5 | 125 | 0.16667
Maniknagar | 137 | 0.375 | 135 | 0.041667 | Khagrachhari | 132 | 0.5 | 125 | 0.041667
Bangabhaban | 137 | 0.375 | 135 | 0.041667 | Matarbari | 124 | 0.375 | 113 | 0.95833
Narinda | 137 | 0.375 | 135 | 0.041667 | Baroiar Hat | 130 | 0.5 | 124 | 18:30
Dhanmondi | 134 | 0.25 | 131 | 0.041667 | Rangamati | 133 | 0.54167 | 126 | 1:00
Lalbag | 136 | 0.375 | 132 | 0.041667 | Goalpara | 135 | 0.75 | 124 | 0.625
Madartek | 134 | 0.29167 | 131 | 0.041667 | Central s/s | 133 | 0.20833 | 125 | 0.5
Dhaka University |  |  |  |  | Noapara | 132 | 0.91667 | 121 | 0.77083
Mirpur | 134 | 0.5 | 131 | 0.041667 | Jessore | 127 | 0.16667 | 116 | 0.5
Kalyanpur | 135 | 0.375 | 131 | 0.041667 | Benapol | 129 | 0.20833 | 116 | 0.54167
Gulshan | 134 | 0.375 | 130 | 0.041667 | Jhenida | 129 | 0.91667 | 112 | 0.8125
Uttara | 137 | 0.375 | 133 | 0.041667 | Bottail | 133 | 0.25 | 124 | 0.8125
Uttara New | 135 | 0.5 | 131 | 0.041667 | G.K Project | 139 | 0.75 | 134 | 0.79167
Kamrangirchar | 133 | 0.5 | 129 | 0.041667 | Faridpur | 137 | 0.20833 | 127 | 0.041667
Savar | 134 | 0.5 | 130 | 0.041667 | Madaripur | 139 | 0.29167 | 130 | 0.875
Bhasantec | 133 | 0.5 | 129 | 0.041667 | Sariatpur | 138 | 0.25 | 129 | 0.041667
Agargaon | 134 | 0.5 | 131 | 0.041667 | Gopalganj | 141 | 0.25 | 129 | 0.041667
Satmosjid | 133 | 0.5 | 130 | 0.041667 | Bagerhat | 132 | 0.75 | 120 | 0.5
Tongi | 141 | 0.33333 | 136 | 0.75 | Mongla | 130 | 0.125 | 120 | 0.625
Kabirpur | 136 | 0.41667 | 131 | 0.875 | Satkhira | 134 | 0.25 | 122 | 0.625
Basundhara | 134 | 0.375 | 131 | 0.83333 | Gallamari | 136 | 0.25 | 125 | 0.77083
Manikganj | 133 | 0.66667 | 127 | 0.083333 | Magura | 126 | 0.91667 | 111 | 0.79167
Joydevpur | 145 | 0.70833 | 140 | 0.875 | Norail | 126 | 0.95833 | 107 | 0.79167
New Tongi | 140 | 0.41667 | 134 | 0.041667 | Chuadanga | 129 | 0.91667 | 103 | 0.79167
Kodda | 135 | 0.75 | 129 | 0.041667 | Barisal(N) | 138 | 0.25 | 130 | 0.041667
Dhamrai | 135 | 0.41667 | 130 | 0.875 | Barisal (S) | 137 | 0.70833 | 128 | 0.041667
Rajendrapur | 139 | 0.375 | 128 | 0.8125 | Patuakhali | 134 | 0.25 | 124 | 0.8125
Valuka | 134 | 0.29167 | 127 | 0.875 | Bhandaria | 135 | 0.29167 | 125 | 0.041667
Tangail | 138 | 0.41667 | 130 | 0.875 | Ishurdi | 137 | 0.20833 | 132 | 0.83333
Mymensing | 136 | 0.29167 | 126 | 0.875 | Ruppur Paromanobik | 136 | 0.75 | 130 | 0.83333
Kishorganj | 137 | 0.375 | 130 | 0.70833 | Natore | 134 | 0.16667 | 128 | 0.875
Netrokona | 133 | 0.5 | 124 | 0.75 | Bogra | 135 | 0.25 | 130 | 0.83333
Jamalpur | 135 | 0.45833 | 126 | 0.875 | Noagaon | 132 | 0.25 | 125 | 21:0
Sherpur | 134 | 0.5 | 122 | 0.875 | Rajshahi | 132 | 0.77083 | 125 | 0.875
Srimongal | 142 | 0.45833 | 138 | 0.041667 | Rajshahi New | 132 | 0.77083 | 123 | 0.83333
Shahjibazar | 141 | 0.33333 | 134 | 1:00 | C.Nawabganj | 131 | 0.77083 | 123 | 0.29167
Fenchuganj | 140 | 0.33333 | 135 | 0.041667 | Amnura | 131 | 0.77083 | 123 | 0.29167
Khulawara | 139 | 0.33333 | 134 | 0.041667 | Pabna | 134 | 0.75 | 129 | 0.83333
Sylhet | 138 | 0.16667 | 135 | 0.041667 | Shahjadpur | 140 | 18:0 | 136 | 0.83333
Chatak | 138 | 0.29167 | 134 | 0.041667 | Serajganj | 135 | 0.20833 | 130 | 0.83333
Sunamganj | 138 | 0.29167 | 133 | 0.041667 | Niyamatpur | 132 | 0.25 | 123 | 0.83333
Biani Bazar | 139 | 0.29167 | 133 | 0.041667 | Joypurhat | 134 | 0.25 | 126 | 0.83333
Comilla(s) | 133 | 0.5 | 126 | 0.77083 | Sherpur(Bogura) | 136 | 0.20833 | 131 | 0.875
Comilla(n) | 137 | 0.54167 | 130 | 0.95833 | Mohastangor | 135 | 0.25 | 129 | 0.83333
Chandpur | 130 | 0.33333 | 125 | 0.91667 | Rangpur | 135 | 0.25 | 126 | 0.79167
Feni | 129 | 0.54167 | 125 | 0.91667 | Lalmonirhat | 132 | 0.25 | 120 | 0.83333
Chowmuhani | 129 | 0.625 | 121 | 0.54167 | Saidpur | 134 | 0.20833 | 123 | 0.79167
Ashuganj | 142 | 0.33333 | 136 | 0.041667 | Purbasadipur | 132 | 0.20833 | 118 | 0.79167
Daudkandi | 133 | 0.45833 | 127 | 0.83333 | Thakurgaon | 131 | 0.20833 | 118 | 0.83333
B.Baria | 138 | 0.45833 | 135 | 0.77083 | Palashbari | 135 | 0.25 | 123 | 0.83333
Ramganj | 121 | 0.75 | 116 | 0.83333 | Barapukuria | 132 | 0.25 | 125 | 0.83333
Chaddagram | 132 | 0.5 | 127 | 0.79167 | Panchagar | 131 | 0.25 | 115 | 0.83333
PHP | 127 | 0.33333 | 121 | 0.77083 | Joldhaka | 133 | 0.16667 | 114 | 0.8125
Madanhat | 135 | 0.5 | 128 | 0.041667 | Kurigram | 135 | 0.25 | 121 | 0.8125

## L-Curve
Date | 2020-04-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 395 | 4118 | 2760 | 6878 |  |  |  | QF-LDC-12
0:30 | 347.5 | 4331 | 2866 | 7197 | Date: | 2020-04-17
1:00 | 300 | 4544 | 2972 | 7516
1:30 | 214.5 | 4493.5 | 2771.5 | 7265
2:00 | 129 | 4443 | 2571 | 7014
2:30 | 147 | 4332 | 2491.5 | 6823.5 | [5 empty] | Gen. at Eve. Peak | 8830 | 8830 MW (19:30 )
3:00 | 165 | 4221 | 2412 | 6633 | [6 empty] | 19:30
3:30 | 163.5 | 4200 | 2337 | 6537 | [5 empty] | Gen. at Day Peak | 5671.3 | 5671.3 MW (12:00 )
4:00 | 162 | 4179 | 2262 | 6441 | [6 empty] | 12:00
4:30 | 150 | 4177 | 2252.5 | 6429.5 | [5 empty] | Highest Generation | 8830
5:00 | 138 | 4175 | 2243 | 6418 | [6 empty] | 19:30
5:30 | 129.5 | 4051.95 | 2172.5 | 6224.45
6:00 | 121 | 3928.9 | 2102 | 6030.9
6:30 | 105.5 | 3887.8 | 2072.05 | 5959.85
7:00 | 90 | 3846.7 | 2042.1 | 5888.8
7:30 | 112 | 3794.9 | 2000.95 | 5795.85
8:00 | 134 | 3743.1 | 1959.8 | 5702.9
8:30 | 144.5 | 3681.4 | 1949.3 | 5630.7
9:00 | 155 | 3619.7 | 1938.8 | 5558.5
9:30 | 119.5 | 3569.15 | 1969.2 | 5538.35
10:00 | 84 | 3518.6 | 1999.6 | 5518.2
10:30 | 66.5 | 3481 | 2050.1 | 5531.1
11:00 | 49 | 3443.4 | 2100.6 | 5544
11:30 | 91 | 3500.25 | 2107.4 | 5607.65
12:00 | 133 | 3557.1 | 2114.2 | 5671.3
12:30 | 160 | 3693 | 2164.2 | 5857.2
13:00 | 187 | 3828.9 | 2214.2 | 6043.1
13:30 | 161.5 | 3913.95 | 2251.05 | 6165
14:00 | 136 | 3999 | 2287.9 | 6286.9
14:30 | 128 | 3997.2 | 2301.3 | 6298.5
15:00 | 120 | 3995.4 | 2314.7 | 6310.1
15:30 | 101 | 3986.35 | 2264.45 | 6250.8
16:00 | 82 | 3977.3 | 2214.2 | 6191.5
16:30 | 109.5 | 3956.2 | 2110 | 6066.2
17:00 | 137 | 3935.1 | 2005.8 | 5940.9
17:30 | 123.5 | 3944.05 | 1994.5 | 5938.55
18:00 | 110 | 3953 | 1983.2 | 5936.2
18:30 | 135 | 4501 | 2679.1 | 7180.1
19:00 | 160 | 5049 | 3375 | 8424
19:30 | 130 | 5249 | 3581 | 8830
20:00 | 182 | 5160 | 3594 | 8754 |  |  |  | Executive Engineer
20:30 | 206.5 | 5127 | 3591 | 8718 |  |  |  | Network Operation Division
21:00 | 231 | 5094 | 3588 | 8682
21:30 | 319.5 | 4904 | 3455 | 8359
22:00 | 408 | 4714 | 3322 | 8036 |  |  |  |  | Page 6 of 7
22:30 | 484 | 4468 | 3163 | 7631
23:00 | 560 | 4222 | 3004 | 7226
23:30 | 477.5 | 4170 | 2882 | 7052
24:00 | 395 | 4118 | 2760 | 6878
8830 MW (19:30 )
5671.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-04-17 |  | Energy | 161412276
[10 empty] | 2020-04-17 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3789 | 829 | 1291 | 327 | 542 | 35 | 0 | 0 | 120
0:30 | 4032.5 | 653 | 1274.5 | 397.5 | 677 | 35 | 36 | 0 | 119 | Date: | 2020-04-17
1:00 | 4276 | 477 | 1258 | 468 | 812 | 35 | 72 | 0 | 118
1:30 | 4248.5 | 341 | 1275 | 399.5 | 788.5 | 35.5 | 61 | 0 | 116 | [7 empty] | Total Energy | 161.4123 | Total Energy Gen 161.412 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.412 MKWHr
2:00 | 4221 | 205 | 1292 | 331 | 765 | 36 | 50 | 0 | 114 | [7 empty] | Energy not Served | 0
2:30 | 4214.5 | 205.5 | 1231.5 | 286 | 710 | 36 | 25 | 0 | 115 | [7 empty] | Energy Requirement | 161.4123
3:00 | 4208 | 206 | 1171 | 241 | 655 | 36 | 0 | 0 | 116
3:30 | 4179 | 205.5 | 1161 | 231 | 610.5 | 36 | 0 | 0 | 114 | [6 empty] | Shortage
4:00 | 4150 | 205 | 1151 | 221 | 566 | 36 | 0 | 0 | 112
4:30 | 4163 | 205 | 1147 | 213.5 | 554 | 36 | 0 | 0 | 111
5:00 | 4176 | 205 | 1143 | 206 | 542 | 36 | 0 | 0 | 110
5:30 | 4025.5 | 205.5 | 1114 | 188.5 | 541.5 | 36.5 | 6.5 | 0 | 106
6:00 | 3875 | 206 | 1085 | 171 | 541 | 37 | 13 | 0 | 102
6:30 | 3843 | 205.5 | 1062.5 | 166 | 522 | 37 | 21 | 0 | 100 |  |  |  |  | Coal
7:00 | 3811 | 205 | 1040 | 161 | 503 | 37 | 29 | 0 | 98
7:30 | 3757.5 | 206 | 1018.5 | 152 | 487.5 | 37.5 | 29 | 0 | 99 |  |  |  | Oil |  |  |  | ,
8:00 | 3704 | 207 | 997 | 143 | 472 | 38 | 29 | 0 | 100
8:30 | 3638 | 206.5 | 1000.5 | 141.5 | 471.5 | 37.5 | 29 | 0 | 93
9:00 | 3572 | 206 | 1004 | 140 | 471 | 37 | 29 | 0 | 86
9:30 | 3546.5 | 255.5 | 950.5 | 162.5 | 461.5 | 37 | 29 | 0 | 78
10:00 | 3521 | 305 | 897 | 185 | 452 | 37 | 29 | 0 | 70
10:30 | 3523 | 329 | 883.5 | 192.5 | 451.5 | 37 | 22 | 0 | 70
11:00 | 3525 | 353 | 870 | 200 | 451 | 37 | 15 | 0 | 70
11:30 | 3557.5 | 353 | 912 | 200 | 451.5 | 36.5 | 15 | 0 | 66
12:00 | 3590 | 353 | 954 | 200 | 452 | 36 | 15 | 0 | 62
12:30 | 3644.5 | 353 | 1055.5 | 225 | 451.5 | 35.5 | 15 | 0 | 64
13:00 | 3699 | 353 | 1157 | 250 | 451 | 35 | 15 | 0 | 66
13:30 | 3699 | 353 | 1157 | 250 | 451 | 35 | 15 | 0 | 66
14:00 | 3699 | 353 | 1157 | 250 | 451 | 35 | 15 | 0 | 66
14:30 | 3731 | 348.5 | 1251.5 | 253 | 451.5 | 35.5 | 15 | 0 | 73
15:00 | 3763 | 344 | 1346 | 256 | 452 | 36 | 15 | 0 | 80
15:30 | 3754 | 343.5 | 1303.5 | 256 | 452 | 36 | 7.5 | 0 | 84
16:00 | 3745 | 343 | 1261 | 256 | 452 | 36 | 0 | 0 | 88
16:30 | 3691 | 343.5 | 1235 | 215 | 451.5 | 36 | 0 | 0 | 88
17:00 | 3637 | 344 | 1209 | 174 | 451 | 36 | 0 | 0 | 88
17:30 | 3630 | 344 | 1199 | 176 | 461 | 36.5 | 0 | 0 | 91
18:00 | 3623 | 344 | 1189 | 178 | 471 | 37 | 0 | 0 | 94
18:30 | 4022.5 | 636.5 | 1404.5 | 388.5 | 514 | 37 | 67 | 0 | 110
19:00 | 4422 | 929 | 1620 | 599 | 557 | 37 | 134 | 0 | 126
19:30 | 4533 | 928 | 1636 | 833 | 603 | 37 | 134 | 0 | 126
20:00 | 4462 | 928 | 1674 | 788 | 638 | 37 | 99 | 0 | 128
20:30 | 4481.5 | 926 | 1679.5 | 749 | 641 | 37 | 79 | 0 | 125
21:00 | 4501 | 924 | 1685 | 710 | 644 | 37 | 59 | 0 | 122
21:30 | 4417 | 924 | 1555 | 603.5 | 644 | 36.5 | 55 | 0 | 124
22:00 | 4333 | 924 | 1425 | 497 | 644 | 36 | 51 | 0 | 126
22:30 | 4108.5 | 924.5 | 1390 | 412 | 610.5 | 36 | 25.5 | 0 | 124
23:00 | 3884 | 925 | 1355 | 327 | 577 | 36 | 0 | 0 | 122
23:30 | 3836.5 | 877 | 1323 | 327 | 559.5 | 35.5 | 0 | 0 | 121 | Max Temp. in Dhaka |  | 33.5° C
24:00 | 3789 | 829 | 1291 | 327 | 542 | 35 | 0 | 0 | 120
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 161.412 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.412 MKWHr
Note on W13: Author:

## Generation
g | 2020-04-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 36 | 36 | 36 | 36 | 37 | 37 | 38 | 37 | 37 | 37 | 36 | 35 | 35 | 36 | 36 | 36 | 37 |  | 37 | 37 | 37 | 37 | 36 | 36 | 35 | 802080
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 95 | 100 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 1 | 5 | 9 | 16 | 16 | 16 | 0 | 76075
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.7 | 4.3 | 9 | 8.1 | 13.1 | 17.2 |  | 9.3 | 5 | 11 | 6.7 | [10 empty] | 98520
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 210 | 211 | 211 | 210 | 210 | 210 | 210 | 210 | 210 | 211 |  | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 5165061
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 140 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 2446394
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 34 | 34 | 34 | 17 | 17 |  |  | 108931
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 98 | 100 | 100 | 100 | 100 | 93 | 68 | 70 | 125 | 78 | 105 | 110 | 110 | 110 | 77 | 75 | 75 | 77 |  | 115 | 120 | 75 | 78 | 72 | 72 | 72 | 2388000
17 | Siddhirganj 335 MW CCPP | 170 | 170 | 170 | 170 | 170 | 130 | 130 | 130 | 150 | 150 | 150 | 180 | 180 | 180 | 200 | 200 | 140 | 140 |  | 228 | 230 | 200 | 200 | 140 | 140 | 140 | 4233675
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 368000
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 496000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 210 |  | 280 | 280 | 280 | 280 | 280 | 210 | 210 | 5282209
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 110 | 135 | 100 | 100 | 100 | 80 | 80 | 2026630
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 30 | 42 | 42 | 35 | 5 | 5 | 434376
33 | Ashuganj 225 MW CCPP | 172 | 161 | 170 | 166 | 169 | 158 | 159 | 151 | 150 | 151 | 151 | 152 | 190 | 180 | 161 | 161 | 181 | 183 |  | 179 | 179 | 179 | 179 | 179 | 140 | 140 | 4014000
34 | Ashuganj 450 MW CCPP(South) | 280 | 270 | 275 | 270 | 275 | 250 | 250 | 250 | 220 | 220 | 220 | 220 | 250 | 250 | 250 | 250 | 250 | 250 |  | 260 | 260 | 260 | 265 | 265 | 250 | 235 | 6178000
| Ashuganj 450 MW CCPP(North) | 330 | 320 | 330 | 320 | 330 | 275 | 275 | 275 | 275 | 310 | 295 | 275 | 275 | 310 | 275 | 275 | 300 | 330 |  | 310 | 310 | 310 | 310 | 310 | 260 | 230 | 7441000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 20 | 5 | 5 | 5 | 5 | 5 | 151200
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 82 | 79 | 84 | 86 | 82 | 80 | 91 | 1677190
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 339 | 339 | 335 | 335 | 334 | 333 | 323 | 289 | 268 | 266 | 266 | 266 | 266 | 290 | 303 | 286 | 265 |  | 295 | 334 | 335 | 336 | 335 | 305 | 264 | 7425020
40 | Meghnaghat 450 MW CCPP(MPL) | [10 empty] | 25 | 25 | 150 | 200 | 225 | 225 | 225 | 160 |  | 225 | 225 | 225 | 225 | 225 | 190 | 190 | 2228500
41 | Haripur 360MW CCPP(HPL) | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 233 | 233 | 233 | 234 | 233 | 233 | 233 | 263 | 263 | 263 | 263 |  | 303 | 303 | 304 | 302 | 252 | 252 | 252 | 6093000
42 | RPCL 210MW CCPP | 209 | 213 | 213 | 213 | 213 | 214 | 216 | 187 | 148 | 148 | 148 | 148 | 147 | 148 | 146 | 147 | 147 | 149 |  | 212 | 212 | 212 | 212 | 213 | 216 | 215 | 4338080
43
44 | Fenchugonj CCPP Phase-1 | 69 | 69 | 68 | 68 | 68 | 70 | 68 | 68 | 68 | 70 | 50 | 50 | 50 | 51 | 41 | 41 | 41 | 46 |  | 52 | 55 | 55 | 86 | 86 | 87 | 86 | 1492000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 |  | 30 | 30 | 30 | 30 | 30 | 0 |  | 492000
46 | Shajibazar 330 MW CCPP | 289 | 282 | 286 | 285 | 285 | 281 | 282 | 279 | 280 | 264 | 261 | 255 | 253 | 266 | 253 | 255 | 262 | 265 |  | 252 | 254 | 254 | 251 | 256 | 253 | 253 | 6091000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 978048
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 74 | 74 | 78 | 78 | 5 | 5 | 5 | 381120
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 70 | 70 | 40 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 120 | 120 | 99 | 98 | 70 | 70 | 70 | 1523830
51 | Sylhet 20 MW GTPP | [19 empty] | 19 | 19 | 19 | 19 |  |  |  | 58000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [19 empty] | 10 | 10 | 9 | 10 |  |  |  | 32940
54 | Hobiganj 11MW PP Cofidence-E | [19 empty] | 8 | 8 | 8 | 8 | 8 |  |  | 29000
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 23 | 48 | 50 | 23 | 5 | 5 | 5 | 215400
56 | Shahjahanulla 25 MW PP | [19 empty] | 24 | 24 | 24 | 22 |  |  |  | 68472
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 310 | 305 | 310 | 305 | 290 | 275 | 270 | 280 | 230 | 175 | 220 | 270 | 305 | 300 | 300 | 290 | 300 |  | 300 | 260 | 280 | 290 | 270 | 270 | 285 | 6919500
58 | Nababganj 55 MW PP (Southern power ) | [20 empty] | 15 | 17 | 17 | 17 | 17 | 17 | 86327
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 451152
61 | Narshingdi 22 MW PP (Doreen) | [21 empty] | 19 | 19 | 19 |  |  | 93276
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | [11 empty] | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 247536
63 | Impoprt (Tripura) | 118 | 114 | 116 | 112 | 110 | 102 | 98 | 100 | 86 | 70 | 70 | 62 | 66 | 74 | 80 | 88 | 88 | 94 |  | 126 | 126 | 128 | 122 | 126 | 122 | 120 | 2454720
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 17 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 15 | 42 | 42 | 1027680
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 464976
66 | Feni 11 MW PP (Doreen) | [19 empty] | 5 | 5 | 8 |  | 11 |  |  | 25740
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 558100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 15 | 15 |  | 10 | 10 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 431390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 8 | 11 | 11 | 11 | 11 | 8 | 183060
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 651400
72 | Rupganj 33 MW PP(Summit) | 8 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 8 | 8 | 8 | 20 | 20 | 20 | 20 | 20 | 20 | 17 |  | 17 | 20 | 20 | 25 | 25 | 25 | 24 | 504500
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | [15 empty] | 22 |  | 33 | 33 | 32 | 34 | 34 | 12 | 12 | 193409
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 113 | 46 | 46 | 26 | 26 | 26 | 26 | 8 | [11 empty] | 55 | 113 | 113 | 113 | 113 | 94 | 75 | 926520
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [19 empty] | 3 | 8 | 8 |  |  |  |  | 12480
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [5 empty] | 0.2 | 0.4 | 2.4 | 3.7 | 4.4 | 0.9 | 0 | 0.3 | 2.2 | 1.4 | 1 | 0.7 | [9 empty] | 16804
| Jodiac Power | [26 empty] | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 15 | 15 | 15 | 15 |  | 16 | 18 | 30 | 30 | 30 | 15 | 15 | 438
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 135 | 130 | 130 | 130 | 135 | 120 | 120 | 120 | 125 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 120 | 120 | 120 | 120 | 120 | 125 | 125 | 3024291
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | 50 | 50 | [24 empty] | 109760
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | [17 empty] | 15 | 28 | 28 | 28 | 5 | 5 | 5 | 150624
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 9 | 20 | 25 | 20 | 8 | 8 | 8 | 261004
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 100 | 100 | 140 | 140 | 140 | 140 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2903645
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0.7 | 0.9 | 1.1 | 0.3 | 2.1 | 2.3 | 1.8 | 1 | 0.6 | 0.4 | [9 empty] | 9950
103 | Kamalaghat 54 MW PP(Banco Energy) | [26 empty] | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 40 | 40 | [17 empty] | 48 | 70 | 70 | 32 | 32 |  |  | 336000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [26 empty] | 0
115 | Juldah 100 MW PP Unit-3 (Acorn) | [26 empty] | 0
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | 16 | [18 empty] | 50 | 32 | 16 |  |  |  |  | 102873
| Juldah unit-2 | 100 | 100 | 50 | 50 | 30 | 10 | [11 empty] | 4 |  | 70 | 70 | 50 | 50 | 30 | 10 | 10 | 616320
120 | Eastern Zone Total | 4544 | 4443 | 4221 | 4179 | 4175 | 3928.9 | 3846.7 | 3743.1 | 3619.7 | 3518.6 | 3443.4 | 3557.1 | 3828.9 | 3999 | 3995.4 | 3977.3 | 3935.1 | 3953 | 0 | 5049 | 5249 | 5160 | 5094 | 4714 | 4222 | 4118 | 100397226
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | [11 empty] | 10 | 16 | 16 | 16 |  |  |  | 87 | 115 | 115 | 115 | 89 |  |  | 555840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 24 | 23 | 24 | [19 empty] | 23 | 24 | 24 | 23 | 161100
| Bhola 225 MW CCPP | 179 | 179 | 179 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 |  | 173 | 167 | 178 | 178 | 179 | 178 | 179 | 3984626
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 25 | 24 | 22 | 18 | 15 | 15 | 15 | 17 | 18 | 19 | 17 | 22 | 20 | 19 | 13 | 26 |  | 27 | 29 | 30 | 31 | 31 | 30 | 28 | 510552
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 19 | 100 | 98 | 100 |  |  |  | 279360
142 | Noapara 40 MW PP (Khanjahan Ali) | [12 empty] | 40 | 40 | 40 | 40 | 0 | 0 |  | 40 | 32 | 32 | 32 |  |  |  | 246000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 477 | 205 | 206 | 205 | 205 | 206 | 205 | 207 | 206 | 305 | 353 | 353 | 353 | 353 | 344 | 343 | 344 | 344 |  | 929 | 928 | 928 | 924 | 924 | 925 | 829 | 10624727
147 | Bheramara 410 MW CCPP | 340 | 330 | 340 | 330 | 340 | 240 | 235 | 230 | 230 | 230 | 230 | 230 | 230 | 265 | 265 | 265 | 235 | 220 |  | 335 | 330 | 330 | 335 | 330 | 290 | 290 | 6914304
148 | Payra 1320 MW | 571 | 524 | 414 | 325 | 300 | 300 | 261 | 230 | 230 | 231 | 230 | 231 | 230 | 231 | 231 | 232 | 230 | 249 |  | 335 | 361 | 396 | 402 | 402 | 335 | 300 | 7592000
149
150 | Barapukuria TPP Unit-1 | 71 | 71 | 71 | 71 | 72 | 71 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 71 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1706181
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 3940500
153 | Baghabari 71 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 60 | 50 | 65 | 65 | 70 | 70 | 70 | 70 | 40 | 40 |  | 70 | 70 | 70 | 70 | 70 | 40 | 40 | 1540000
156 | Baghabari 100 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 50 | 50 |  | 65 | 65 | 65 | 65 | 65 | 65 | 50 | 1385000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 170 | 180 | 200 | 214 | 214 | 180 | 180 | 140 |  | 160 | 180 | 180 | 180 | 150 | 150 | 150 | 4200245
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 162 | 162 | 161 | 160 | 145 | 140 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 150 | 145 | 145 | 146 | 145 | 135 | 141 | 3715845
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 173 | 171 | 171 | 171 | 170 | 171 | 171 | 144 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 154 | 178 | 178 | 178 | 175 | 130 | 130 | 3935400
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 369 | 370 | 370 | 370 | 369 | 330 | 303 | 286 | 286 | 245 | 246 | 245 | 275 | 303 | 326 | 282 | 246 | 246 |  | 390 | 374 | 396 | 404 | 376 | 374 | 310 | 7749327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 17 | 17 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 17 | 17 | 17 | 17 | 17 | 17 | 5 | 205200
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 120780
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  |  |  | 10 | 5 | 11 | 11 | 11 | 11 | 5 | 188316
165 | Amnura 50 MW PP(Sinha) | [9 empty] | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 24 | 24 |  | 42 | 50 | 50 | 50 | 50 | 50 | 30 | 647070
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 22 |  |  |  |  | 13 | 29 | 29 | 29 | 29 | 15 | 15 | 15 | [13 empty] | 206748
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [6 empty] | 10560
170 | Chapainawabganj 100 MW Peaking PP | 50 | 50 | [17 empty] | 100 | 100 | 65 | 42 | 34 |  |  | 346090
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 30 | 50 | 35 | 35 |  |  |  | 142080
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [14 empty] | 15 | [11 empty] | 11000
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 10 | 35 | 25 |  |  |  |  | 55680
177 | Sympa Solar Power 8MW | [6 empty] | 0.1 | 0.8 | 0.8 | 3.6 | 4.6 | 7.2 | 5.2 | 4.9 | 4.7 | 2.2 | 0.8 | 0.2 | [8 empty] | 40519
178
178