## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March' 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | March 2020 |  | February 2020 |  | March 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10790 | 18/03/20 | 9729 | 23/02/20 | 10933 | 30/03/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 5676.1 | 03/03/20 | 5180 | 08/02/20 | 4710 | 02/03/19 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10790 | 18/03/20 | 9729 | 23/02/20 | 10933 | 30/03/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9428.9 | 18/03/20 | 8304.1 | 29/02/20 | 9132.3 | 31/03/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10790 | 18/03/20 | 9729 | 23/02/20 | 10933 | 30/03/19 | 12893 | 29/05/19
|  |  | 19:30 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9878.5806 |  | 9075.8966 |  | 9524.1613 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 8156.329 |  | 7583.6138 |  | 7899.1097 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 943 | 23/03/2020 | 882 | 29/02/20 | 956 | 27/03/19 | 956 | 27/3/2019
|  |  | 20:00 |  | 21:30 |  | 19:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 152 | 15/03/2020 | 124 | 23/02/2020 | 172 | 25/03/19 | 194 | 12/06/19
|  |  | 18:30 |  | 18:30 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3442.7368 |  | 3025.8906 |  | 3315.9631 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 103.8241 |  | 96.5529 |  | 120.7397
22 | Net Generation of BPDB (MKWH) | 3338.9126 |  | 2929.3377 |  | 3195.2234
23 | Net Generation of IPP & RPCL (MKWH) | 1608.1902 |  | 1337.8443 |  | 1441.9411
24 | Net Generation of REB (MKWH) | 135.7736 |  | 120.8486 |  | 138.6817
24 | Net Generation of Rental Power Plant (MKWH) | 297.8023 |  | 239.875 |  | 370.9007
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5380.6788 |  | 4627.9057 |  | 5146.7469 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 4372.4084 |  | 3767.6127 |  | 4289.7961 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 137.8528 |  | 105.9214 |  | 118.3913 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 556.2721 |  | 474.6048 |  | 676.8041 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 49.3088 |  | 46.1171 |  | 52.3268 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 6.9723 |  | 5.2287 |  | 3.9096 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 361.6886 |  | 324.9738 |  | 126.2587 |  | 243.72 | Sept-18
32 | Enegry Import from India (HVDC & AC) (MKWH) | 453.512 |  | 350.9948 |  | 611.4663 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 73.9685 |  | 74.9544 |  | 72.2749 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10790 | 18/03/20 | 19:30
Generation Period
| Dhaka | MW | 3718
| Chattogram | MW | 1141
| Cumilla | MW | 900
| Mymensingh | MW | 834
| Sylhet | MW | 369
a) | Total supply in East zone | MW | 6962
| Khulna | MW | 1231
| Barisal | MW | 272
| Rajshahi | MW | 1076
| Rangpur | MW | 652
b) | Total supply in West zone | MW | 3231
c) | Total supply in both zone ( a+b) | MW | 10193
Ref: | 27.21.0000.603.16.087.20.262 | Date: 20/04/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 20/03/20 | 18:30
| b) Ishurdi end | MW | 239 | 21/03/20 | 23:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 590 | 21/03/20 | 23:00
| b) Ishurdi end | MW | 241 | 20/03/20 | 18:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 28.08
| b) Ishurdi end | MKWH | 20.9175
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 20.2899
| b) Ishurdi end | MKWH | 27.2621
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 510 | 20/03/20 | 19:00
| b)Serajganj end | MW | 480 | 21/03/20 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 510 | 21/03/20 | 23:00
| b)Sirajganj end | MW | 480 | 20/03/20 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.348 | 03/03/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 3.31 | 03/03/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 52.626
| b)Sirajganj end | MKWH | 52.626
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 50.926
| b)Sirajganj end | MKWH | 50.926
30 | Transmission loss of EWI /NO-2 | % | 0.914
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 33 kV incoming CB | 2020-03-01 15:10 | 2020-03-01 16:22 | 1:12 | T | Tripped showing 33 kV feeder fault | 120 | 144 | Power interruption
Joydevpur | 132/33 kV Transformer-GT2 | 2020-03-03 04:47 | 2020-03-03 05:04 | 0:17 | T | Tripped showing dist. relay | 30 | 8.5 | Power interruption
Uttara | 132/33 kV Transformer-T2 | 2020-03-03 19:49 | 2020-03-11 14:43 | 186:54 | T | Tripped showing O/C relay at 33 kV end. | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T1 | 2020-03-20 23:10 | 2020-03-21 02:25 | 3:15 | T | Tripped showing 33 kV winding temperature high | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T3 | 2020-03-29 04:20 | 2020-03-29 05:20 | 1:00 | T | Tripped showing diff. & E/F relay | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-03-30 17:34 | 2020-03-30 18:40 | 0:23 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 193:01 |  | Unserved Energy: |  | 152.5
Dhaka (South) Grid Circle :
Hasnabad | 33 kV full Bus | 2020-03-06 03:47 | 2020-03-06 04:13 | 0:26 | T | Tripped showing feeder fault | 104 | 45.0667 | Power interruption
Shyampur(O) | 132/33 kV Transformers-T1 | 2020-03-12 18:13 | 2020-03-12 18:13 | 0:00 | T | Tripped showing operating differential relay at 33kV side
| 132/33 kV Transformers-T3 | 2020-03-12 18:13 | 2020-03-12 18:35 | 0:22 | T |  | 120 | 44 | Power interruption 18:13 to 18:35
| 132/33 kV Transformers-T4 | 2020-03-12 18:13 | 2020-03-12 19:02 | 0:49 | T
Narsinghdi | 132/33 kV Transformers-T2 | 2020-03-15 08:50 | 2020-03-15 15:23 | 0:23 | E/O | Due to Oil keakage | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformers-T2 | 2020-03-18 15:58 | 2020-03-18 17:12 | 1:14 | T | Tripped showing O/C relay at 33 kV end. | 0 | 0 | No interruption
Shyampur | 132/33 kV Transformer-T4 | 2020-03-22 18:12 | 2020-03-22 20:55 | 2:43 | T | Tripped showing O/C relay at 33 kV end. | 90 | 244.5 | Power interruption
Ullon | 132/33 kV all Transformers | 2020-03-27 06:45 | 2020-03-27 07:52 | 1:07 | T | Tripped showing O/C relay at 33 kV end. | 20 | 22.3333 | Power interruption
|  |  | Total : | 7:04 |  | Unserved Energy: |  | 355.9
Chattogram Grid Circle :
Khulshi | 132/33 kV Transformer-T1 | 2020-03-15 00:23 | 2020-03-23 13:38 | 205:15 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-03-27 19:52 | 2020-03-27 22:07 | 2:15 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Rangamati | 132/33 kV Transformer-T2 | 2020-03-31 22:49 | 2020-03-31 22:59 | 0:23 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2020-03-03 08:47 | 2020-03-03 09:06 | 0:19 | T | Tripped showing E/F relay at 33 kV side | 56 | 17.7333 | Power interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-03-04 03:48 | 2020-03-04 04:17 | 0:29 | T | Tripped showing buchholz relay | 15 | 7.25 | Power interruption
| 132/33 kV Transformer-T2 | 2020-03-04 15:13 | 2020-03-04 15:56 | 0:43 | T |  | 33 | 23.65 | Power interruption
Baroierhat | 132/33 kV Transformer-T1 | 2020-03-16 10:02 | 2020-03-16 11:16 | 1:14 | T | Tripped showing differential relay | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T5 | 2020-03-19 09:49 | 2020-03-19 16:48 | 0:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformers-T1 & T2 | 2020-03-20 05:49 | 2020-03-20 06:09 | 0:20 | T | Tripped showing Backup protection relay | 12 | 4 | Power interruption
Srimongal | 132/33 kV Transformer-T1 | 2020-03-23 10:01 | 2020-03-23 12:20 | 0:23 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2020-03-24 12:02 | 2020-03-24 12:09 | 0:07 | T | Tripped showing O/C & E/F relay | 34 | 3.9667 | Power interruption
|  |  | Total : | 3:58 |  | Unserved Energy: |  | 56.6
Khulna Grid Circle :
Barishal(N) | 132/33 kV Transformers-T1 & T2 | 2020-03-05 18:40 | 2020-03-05 18:57 | 0:17 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1 | 2020-03-14 05:53 | 2020-03-14 05:59 | 0:06 | T | Tripped showing O/C relay | 8 | 0.8 | Power interruption
| 132/33 kV Transformer-T4 | 2020-03-14 05:53 | 2020-03-14 06:01 | 0:08 | T | Tripped showing O/C & E/F relay at 33 kV side | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2020-03-16 15:22 | 2020-03-16 16:11 | 0:49 | E/O | Due to red-hot maintenance at 33 kV side | 22 | 17.9667 | Power interruption
Bhandaria | 132/33 kV Transformer-T2 | 2020-03-18 09:48 | 2020-03-18 11:09 | 1:21 | E/O | Due to Oil keakage at 33 kV side | 0 | 0 | No interruption
Patuakhali | 33 kV Bus | 2020-03-27 07:28 | 2020-03-27 07:28 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Gopalganj | 400/132 kV Transformer T2 | 2020-03-29 15:11 | 2020-03-29 15:46 | 0:35 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T2 | 2020-03-30 09:14 | 2020-03-30 09:22 | 0:08 | E/O | Due to red-hot maintenance | 22 | 2.9333 | Power interruption
Madaripur | 132/33 kV Transformer-T1 | 2020-03-30 10:40 | 2020-03-30 10:52 | 0:12 | T | Due to 33 kV feeder fault | 5 | 1 | Power interruption
|  |  | Total : | 3:36 |  | Unserved Energy: |  | 22.7
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC Pole-1 | 2020-02-03 09:41 | 2020-02-03 10:51 | 1:10 | T | Due to smoke detector activated | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T1 | 2020-03-12 12:37 | 2020-03-12 13:01 | 0:24 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Ishurdi | 230 kV breaker | 2020-03-24 07:18 | 2020-03-24 07:18 | 0:00 | E/O | Due to Oil leakage maintenance | 0 | 0 | No interruption
|  |  | Total : | 1:34 |  |  |  | 0
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Niyamatpur | 132/33 kV Transformer-T1 | 2020-03-06 08:15 | 2020-03-06 08:30 | 0:15 | T | Tripped showing E/F & O/. relay at 33 kV feeder fault | 27 | 6.75 | Power interruption
| 132/33 kV Transformer-T2 | 2020-03-06 08:36 | 2020-03-06 09:35 | 0:59 | E/O | Due to sparking at 33 kV feeder fault | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 with 33 kV Bus | 2020-03-13 06:52 | 2020-03-13 07:45 | 0:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2020-03-14 14:38 | 2020-03-14 14:42 | 0:04 | E/O | Due to 33 kV Godagari feeder fault | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-03-17 10:06 | 2020-03-17 13:31 | 3:25 | E/O | Due to bursting of L/A | 17 | 58.0833 | Power interruption
| 132/33 kV Transformer-T4 | 2020-03-17 09:58 | 2020-03-17 11:58 | 2:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2020-03-17 11:10 | 2020-03-17 11:40 | 0:30 | E/O | Due to Flashing of 33 kV feeder | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformers-T1 & T2 | 2020-03-19 03:53 | 2020-03-19 04:05 | 0:12 | E/O | Due to 33 kV feeder fault | 28 | 5.6 | Power interruption
Barapukuria | 230/132 kV Transformer-T1 | 2020-03-19 13:05 | 2020-03-19 19:14 | 6:09 | T | Tripped showing RET 521(self protection ) oil leavel low,OLTC at 230 kV side | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-03-25 04:16 | 2020-03-25 05:52 | 1:36 | T | Tripped showing diff. relay | 67 | 107.2 | Power interruption
| 132/33 kV Transformers-T1 | 2020-03-25 04:16 | 2020-03-25 05:20 | 1:04 | T | Tripped showing 33 kV Joypurhat feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-03-25 04:16 | 2020-03-25 06:10 | 1:54 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-25 21:30 | 2020-03-25 22:55 | 1:25 | E/O | Due to red-hot maintenance | 35 | 49.5833 | Power interruption
Palshbari | 132/33 kV Transformer-T4 | 2020-03-26 20:18 | 2020-03-26 22:01 | 1:43 | E/O | Due to red-hot maintenance at 33 kV side | 13 | 22.3167 | Power interruption
Amnura | 132/33 kV Transformer-T1 | 2020-03-28 20:17 | 2020-03-28 20:37 | 0:20 | T | Tripped showing O/C relay | 34 | 11.3333 | Power interruption
|  |  | Total : | 21:59 |  | Unserved Energy: |  | 260.8667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 231:12 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2020-03-04 19:30 | 2020-03-04 20:12 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Valuka 132 kV line-1 & 2 | 2020-03-04 20:11 | 2020-03-04 20:31 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2020-03-20 21:11 | 2020-03-21 00:07 | 2:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2020-03-20 21:11 | 2020-03-21 00:15 | 3:04 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-03-21 23:46 | 2020-03-21 23:54 | 0:08 | T | Tripped showing dist.CSW,CAT,CD & CE signal | 0 | 0 | No interruption
| Tongi-Kadda 300 MW 132 kV line | 2020-03-22 22:43 | 2020-03-23 00:24 | 1:41 | T | Tripped showing .E/F relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV line-1 | 2020-03-23 12:00 | 2020-03-23 12:02 | 0:02 | T | Tripped showing dist.(C-phae) relay | 308 | 10.2667 | Power interruption
| Tongi-Kabirpur 132 kV line-2 | 2020-03-23 12:08 | 2020-03-23 12:14 | 0:06 | T
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-03-24 12:38 | 2020-03-24 14:17 | 1:39 | E/O | Due to Emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 10:38 |  | Unserved Energy: |  | 10.2667
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2020-03-03 07:40 | 2020-03-03 08:24 | 0:44 | T | Tripped showing . O/C relay | 38 | 27.8667 | Power interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-03-04 12:32 | 2020-03-04 17:09 | 4:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ullon | Ullon-Siddirganj 132 kV line & Haripur-2 | 2020-03-04 20:51 | 2020-03-04 20:59 | 0:08 | T | Tripped showing dist. relay | 105 | 14 | Power interruption
Siddhirganj | Siddhirganj-EGCB P/S 132 kV line-1 | 2020-03-11 11:26 | 2020-03-11 12:02 | 0:36 | T | Tripped showing master protection . relay | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV line-2 | 2020-03-11 11:28 | 2020-03-11 12:31 | 1:03 | T | Tripped showing differential relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV line-1 | 2020-03-17 11:03 | 2020-03-17 14:55 | 3:52 | E/O | Due to air leakage | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2020-03-18 17:30 | 2020-03-18 18:22 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2020-03-21 12:56 | 2020-03-21 13:33 | 0:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 132 kV line | 2020-03-25 17:05 | 2020-03-25 21:17 | 4:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hasnabad-Lalbagh 132 kV line | 2020-03-26 10:48 | 2020-03-26 10:57 | 0:09 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Shyampur | Shyampur-Shyampur 230 kV line-1 | 2020-03-28 15:35 | 2020-03-28 16:47 | 1:12 | E/O | Due to air leakage | 0 | 0 | No interruption
| Shyampur-Shyampur 230 kV line-2 | 2020-03-28 16:51 | 2020-03-28 17:21 | 0:30 | E/O | Due to air leakage | 0 | 0 | No interruption
Siddhirganj | Siddirganj-Ullon 132 kV line-1 | 2020-03-31 07:34 | 2020-03-31 07:34 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Siddhirganj-Matuail 132 kV line | 2020-03-31 10:51 | 2020-03-31 10:58 | 0:07 | T | Tripped showing E/F. relay | 35 | 4.0833 | Power interruption
|  |  | Total : | 18:39 |  | Unserved Energy: |  | 45.95
Chattagram Grid Circle :
Halishahar | Halishahar-Juldah 132 kV line-1 & 2 | 2020-03-02 08:09 | 2020-03-02 08:28 | 0:19 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-T.K Chemical 132 kV line | 2020-03-22 14:14 | 2020-03-22 17:38 | 3:24 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV feeder | 2020-03-24 19:55 | 2020-03-24 20:43 | 0:48 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-T.K Chemical 132 kV line | 2020-03-30 00:19 | 2020-03-30 00:32 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 4:44 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV line-2 | 2020-03-03 02:09 | 2020-03-03 02:31 | 0:22 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2020-03-05 16:04 | 2020-03-05 16:17 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-03-05 12:46 | 2020-03-05 15:00 | 2:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj | Ashuganj-B.Baria Sirajganj 132 kV line-1 & 2 | 2020-03-22 00:30 | 2020-03-22 01:30 | 1:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-2 | 2020-03-22 00:30 | 2020-03-22 11:55 | 11:25 | E/O |  | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV line | 2020-03-22 02:32 | 2020-03-22 02:56 | 0:24 | T | Tripped showing O/C & E/F. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-2 | 2020-03-22 09:14 | 2020-03-22 10:30 | 1:16 | T | Tripped showing dist. relay | 10 | 12.6667 | Power interruption
Chandpur | Chandpur-Chandpur Desh P.P 132 kV line-1 | 2020-03-27 20:15 | 2020-03-27 20:50 | 0:35 | T | Tripped showing O/C & dist. relay | 0 | 0 | No interruption
| Chandpur-Chandpur Desh P.P 132 kV line-2 | 2020-03-27 20:15 | 2020-03-27 20:45 | 0:30 | T |  | 0 | 0 | No interruption
|  |  | Total : | 17:59 |  | Unserved Energy: |  | 12.6667
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line-1 | 2020-03-11 17:44 | 2020-03-11 17:58 | 0:14 | T | Tripped showing dist. relay | 33 | 7.7 | Power interruption 17:44 to 17:58
| Madaripur-Gopalganj 132 kV line-2 | 2020-03-11 17:44 | 2020-03-11 17:59 | 0:15 | T
| Madaripur-Gopalganj 132 kV line-3 | 2020-03-11 17:44 | 2020-03-11 18:02 | 0:18 | T
Barishal(N) | Barishal(N)-Madaripur 132 kV line-1 | 2020-03-11 17:45 | 2020-03-11 18:01 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barishal(N)-Madaripur 132 kV line-2 | 2020-03-11 17:45 | 2020-03-11 18:02 | 0:17 | T |  | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2020-03-14 18:59 | 2020-03-14 18:59 | 0:00 | E/O | Due to Isolator sparking | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-2 | 2020-03-15 08:02 | 2020-03-15 09:01 | 0:59 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali 132 kV line-1 | 2020-03-16 21:47 | 2020-03-16 21:59 | 0:12 | T | Tripped showing dist. relay | 56 | 11.2 | Power interruption
Gopalganj S/s | Gopalganj S/s-Gopalganj P/S 132 kV line | 2020-03-23 11:22 | 2020-03-23 13:14 | 1:52 | E/O | Due to PT bursting | 0 | 0 | No interruption
|  |  | Total : | 4:23 |  | Unserved Energy: |  | 18.9
HVDC Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura(New) | Bogura(New)-Sherpur 132 kV line-1 | 2020-03-13 13:09 | 2020-03-13 15:15 | 2:06 | T | Tripped showing dist.& lockout relay | 0 | 0 | No interruption
| Bogura(New)-Sherpur 132 kV line-1 | 2020-03-13 13:26 | 2020-03-13 13:45 | 0:19 | T | Tripped showing auto reclose & Lockout relay | 2790 | 883.5 | Power interruption
Naogaon | Naogaon-Satahar 132 kV line | 2020-03-13 13:10 | 2020-03-13 14:20 | 1:10 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2020-03-13 13:15 | 2020-03-13 23:11 | 9:56 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Natore | Natore-Rajshahi 132 kV line-1 | 2020-03-16 09:57 | 2020-03-16 11:08 | 1:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-03-17 02:10 | 2020-03-17 11:19 | 9:09 | T | Tripped showing dist. relay | 40 | 366 | Power interruption
Bogura(New) | Bogura(New)-Bogura(O) 12 kV line-1 & 2 | 2020-03-19 19:14 | 2020-03-19 19:31 | 0:17 | T | Tripped showing differential relay | 0 | 0 | No interruption
| Bogura -Mohastanghor 132 kV line-2 | 2020-03-20 08:36 | 2020-03-20 16:25 | 7:49 | E/O | Due to Oil leakage | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rajshahi 132 kV line | 2020-03-24 21:04 | 2020-03-24 22:28 | 1:24 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangaorth 132 kV line-1 | 2020-03-27 12:57 | 2020-03-27 13:04 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:28 |  | Unserved Energy: |  | 1249.5
Others :
Ullon | Ullon-Siddhirganj 132 kV line | 2020-03-03 07:41 | 2020-03-03 07:54 | 0:13 | T | Tripped showing dist. relay | 52 | 11.2667 | Power interruption
| Ullon-Haripur 132 kV line | 2020-03-03 07:42 | 2020-03-03 07:57 | 0:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:28 |  | Unserved Energy: |  | 11.2667
Total outage period of Sub-station Equipment : |  |  |  | 90:19 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kaliakoir | 400/132 kV Transformer-TR2 | 2020-03-01 08:21 | 2020-03-01 14:50 | 6:29 | S/O | Due to C/M work | 90 | 583.5 | Power interruption
Kadda | 132/33 kV Transformer-T5 | 2020-03-02 09:12 | 2020-03-02 12:54 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-03-04 07:51 | 2020-03-04 08:51 | 1:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-03-04 10:06 | 2020-03-04 10:36 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-04 08:53 | 2020-03-04 09:44 | 0:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-03-04 11:56 | 2020-03-04 15:47 | 3:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-04 15:50 | 2020-03-04 17:29 | 1:39 | S/O | Due to tan delta test | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-03-05 09:09 | 2020-03-05 12:11 | 3:02 | S/O | Due to tan delta test | 0 | 0 | No interruption
Kishoreganj | 132 kV full Bus along with outgoing 132 kV Ckt | 2020-03-06 07:08 | 2020-03-06 16:21 | 9:13 | S/O | Due to D/W work | 60 | 553 | Power interruption
Kaliakoir | 400/132 kV Transformer-T1 | 2020-03-06 08:22 | 2020-03-06 12:02 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 with 33 kV Bus | 2020-03-12 13:43 | 2020-03-12 14:51 | 1:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-03-13 07:30 | 2020-03-13 07:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132 kV Bus | 2020-03-13 06:04 | 2020-03-13 06:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T1,T2 & T3 | 2020-03-13 06:10 | 2020-03-13 06:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-13 08:50 | 2020-03-13 08:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2(50/75) |  | 2020-03-15 19:49 |  |  | New connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-03-16 08:28 | 2020-03-16 08:28 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-03-16 09:01 | 2020-03-16 10:38 | 1:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-03-16 10:39 | 2020-03-16 11:28 | 0:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-03-18 08:02 | 2020-03-18 08:30 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-03-19 10:43 | 2020-03-19 18:11 | 7:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2020-03-19 10:38 | 2020-03-19 16:37 | 5:59 | S/O | Due to replacement work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-03-21 13:34 | 2020-03-21 15:17 | 1:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T1 | 2020-03-21 08:15 | 2020-03-21 22:17 | 14:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2020-03-21 22:17 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T2 & 132 kV reserve Bus | 2020-03-22 11:15 | 2020-03-22 15:40 | 4:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT1 |  | 2020-03-23 17:31 |  | S/O | After maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2020-03-24 08:14 | 2020-03-24 10:54 | 2:40 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2020-03-24 11:34 | 2020-03-24 13:26 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-03-24 09:47 | 2020-03-24 11:47 | 2:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T3 | 2020-03-25 11:29 | 2020-03-25 14:28 | 2:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-2 |  | 2020-03-27 11:01 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 400/132 kV Transformer-T01 | 2020-03-27 11:07 | 2020-03-27 15:28 | 4:21 | S/O | Due to conductor demage | 0 | 0 | No interruption
|  |  | Total : | 85:28 |  | Unserved Energy: |  | 1136.5
Dhaka (South) Grid Circle :
Ghorashal | 230/132 kV Transformer-T01 | 2020-03-06 07:39 | 2020-03-06 07:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-03-06 07:12 | 2020-03-06 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2020-03-15 10:25 | 2020-03-15 13:55 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-21 08:28 | 2020-03-21 11:41 | 3:13 | S/O | Due to C/M work | 25 | 80.4167 | Power interruption
Hasnabad | 132/33 kV Transformer-T2 | 2020-03-25 08:30 | 2020-03-25 15:02 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 13:15 |  | Unserved Energy: |  | 80.4167
Chattogram Grid Circle :
Sikalbaha | 230 kV Bus coupler | 2020-03-01 08:47 | 2020-03-01 12:52 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132 kV main Bus -1 | 2020-03-02 07:17 | 2020-03-02 07:17 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus coupler | 2020-03-02 08:39 | 2020-03-02 13:04 | 4:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-1 | 2020-03-06 08:06 | 2020-03-06 08:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T1 | 2020-03-06 08:03 | 2020-03-06 12:13 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-2 | 2020-03-14 07:22 | 2020-03-14 07:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2020-03-14 09:43 | 2020-03-14 17:19 | 7:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Juldah | 132 kV main Bus |  | 2020-03-14 19:05 |  | S/O | After maintenance work | 0 | 0 | No interruption
Page: 2/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T2 | 2020-03-16 06:53 | 2020-03-16 08:57 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2020-03-20 08:18 | 2020-03-20 09:39 | 1:21 | S/O | Due to 33 kV DS problem | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1(New) |  | 2020-03-23 13:38 |  |  | Due to new connection | 0 | 0 | No interruption
|  |  | Total : | 23:41 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
B.Baria | 132/33 kV Transformer-T1 | 2020-03-03 07:53 | 2020-03-03 07:53 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chauddagram | 132/33 kV Transformer-T1 & associated Bus | 2020-03-03 10:55 | 2020-03-03 14:33 | 3:38 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1 | 2020-03-04 08:20 | 2020-03-04 12:20 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-04 12:36 | 2020-03-04 13:18 | 0:42 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-05 09:45 | 2020-03-05 22:46 | 13:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Chauddagram | 132/33 kV Transformer-T2 | 2020-03-05 09:10 | 2020-03-05 11:13 | 2:03 | S/O | Due to A/M work | 15 | 30.75 | Power interruption
B.Baria | 132/33 kV Transformer-T3 | 2020-03-05 09:20 | 2020-03-05 12:35 | 3:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-03-06 07:09 | 2020-03-06 17:46 | 10:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2020-03-06 11:27 | 2020-03-06 11:27 | 0:00 | S/O | Due to changing work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2020-03-12 07:05 | 2020-03-12 14:25 | 7:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 & 33 kV Bus-1 | 2020-03-20 08:25 | 2020-03-20 11:05 | 2:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Srimongal | 132/33 kV Transformer-25/41 MVAT-3 |  | 2020-03-22 18:40 |  | S/O | Due to replacment work | 0 | 0 | No interruption
|  |  | Total : | 47:16 |  | Unserved Energy : |  | 30.75
Khulna Grid Circle :
Satkhira | 132/33 kV Transformer-T2 | 2020-03-02 07:40 | 2020-03-02 09:30 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-GT2 |  | 2020-03-03 09:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
Madaripur | 132 kV bus-A | 2020-03-04 11:07 | 2020-03-04 12:15 | 1:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformers-T3 & T4 | 2020-03-11 08:57 | 2020-03-11 17:10 | 8:13 | S/O | Due to D/W work | 17 | 139.6833 | Power interruption
Madaripur | 132/33 kV Transformer-T1 | 2020-03-11 13:08 | 2020-03-11 14:27 | 1:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-03-11 14:40 | 2020-03-11 16:30 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2020-03-13 18:10 | 2020-03-13 19:24 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T6 | 2020-03-13 22:19 | 2020-03-14 12:34 | 14:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T2 | 2020-03-14 07:53 | 2020-03-14 07:53 | 0:00 | S/O | Due to D/W work by PBS | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformers-T1 & T2 | 2020-03-14 10:38 | 2020-03-14 12:18 | 1:40 |  |  | 0 | 0 | No interruption
Bagerhat | 132 kV main Bus | 2020-03-15 07:02 | 2020-03-15 08:55 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | 132 kV Bus-A | 2020-03-15 12:00 | 2020-03-15 12:50 | 0:50 | S/O | Due to changing work | 0 | 0 | No interruption
Khulna © | 132 kV mian Bus-B | 2020-03-20 07:22 | 2020-03-20 17:22 | 10:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 | 2020-03-22 08:37 | 2020-03-22 17:09 | 8:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 |  | 2020-03-22 09:46 |  | S/O | After maintenance work | 0 | 0 | No interruption
Khulna © | 132 kV main Bus | 2020-03-23 07:15 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformer-T1 | 2020-03-30 07:31 | 2020-03-30 09:23 | 1:52 | S/O | Due to replacement work | 8 | 14.9333 | Power interruption
Mongla | 132/33 kV Transformer-T2 | 2020-03-30 08:08 | 2020-03-30 09:17 | 1:09 | S/O | Due to temperature high at 33 kV B-phase Bushing | 0 | 0 | No interruption
|  |  | Total : | 55:45 |  | Unserved Energy : |  | 154.6167
HVDC Grid Circle :
Jessore | 132/33 kV Transformer-T3 | 2020-03-11 09:23 | 2020-03-11 09:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 132/33 kV Transformer-T1with 33 kV Bus | 2020-03-13 07:34 | 2020-03-13 07:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV mian Bus | 2020-03-13 08:24 | 2020-03-13 08:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2020-03-13 08:47 | 2020-03-13 08:47 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenidah | 33 kV Bus | 2020-03-14 09:15 | 2020-03-14 12:05 | 2:50 | S/O | Due to D/W work | 25 | 70.8333 | Power interruption
HVDC Bheramara | HVDC Bheramara AC filter 20DF32 | 2020-03-19 10:16 | 2020-03-19 10:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-HVDC 230 kV line | 2020-03-19 08:10 | 2020-03-19 08:19 | 0:09 | S/O | Due to switch yard checking | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2020-03-20 10:39 | 2020-03-20 20:01 | 9:22 | S/O | Due to 33 kV PBS feeder maintenance | 20 | 187.3333 | Power interruption
HVDC Bheramara | HVDC Bheramara pole-1 |  | 2020-03-21 13:48 |  | S/O | After maintenance work | 0 | 0 | No interruption
| HVDC Bheramara pole-2 |  | 2020-03-21 13:50 |  |  |  | 0 | 0 | No interruption
Bheramara | 132 kV Bus-B | 2020-03-22 09:46 | 2020-03-22 16:49 | 7:03 | S/O | Due to project work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T2 | 2020-03-22 11:06 | 2020-03-22 12:56 | 1:50 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
Bheramara | SAT Bay | 2020-03-24 12:55 | 2020-03-24 15:55 | 3:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 24:14 |  | Unserved Energy : |  | 258.1667
Page: 3/3 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Rangpur | 132/33 kV Transformer-T3 | 2020-03-02 06:52 | 2020-03-02 06:52 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV full Bus along with outgoing 132 kV ckt | 2020-03-06 06:35 | 2020-03-06 06:35 | 0:00 |  |  | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 |  | 2020-03-06 10:11 |  | S/O | After maintenance work | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T2 | 2020-03-11 15:20 | 2020-03-11 20:43 | 5:23 | S/O | Due to tan delta test | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T1with 33 kV Bus | 2020-03-13 08:40 | 2020-03-13 13:26 | 4:46 | S/O | Due to PBS work | 20 | 95.3333 | Power interruption
Baghabari | 230/132 kV Transformer-T-01 |  | 2020-03-14 15:27 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T1 | 2020-03-16 09:15 | 2020-03-16 13:20 | 4:05 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV Transformer-T3 | 2020-03-20 11:32 | 2020-03-20 12:29 | 0:57 | S/O | Due to C/M work | 16 | 15.2 | Power interruption
| 132/33 kV Transformer-T2 | 2020-03-21 13:11 | 2020-03-21 14:18 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 16:18 |  | Unserved Energy : |  | 110.5333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 265:57 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-03-01 07:39 | 2020-03-01 07:39 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2020-03-01 08:38 | 2020-03-01 16:53 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikgaj P/S 132 kV line-1 | 2020-03-01 09:22 | 2020-03-01 20:44 | 11:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-03-02 07:13 | 2020-03-02 07:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 |  | 2020-03-02 15:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 |  | 2020-03-02 17:20 |  | S/O | After maintenance work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 line-1 | 2020-03-02 10:17 | 2020-03-02 17:17 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2020-03-02 08:17 | 2020-03-02 16:32 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Kadda | Kadda-RPCL 132 kV line | 2020-03-03 07:06 | 2020-03-03 16:16 | 9:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 line-2 | 2020-03-03 09:21 | 2020-03-03 20:42 | 11:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2020-03-03 09:40 | 2020-03-03 17:36 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1 & 2 | 2020-03-03 13:30 | 2020-03-03 15:13 | 1:43 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kadda S/S | Kadda S/S-Gazipur 100 P/S 132 kV line | 2020-03-04 07:03 | 2020-03-04 07:03 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-1 | 2020-03-04 07:47 | 2020-03-05 00:12 | 16:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 line-2 | 2020-03-04 09:42 | 2020-03-04 21:07 | 11:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV line-2 | 2020-03-04 09:56 | 2020-03-04 10:45 | 0:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kishoreganj-Ashuganj 132 kV line-2 | 2020-03-04 09:30 | 2020-03-04 10:52 | 1:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | Kadda-Gazipur 100 MW P /S 132 kV line | 2020-03-05 06:54 | 2020-03-05 16:24 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Savar 132 line-2 | 2020-03-05 09:45 | 2020-03-05 22:46 | 13:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 & 2 | 2020-03-05 08:02 | 2020-03-05 16:05 | 8:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Maniknganj P/P 132 kV line-2 | 2020-03-11 09:03 | 2020-03-11 17:47 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Maniknganj P/P 132 kV line-1 | 2020-03-12 09:02 | 2020-03-12 21:26 | 12:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2020-03-13 06:16 | 2020-03-13 06:16 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kishoreganj-Ashuganj 132 kV line-2 | 2020-03-13 06:09 | 2020-03-13 07:58 | 1:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kishoreganj-Mymensingh 132 kV line-1 | 2020-03-13 06:11 | 2020-03-13 08:19 | 2:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-03-14 08:15 | 2020-03-14 18:01 | 9:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-1 | 2020-03-16 09:17 | 2020-03-16 12:59 | 3:42 | S/O | Due to project work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL P/P 132 kV line-1 | 2020-03-16 08:57 | 2020-03-16 10:29 | 1:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2020-03-18 07:26 | 2020-03-18 07:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Maniknganj P/P 132 kV line-2 | 2020-03-18 09:38 | 2020-03-18 17:27 | 7:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Kadda | Kadda S/S -Kadda MW P/P 132 kV line | 2020-03-18 09:57 | 2020-03-18 09:57 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV line-1 | 2020-03-18 10:10 | 2020-03-18 13:48 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalur 132 kV line-2 | 2020-03-18 12:47 | 2020-03-18 16:27 | 3:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Bibiyana (S) 400 kV line |  | 2020-03-18 09:38 |  | S/O | After maintenance work | 0 | 0 | No interruption
Savar | Savar-Manikgaj P/S 132 kV line-1 | 2020-03-19 09:32 | 2020-03-19 17:33 | 8:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL P/P 132 kV line-1 | 2020-03-19 08:45 | 2020-03-19 10:10 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jamalpur-UMPL P/P 132 kV line-2 | 2020-03-19 10:12 | 2020-03-19 11:08 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Sherpur 132 kV line | 2020-03-20 07:26 | 2020-03-20 17:25 | 9:59 | S/O | Due to D/W work | 157 | 1567.3833 | Power interruption
Jamalpur | Jamalpur-UMPL P/P 132 kV line-1 | 2020-03-21 09:37 | 2020-03-21 12:18 | 2:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2020-03-21 09:45 | 2020-03-21 12:26 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2020-03-22 08:33 | 2020-03-22 10:29 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jamalpur-Mymensingh 132 kV line-2 | 2020-03-22 08:36 | 2020-03-22 18:25 | 9:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Maniknganj P/P 132 kV line-1 | 2020-03-23 09:42 | 2020-03-23 20:07 | 10:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalur 132 kV line-1 | 2020-03-23 09:10 | 2020-03-23 17:23 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 236:55 |  | Unserved Energy: |  | 1567.3833
Page: 2/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Shyampur GIS | Shyampur GIS-Brahmangaon P/S 132 kV line | 2020-03-07 09:57 | 2020-03-07 09:57 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Shyampur GIS-Haripur 132 kV line | 2020-03-07 09:40 | 2020-03-07 09:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line | 2020-03-08 03:58 | 2020-03-08 03:58 | 0:00 | S/O | Due to safety as tower #2 | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2020-03-13 06:37 | 2020-03-13 06:37 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2020-03-14 08:31 | 2020-03-14 17:06 | 8:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2020-03-15 09:17 | 2020-03-15 12:59 | 3:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-03-15 08:28 | 2020-03-15 17:44 | 9:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2020-03-16 08:46 | 2020-03-16 16:45 | 7:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2020-03-18 08:12 | 2020-03-18 16:14 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2020-03-19 07:15 | 2020-03-19 07:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2020-03-19 06:18 | 2020-03-19 06:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-1 |  | 2020-03-19 09:37 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Rampura-Ullon 132 kV line-2 | 2020-03-20 06:17 | 2020-03-20 06:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-1 | 2020-03-20 08:25 | 2020-03-20 17:43 | 9:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| Meghnaghat-Haripur 230 kV line-2 | 2020-03-20 08:27 | 2020-03-20 17:46 | 9:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Meghnaghat IEL 132 kV line | 2020-03-20 08:20 | 2020-03-20 17:40 | 9:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV line-1 | 2020-03-22 06:15 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-EGCB 132 kV 132 kV line-1 | 2020-03-22 10:40 | 2020-03-22 12:12 | 1:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Siddhirganj S/S-EGCB 132 kV 132 kV line-2 | 2020-03-22 10:40 | 2020-03-22 15:38 | 4:58 | S/O |  | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 |  | 2020-03-24 17:12 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line-1 |  | 2020-03-24 16:57 |  | S/O | After maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2020-03-25 09:14 | 2020-03-25 12:05 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 74:52 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khulshi | Khulshi-Hathazari 132 kV line | 2020-03-01 11:57 | 2020-03-01 12:56 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2020-03-02 06:43 | 2020-03-02 10:04 | 3:21 | S/O | Due to replacement work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-1 | 2020-03-04 12:20 | 2020-03-04 17:38 | 5:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Bakulia 132 kV line-1 | 2020-03-05 10:28 | 2020-03-05 18:01 | 7:33 | S/O | Due to changing work | 0 | 0 | No interruption
Hathazari | Hathazari-AkS 230 kV line | 2020-03-06 08:39 | 2020-03-06 17:00 | 8:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Maduaghat | Maduaghat-Sikalbaha 132 kV line-1 | 2020-03-12 07:08 | 2020-03-12 13:21 | 6:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.k chemical 132 kV line-1 | 2020-03-12 07:11 | 2020-03-12 13:17 | 6:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2020-03-13 06:31 | 2020-03-13 06:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baraulia | Baraulia-AKSPL 132 kV line | 2020-03-18 09:18 | 2020-03-18 17:41 | 8:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-AKSPL 132 kV line | 2020-03-18 09:27 | 2020-03-18 17:49 | 8:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2020-03-19 06:34 | 2020-03-19 06:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-1 | 2020-03-22 07:37 | 2020-03-22 07:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Cox'sbazar 132 kV line-1 | 2020-03-24 12:35 | 2020-03-24 13:50 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 55:51 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2020-03-01 07:51 | 2020-03-01 20:45 | 12:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-03-04 10:47 | 2020-03-04 11:28 | 0:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-1 | 2020-03-16 15:26 | 2020-03-16 21:01 | 5:35 | S/O | Due to D/W work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV 132 kV line-2 |  | 2020-03-22 11:55 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1 |  | 2020-03-22 14:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Desh Energy P/S 132 kV line-1 | 2020-03-23 09:56 | 2020-03-23 18:12 | 8:16 | S/O | Due to C/M work | 0 | 0 | No interruption
| Chandpur S/S-Desh Energy P/S 132 kV line-2 | 2020-03-24 08:55 | 2020-03-24 17:12 | 8:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-03-25 08:48 | 2020-03-25 16:56 | 8:08 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 43:51 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal | Barishal-Patuakhali 132 kV line | 2020-03-06 07:16 | 2020-03-06 16:59 | 9:43 | S/O | Due to D/W work | 31 | 301.2167 | Power interruption
Madaripur | Madaripur-Gopalganj (N)132 kV line-3 | 2020-03-11 13:05 | 2020-03-11 14:30 | 1:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-03-11 06:55 | 2020-03-11 18:50 | 11:55 | S/O | Due to D/W work | 40 | 476.6667 | Power interruption
Madaripur | Madaripur-Barishal(N) 132 kV line-2 | 2020-03-11 14:37 | 2020-03-11 16:59 | 2:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madaripur-Barishal(N) 132 kV line-2 | 2020-03-12 07:36 | 2020-03-12 09:26 | 1:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-03-13 06:36 | 2020-03-13 06:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barishal(S)-Patuakhali 132 kV line | 2020-03-14 06:57 | 2020-03-14 06:57 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Payra 400 kV line-2 | 2020-03-14 08:02 | 2020-03-14 17:04 | 9:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj | Gopalganj-Madumati P/S 132 kV line | 2020-03-14 08:11 | 2020-03-14 17:22 | 9:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Madaroipur 132 kV line-1 | 2020-03-14 12:02 | 2020-03-14 13:36 | 1:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj (N)132 kV line-1 & 2 | 2020-03-14 08:28 | 2020-03-14 10:04 | 1:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Madaripur 132 kV line-2 | 2020-03-14 13:38 | 2020-03-14 16:19 | 2:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line-1 | 2020-03-15 07:20 | 2020-03-15 09:01 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj-Payra 400 kV line-2 | 2020-03-15 07:55 | 2020-03-15 07:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj-Payra 400 kV line-2 | 2020-03-16 07:50 | 2020-03-16 16:43 | 8:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-03-16 14:31 | 2020-03-16 16:38 | 2:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-03-17 02:35 | 2020-03-17 02:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj-Payra 400 kV line-2 | 2020-03-18 08:08 | 2020-03-18 16:18 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Barishal(S) | Barishal(S)-Patuakhali 132 kV line | 2020-03-18 13:00 | 2020-03-18 16:37 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 75:47 |  | Unserved Energy: |  | 777.8833
HVDC Grid Circle :
Jhenidah | Jhenidah-Chuadanga 132 kVline | 2020-03-05 07:21 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Sirajganj 132 kV line-1 | 2020-03-05 15:06 | 2020-03-05 15:58 | 0:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-1 & 2 | 2020-03-06 06:28 | 2020-03-06 17:53 | 11:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara G.K-Bheramara 132 kV line-1 | 2020-03-20 07:04 | 2020-03-20 10:58 | 3:54 | S/O | Due to D/W work | 26 | 101.4 | Power interruption
| Bheramara-Rental 132 kV line | 2020-03-20 07:05 | 2020-03-20 07:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara HVDC-Bheramara 400 kV line-1 | 2020-03-20 08:42 | 2020-03-20 08:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara HVDC-Bheramara 400 kV line-2 | 2020-03-20 08:43 | 2020-03-20 08:43 | 0:00 |  |  | 0 | 0 | No interruption
Jessore | Jessore-Jhenidah 132 kV line-2 | 2020-03-21 17:08 | 2020-03-21 18:02 | 0:54 | S/O | Due to kite thead removing | 0 | 0 | No interruption
Bheramara HVDC | Bheramara-Khulna(S) 230 kV line-2 | 2020-03-23 06:50 | 2020-03-23 06:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Khulna(S) 230 kV line-1 |  | 2020-03-25 11:28 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Natore 132 kV line-2 | 2020-03-25 10:45 | 2020-03-25 12:12 | 1:27 | S/O | Due to C/M work | 0 | 0
Jhenidah | Jhenidah-Bottail 132 kV line-2 | 2020-03-31 07:49 | 2020-03-31 09:10 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 19:53 |  | Unserved Energy: |  | 101.4
Bogura Grid Circle :
Rangpur | Rangpur-Barapukuria 132 kV line-2 | 2020-03-01 07:20 | 2020-03-01 13:26 | 6:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-1 | 2020-03-01 10:17 | 2020-03-01 10:55 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Barapukuria 132 kV line-1 | 2020-03-02 06:55 | 2020-03-02 12:15 | 5:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Saidpur 132 kV line-1 & 2 | 2020-03-02 12:25 | 2020-03-02 16:10 | 3:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Rangpur Confidence 132 kV line-1 & 2 | 2020-03-03 06:58 | 2020-03-03 11:47 | 4:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2020-03-17 11:58 | 2020-03-17 14:10 | 2:12 | S/O | Due to project work | 40 | 88 | Power interruption
Bogura New | Bogura New-Bogura (O) 132 kV line-1 | 2020-03-18 20:53 | 2020-03-18 20:53 | 0:00 | S/O | Due to unbalance current | 0 | 0 | No interruption
Rajshahi(New) | Rajshahi(New)-Bheramara HVDC 230 kV line-2 | 2020-03-21 13:27 | 2020-03-21 13:50 | 0:23 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajshahi(New)-Bheramara HVDC 230 kV line-1 & 2 |  | 2020-03-21 15:58 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 23:13 |  | Unserved Energy: |  | 88
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 530:22 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March' 2020
| Area | Previous Month (February 2020) |  |  |  | Current Month (March 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | 6 | 83 | 96 | 13 | 2 | 76 | 91
2 | Dhaka (South) Grid Circle. | 22 | 4 | 31 | 57 | 17 | 5 | 27 | 49
3 | Chattogram Grid Circle. | 5 | 3 | 38 | 46 | 4 | 3 | 23 | 30
4 | Cumilla Grid Circle. | 6 | 4 | 57 | 67 | 13 | 4 | 20 | 37
5 | Khulna Grid Circle. | 17 | 3 | 34 | 54 | 11 | 7 | 36 | 54
6 | Bheramara HVDC Grid Circle | 5 | 1 | 12 | 18 | 2 | 1 | 13 | 16
7 | Bogura Grid Circle. | 9 | 8 | 56 | 73 | 11 | 13 | 18 | 42
8 | Others | 1 | 1 | 4 | 6 | 2 |  |  | 2
9 | Total | 72 | 30 | 315 | 417 | 73 | 35 | 213 | 321
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March' 2020
| Area | Previous Month (February 2020) |  |  |  | Current Month (March 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 115.6667 | 107.4167 | 701.75 | 924.8333 | 162.77 |  | 2703.88 | 2866.65
2 | Dhaka (South) Grid Circle. | 255.33 |  |  | 255.33 | 401.85 |  | 80.42 | 482.27
3 | Chattogram Grid Circle. | Energy unserved ( MWH ) due to T: 75.12; Energy unserved ( MWH ) due to Total: 75.12; Energy unserved ( MWH ) due to Total: 0
4 | Cumilla Grid Circle. |  |  | 64.5 | 64.5 | 69.27 |  | 30.75 | 100.02
5 | Khulna Grid Circle. | 66.97 | 16 | 293.25 | 376.22 | 20.7 | 20.9 | 932.5 | 974.1
6 | Bheramara HVDC Grid Circle | 10.67 |  | 298.8 | 309.47 |  |  | 359.57 | 359.57
7 | Bogura Grid Circle. | 274.97 | 8.17 | 2507.33 | 2790.47 | 1374.78 | 135.58 | 198.53 | 1708.89
8 | Others | Energy unserved ( MWH ) due to T: 29; Energy unserved ( MWH ) due to Total: 29; Energy unserved ( MWH ) due to T: 11.27; Energy unserved ( MWH ) due to Total: 11.27
9 | Total | 827.7267 | 131.5867 | 3865.63 | 4824.9433 | 2040.64 | 156.48 | 4305.65 | 6502.77
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 2 | 2 | 4 |  |  | 4 | 1289
2 | Dhaka (South) | 5031.6 | 4 | 1 | 5 | 2 |  | 3 | 436.32
3 | Chattogram | 2042
4 | Khulna | 2434 | 4 | 2 | 6 | 3 | 1 | 2 | 177.32
5 | Bheramara (HVDC) | 2423.3 |  | 2 |  |  |  | 2 | 258.17
6 | Bogura | 3145.6 | 7 | 2 | 9 | 3 | 1 | 5 | 371.4
7 | Cumilla | 2981 | 5 | 1 | 6 | 4 | 1 | 1 | 87.35
8 | Others | -
| Total | 23365.5 | [6 empty] | 2619.56
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.41%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 98.37%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.91% | [6 empty] | Executive Engineer
6 | Bogura | 99.9% | [6 empty] | Information Management Division
7 | Cumilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | 1 | 2 | 1 |  | 1 | 1577.65
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 | 1 | - | 45.95
3 | Chattogram | 917 | 20+9(Partial) | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | 21 | 2 | 2 | 4 | 2 |  | 2 | 796.78
5 | Bheramara (HVDC) | 598.7 |  |  | 1 | 1 |  | - | 1 | 101.4
6 | Bogura | 1803.3 | 38 | 2 | 1 | 3 | 1 |  | 2 | 1337.5
7 | Cumilla | 1648.16 | 17 | 1 |  | 1 |  | - | 1 | 12.67
7 | Others | - |  | 1 | - | 1 | 1 | - | - | 11.27
| Total | 8862.13 | 150+24(Partial) | [6 empty] | 3883.22
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.88%
3 | Chattogram | 99.99%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-03-18 | 16 | - | - | - | 1 | 0hr14min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:March' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 1:12 | 120 | 144 | Due to tripping of 33 kV incoming CB
Joydevpur | 1 | 0:17 | 30 | 8.5 | Due to tripping of 132/33 kV Transformer GT2
Tongi | 1 | 0:02 | 308 | 10.2667 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
Kaliakoir | 1 | 6:29 | 90 | 583.5 | Due to S/D of 400/132 kV Transformer-TR2
Kishoreganj | 1 | 9:13 | 60 | 553 | Due to S/D of 132 kV full Bus along with outgoing 132 kV Ckt
Jamalpur | 1 | 9:59 | 157 | 1567.3833 | Due to S/D of Jamalpur-Sherpur 132 kV line
Hasnabad | 1 | 0:26 | 104 | 45.0667 | Due to S/D of 33 kV full Bus
Shyampur(O) | 1 | 0:22 | 120 | 44 | Due to tripping of 132/33 kV Transformers T1 ,T3 & T4
Shyampur | 1 | 2:43 | 90 | 244.5 | Due to tripping of 132/33 kV Transformer T4
Ullon | 1 | 1:07 | 20 | 22.3333 | Due to tripping of 132/33 kV all Transformers
Hasnabad | 1 | 0:44 | 38 | 27.8667 | Due to tripping of Hasnabad--Lalbagh 132 kV line
Ullon | 2 | 0:08 | 105 | 14 | Due to tripping of Ullon-Siddirganj 132 kV line
|  | 0:13 | 52 | 11.2667
Siddhirganj | 1 | 0:07 | 35 | 4.0833 | Due to tripping of Siddhirganj-Matuail 132 kV line
Sonargaon |  | 3:13 | 25 | 80.4167 | Due to S/D of132/33 kV Transformer-T2
Cumilla(N) | 1 | 0:19 | 56 | 17.7333 | Due to trippnig of 132/33 kV Transformers-T3 & T4
Shahjibazar | 2 | 0:29 | 15 | 7.25 | Due to tripping of 132/33 kV Transformer T2
|  | 0:43 | 33 | 23.65
Sunamganj | 1 | 0:20 | 12 | 4 | Due to tripping of 132/33 kV Transformers-T1 & T2
Chowmuhani | 1 | 0:07 | 34 | 3.9667 | Due to tripping of 132/33 kV Transformer-T1
Fenchuganj | 1 | 1:16 | 10 | 12.6667 | Due to tripping of Fenchuganj-Kulaura 132 kV line-2
Chauddagram |  | 2:03 | 15 | 30.75 | Due to S/D of132/33 kV Transformer-T2
Noapara |  | 0:06 | 8 | 0.8 | Due to tripping of 132/33 kV Transformer-T1
Mongla |  | 0:49 | 22 | 17.9667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Patuakhali |  | 0:08 | 22 | 2.9333
Madaripur | 2 | 0:12 | 5 | 1 | Due to trippnig of 132/33 kV Transformer-T1
|  | 0:14 | 33 | 7.7 | Due to tripping of Madaripur-Gopalganj 132 kV line-1 & 2
Barishal |  | 0:12 | 56 | 11.2 | Due to tripping of Barishal-Patuakhali 132 kV line-1
| 1 | 8:13 | 17 | 139.6833 | Due to S/D of 132/33 kV Transformers T3 & T4
Patuakhali | 1 | 1:52 | 8 | 14.9333 | Due to S/D of 132/33 kV Transformer-T1
Barishal | 2 | 9:43 | 31 | 301.2167 | Due to S/D of Barishal-Patuakhali 132 kV line
|  | 11:55 | 40 | 476.6667
Jhenidah |  | 2:50 | 25 | 70.8333 | Due to S/D of 33 kV Bus
Shahjadpur |  | 9:22 | 20 | 187.3333 | Due to S/D of 132/33 kV Transformer T1
Bheramara |  | 3:54 | 26 | 101.4 | Due to S/D of Bheramara G.K-Bheramara 132 kV line-1
Niyamatpur |  | 0:15 | 27 | 6.75 | Due to tripping of 132/33 kV Transformer T2
Barapukuria |  | 3:25 | 17 | 58.0833 | Due to tripping of 132/33 kV Transformer T3
Sirajganj |  | 0:12 | 28 | 5.6 | Due to tripping of 132/33 kV Transformers T1 & T2
Naogaon | 2 | 1:36 | 67 | 107.2 | Due to tripping of 132/33 kV Transformer T3
|  | 1:25 | 35 | 49.5833 | Due to tripping of 132/33 kV Transformer T2
Palshbari | 1 | 1:43 | 13 | 22.3167 | Due to red-hot maintenance of 132/33 kV Transformer T4
Amnura | 1 | 0:20 | 34 | 11.3333 | Due to tripping of 132/33 kV Transformer T1
Bogura(New) | 1 | 0:19 | 2790 | 883.5 | Due to tripping of Bogura(New)-Sherpur 132 kV line-1
Naogaon | 1 | 9:09 | 40 | 366 | Due to tripping of Naogaon-Niyamatpur 132 kV line
|  | 2:12 | 40 | 88 | Due to S/D ofNaogaon-Niyamatpur 132 kV line
Purbasadipur | 1 | 4:46 | 20 | 95.3333 | Due to S/D of 132/33 kV Transformer T1 & 33 kV Bus
Rajshahi(O) |  | 0:57 | 16 | 15.2 | Due to S/D of 13233 kV Transformer T3
| Total Unserved energy : |  |  | 6502.7667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 138 | 16 | 2020-03-03 | 13:00
2 | Munsiganj | 108 | 28 | 2020-03-03 | 20:00
3 | Sonargaon | 81 | 16 | 2020-03-03 | 19:30
4 | Shyampur | 200 | 9 | 2020-03-03 | 0.45833
5 | Bhulta | 184 | 18 | 2020-03-03 | 11:00
6 | Madanganj | 67 | 7 | 2020-03-03 | 21:00
7 | Shitalakhya | 118 | 21 | 2020-03-03 | 10:00
8 | Rahim steel | 26 | 19 | 2020-03-03 | 13:00
9 | Matuail | 100 | 19 | 2020-03-03 | 0.41667
10 | Ghorasal | 69 | 1 | 2020-03-03 | 19:00
11 | Narsingdi | 133 | 16 | 2020-03-03 | 19:30
12 | Haripur (SBU) | 112 | 12 | 2020-03-03 | 19:00
13 | Ullon | 68 | 19 | 2020-03-03 | 0.54167
14 | Hasnabad | 174 | 19 | 2020-03-03 | 0.79167
15 | Magbazar | 101 | 18 | 2020-03-03 | 12:00
16 | Maniknagar | 94 | 15 | 2020-03-03 | 0.66667
17 | Bangabhaban | 32 | 15 | 2020-03-03 | 0.66667
18 | Narinda | 94 | 12 | 2020-03-03 | 0.54167
19 | Dhanmondi | 141 | 16 | 2020-03-03 | 0.5
20 | Lalbag | 72 | 19 | 2020-03-03 | 13:00
21 | Madartek | 66 | 28 | 2020-03-03 | 20:00
22 | Dhaka University | - | - | - | -
23 | Mirpur | 91 | 18 | 2020-03-03 | 0.77083
24 | Kalyanpur | 88 | 16 | 2020-03-03 | 19:00
25 | Gulshan | 118 | 16 | 2020-03-03 | 14:00
26 | Uttara | 64 | 13 | 2020-03-03 | 19:00
27 | Uttara(new) | 40 | 15 | 2020-03-03 | 0.79167
28 | Kamrangirchar | 91 | 4 | 2020-03-03 | 19:00
29 | Savar | 131 | 19 | 2020-03-03 | 15:00
30 | Bhasantec | 124 | 18 | 2020-03-03 | 19:00
31 | Agargaon | 47 | 12 | 2020-03-03 | 0.54167
32 | Satmosjid | 90 | 11 | 2020-03-03 | 0.54167
33 | Tongi | 129 | 12 | 2020-03-03 | 18:00
34 | Kabirpur | 220 | 21 | 2020-03-03 | 0.625
35 | Basundhara | 132 | 16 | 2020-03-03 | 18:30
36 | Manikganj | 82 | 4 | 2020-03-03 | 19:00
37 | Joydevpur | 182 | 26 | 2020-03-03 | 11:00
38 | New Tongi | 97 | 18 | 2020-03-03 | 14:00
39 | Kodda | 232 | 18 | 2020-03-03 | 15:00
40 | Dhamrai | 68 | 21 | 2020-03-03 | 15:00
41 | Rajendrapur | 74 | 4 | 2020-03-03 | 18:30
42 | Valuka | 96 | 21 | 2020-03-03 | 0.45833
43 | Tangail | 201 | 28 | 2020-03-03 | 19:00
44 | Mymensing | 214 | 21 | 2020-03-03 | 19:00
45 | Kishorganj | 132 | 28 | 2020-03-03 | 21:00
46 | Netrokona | 121 | 29 | 2020-03-03 | 19:30
47 | Jamalpur | 128 | 29 | 2020-03-03 | 20:00
48 | Sherpur | 108 | 27 | 2020-03-03 | 19:00
49 | Srimongal | 38 | 28 | 2020-03-03 | 0.8125
50 | Shahjibazar | 94 | 15 | 2020-03-03 | 19:30
51 | Fenchuganj | 34 | 15 | 2020-03-03 | 18:00
52 | Kulawara | 38 | 29 | 2020-03-03 | 19:30
53 | Sylhet | 120 | 16 | 2020-03-03 | 18:30
54 | Chatak | 24 | 21 | 2020-03-03 | 20:00
55 | Sunamganj | 35 | 27 | 2020-03-03 | 18:30
56 | Bianibazar | 47 | 30 | 2020-03-03 | 19:00
57 | Cumilla (S) | 152 | 15 | 2020-03-03 | 0.77083
58 | Cumilla(N) | 119 | 28 | 2020-03-03 | 19:30
59 | Chandpur | 96 | 12 | 2020-03-03 | 18:30
60 | Feni | 105 | 29 | 2020-03-03 | 21:00
61 | Chowmuhani | 162 | 15 | 2020-03-03 | 20:00
62 | Ashuganj | 51 | 21 | 2020-03-03 | 19:00
63 | Daudkandi | 134 | 28 | 2020-03-03 | 0.8125
64 | B.Baria | 136 | 28 | 2020-03-03 | 21:00
65 | Ramganj | 94 | 28 | 2020-03-03 | 20:00
66 | Chaddagram | 48 | 30 | 2020-03-03 | 20:00
67 | PHP | 10 | 19 | 2020-03-03 | 10:00
68 | Madanhat | 67 | 15 | 2020-03-03 | 18:30
69 | Hathazari | 83 | 28 | 2020-03-03 | 0.8125
70 | Khulshi | 183 | 24 | 2020-03-03 | 18:30
71 | Halishahar | 152 | 19 | 2020-03-03 | 15:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Baraulia | 199 | 28 | 2020-03-03 | 15:00
73 | Sikalbaha | 28 | 17 | 2020-03-03 | 19:30
74 | Dohazari | 92 | 19 | 2020-03-03 | 19:30
75 | Cox'sbazar | 100 | 15 | 2020-03-03 | 19:30
76 | Chandraghona | 28 | 15 | 2020-03-03 | 18:30
77 | Kaptai | 4.2 | 17 | 2020-03-03 | 19:00
78 | A. Khaer Stl. | 24 | 2 | 2020-03-03 | 23:00
79 | Bakulia | 102 | 16 | 2020-03-03 | 0.77083
80 | Julda | 25 | 15 | 2020-03-03 | 0.625
81 | TK chemical | 17 | 28 | 2020-03-03 | 19:00
82 | Modern Steel | 18 | 19 | 2020-03-03 | 11:00
83 | Shahmirpur | 28 | 12 | 2020-03-03 | 18:30
84 | Khagrachhari | 22 | 15 | 2020-03-03 | 18:30
85 | Matarbari | 29 | 28 | 2020-03-03 | 19:00
86 | Baroiar Hat | 34 | 1 | 2020-03-03 | 18:30
87 | Rangamati | 12 | 15 | 2020-03-03 | 0.79167
88 | Abul Khair 230 | 205 | 22 | 2020-03-03 | 14:00
89 | BSRM | 165 | 7 | 2020-03-03 | 4:00
90 | GPH Ispat | 69 | 5 | 2020-03-03 | 10:00
91 | Goalpara | 32 | 21 | 2020-03-03 | 12:00
92 | Central s/s | 75 | 12 | 2020-03-03 | 19:30
93 | Noapara | 63 | 3 | 2020-03-03 | 0.79167
94 | Jashore | 120 | 28 | 2020-03-03 | 20:00
95 | Benapol | 44 | 28 | 2020-03-03 | 19:30
96 | Jhenidah | 105 | 28 | 2020-03-03 | 19:00
97 | Bottail | 112 | 21 | 2020-03-03 | 19:30
98 | G.K Project | 47 | 28 | 2020-03-03 | 19:00
99 | Faridpur | 152 | 28 | 2020-03-03 | 20:00
100 | Madaripur | 81 | 28 | 2020-03-03 | 21:00
101 | Sariatpur | 50 | 28 | 2020-03-03 | 19:30
102 | Gopalganj | 82 | 29 | 2020-03-03 | 19:00
103 | Bagerhat | 77 | 24 | 2020-03-03 | 19:00
104 | Mongla | 49 | 25 | 2020-03-03 | 14:00
105 | Satkhira | 96 | 28 | 2020-03-03 | 21:00
106 | Gallamari | 55 | 21 | 2020-03-03 | 19:30
107 | Magura | 46 | 21 | 2020-03-03 | 19:00
108 | Norail | 35 | 28 | 2020-03-03 | 19:30
109 | Chuadanga | 81 | 28 | 2020-03-03 | 19:30
110 | Barsal(N) | 42 | 20 | 2020-03-03 | 21:00
111 | Barsal(S) | 88 | 12 | 2020-03-03 | 21:00
112 | Patuakhali | 95 | 15 | 2020-03-03 | 20:00
113 | Bhandaria | 45 | 21 | 2020-03-03 | 20:00
114 | Borhan Uddin | 34 | 20 | 2020-03-03 | 19:00
115 | Ishurdi | 51 | 28 | 2020-03-03 | 20:00
116 | Ruppur Paromanobik | 2 | 2 | 2020-03-03 | 0.45833
117 | Natore | 119 | 28 | 2020-03-03 | 19:00
118 | Bogura | 155 | 21 | 2020-03-03 | 19:30
119 | Naogaon | 119 | 21 | 2020-03-03 | 19:30
120 | Rajshahi | 117 | 28 | 2020-03-03 | 21:00
121 | Rajshahi New | 13 | 29 | 2020-03-03 | 0.8125
122 | C.Nawabganj | 77 | 28 | 2020-03-03 | 19:30
123 | Amnura | 54 | 29 | 2020-03-03 | 20:00
124 | Pabna | 94 | 28 | 2020-03-03 | 20:00
125 | Shahjadpur | 97 | 22 | 2020-03-03 | 19:30
126 | Serajganj | 89 | 24 | 2020-03-03 | 19:30
127 | Niyamatpur | 91 | 17 | 2020-03-03 | 0.79167
128 | Joypurhat | 64 | 29 | 2020-03-03 | 19:00
129 | Sherpur(Bogura) | 48 | 29 | 2020-03-03 | 19:00
130 | Mohastangar | 46 | 30 | 2020-03-03 | 19:30
131 | Rangpur | 132 | 28 | 2020-03-03 | 19:00
132 | Lalmonirhat | 57 | 30 | 2020-03-03 | 19:30
133 | Saidpur | 103 | 21 | 2020-03-03 | 19:00
134 | Purbasadipur | 100 | 11 | 2020-03-03 | 8:00
135 | Thakurgaon | 74 | 31 | 2020-03-03 | 19:00
136 | Palshbari | 117 | 29 | 2020-03-03 | 0.79167
137 | Barapukuria | 50 | 21 | 2020-03-03 | 19:30
138 | Panchugar | 45 | 30 | 2020-03-03 | 0.8125
139 | Joldhaka | 29 | 31 | 2020-03-03 | 0.79167
140 | Kurigram | 55 | 30 | 2020-03-03 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 3742 | 18.03.2020 | 19:00
Chattogram | 1293 | 19.03.2020 | 15:00
Khulna | 1285 | 28.03.2020 | 20:00
Rajshahi | 1169 | 28.03.2020 | 20:00
Cumilla | 1031 | 28.03.2020 | 19:30
Mymensingh | 930 | 28.03.2020 | 19:00
Sylhet | 400 | 14.03.2020 | 18:30
Barisal | 275 | 18.03.2020 | 19:00
Rangpur | 729 | 31.03.2020 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 405 | 1 | 2020-03-03 | 4:00 | 386 | 18 | 2020-03-03 | 11:00
2 | Bheramara | 400 | 406 | 6 | 2020-03-03 | 2:00 | 382 | 31 | 2020-03-03 | 20:00
3 | Ashuganj(N) | 400 | 404 | 3 | 2020-03-03 | 8:00 | 380 | 22 | 2020-03-03 | 10:00
4 | Payra | 400 | 435 | 3 | 2020-03-03 | 7:00 | 359 | 11 | 2020-03-03 | 18:30
5 | Kaliakoir | 400 | 389 | 1 | 2020-03-03 | 3:00 | 360 | 21 | 2020-03-03 | 10:00
6 | Bhulta | 400 | 400 | 3 | 2020-03-03 | 8:00 | 373 | 22 | 2020-03-03 | 10:00
7 | Gopalganj | 400 | 433 | 3 | 2020-03-03 | 7:00 | 354 | 18 | 2020-03-03 | 12:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 28 | 2020-03-03 | 18:00 | 230 | 5 | 2020-03-03 | 8:00
2 | Ishurdi | 230 | 242 | 2 | 2020-03-03 | 4:00 | 224 | 19 | 2020-03-03 | 7:00
3 | Ashuganj | 230 | 242 | 1 | 2020-03-03 | 1:00 | 229 | 22 | 2020-03-03 | 9:00
4 | Serajganj | 230 | 238 | 5 | 2020-03-03 | 20:00 | 224 | 24 | 2020-03-03 | 11:00 |  | 255 |  | 232
5 | Baghabari | 230 | 249 | 2 | 2020-03-03 | 3:00 | 232 | 19 | 2020-03-03 | 7:00 |  | 224 |  | 204
6 | Barapukuria | 230 | 240 | 6 | 2020-03-03 | 9:00 | 223 | 26 | 2020-03-03 | 19:00
7 | Bogura | 230 | 238 | 19 | 2020-03-03 | 19:30 | 212 | 1 | 2020-03-03 | 8:00
8 | Khulna South | 230 | 242 | 7 | 2020-03-03 | 5:00 | 204 | 25 | 2020-03-03 | 7:00
9 | Rampura | 230 | 233 | 3 | 2020-03-03 | 8:00 | 220 | 22 | 2020-03-03 | 11:00
10 | Haripur | 230 | 236 | 3 | 2020-03-03 | 8:00 | 220 | 18 | 2020-03-03 | 12:00
11 | Hasnabad | 230 | 235 | 3 | 2020-03-03 | 8:00 | 220 | 5 | 2020-03-03 | 15:00
12 | Shyampur | 230 | 236 | 3 | 2020-03-03 | 8:00 | 216 | 18 | 2020-03-03 | 10:00
13 | Aminbazar | 230 | 234 | 20 | 2020-03-03 | 22:00 | 218 | 18 | 2020-03-03 | 12:00
14 | Tongi | 230 | 235 | 3 | 2020-03-03 | 8:00 | 213 | 23 | 2020-03-03 | 15:00
15 | Comilla (N) | 230 | 239 | 3 | 2020-03-03 | 9:00 | 223 | 7 | 2020-03-03 | 18:30
16 | Hathazari | 230 | 225 | 8 | 2020-03-03 | 19:30 | 210 | 18 | 2020-03-03 | 16:00
17 | Megnaghat | 230 | 238 | 1 | 2020-03-03 | 5:00 | 222 | 5 | 2020-03-03 | 15:00
18 | Fenchuganj | 230 | 243 | 29 | 2020-03-03 | 19:00 | 230 | 28 | 2020-03-03 | 11:00
19 | Siddhirganj | 230 | 239 | 3 | 2020-03-03 | 8:00 | 221 | 18 | 2020-03-03 | 15:00
20 | Maniknagar | 230 | 239 | 3 | 2020-03-03 | 8:00 | 219 | 16 | 2020-03-03 | 16:00
21 | Old Airport | 230 | 237 | 3 | 2020-03-03 | 8:00 | 217 | 18 | 2020-03-03 | 10:00
22 | Barisal | 230 | 255 | 3 | 2020-03-03 | 17:00 | 230 | 11 | 2020-03-03 | 18:30
23 | AKSML | 230 | 229 | 1 | 2020-03-03 | 6:00 | 207 | 25 | 2020-03-03 | 14:00
24 | BSRM | 230 | 227 | 1 | 2020-03-03 | 6:00 | 209 | 23 | 2020-03-03 | 11:00
25 | Bibiyana | 230 | 241 | 29 | 2020-03-03 | 19:00 | 230 | 23 | 2020-03-03 | 16:00
26 | Bhulta | 230 | 239 | 3 | 2020-03-03 | 8:00 | 221 | 18 | 2020-03-03 | 12:00
27 | Ashuganj (S) | 230 | 239 | 1 | 2020-03-03 | 2:00 | 226 | 22 | 2020-03-03 | 10:00
28 | Kaliakoir | 230 | 237 | 3 | 2020-03-03 | 5:00 | 220 | 5 | 2020-03-03 | 15:00
29 | GPH | 230 | 224 | 14 | 2020-03-03 | 8:00 | 207 | 25 | 2020-03-03 | 14:00
| 132 kV Substation | [10 empty] | Max |  | Min
1 | Siddhirganj | 132 | 140 | 3 | 2020-03-03 | 0.375 | 125 | 22 | 2020-03-03 | 0.45833 |  | 151 | Gopalganj | 105 | Chuadanga
2 | Munsiganj | 132 | 139 | 3 | 2020-03-03 | 0.33333 | 123 | 25 | 2020-03-03 | 0.45833 |  | 127 | Cox'sbazar | 134 | Ghorasal
3 | Sonargaon | 132 | 135 | 3 | 2020-03-03 | 0.79167 | 123 | 4 | 2020-03-03 | 0.5
4 | Shyampur | 132 | 141 | 3 | 2020-03-03 | 0.33333 | 125 | 18 | 2020-03-03 | 0.5
5 | Bhulta | 132 | 130 | 3 | 2020-03-03 | 0.33333 | 120 | 5 | 2020-03-03 | 0.5
6 | Madanganj | 132 | 139 | 3 | 2020-03-03 | 8:00 | 123 | 18 | 2020-03-03 | 0.375
7 | Shitalakhya | 132 | 141 | 3 | 2020-03-03 | 0.33333 | 122 | 25 | 2020-03-03 | 0.5
8 | Rahim Steal | 132 | 138 | 3 | 2020-03-03 | 8:00 | 125 | 22 | 2020-03-03 | 0.45833
9 | Matuail | 132 | 139 | 2 | 2020-03-03 | 0.8125 | 123 | 22 | 2020-03-03 | 24:00
10 | Ghorasal | 132 | 140 | 1 | 2020-03-03 | 0.77083 | 134 | 1 | 2020-03-03 | 0.041667
11 | Narsinghdi | 132 | 135 | 6 | 2020-03-03 | 0.54167 | 119 | 22 | 2020-03-03 | 0.375
12 | Haripur (SBU) | 132 | 138 | 3 | 2020-03-03 | 0.33333 | 126 | 22 | 2020-03-03 | 0.45833
13 | Ullon | 132 | 135 | 20 | 2020-03-03 | 0.91667 | 122 | 11 | 2020-03-03 | 0.66667
14 | Hasnabad | 132 | 140 | 3 | 2020-03-03 | 0.33333 | 124 | 5 | 2020-03-03 | 0.66667
15 | Magbazar | 132 | 135 | 1 | 2020-03-03 | 0.25 | 122 | 5 | 2020-03-03 | 0.66667
16 | Maniknagar | 132 | 138 | 3 | 2020-03-03 | 0.33333 | 126 | 18 | 2020-03-03 | 0.66667
17 | Bangabhaban | 132 | 138 | 3 | 2020-03-03 | 0.33333 | 126 | 18 | 2020-03-03 | 0.66667
18 | Narinda | 132 | 138 | 3 | 2020-03-03 | 0.33333 | 126 | 18 | 2020-03-03 | 0.66667
19 | Dhanmondi | 132 | 135 | 20 | 2020-03-03 | 0.91667 | 122 | 11 | 2020-03-03 | 0.66667
20 | Lalbag | 132 | 138 | 3 | 2020-03-03 | 9:00 | 121 | 4 | 2020-03-03 | 0.5
21 | Madartek | 132 | 135 | 20 | 2020-03-03 | 0.91667 | 122 | 11 | 2020-03-03 | 0.66667
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Mirpur | 132 | 137 | 4 | 2020-03-03 | 0.25 | 123 | 18 | 2020-03-03 | 16:00
24 | Kalyanpur | 132 | 136 | 6 | 2020-03-03 | 0.58333 | 124 | 18 | 2020-03-03 | 0.66667
25 | Gulshan | 132 | 135 | 7 | 2020-03-03 | 0.16667 | 122 | 1 | 2020-03-03 | 0.5
26 | Uttara | 132 | 136 | 3 | 2020-03-03 | 0.25 | 122 | 18 | 2020-03-03 | 0.5
27 | Uttara(New) | 132 | 136 | 1 | 2020-03-03 | 0.20833 | 122 | 2 | 2020-03-03 | 0.45833
28 | Kamrangirchar | 132 | 136 | 13 | 2020-03-03 | 0.77083 | 120 | 18 | 2020-03-03 | 0.66667
29 | Savar | 132 | 135 | 1 | 2020-03-03 | 0.20833 | 122 | 18 | 2020-03-03 | 0.5
30 | Bhasantec | 132 | 135 | 1 | 2020-03-03 | 0.20833 | 123 | 16 | 2020-03-03 | 0.625
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Agargaon | 132 | 136 | 1 | 2020-03-03 | 0.20833 | 124 | 18 | 2020-03-03 | 0.41667
32 | Satmosjid | 132 | 136 | 4 | 2020-03-03 | 0.20833 | 124 | 1 | 2020-03-03 | 0.5
33 | Tongi | 132 | 141 | 3 | 2020-03-03 | 0.33333 | 125 | 23 | 2020-03-03 | 0.8125
34 | Kabirpur | 132 | 140 | 21 | 2020-03-03 | 0.95833 | 123 | 1 | 2020-03-03 | 0.45833
35 | Basundhara | 132 | 140 | 26 | 2020-03-03 | 19:30 | 122 | 5 | 2020-03-03 | 0.58333
36 | Manikganj | 132 | 142 | 21 | 2020-03-03 | 24:00 | 113 | 23 | 2020-03-03 | 0.625
37 | Joydevpur | 132 | 142 | 3 | 2020-03-03 | 24:00 | 132 | 5 | 2020-03-03 | 0.625
38 | New Tongi | 132 | 140 | 27 | 2020-03-03 | 0.79167 | 124 | 5 | 2020-03-03 | 0.625
39 | Kodda | 132 | 141 | 11 | 2020-03-03 | 0.83333 | 116 | 5 | 2020-03-03 | 0.625
40 | Dhamrai | 132 | 139 | 21 | 2020-03-03 | 0.95833 | 121 | 1 | 2020-03-03 | 0.5
41 | Rajendrapur | 132 | 140 | 3 | 2020-03-03 | 0.25 | 118 | 18 | 2020-03-03 | 0.33333
42 | Valuka | 132 | 135 | 22 | 2020-03-03 | 0.041667 | 112 | 18 | 2020-03-03 | 0.45833
43 | Tangail | 132 | 136 | 21 | 2020-03-03 | 0.95833 | 117 | 1 | 2020-03-03 | 0.45833
44 | Mymensing | 132 | 137 | 6 | 2020-03-03 | 0.58333 | 114 | 25 | 2020-03-03 | 0.58333
45 | Kishorganj | 132 | 137 | 22 | 2020-03-03 | 0.041667 | 119 | 25 | 2020-03-03 | 0.58333
46 | Netrokona | 132 | 136 | 6 | 2020-03-03 | 0.66667 | 109 | 27 | 2020-03-03 | 0.77083
47 | Jamalpur | 132 | 140 | 6 | 2020-03-03 | 0.58333 | 113 | 1 | 2020-03-03 | 7:00
48 | Sherpur | 132 | 140 | 6 | 2020-03-03 | 0.58333 | 109 | 25 | 2020-03-03 | 14:00
49 | Srimongal | 132 | 140 | 5 | 2020-03-03 | 0.25 | 133 | 16 | 2020-03-03 | 0.625
50 | Shahjibazar | 132 | 138 | 29 | 2020-03-03 | 4:00 | 130 | 16 | 2020-03-03 | 0.625
51 | Fenchuganj | 132 | 138 | 2 | 2020-03-03 | 0.16667 | 132 | 16 | 2020-03-03 | 16:00
52 | Khulawara | 132 | 138 | 3 | 2020-03-03 | 0.125 | 132 | 11 | 2020-03-03 | 0.75
53 | Sylhet | 132 | 136 | 1 | 2020-03-03 | 0.041667 | 129 | 19 | 2020-03-03 | 0.45833
54 | Chattak | 132 | 140 | 1 | 2020-03-03 | 0.16667 | 128 | 19 | 2020-03-03 | 0.54167
55 | Sunamganj | 132 | 136 | 2 | 2020-03-03 | 0.041667 | 127 | 12 | 2020-03-03 | 0.75
56 | Biani Bazar | 132 | 137 | 5 | 2020-03-03 | 0.083333 | 128 | 19 | 2020-03-03 | 14:00
57 | Comilla(South) | 132 | 134 | 8 | 2020-03-03 | 0.16667 | 121 | 29 | 2020-03-03 | 0.77083
58 | Comilla (North) | 132 | 140 | 3 | 2020-03-03 | 0.8125 | 126 | 25 | 2020-03-03 | 0.625
59 | Chandpur | 132 | 137 | 3 | 2020-03-03 | 8:00 | 115 | 25 | 2020-03-03 | 0.45833
60 | Feni | 132 | 137 | 3 | 2020-03-03 | 0.41667 | 121 | 27 | 2020-03-03 | 0.625
61 | Chowmuhani | 132 | 134 | 3 | 2020-03-03 | 0.29167 | 115 | 24 | 2020-03-03 | 1899-12-31
62 | Ashuganj | 132 | 139 | 22 | 2020-03-03 | 0.25 | 131 | 16 | 2020-03-03 | 0.625
63 | Daudkandi | 132 | 139 | 3 | 2020-03-03 | 0.33333 | 112 | 30 | 2020-03-03 | 0.625
64 | Brahminbaria | 132 | 136 | 13 | 2020-03-03 | 0.29167 | 127 | 16 | 2020-03-03 | 0.83333
65 | Ramganj | 132 | 133 | 3 | 2020-03-03 | 0.375 | 111 | 25 | 2020-03-03 | 0.625
66 | Chaddagram | 132 | 136 | 3 | 2020-03-03 | 0.375 | 121 | 25 | 2020-03-03 | 0.625
67 | PHP | 132 | 135 | 3 | 2020-03-03 | 0.375 | 119 | 25 | 2020-03-03 | 0.625
68 | Madanhat | 132 | 135 | 7 | 2020-03-03 | 0.79167 | 127 | 6 | 2020-03-03 | 0.95833
69 | Hathazari | 132 | 135 | 7 | 2020-03-03 | 0.83333 | 126 | 31 | 2020-03-03 | 1899-12-31
70 | Khulshi | 132 | 132 | 7 | 2020-03-03 | 0.8125 | 121 | 6 | 2020-03-03 | 0.95833
71 | Halishahar | 132 | 135 | 7 | 2020-03-03 | 0.8125 | 124 | 25 | 2020-03-03 | 0.45833
72 | Baraulia | 132 | 134 | 7 | 2020-03-03 | 0.83333 | 123 | 23 | 2020-03-03 | 0.66667
73 | Sikalbaha | 132 | 135 | 7 | 2020-03-03 | 0.83333 | 125 | 18 | 2020-03-03 | 0.66667
74 | Dohazari | 132 | 132 | 2 | 2020-03-03 | 0.83333 | 121 | 18 | 2020-03-03 | 0.66667
75 | Cox'sbazar | 132 | 127 | 3 | 2020-03-03 | 0.5 | 108 | 19 | 2020-03-03 | 0.77083
76 | Chandraghona | 132 | 134 | 7 | 2020-03-03 | 0.8125 | 126 | 23 | 2020-03-03 | 0.625
77 | Kaptai | 132 | 133 | 2 | 2020-03-03 | 0.8125 | 126 | 9 | 2020-03-03 | 0.54167
78 | A. Khaer Stl. | 132 | 137 | 21 | 2020-03-03 | 0.20833 | 122 | 12 | 2020-03-03 | 0.75
79 | Bakulia | 132 | 133 | 20 | 2020-03-03 | 0.8125 | 124 | 25 | 2020-03-03 | 0.45833
80 | Julda | 132 | 133 | 7 | 2020-03-03 | 0.79167 | 125 | 7 | 2020-03-03 | 0.66667
81 | TK Chemical | 132 | 134 | 7 | 2020-03-03 | 0.83333 | 125 | 25 | 2020-03-03 | 0.625
82 | Modern Steel | 132 | 133 | 7 | 2020-03-03 | 0.8125 | 124 | 23 | 2020-03-03 | 0.625
83 | Shahmirpur | 132 | 133 | 7 | 2020-03-03 | 0.79167 | 125 | 18 | 2020-03-03 | 0.66667
84 | Khagrachhari | 132 | 133 | 3 | 2020-03-03 | 0.45833 | 120 | 13 | 2020-03-03 | 0.041667
85 | Matarbari | 132 | 132 | 26 | 2020-03-03 | 0.875 | 113 | 2 | 2020-03-03 | 11:00
86 | Baroiar Hat | 132 | 136 | 3 | 2020-03-03 | 0.41667 | 122 | 18 | 2020-03-03 | 0.66667
87 | Rangamati | 132 | 133 | 7 | 2020-03-03 | 0.8125 | 125 | 18 | 2020-03-03 | 0.66667
88 | Goalpara | 132 | 143 | 20 | 2020-03-03 | 0.8125 | 122 | 24 | 2020-03-03 | 12:00
89 | Khulna Central | 132 | 140 | 21 | 2020-03-03 | 0.16667 | 120 | 8 | 2020-03-03 | 18:30
90 | Noapara | 132 | 138 | 7 | 2020-03-03 | 0.16667 | 117 | 12 | 2020-03-03 | 19:00
91 | Jessore | 132 | 137 | 7 | 2020-03-03 | 0.25 | 111 | 12 | 2020-03-03 | 0.79167
92 | Benapol | 132 | 137 | 22 | 2020-03-03 | 0.20833 | 115 | 12 | 2020-03-03 | 0.79167
93 | Jhenida | 132 | 138 | 21 | 2020-03-03 | 0.95833 | 112 | 12 | 2020-03-03 | 0.79167
94 | Bottail | 132 | 139 | 3 | 2020-03-03 | 0.25 | 122 | 19 | 2020-03-03 | 0.29167
95 | G.K Project | 132 | 141 | 2 | 2020-03-03 | 0.20833 | 129 | 19 | 2020-03-03 | 0.29167
96 | Faridpur | 132 | 140 | 3 | 2020-03-03 | 0.29167 | 122 | 11 | 2020-03-03 | 0.79167
97 | Madaripur | 132 | 144 | 3 | 2020-03-03 | 0.29167 | 121 | 11 | 2020-03-03 | 0.77083
98 | Sariatpur | 132 | 148 | 3 | 2020-03-03 | 0.29167 | 122 | 11 | 2020-03-03 | 0.75
99 | Gopalganj | 132 | 151 | 3 | 2020-03-03 | 0.29167 | 124 | 11 | 2020-03-03 | 0.77083
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Bagerhat | 132 | 138 | 22 | 2020-03-03 | 0.25 | 116 | 12 | 2020-03-03 | 0.77083
101 | Mongla | 132 | 138 | 22 | 2020-03-03 | 0.20833 | 116 | 24 | 2020-03-03 | 0.77083
102 | Satkhira | 132 | 140 | 22 | 2020-03-03 | 0.25 | 116 | 24 | 2020-03-03 | 0.5
103 | Gallamari | 132 | 140 | 20 | 2020-03-03 | 0.25 | 121 | 12 | 2020-03-03 | 0.79167
104 | Magura | 132 | 139 | 21 | 2020-03-03 | 0.95833 | 110 | 16 | 2020-03-03 | 0.77083
105 | Norail | 132 | 136 | 21 | 2020-03-03 | 0.95833 | 108 | 29 | 2020-03-03 | 0.79167
106 | Chuadanga | 132 | 136 | 3 | 2020-03-03 | 0.25 | 105 | 28 | 2020-03-03 | 0.79167
107 | Barisal(N) | 132 | 143 | 6 | 2020-03-03 | 0.125 | 128 | 11 | 2020-03-03 | 0.77083
108 | Barisal(S) | 132 | 143 | 3 | 2020-03-03 | 0.29167 | 127 | 2 | 2020-03-03 | 0.77083
109 | Patuakhali | 132 | 141 | 3 | 2020-03-03 | 0.29167 | 122 | 28 | 2020-03-03 | 0.8125
110 | Bhandaria | 132 | 142 | 5 | 2020-03-03 | 0.75 | 125 | 4 | 2020-03-03 | 0.77083
111 | Ishurdi | 132 | 138 | 2 | 2020-03-03 | 0.16667 | 126 | 19 | 2020-03-03 | 0.29167
112 | Ruppur paromanobik | 132 | 138 | 3 | 2020-03-03 | 0.125 | 127 | 19 | 2020-03-03 | 0.29167
113 | Natore | 132 | 137 | 4 | 2020-03-03 | 0.75 | 122 | 24 | 2020-03-03 | 0.83333
114 | Bogra | 132 | 140 | 19 | 2020-03-03 | 0.83333 | 122 | 12 | 2020-03-03 | 8:00
115 | Noagaon | 132 | 139 | 19 | 2020-03-03 | 0.875 | 115 | 31 | 2020-03-03 | 0.33333
116 | Rajshahi | 132 | 135 | 4 | 2020-03-03 | 0.70833 | 119 | 18 | 2020-03-03 | 0.5
117 | Rajshahi New | 132 | 134 | 4 | 2020-03-03 | 0.66667 | 117 | 18 | 2020-03-03 | 0.5
118 | C.Nawabganj | 132 | 136 | 7 | 2020-03-03 | 0.25 | 114 | 28 | 2020-03-03 | 0.5
119 | Amnura | 132 | 136 | 4 | 2020-03-03 | 0.66667 | 115 | 28 | 2020-03-03 | 0.5
120 | Pabna | 132 | 136 | 2 | 2020-03-03 | 0.125 | 120 | 17 | 2020-03-03 | 0.33333
121 | Shahjadpur | 132 | 144 | 22 | 2020-03-03 | 4:00 | 113 | 12 | 2020-03-03 | 19:30
122 | Serajganj | 132 | 138 | 2 | 2020-03-03 | 0.125 | 120 | 12 | 2020-03-03 | 19:30
123 | Niyamatpur | 132 | 134 | 6 | 2020-03-03 | 0.58333 | 111 | 19 | 2020-03-03 | 0.29167
124 | Joypurhat | 132 | 137 | 6 | 2020-03-03 | 0.58333 | 111 | 29 | 2020-03-03 | 0.29167
125 | Sherpur(Bogura) | 132 | 142 | 19 | 2020-03-03 | 0.8125 | 119 | 25 | 2020-03-03 | 0.79167
126 | Mohastangor | 132 | 139 | 22 | 2020-03-03 | 0.041667 | 123 | 1 | 2020-03-03 | 0.33333
127 | Rangpur | 132 | 137 | 22 | 2020-03-03 | 0.041667 | 116 | 2 | 2020-03-03 | 0.33333
128 | Lalmonirhat | 132 | 133 | 22 | 2020-03-03 | 0.041667 | 110 | 18 | 2020-03-03 | 0.33333
129 | Saidpur | 132 | 138 | 22 | 2020-03-03 | 0.041667 | 115 | 2 | 2020-03-03 | 0.33333
130 | Purbasadipur | 132 | 133 | 22 | 2020-03-03 | 0.083333 | 110 | 26 | 2020-03-03 | 0.79167
131 | Thakurgaon | 132 | 136 | 22 | 2020-03-03 | 0.041667 | 110 | 1 | 2020-03-03 | 0.33333
132 | Palashbari | 132 | 138 | 22 | 2020-03-03 | 0.041667 | 115 | 1 | 2020-03-03 | 0.33333
133 | Barapukuria | 132 | 140 | 6 | 2020-03-03 | 0.45833 | 123 | 26 | 2020-03-03 | 0.79167
134 | Panchagar | 132 | 136 | 22 | 2020-03-03 | 0.041667 | 105 | 2 | 2020-03-03 | 0.33333
135 | Joldhaka | 132 | 137 | 22 | 2020-03-03 | 0.041667 | 113 | 26 | 2020-03-03 | 0.79167
136 | Kurigram | 132 | 138 | 6 | 2020-03-03 | 0.25 | 111 | 18 | 2020-03-03 | 0.33333
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:March' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 142 | 375
Hasnabad | TR2 | 225 | 128 | 375 | 14.03.2020 | 11:00
| TR3 | 225 | 118 | 370
| TR1 | 225 | 160 | 490
Tongi | TR2 | 225 | 160 | 490 | 13.03.2020 | 12:00
| TR3 | 225 | 160 | 490
Haripur | TR1 | 225 | 88 | 250 | 22.03.2020 | 10:00
| TR3 | 225 | 88 | 250
| TR1 | 225 | 151 | 420
Rampura | TR2 | 225 | 151 | 420 | 16.03.2020 | 16:00
| TR3 | 225 | 151 | 420
| TR1 | 225 | 112 | 322
Aminbazar | TR2 | 225 | 112 | 322 | 08.03.2020 | 14:00
| TR3 | 225 | 116 | 322
Maniknagar | TR1 | 300 | 107 | 320 | 19.03.2020 | 13:00
| TR2 | 300 | 107 | 320
Cumilla (N) | TR1 | 225 | 194 | 554 | 21.03.2020 | 23:00
| TR2 | 225 | 192 | 551
Fenchuganj | TR1 | 300 | 278 | 686 | 09.03.2020 | 08':00
| MT1 | 150 | 91 | 270
Hathazari | MT2 | 150 | 91 | 270 | 21.03.2020 | 24:00
| MT3 | 150 | 91 | 270
| MT4 | 150 | 91 | 270
| TR1 | 225 | 160 | 430
Ishurdi | TR2 | 225 | 160 | 430 | 19.03.2020 | 19:30
| TR3 | 225 | 160 | 430
Khulna(S) | TR1 | 225 | 122 | 346
| TR2 | 225 | 122 | 346 | 29.03.2020 | 19:00
| TR3 | 300 | 160 | 447
Bogra | TR1 | 225 | 156 | 449 | 02.03.2020 | 19:30
| TR2 | 225 | 156 | 449
| TR3 | 225 | 211 | 585
Baghabari | TR1 | 300 | 124 | 340 | 24.03.2020 | 19:00
| TR2 | 225 | 93 | 250
Barapukuria | TR1 | 225 | 181 | 890 | 09.03.2020 | 8:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 153 | 740 |  |  | 132 kV current is being provided
| TR6 | 300 | 198 | 980
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:March' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 213 | 355 | 06.03.2020 | 14:00
| TR2(400/230 kV) | 520 | 213 | 355
| TR1(400/132 kV) | 325 | 217 | 364 | 21.03.2020 | 19:00
| TR2(400/132 kV) | 325 | 217 | 364
Bibiyana | ICT1(400/230 kV) | 520 | 117 | 191 | 19.03.2020 | 8:00
| ICT2(400/230kV) | 520 | 116 | 193
Bhulta | ATR1(400/230 kV) | 520 | 190 | 340 | 25.03.2020 | 11:15
| ATR2(400/230kV) | 520 | 190 | 340
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-03-20 | 9719 | 9719 | - | - | - | - | - | - | - | - | - | - | - | - | 01-03-20 | 8291.6 | 8291.6 | - | - | - | - | - | - | - | - | - | - | - | -
02-03-20 | 9756 | 9756 | - | - | - | - | - | - | - | - | - | - | - | - | 02-03-20 | 8214.4 | 8214.4 | - | - | - | - | - | - | - | - | - | - | - | -
03-03-20 | 9340 | 9340 | - | - | - | - | - | - | - | - | - | - | - | - | 03-03-20 | 7364.1 | 7364.1 | - | - | - | - | - | - | - | - | - | - | - | -
04-03-20 | 9315 | 9315 | - | - | - | - | - | - | - | - | - | - | - | - | 04-03-20 | 8194.6 | 8194.6 | - | - | - | - | - | - | - | - | - | - | - | -
05-03-20 | 9481 | 9481 | - | - | - | - | - | - | - | - | - | - | - | - | 05-03-20 | 8137.5 | 8137.5 | - | - | - | - | - | - | - | - | - | - | - | -
06-03-20 | 8460 | 8460 | - | - | - | - | - | - | - | - | - | - | - | - | 06-03-20 | 6439.1 | 6439.1 | - | - | - | - | - | - | - | - | - | - | - | -
07-03-20 | 9346 | 9346 | - | - | - | - | - | - | - | - | - | - | - | - | 07-03-20 | 7538.8 | 7538.8 | - | - | - | - | - | - | - | - | - | - | - | -
08-03-20 | 9578 | 9578 | - | - | - | - | - | - | - | - | - | - | - | - | 08-03-20 | 8004.9 | 8004.9 | - | - | - | - | - | - | - | - | - | - | - | -
09-03-20 | 9589 | 9589 | - | - | - | - | - | - | - | - | - | - | - | - | 09-03-20 | 7925.8 | 7925.8 | - | - | - | - | - | - | - | - | - | - | - | -
10-03-20 | 9732 | 9732 | - | - | - | - | - | - | - | - | - | - | - | - | 10-03-20 | 8077.3 | 8077.3 | - | - | - | - | - | - | - | - | - | - | - | -
11-03-20 | 9954 | 9954 | - | - | - | - | - | - | - | - | - | - | - | - | 11-03-20 | 8257.6 | 8257.6 | - | - | - | - | - | - | - | - | - | - | - | -
12-03-20 | 10623 | 10623 | - | - | - | - | - | - | - | - | - | - | - | - | 12-03-20 | 8799.3 | 8799.3 | - | - | - | - | - | - | - | - | - | - | - | -
13-03-20 | 9853 | 9853 | - | - | - | - | - | - | - | - | - | - | - | - | 13-03-20 | 7738.4 | 7738.4 | - | - | - | - | - | - | - | - | - | - | - | -
14-03-20 | 9582 | 9582 | - | - | - | - | - | - | - | - | - | - | - | - | 14-03-20 | 7866.1 | 7866.1 | - | - | - | - | - | - | - | - | - | - | - | -
15-03-20 | 10361 | 10361 | - | - | - | - | - | - | - | - | - | - | - | - | 15-03-20 | 8519.1 | 8519.1 | - | - | - | - | - | - | - | - | - | - | - | -
16-03-20 | 10610 | 10610 | - | - | - | - | - | - | - | - | - | - | - | - | 16-03-20 | 9230.1 | 9230.1 | - | - | - | - | - | - | - | - | - | - | - | -
17-03-20 | 9995 | 9995 | - | - | - | - | - | - | - | - | - | - | - | - | 17-03-20 | 8338.8 | 8338.8 | - | - | - | - | - | - | - | - | - | - | - | -
18-03-20 | 10790 | 10790 | - | - | - | - | - | - | - | - | - | - | - | - | 18-03-20 | 9428.9 | 9428.9 | - | - | - | - | - | - | - | - | - | - | - | -
19-03-20 | 10593 | 10593 | - | - | - | - | - | - | - | - | - | - | - | - | 19-03-20 | 9219.8 | 9219.8 | - | - | - | - | - | - | - | - | - | - | - | -
20-03-20 | 9727 | 9727 | - | - | - | - | - | - | - | - | - | - | - | - | 20-03-20 | 7792.2 | 7792.2 | - | - | - | - | - | - | - | - | - | - | - | -
21-03-20 | 10529 | 10529 | - | - | - | - | - | - | - | - | - | - | - | - | 21-03-20 | 7808.8 | 7808.8 | - | - | - | - | - | - | - | - | - | - | - | -
22-03-20 | 10186 | 10186 | - | - | - | - | - | - | - | - | - | - | - | - | 22-03-20 | 8544.4 | 8544.4 | - | - | - | - | - | - | - | - | - | - | - | -
23-03-20 | 10093 | 10093 | - | - | - | - | - | - | - | - | - | - | - | - | 23-03-20 | 8829.3 | 8829.3 | - | - | - | - | - | - | - | - | - | - | - | -
24-03-20 | 10264 | 10264 | - | - | - | - | - | - | - | - | - | - | - | - | 24-03-20 | 8812.3 | 8812.3 | - | - | - | - | - | - | - | - | - | - | - | -
25-03-20 | 9939 | 9939 | - | - | - | - | - | - | - | - | - | - | - | - | 25-03-20 | 8801.1 | 8801.1 | - | - | - | - | - | - | - | - | - | - | - | -
26-03-20 | 9492 | 9492 | - | - | - | - | - | - | - | - | - | - | - | - | 26-03-20 | 7486.4 | 7486.4 | - | - | - | - | - | - | - | - | - | - | - | -
27-03-20 | 9834 | 9834 | - | - | - | - | - | - | - | - | - | - | - | - | 27-03-20 | 7907.4 | 7907.4 | - | - | - | - | - | - | - | - | - | - | - | -
28-03-20 | 10217 | 10217 | - | - | - | - | - | - | - | - | - | - | - | - | 28-03-20 | 7963.5 | 7963.5 | - | - | - | - | - | - | - | - | - | - | - | -
29-03-20 | 9915 | 9915 | - | - | - | - | - | - | - | - | - | - | - | - | 29-03-20 | 7840.6 | 7840.6 | - | - | - | - | - | - | - | - | - | - | - | -
30-03-20 | 9700 | 9700 | - | - | - | - | - | - | - | - | - | - | - | - | 30-03-20 | 7587.6 | 7587.6 | - | - | - | - | - | - | - | - | - | - | - | -
31-03-20 | 9663 | 9663 | [12 empty] | 31-03-20 | 7886.4 | 7886.4

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10790 | 18/03/20 | 19:30
2 | Maximum Day Peak Genaration | MW | 9428.9 | 18/03/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 10790 | 18/03/20 | 19:30
4 | Minimum Generation | MW | 5676.1 | 03/03/20 | 5:00
5 | Average of the daily evening peak Genaration | MW | 9878.5806
6 | Average of the daily day peak Genaration | MW | 8156.329
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5938.0149
12 | Total Generation by BPDB | MKWH | 3442.7368 | % of total Gen. | 57.98%
13 | Total Generation by IPP | MKWH | 1469.8465 | '' | 24.75%
14 | A) Total Generation by RPCL | MKWH | 138.3437 | '' | 2.33%
| B) Total Generation by REB | MKWH | 135.7736 | " | 2.287%
| C) Total Generation by RENTAL | MKWH | 297.8023 | " | 5.015%
| D) Total Imported from India (HVDC) | MKWH | 375.9582 | " | 6.331%
| E) Total Imported from Tripura, India (A.C) | MKWH | 77.5538 | " | 1.306%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4372.4084 | % of total Gen. | 73.63%
| B) Oil | MKWH | 694.1248 | '' | 11.69%
| C) Hydro | MKWH | 49.3088 | '' | 0.8304%
| D) Solar | MKWH | 6.9723 | '' | 0.1174%
| E) Coal | MKWH | 361.6886 | '' | 6.091%
| F) HVDC (Import from India) | MKWH | 375.9582 | '' | 6.331%
| G) A.C (Import from Tripura, India) | MKWH | 77.5538 | '' | 1.306%
16 | Maximun of the daily total Generation . | MKWH | 213.1719 | 19/03/2020
17 | Monthly Load factor | % | 73.9685
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 10750.8703
| A) Gas | M.Taka | 4082.6337
| B) Liquid fuel | M.Taka | 5431.5705
| C) Coal | M.Taka | 1236.6661
| D) HVDC (Import from India) | M.Taka | 1917.3867
| E) Tripura(Import from India) | M.Taka | 581.6535
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 545.6572 | 19/03/2020
| A) Gas | M.Taka | 165.4358 | 31/03/2020
| B) Liquid fuel | M.Taka | 370.0248 | 19/03/2020
| C) Coal | M.Taka | 79.2467 | 31/03/2020
| D) HVDC (Import from India) | M.Taka | 90.1495 | 25-03-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.5797
| B) Excluding Hydro & Solar | Taka/KWHR | 2.604
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.51 | 31/03/2020 | 06:00
b) | Actual | FT (MSL) | 88.17 | 31/01/2020 | 06:00
22 | Peak Genaration of March 2019 | MW | 10933 | 30/03/19 | 20:00
23 | Peak Demand of March 2019 | MW | 10933 | 30/03/19 | 20:00
24 | Maximum peak Generation recorded upto 31/03/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/03/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.