## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-04-27 | Monday
|  | Date (day): | 2020-04-27 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11959.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15040 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-04-26 | 2020-04-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 250 | 300 | 300 | 65 |  | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 107 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 339 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 272 | 323 | 310 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 390 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 135 | 125 | 135 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 12 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 10 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 37 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 160 | 180 | 150 | 217 |  | 118 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 35 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1631 | 1910 | 3413 | 4245 | 621 | 939
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 37 | 37 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 224 | 223 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 107 | 139 | 140 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 42 | 42 | 42
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0.4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 0 | 0 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 516.1 | 563 | 1608 | 1718 | 450 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 100 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 186 | 200 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 310 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 260 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 40 | 40 | 40
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 20 | 5 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 16 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 92 | 118 | 141
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 8 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 958 | 1183 | 1657 | 2305 | 485 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 204 | 198 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.8 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 65 | 170 | 170 |  | 30 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 237.8 | 283 | 611.6 | 610 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 57 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 150 | 150 | 150 |  | 180 | GT-1 Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 28 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 51 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 40 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 50 | 81 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 79 | 150 | 100 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 777 | 1020 | 1121 | 1171 | 0 | 670
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 301 | 299 | 307 | 850
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 330 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 676 | 645 | 1092 | 2095 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 8 | 20 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 120 |  | 68 | ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 300 | 401 | 300 | 400 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 368 | 481 | 519 | 775 | 0 | 81
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 40 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 180 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 147 | 198 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 347 | 429 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 17 | 17 | 17
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 685 | 913 | 1617 | 1776 | 320 | 17
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 70 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 38 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 227.6 | 258 | 321 | 345 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 6076.5 | 7256 | 11959.6 | 15040 | 2046 | 1968
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5747.3842 | 6863 | 11311.8433 | 14225.4024
A. |  | 2020-04-26 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 7256 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 4694 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7256 | MW
3 | Day peak Generation : |  |  | 6076.5 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6863 | MW
4 | Evening peak Generation : |  |  | 7256 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 145.8168 | MKWHr | By Solar | 0.1474 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 118.852 | MKWHr |  | By Oil: | 4.2101 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 12.7421 | MKWHr |  | By Hydro: | 0.85225 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2046 | MW | Dhaka | 2079 | 2079 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1968 | MW | Chittagong | 635 | 635 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4014 | MW | Khulna | 972 | 972 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 973.11 | MMCFD |  |  | Rajshahi | 818 | 818 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 133953238.392 | ii) Oil : | Taka | 11765865.1 | Comilla | 664 | 664 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 62499904.43 | Total | Taka | 208219007.922 | Mymensingh | 653 | 653 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.968 | MKWHr. | Sylhet | 322 | 322 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -250 | MW (E to W) at | 21:00 | hrs | Barisal | 190 | 190 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -303 | MW at | 2:00 | hrs | Rangpur | 530 | 530 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.7° C |  |  | Total | 6863 | 6863 |  | 0
B. |  | 2020-04-27 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 32.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15040 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
4 | Reserve(Generation end) |  |  |  | 6540 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 170.8163 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4535.6 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 7.3695 | MKWHr. | ii) HVDC Flow at Peak Time |  | 299 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6435 | MKWHr. | iii) Maximum HVDC Flow : |  | 622 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.74 |  | (b) Today: | 78.74 |  | (c) Rule Curve: |  | 82.8
.

## YesterdayGen
2020-04-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 335 | 245 |  | 0 | 300 | 135 | 0 | 0 | 0 | 140 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 217 | 0 | 94 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 260 | 250 | 170 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 74 | 184 | 0 | 20 | 0 | 56 | 0 | 5 | 5 | 100 | 150 | 40 | 5 | 0 | 100 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 622 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 72 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 3879 | 2184 | 6063 | 3230 | 622 | 1441 | 135 | 523 | 38 | 0 | 74 | 0 | 0 | 78.75
2:00 | 24 | 0 | 0 | 0 | 220 | 12 | 0 | 367 | 260 |  | 0 | 320 | 135 | 0 | 0 | 0 | 140 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 216 | 0 | 97 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 295 | 285 | 183 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 76 | 183 | 0 | 20 | 0 | 56 | 0 | 5 | 5 | 100 | 210 | 40 | 5 | 0 | 110 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 257 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 70 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 |  | 4148 | 1855 | 6003 | 3462 | 257 | 1513 | 135 | 522 | 38 | 0 | 76 | 0 | 0 | 78.75
3:00 | 24 | 0 | 0 | 0 | 240 | 12 | 0 | 357 | 360 |  | 0 | 400 | 135 | 0 | 0 | 0 | 170 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 216 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 320 | 280 | 192 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 90 | 211 | 0 | 20 | 0 | 56 | 0 | 5 | 5 | 130 | 200 | 64 | 5 | 0 | 150 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 257 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 70 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4595 | 2027 | 6622 | 3843 | 257 | 1736 | 138 | 521 | 37 | 0 | 90 | 0 | 0 | 78.75
4:00 | 24 | 0 | 0 | 0 | 280 | 12 | 0 | 345 | 300 |  | 0 | 380 | 130 | 0 | 0 | 0 | 170 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 216 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 310 | 265 | 177 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 92 | 213 | 0 | 20 | 0 | 56 | 0 | 5 | 5 | 130 | 190 | 64 | 5 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 258 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 71 | 0 | 149 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4415 | 1952 | 6367 | 3735 | 258 | 1595 | 130 | 521 | 36 | 0 | 92 | 0 | 0 | 78.74
5:00 | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 306 | 240 |  | 0 | 300 | 120 | 0 | 0 | 0 | 80 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 240 | 230 | 142 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 167 | 0 | 0 | 0 | 56 | 0 | 5 | 5 | 100 | 143 | 40 | 5 | 0 | 80 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 257 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 |  | 3509 | 1613 | 5122 | 2900 | 257 | 1267 | 120 | 483 | 35 | 0 | 60 | 0 | 0 | 78.74
6:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 255 | 240 |  | 0 | 280 | 110 | 0 | 0 | 0 | 60 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 230 | 215 | 129 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 168 | 0 | 0 | 0 | 56 | 0 | 5 | 5 | 100 | 144 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 257 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 250 |  | 3170.9 | 1523.1 | 4694 | 2720 | 257 | 1093 | 110 | 470 | 35 | 0 | 8 | 1 | 0 | 78.74
7:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 250 | 220 |  | 0 | 280 | 110 | 0 | 0 | 0 | 60 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 25 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 80 | 0 | 0 | 250 | 220 | 129 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 167 | 0 | 0 | 0.4 | 56 | 0 | 5 | 5 | 100 | 145 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 257 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 252 |  | 3142.1 | 1558.7 | 4700.8 | 2723 | 257 | 1083 | 110 | 472 | 36 | 0 | 16 | 3.8 | 0 | 78.73
8:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 285 | 240 |  | 0 | 300 | 130 | 0 | 0 | 0 | 80 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 80 | 0 | 0 | 250 | 245 | 166 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 208 | 0 | 0 | 0.9 | 57 | 0 | 5 | 5 | 100 | 152 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 |  | 3429.2 | 1618 | 5047.2 | 2942 | 255 | 1164 | 133 | 471 | 36 | 0 | 34 | 12.2 | 0 | 78.73
9:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 368 | 242 |  | 0 | 300 | 135 | 0 | 0 | 0 | 80 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 184 | 0 | 113 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 80 | 0 | 0 | 300 | 305 | 183 | 8 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 204 | 0 | 17 | 0.7 | 58 | 0 | 5 | 5 | 100 | 163 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 270 |  | 3841.1 | 1772.4 | 5613.5 | 3295 | 302 | 1298 | 140 | 491 | 36 | 0 | 42 | 9.5 | 0 | 78.73
10:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 371 | 242 |  | 0 | 300 | 135 | 0 | 0 | 0 | 130 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 80 | 0 | 0 | 295 | 300 | 183 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56 | 204 | 0 | 17 | 1 | 58 | 0 | 5 | 5 | 100 | 155 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 10 |  | 302 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 299 |  | 3984.4 | 1925.8 | 5910.2 | 3440 | 302 | 1377 | 161 | 520 | 37 | 0 | 56 | 17.2 | 0 | 78.73
11:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 374 | 272 |  | 0 | 330 | 135 | 0 | 12 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 295 | 295 | 183 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 62 | 204 | 0 | 17 | 0.8 | 58 | 0 | 5 | 5 | 100 | 160 | 40 | 5 | 0 | 79 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 8 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0 | 300 |  | 4119.9 | 1956.6 | 6076.5 | 3541 | 301 | 1428 | 163 | 521 | 37 | 0 | 62 | 23.5 | 0 | 78.73
12:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 369 | 272 |  | 0 | 330 | 135 | 0 | 15 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 224 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 80 | 0 | 0 | 285 | 290 | 183 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 68 | 204 | 0 | 17 | 0.8 | 58 | 0 | 5 | 5 | 100 | 156 | 40 | 5 | 0 | 100 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 8 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 69 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 0 | 302 |  | 4106.3 | 1967.3 | 6073.6 | 3545 | 302 | 1428 | 166 | 521 | 36 | 0 | 68 | 7.6 | 0 | 78.73
13:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 353 | 271 |  | 0 | 330 | 135 | 0 | 25 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 80 | 0 | 0 | 270 | 270 | 174 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 84 | 207 | 0 | 20 | 0.8 | 58 | 0 | 5 | 5 | 100 | 150 | 40 | 5 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 0 | 298 |  | 4073 | 1949.9 | 6022.9 | 3461 | 302 | 1432 | 176 | 523 | 37 | 0 | 84 | 7.9 | 0 | 78.73
14:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 333 | 242 |  | 0 | 300 | 120 | 0 | 20 | 0 | 100 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 80 | 0 | 0 | 260 | 260 | 164 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 181 | 0 | 20 | 0.9 | 58 | 0 | 5 | 5 | 100 | 140 | 40 | 5 | 0 | 100 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 298 |  | 3801.6 | 1894.5 | 5696.1 | 3254 | 302 | 1333 | 156 | 521 | 37 | 0 | 68 | 25.1 | 0 | 78.73
15:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 265 | 210 |  | 0 | 300 | 120 | 0 | 0 | 0 | 50 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 14 | 0 | 0 | 70 | 0 | 100 | 0 | 0 | 210 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 21 | 80 | 0 | 0 | 280 | 230 | 150 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 179 | 0 | 20 | 0.6 | 59 | 0 | 5 | 5 | 100 | 152 | 40 | 5 | 0 | 49 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0 | 298 |  | 3522.4 | 1737.7 | 5260.1 | 2971 | 302 | 1193 | 120 | 519 | 70 | 0 | 68 | 17.1 | 0 | 78.73
16:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 282 | 242 |  | 0 | 320 | 120 | 0 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 14 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 190 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 260 | 230 | 152 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 180 | 0 | 20 | 0.3 | 58 | 0 | 5 | 5 | 100 | 140 | 40 | 5 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 | 301 |  | 3560.5 | 1770.1 | 5330.6 | 2960 | 302 | 1312 | 120 | 522 | 35 | 0 | 70 | 9.6 | 0 | 78.73
17:00 | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 335 | 262 |  | 0 | 320 | 125 | 0 | 0 | 0 | 80 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 33 | 14 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 190 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 290 | 275 | 150 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 179 | 0 | 20 | 0.3 | 58 | 0 | 5 | 5 | 100 | 142 | 40 | 5 | 0 | 99 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 300 |  | 3772.5 | 1861.4 | 5633.9 | 3159 | 302 | 1412 | 125 | 521 | 36 | 0 | 74 | 4.9 | 0 | 78.73
18:00 | 24 | 0 | 0 | 0 | 200 | 14 | 0 | 333 | 286 |  | 0 | 320 | 125 | 0 | 0 | 0 | 100 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 33 | 20 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 220 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 310 | 260 | 150 | 16 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 80 | 165 | 0 | 20 | 0 | 58 | 0 | 5 | 5 | 100 | 138 | 40 | 5 | 0 | 120 | 19 | 0 | 7 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 0 | 235 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 71 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 301 |  | 4026 | 1946.2 | 5972.2 | 3325 | 302 | 1554 | 155 | 521 | 35 | 0 | 80 | 0.2 | 0 | 78.73
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 0 | 0 | 243 | 83 | 0 | 334 | 345 |  | 0 | 420 | 125 | 0 | 10 | 0 | 160 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 3 | 33 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 145 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 40 | 125 | 0 | 0 | 310 | 260 | 181 | 16 | 0 | 20 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 86 | 184 | 0 | 20 | 0 | 58 | 0 | 5 | 50 | 100 | 138 | 40 | 20 | 0 | 150 | 19 | 0 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 |  | 298 | 0 | 335 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 71 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 |  | 4782 | 2141 | 6923 | 3768 | 298 | 1831 | 295 | 558 | 36 | 51 | 86 | 0 | 0 | 78.73
19:30 | 24 | 0 | 0 | 0 | 250 | 91 | 0 | 338 | 323 |  | 0 | 390 | 125 | 0 | 15 | 0 | 218 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 25 | 5 | 33 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 310 | 260 | 181 | 16 | 0 | 27 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 0 | 88 | 187 | 0 | 20 | 0 | 58 | 0 | 5 | 51 | 130 | 145 | 40 | 50 | 0 | 149 | 19 | 0 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 |  | 299 | 0 | 335 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 70 | 0 | 151 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 375 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 380 |  | 4955 | 2277 | 7232 | 3923 | 299 | 1859 | 375 | 601 | 36 | 51 | 88 | 0 | 0 | 78.73
20:00 | 24 | 0 | 0 | 0 | 250 | 99 | 0 | 334 | 323 |  | 0 | 390 | 120 | 0 | 15 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 25 | 10 | 33 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 310 | 260 | 180 | 16 | 0 | 40 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 8 | 86 | 187 | 0 | 20 | 0 | 58 | 0 | 5 | 51 | 130 | 143 | 40 | 50 | 0 | 149 | 19 | 0 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 71 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 405 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 379 |  | 4880 | 2282 | 7162 | 3899 | 300 | 1912 | 294 | 600 | 37 | 34 | 86 | 0 | 0 | 78.73
21:00 | 24 | 0 | 0 | 0 | 250 | 107 | 0 | 339 | 323 |  | 0 | 390 | 125 | 0 | 15 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 25 | 10 | 33 | 25 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 310 | 260 | 186 | 16 | 0 | 40 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 8 | 92 | 198 | 0 | 20 | 0 | 57 | 0 | 28 | 51 | 130 | 150 | 40 | 50 | 0 | 150 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 70 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 429 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 401 |  | 4959 | 2297 | 7256 | 3939 | 299 | 1992 | 276 | 621 | 37 | 0 | 92 | 0 | 0 | 78.73
22:00 | 24 | 0 | 0 | 0 | 220 | 107 | 0 | 334 | 323 |  | 0 | 350 | 120 | 0 | 15 | 0 | 180 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 10 | 33 | 25 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 260 | 260 | 180 | 16 | 0 | 40 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 8 | 80 | 200 | 0 | 20 | 0 | 59 | 0 | 31 | 51 | 130 | 140 | 40 | 50 | 0 | 150 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 |  | 4786 | 2156 | 6942 | 3783 | 300 | 1905 | 217 | 619 | 38 | 0 | 80 | 0 | 0 | 0
23:00 | 24 | 0 | 0 | 0 | 220 | 42 | 0 | 334 | 283 |  | 0 | 300 | 125 | 0 | 0 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 10 | 33 | 25 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 260 | 260 | 180 | 16 | 0 | 40 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 8 | 80 | 214 | 0 | 20 | 0 | 58 | 0 | 5 | 10 | 110 | 140 | 40 | 10 | 0 | 150 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 |  | 4261 | 1915 | 6176 | 3516 | 299 | 1510 | 192 | 541 | 38 | 0 | 80 | 0 | 0 | 0
24:00 | 24 | 0 | 0 | 0 | 220 | 0 | 0 | 334 | 283 |  | 0 | 300 | 125 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 28 | 25 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 0 | 0 | 260 | 260 | 180 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 213 | 0 | 0 | 0 | 58 | 0 | 2 | 0 | 110 | 140 | 40 | 5 | 0 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 |  | 3831 | 1821 | 5652 | 3262 | 299 | 1376 | 125 | 478 | 38 | 0 | 74 | 0 | 0 | 0
KWH | 488000 | 0 | 0 | 0 | 5127491 | 480909 | 0 | 8017920 | 6481000 |  | 0 | 7961500 | 3022284 | 0 | 160056 | 0 | 3266838 | 0 | 1014000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102057 | 24948 | 600000 | 175140 | 788900 | 644000 | 0 | 0 | 852245 | 0 | 2300000 | 0 | 0 | 5017290 | 0 | 2391316 | 0 |  | 0 | 0 | 89208 | 0 | 0 | 0 | 471408 | 879840 | 2194692 | 0 | 0 | 7082900 | 6378000 | 4106000 | 334545 | 0 | 388872 | 153600 | 0 | 375116 | 0 | 0 | 0 | 131256 | 62460 | 216100 | 199710 | 1643520 | 4511800 | 0 | 364428 | 8900 | 1386000 | 0 | 165600 | 391176 | 2911173 | 3548000 | 1010688 | 340800 | 0 | 2384480 | 95000 | 0 | 49860 | 6978500 | 120555 | 63000 | 0 | 0 | 0 | 0 | 458400 | 0 | 15840 | 81810 | 0 | 0 | 0 | 0 | 34800 | 0 | 0 | 4680 | 0 | 0 | 0 | 0 | 49560 | 8640 |  | 7369455 | 0 | 7305984 | 0 | 113280 | 0 | 0 | 0 | 0 | 0 | 0 | 1413000 | 334600 | 0 | 0 | 0 | 1110000 | 0 | 0 | 0 | 51320 | 0 | 0 | 0 | 0 | 97920 | 85282 | 216846 | 1706181 | 0 | 3654400 | 0 | 0 | 3866800 | 0 | 0 | 0 | 0 | 0 | 4150000 | 0 | 8196782 | 0 | 0 | 0 | 0 | 104640 | 0 | 52013 | 0 | 7381500 |  | 98606811 | 47210003 | 145816814 | 82633822 | 7369455 | 36218203 | 4120877 | 12742081 | 852245 | 89208 | 1643520 | 147403 | 0
Fuel Cost | 800320 | 0 | 0 | 0 | 5691515.01 | 634799.88 | 0 | 8098099.2 | 6675430 |  | 0 | 8678035 | 3354735.24 | 0 | 1102785.84 | 0 | 3397511.52 | 0 | 1754220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006282.02 | 18711 | 450000 | 0 | 0 | 0 | 0 | 0 | 230106.15 | 0 | 4163000 | 0 | 0 | 5468846.1 | 0 | 4065237.2 | 0 |  | 0 | 0 | 865317.6 | 0 | 0 | 0 | 593974.08 | 2613124.8 | 3248144.16 | 0 | 0 | 5241346 | 6378000 | 3777520 | 431563.05 | 0 | 439425.36 | 215040 | 0 | 641448.36 | 0 | 0 | 0 | 166695.12 | 46845 | 378175 | 149782.5 | 12326400 | 4782508 | 0 | 462823.56 | 141866 | 2273040 | 0 | 294768 | 610234.56 | 3318737.22 | 3689920 | 1991055.36 | 650928 | 0 | 4125150.4 | 208050 | 0 | 101714.4 | 7048285 | 90416.25 | 47880 | 0 | 0 | 0 | 0 | 2383680 | 0 | 155865.6 | 956358.9 | 0 | 0 | 0 | 0 | 317376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424729.2 | 57542.4 |  | 42448060.8 | 0 | 7671283.2 | 0 | 890380.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1596690 | 518630 | 0 | 0 | 0 | 2275500 | 0 | 0 | 0 | 395164 | 0 | 0 | 0 | 0 | 188006.4 | 132187.1 | 164152.422 | 10288271.43 | 0 | 19806848 | 0 | 0 | 4524156 | 0 | 0 | 0 | 0 | 0 | 4855500 | 0 | 8114814.18 | 0 | 0 | 0 | 0 | 812006.4 | 0 | 574743.65 | 0 | 32404785 |  | 127235364.04 | 137661179.382 | 264896543.422 | 93085492.442 | 42448060.8 | 40867745.95 | 10900547.5 | 62499904.43 | 230106.15 | 865317.6 | 12326400 | 1672968.55 | 0
Yesterday Day Peak | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 374 | 272 |  | 0 | 330 | 135 | 0 | 12 | 0 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 33 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 107 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 295 | 295 | 183 | 16 | 0 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 62 | 204 | 0 | 17 | 0.8 | 58 | 0 | 5 | 5 | 100 | 160 | 40 | 5 | 0 | 79 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 8 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 0 | 300 |  | 6076.5 | DayPeak
Yesterday Evening Peak | 24 | 0 | 0 | 0 | 250 | 107 | 0 | 339 | 323 | 0 | 0 | 390 | 125 | 0 | 15 | 0 | 180 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 25 | 10 | 33 | 25 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 310 | 260 | 186 | 16 | 0 | 40 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 8 | 92 | 198 | 0 | 20 | 0 | 57 | 0 | 28 | 51 | 130 | 150 | 40 | 50 | 0 | 150 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 70 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 429 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 401 |  | 7256 | EvPeak
Forecast for Evening | 24 | 0 | 0 | 0 | 300 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 217 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 135 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 40 | 20 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 141 | 210 | 95 | 20 | 0 | 60 | 0 | 51 | 44 | 163 | 150 | 66 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 170 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 850 | 40 | 410 |  | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 120 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 0 | 0 | 200 | 17 | 15 | 210 | 0 | 0 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 400
Forecast for Day | 24 | 0 | 0 | 0 | 300 | 108 | 0 | 412 | 310 | 0 | 0 | 450 | 135 | 100 | 100 | 55 | 150 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 100 | 0 | 0 | 360 | 360 | 200 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 118 | 210 | 95 | 20 | 1.6 | 60 | 0 | 51 | 44 | 163 | 150 | 66 | 81 | 0 | 100 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 0 | 0 | 170 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 114 | 113 | 100 |  | 307 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 20 | 50 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 40 | 0 | 17 | 11 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 300
Generation at 08:00(Today) | 24 | 0 | 0 | 0 | 200 | 0 | 0 | 338 | 255 | 0 | 0 | 300 | 110 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 25 | 25 | 0 | 0 | 36 | 0 | 90 | 0 | 0 | 184 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 0 | 230 | 235 | 141 | 8 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 66 | 147 | 0 | 0 | 0.5 | 63 | 0 | 2 | 0 | 100 | 140 | 15 | 1 | 0 | 100 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 0 | 253 | 0
199
| Minimum Generation |  | 4694 | 6:00
| Highest Generation |  | 7256 | 21:00
| Day Peak Generation |  | 6076.5 | 11:00
| Evening Peak Generation |  | 7256 | 21:00
| HVDC Max Flow |  | 622 | 1:00
| HVDC EvPeak Flow |  | 299 | 21:00
| Load factor L.F |  | 83.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-04-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-04-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6076.5 | MW Hour : | 11:00 | Min. Gen. at | 6:00 | 4535.6 | MW
Evening Peak Generation : |  | 7256 | MW Hour : | 21:00 | Available Max Generation : |  | 15040 | MW
E.P. Demand (at gen end) : |  | 7256 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 7256 | MW Hour : | 21:00 | Reserve(Generation end) |  | 6540 | MW
Total Gen. (MKWH) : |  | 145.8168 | System Load Factor : | 83.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -303 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-04-27
Actual : | 78.74 | Ft.(MSL) , | Rule curve : | 82.8 | Ft.( MSL )
Gas Consumed : | Total = | 973.11 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 133953238.392
: |  | Coal : | 62499904.43 | Oil : | 11765865.1 | Total : | 208219007.922
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3006.882 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1015.6836 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 908.8031 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 820.7486 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 741.9367 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 598.6994 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 343.543 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 154.3814 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 461.7047 |  |  | 0 | 0%
Total | 0 |  | 8052.3826 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Bibiyana #3
|  |  |  | 2) Siddhirganj 210 MW GT-1 | 11) Shahjibazar-330 MW GT-1
3) Ghorasal Unit-1,3,4 & 5.
4) Ashuganj unit-4,5
5) Siddirganj-335 MW ST
6) Kaptai-2,5
7) Raozan #1 & 2
8) Fenchuganj 3, 4
9) Chandpur 163 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Chandpur S/S-Chandpur P/S 132 kV Ckt was under shut down from 10:09 to 13:45 for maint. Work.
b) Chapainawabganj 132/33 kV T-4 transformer tripped at 12:46 showing O/C relay due to 33 kV
Godagari feeder fault and was switched on at 12:54.
c) Madanganj 132/33 kV T-1 transformer was under shut down from 12:36 to 15:28 for C/M.
d) Haripur-Rahim Steel 132 kV Ckt tripped at 14:02 showing O/C & E/F relays and was switched on at 15:18.
e) Naogaon 132/33 kV T-3 transformer tripped at 17:03 showing differential relay and was switched on at 17:12.
f) Shariatpur 132/33 kV T-2 transformer was shut down at 21:36 due to red hot maintenance at 33 kV |  |  |  |  | About 25 MW power interruption under Shariatpur S/S area
Y-phase loop join isolator and was switched on at 22:52. |  |  |  |  | from 21:36 to 22:22.
g) Siddirganj Peaking GT-2 was shut down at 23:23 due to low gas pressure.
h) Barapukuria #2 was shut down at 07:59(27/4/20) due to coal shortage.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-04-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 488000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 5127491
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 107 | 480909 | Gas shortage.
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 339 | 8017920 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 6481000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 390 | 7961500 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 125 | 3022284 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 160056 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 24948
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 37 | 1014000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 180 | 3266838 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 102057 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 775140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 644000 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 15840 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1910 | 38370883
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 81810
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 852245 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 223 | 5017290 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 2391316 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 89208 | Reserve
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 471408
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 879840
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 4680
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 0 | 8640 | Reserve
| Chattogram area Total |  |  |  | 2166 | 563 | 12096437
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2194692 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 186 | 4106000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7082900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6378000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 388872
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 153600 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 334545 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 375116
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 131256
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 62460
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 1643520 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 216100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 8 | 199710 | Reserve
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 49560 | Reserve
| Cumilla Area Total |  |  |  | 2980 | 1183 | 23316331
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 198 | 4511800
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 364428
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8900
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 65 | 458400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 34800 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 283 | 5378328
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 57 | 1386000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2911173 | Frequency control.
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 150 | 3548000 | FGMO & GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 28 | 165600 | Low demand
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 391176
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 63000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1010688 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 340800 | Frequency control.
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 150 | 2384480
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 95000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 120555
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6978500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 49860
| Sylhet Area Total |  |  |  | 1949 | 1020 | 19444832
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 299 | 7369455 | Low demand
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 113280 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 7305984 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 645 | 14788719
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 20 | 334600 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1413000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 0 | Reserve
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 401 | 7381500 | On test
| Barisal Area Total |  |  |  | 462 | 481 | 9129100
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1110000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 51320 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 3866800 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under S/D.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 198 | 4150000 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 429 | 8196782 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 17 | 97920 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 85282
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216846
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 913 | 17774950
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1706181
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3654400 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 38 | 104640 | Reserve
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 52013
| Rangpur Area Total |  |  |  | 605 | 258 | 5517234
| Total |  |  |  | 19107 | 7256 | 145816814
| Eastern Grid Total |  |  |  | 13543 | 4959 | 98606811
| Western Grid Total |  |  |  | 5564 | 2297 | 47210003
| National Grid Total |  |  |  | 19107 | 7256 | 145816814
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-04-26
(a) ENTIRE EASTERN GRID : |  | 4353 | MW | (b) ENTIRE WESTERN GRID : |  | 2510 | MW
i) Dhaka area |  | 2079 | MW | i) Khulna area |  | 972 | MW
ii) Chittagong area |  | 635 | MW | ii) Rajshahi area |  | 818 | MW
iii) Comilla area |  | 664 | MW | iii) Barisal area |  | 190 | MW
iv) Mymensingh area |  | 653 | MW | iv) Rangpur area |  | 530 | MW
v) Sylhet area |  | 322 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 6863 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 76 | 13:00 | Sherpur | 80 | 19:30 | Benapol | 28 | 13:00
Munsiganj | 78 | 12:00 | Srimongal | 29 | 19:30 | Jhenida | 76 | 19:30
Sonargaon | 42 | 13:00 | Shahjibazar | 59 | 20:00 | Bottail | 74 | 19:30
Shyampur | 120 | 1:00 | Fenchuganj | 26 | 19:00 | G.K Project | 40 | 21:00
Bhulta | 83 | 11:00 | Kulawara | 31 | 20:00 | Faridpur | 120 | 19:30
Madanganj | 46 | 12:00 | Sylhet | 94 | 19:00 | Madaripur | 59 | 20:00
Shitalakhya | 50 | 13:00 | Chatak | 18 | 20:00 | Sariatpur | 34 | 21:00
Rahim steel | 7 | 10:00 | Sunamganj | 30 | 18:30 | Gopalganj | 56 | 19:30
Matuail | 42 | 10:00 | Biani Bazar | 45 | 19:00 | Bagerhat | 59 | 21:00
Ghorasal | 46 | 14:00 | Comilla (S) | 92 | 21:00 | Mongla | 36 | 14:00
Narsingdi | 67 | 19:30 | Comilla(N) | 79 | 19:00 | Satkhira | 71 | 19:00
Haripur (SBU) | 37 | 9:00 | Chandpur | 70 | 21:00 | Gallamari | 29 | 18:00
Ullon | 36 | 4:00 | Feni | 73 | 21:00 | Magura | 36 | 19:30
Hasnabad | 113 | 19:00 | Chowmuhani | 94 | 19:00 | Norail | 22 | 19:30
Magbazar | 63 | 13:00 | Ashuganj | 38 | 19:00 | Chuadanga | 67 | 21:00
Maniknagar | 68 | 11:00 | Daudkandi | 68 | 22:00 | Barisal(N) | 27 | 18:30
Bangabhaban | 16 | 11:00 | B.Baria | 89 | 21:00 | Barisal (S) | 64 | 19:30
Narinda | 56 | 22:00 | Ramganj | 54 | 19:00 | Patuakhali | 60 | 19:30
Dhanmondi | 66 | 14:00 | Chaddagram | 20 | 18:30 | Bhandaria | 35 | 20:00
Lalbag | 45 | 14:00 | PHP | 9 | 18:30 | Borhan Uddin | 22 | 18:30
Madartek | 47 | 14:00 | Madunaghat | 44 | 11:00 | Ishurdi | 44 | 2:00
Dhaka University |  |  | Hathazari | 61 | 20:00 | Ruppur Paromanobik | 2 | 9:00
Mirpur | 62 | 21:00 | Khulshi | 102 | 11:00 | Natore | 93 | 3:00
Kalyanpur | 57 | 21:00 | Halishahar | 83 | 10:00 | Bogra | 107 | 3:00
Gulshan | 60 | 19:00 | Baraulia | 129 | 0:00 | Noagaon | 76 | 3:00
Uttara | 43 | 21:00 | Sikalbaha | 15 | 14:00 | Rajshahi | 102 | 3:00
Uttara New | 14 | 21:00 | Dohazari | 72 | 19:00 | Rajshahi New | 8 | 11:00
Kamrangirchar | 42 | 21:00 | Cox'sbazar | 80 | 14:00 | C.Nawabganj | 55 | 1:00
Savar | 76 | 12:00 | Chandraghona | 20 | 18:00 | Amnura | 32 | 8:00
Bhasantec | 88 | 21:00 | Kaptai | 3.4 | 18:00 | Pabna | 74 | 19:30
Agargaon | 31 | 21:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 73 | 3:00
Satmosjid | 65 | 13:00 | Bakulia | 61 | 13:00 | Serajganj | 68 | 9:00
Tongi | 76 | 11:00 | Julda | 13 | 3:00 | Niyamatpur | 39 | 10:00
Kabirpur | 99 | 14:00 | TK chemical | 10 | 18:30 | Joypurhat | 44 | 20:00
Basundhara | 71 | 13:00 | Modern Steel | 14 | 10:00 | Sherpur(Bogura) | 34 | 3:00
Manikganj | 52 | 19:30 | Shahmirpur | 19.5 | 11:00 | Mohastangor | 34 | 3:00
Joydevpur | 88 | 10:00 | Khagrachhari | 16 | 19:00 | Rangpur | 98 | 20:00
New Tongi | 58 | 11:00 | Matarbari | 22.5 | 19:30 | Lalmonirhat | 40 | 20:00
Kodda | 110 | 11:00 | Baroiar Hat | 24 | 18:30 | Saidpur | 74 | 20:00
Dhamrai | 48 | 11:00 | Rangamati | 8 | 18:00 | Purbasadipur | 85 | 19:30
Rajendrapur | 48 | 19:00 | Abul Khair 230 | 13 | 12:00 | Thakurgaon | 56 | 20:00
Valuka | 52 | 20:00 | BSRM | 1 | 1:00 | Palashbari | 81 | 19:30
Tangail | 136 | 9:00 | GPH Ispat | 6 | 11:00 | Barapukuria | 36 | 19:30
Mymensing | 145 | 19:30 | Goalpara | 16 | 21:00 | Panchagar | 34 | 20:00
Kishorganj | 76 | 21:00 | Central s/s | 63 | 19:30 | Joldhaka | 20 | 19:00
Netrokona | 81 | 19:30 | Noapara | 32 | 20:00 | Kurigram | 38 | 0.83333
Jamalpur | 104 | 19:30 | Jessore | 86 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-04-26 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 408 | 0.16667 | 398 | 0.5 | Kaliakoir | 386 | 0.375 | 380 | 0.54167
Bheramara | 405 | 0.041667 | 392 | 0.91667 | Bhulta | 404 | 0.25 | 389 | 0.54167
Ashuganj(N) | 404 | 0.25 | 395 | 0.41667 | Gopalganj | 414 | 0.20833 | 395 | 0.875
Payra | 412 | 0.041667 | 404 | 0.8125
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 238 | 0.58333 | Comilla (N) | 240 | 0.083333 | 234 | 0.41667
Ishurdi | 240 | 0.25 | 224 | 0.8125 | Hathazari | 224 | 0.625 | 212 | 0.41667
Ashuganj | 242 | 0.16667 | 237 | 0.54167 | Megnaghat | 240 | 0.20833 | 232 | 0.5
Serajganj | 236 | 0.20833 | 227 | 0.8125 | Fenchuganj | 244 | 0.16667 | 234 | 0.29167
Baghabari | 245 | 0.25 | 234 | 0.75 | Siddhirganj | 239 | 0.20833 | 232 | 0.5
Barapukuria | 234 | 0.125 | 224 | 0.8125 | Maniknagar | 237 | 0.25 | 230 | 0.54167
Bogra | 237 | 0.25 | 221 | 0.8125 | Old Airport | 237 | 0.25 | 229 | 0.54167
Rajshahi | 226 | 24:00 | 210 | 0.8125 | Barisal | 245 | 0.25 | 228 | 0.54167
Khulna South | 237 | 0.25 | 220 | 0.41667 | AKSML | 222 | 0.66667 | 210 | 0.5
Rampura | 234 | 0.20833 | 230 | 0.41667 | BSRM | 227 | 0.77083 | 217 | 0.5
Haripur | 235 | 0.20833 | 230 | 0.5 | Bibiyana | 242 | 0.16667 | 237 | 0.5
Hasnabad | 234 | 0.041667 | 231 | 0.5 | Bhulta | 238 | 0.25 | 231 | 0.54167
Shyampur | 235 | 0.20833 | 228 | 0.54167 | Ashuganj (S) | 241 | 0.25 | 234 | 0.41667
Aminbazar | 238 | 0.20833 | 230 | 0.5 | Kaliakoir | 238 | 0.20833 | 231 | 0.54167
Tongi | 235 | 0.16667 | 228 | 0.875 | GPH | 221 | 0.20833 | 211 | 0.41667
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 0.77083 | 133 | 0.41667 | Hathazari | 134 | 0.25 | 131 | 0.041667
Munsiganj | 136 | 0.58333 | 131 | 0.45833 | Khulshi | 131 | 0.25 | 127 | 0.45833
Sonargaon | 136 | 0.91667 | 132 | 0.041667 | Halishahar | 134 | 0.77083 | 129 | 0.45833
Shyampur | 139 | 0.625 | 135 | 0.125 | Baraulia | 132 | 0.25 | 128 | 0.45833
Bhulta | 130 | 0.125 | 127 | 0.29167 | Sikalbaha | 132 | 0.25 | 128 | 0.45833
Madanganj | 139 | 0.77083 | 134 | 0.41667 | Dohazari | 130 | 0.25 | 125 | 0.041667
Shitalakhya | 139 | 0.25 | 134 | 0.45833 | Cox'sbazar | 130 | 0.25 | 121 | 0.58333
Rahim steal | 136 | 0.20833 | 133 | 0.45833 | Chandraghona | 133 | 0.25 | 130 | 0.041667
Matuail | 136 | 0.25 | 132 | 0.41667 | Kaptai | 133 | 0.29167 | 130 | 0.5
Ghorasal | 145 | 0.75 | 140 | 0.041667 | A. Khaer Stl. | 130 | 0.041667 | 129 | 0.41667
Narsinghdi | 134 | 0.25 | 131 | 0.041667 | Bakulia | 130 | 0.25 | 127 | 0.45833
Haripur (SBU) | 136 | 0.25 | 134 | 0.041667 | Julda | 131 | 0.29167 | 127 | 0.41667
Ullon | 134 | 0.54167 | 130 | 0.5 | TK Chemical | 131 | 0.25 | 128 | 0.54167
Hasnabad | 138 | 0.625 | 134 | 0.45833 | Modern Steel | 132 | 0.20833 | 128 | 0.45833
Magbazar | 135 | 0.041667 | 130 | 0.45833 | Shahmirpur | 130 | 0.20833 | 128 | 0.041667
Maniknagar | 138 | 0.041667 | 136 | 0.45833 | Khagrachhari | 132 | 0.25 | 129 | 0.45833
Bangabhaban | 138 | 0.041667 | 136 | 0.041667 | Matarbari | 133 | 0.29167 | 121 | 0.75
Narinda | 138 | 0.54167 | 136 | 0.45833 | Baroiar Hat | 133 | 0.20833 | 129 | 1:00
Dhanmondi | 134 | 0.25 | 130 | 0.5 | Rangamati | 133 | 0.29167 | 129 | 11:00
Lalbag | 139 | 0.25 | 134 | 0.41667 | Goalpara | 138 | 0.25 | 127 | 0.875
Madartek | 134 | 0.25 | 130 | 0.45833 | Central s/s | 138 | 0.25 | 125 | 0.83333
Dhaka University |  |  |  |  | Noapara | 136 | 0.25 | 123 | 0.83333
Mirpur | 137 | 0.75 | 132 | 0.5 | Jessore | 133 | 0.625 | 120 | 0.83333
Kalyanpur | 137 | 0.79167 | 133 | 0.5 | Benapol | 136 | 0.25 | 121 | 0.83333
Gulshan | 133 | 0.75 | 130 | 0.5 | Jhenida | 135 | 0.25 | 120 | 0.83333
Uttara | 138 | 0.20833 | 132 | 0.45833 | Bottail | 137 | 0.58333 | 128 | 0.83333
Uttara New | 135 | 0.75 | 132 | 0.5 | G.K Project | 141 | 0.125 | 136 | 0.875
Kamrangirchar | 138 | 0.79167 | 132 | 0.45833 | Faridpur | 140 | 0.25 | 133 | 0.8125
Savar | 137 | 0.70833 | 131 | 0.5 | Madaripur | 140 | 0.16667 | 133 | 0.8125
Bhasantec | 136 | 0.20833 | 132 | 0.5 | Sariatpur | 141 | 0.66667 | 130 | 0.83333
Agargaon | 137 | 0.20833 | 132 | 0.5 | Gopalganj | 144 | 0.20833 | 136 | 0.8125
Satmosjid | 137 | 6:: | 132 | 0.45833 | Bagerhat | 137 | 0.25 | 120 | 0.875
Tongi | 140 | 0.91667 | 135 | 0.45833 | Mongla | 134 | 0.25 | 120 | 0.83333
Kabirpur | 136 | 0.95833 | 130 | 0.41667 | Satkhira | 136 | 0.25 | 122 | 0.875
Basundhara | 134 | 0.20833 | 130 | 0.45833 | Gallamari | 139 | 0.25 | 126 | 0.83333
Manikganj | 141 | 0.58333 | 133 | 0.45833 | Magura | 135 | 0.25 | 120 | 0.83333
Joydevpur | 143 | 0.875 | 140 | 0.33333 | Norail | 133 | 0.25 | 119 | 0.83333
New Tongi | 139 | 0.77083 | 133 | 0.45833 | Chuadanga | 131 | 0.25 | 115 | 0.83333
Kodda | 135 | 1904-01-02 | 127 | 0.375 | Barisal(N) | 139 | 0.20833 | 130 | 0.83333
Dhamrai | 135 | 1904-01-02 | 130 | 0.375 | Barisal (S) | 137 | 0.625 | 129 | 0.83333
Rajendrapur | 141 | 0.91667 | 137 | 0.375 | Patuakhali | 136 | 0.70833 | 130 | 0.77083
Valuka | 130 | 0.20833 | 124 | 0.375 | Bhandaria | 137 | 0.20833 | 126 | 0.83333
Tangail | 135 | 0.77083 | 129 | 0.45833 | Ishurdi | 139 | 0.20833 | 133 | 0.79167
Mymensing | 130 | 0.20833 | 125 | 0.875 | Ruppur Paromanobik | 139 | 0.20833 | 133 | 0.77083
Kishorganj | 133 | 0.54167 | 130 | 0.41667 | Natore | 137 | 0.625 | 132 | 0.8125
Netrokona | 131 | 0.20833 | 122 | 0.083333 | Bogra | 137 | 0.20833 | 131 | 0.5
Jamalpur | 130 | 0.20833 | 118 | 0.125 | Noagaon | 134 | 0.20833 | 127 | 0.375
Sherpur | 126 | 0.20833 | 116 | 0.70833 | Rajshahi | 137 | 0.16667 | 131 | 0.29167
Srimongal | 140 | 0.20833 | 138 | 0.041667 | Rajshahi New | 138 | 0.625 | 131 | 0.875
Shahjibazar | 138 | 0.20833 | 136 | 1:00 | C.Nawabganj | 136 | 0.54167 | 128 | 0.375
Fenchuganj | 139 | 0.625 | 136 | 0.083333 | Amnura | 136 | 0.54167 | 130 | 0.375
Khulawara | 138 | 0.20833 | 136 | 0.45833 | Pabna | 137 | 0.20833 | 131 | 0.83333
Sylhet | 137 | 0.25 | 135 | 0.041667 | Shahjadpur | 140 | 0.54167 | 136 | 0.45833
Chatak | 136 | 0.16667 | 134 | 0.41667 | Serajganj | 136 | 0.20833 | 130 | 0.29167
Sunamganj | 136 | 0.20833 | 133 | 0.54167 | Niyamatpur | 133 | 0.20833 | 124 | 0.375
Biani Bazar | 137 | 0.25 | 133 | 0.54167 | Joypurhat | 134 | 0.75 | 125 | 0.375
Comilla(s) | 135 | 0.25 | 130 | 0.41667 | Sherpur(Bogura) | 131 | 0.5 | 124 | 0.8125
Comilla(n) | 140 | 0.29167 | 135 | 0.54167 | Mohastangor | 136 | 0.20833 | 129 | 0.8125
Chandpur | 134 | 0.33333 | 131 | 0.58333 | Rangpur | 134 | 0.29167 | 124 | 0.79167
Feni | 135 | 0.8125 | 130 | 0.70833 | Lalmonirhat | 130 | 0.25 | 120 | 0.79167
Chowmuhani | 130 | 0.625 | 127 | 0.45833 | Saidpur | 133 | 0.25 | 123 | 0.54167
Ashuganj | 141 | 0.75 | 138 | 0.041667 | Purbasadipur | 130 | 0.25 | 118 | 0.54167
Daudkandi | 136 | 0.29167 | 133 | 0.5 | Thakurgaon | 130 | 0.25 | 119 | 0.5
B.Baria | 137 | 0.91667 | 136 | 0.5 | Palashbari | 130 | 0.20833 | 120 | 0.79167
Ramganj | 130 | 0.8125 | 125 | 0.54167 | Barapukuria | 132 | 0.16667 | 127 | 0.79167
Chaddagram | 136 | 0.29167 | 130 | 0.54167 | Panchagar | 127 | 0.20833 | 114 | 0.79167
PHP | 133 | 0.8125 | 128 | 0.54167 | Joldhaka | 132 | 0.25 | 120 | 0.8125
Madanhat | 135 | 0.77083 | 131 | 0.041667 | Kurigram | 133 | 0.25 | 122 | 0.79167

## L-Curve
Date | 2020-04-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 37 | 3831 | 1821 | 5652 |  |  |  | QF-LDC-12
0:30 | 115.5 | 3855 | 2002.5 | 5857.5 | Date: | 2020-04-26
1:00 | 194 | 3879 | 2184 | 6063
1:30 | 248.5 | 4013.5 | 2019.5 | 6033
2:00 | 303 | 4148 | 1855 | 6003
2:30 | 286 | 4371.5 | 1941 | 6312.5 | [5 empty] | Gen. at Eve. Peak | 7256 | 7256 MW (21:00 )
3:00 | 269 | 4595 | 2027 | 6622 | [6 empty] | 21:00
3:30 | 158 | 4505 | 1989.5 | 6494.5 | [5 empty] | Gen. at Day Peak | 6076.5 | 6076.5 MW (11:00 )
4:00 | 47 | 4415 | 1952 | 6367 | [6 empty] | 11:00
4:30 | 68.5 | 3962 | 1782.5 | 5744.5 | [5 empty] | Highest Generation | 7256
5:00 | 90 | 3509 | 1613 | 5122 | [6 empty] | 21:00
5:30 | 71 | 3339.95 | 1568.05 | 4908
6:00 | 52 | 3170.9 | 1523.1 | 4694
6:30 | 29 | 3156.5 | 1540.9 | 4697.4
7:00 | 6 | 3142.1 | 1558.7 | 4700.8
7:30 | 6 | 3285.65 | 1588.35 | 4874
8:00 | 6 | 3429.2 | 1618 | 5047.2
8:30 | 51.5 | 3635.15 | 1695.2 | 5330.35
9:00 | 97 | 3841.1 | 1772.4 | 5613.5
9:30 | 130 | 3912.75 | 1849.1 | 5761.85
10:00 | 163 | 3984.4 | 1925.8 | 5910.2
10:30 | 145 | 4052.15 | 1941.2 | 5993.35
11:00 | 127 | 4119.9 | 1956.6 | 6076.5
11:30 | 118.5 | 4113.1 | 1961.95 | 6075.05
12:00 | 110 | 4106.3 | 1967.3 | 6073.6
12:30 | 60 | 4089.65 | 1958.6 | 6048.25
13:00 | 10 | 4073 | 1949.9 | 6022.9
13:30 | 65 | 3937.3 | 1922.2 | 5859.5
14:00 | 120 | 3801.6 | 1894.5 | 5696.1
14:30 | 155 | 3662 | 1816.1 | 5478.1
15:00 | 190 | 3522.4 | 1737.7 | 5260.1
15:30 | 190 | 3541.45 | 1753.9 | 5295.35
16:00 | 190 | 3560.5 | 1770.1 | 5330.6
16:30 | 212 | 3666.5 | 1815.75 | 5482.25
17:00 | 234 | 3772.5 | 1861.4 | 5633.9
17:30 | 217 | 3899.25 | 1903.8 | 5803.05
18:00 | 200 | 4026 | 1946.2 | 5972.2
18:30 | 140.5 | 4404 | 2043.6 | 6447.6
19:00 | 81 | 4782 | 2141 | 6923
19:30 | 218 | 4955 | 2277 | 7232
20:00 | 228 | 4880 | 2282 | 7162 |  |  |  | Executive Engineer
20:30 | 239 | 4919.5 | 2289.5 | 7209 |  |  |  | Network Operation Division
21:00 | 250 | 4959 | 2297 | 7256
21:30 | 194 | 4872.5 | 2226.5 | 7099
22:00 | 138 | 4786 | 2156 | 6942 |  |  |  |  | Page 6 of 7
22:30 | 75.5 | 4523.5 | 2035.5 | 6559
23:00 | 13 | 4261 | 1915 | 6176
23:30 | 25 | 4046 | 1868 | 5914
24:00 | 37 | 3831 | 1821 | 5652
7256 MW (21:00 )
6076.5 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-04-26 |  | Energy | 145816814
[10 empty] | 2020-04-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3262 | 299 | 1376 | 192 | 478 | 38 | 0 | 0 | 74
0:30 | 3246 | 460.5 | 1408.5 | 163.5 | 500.5 | 38 | 0 | 0 | 74 | Date: | 2020-04-26
1:00 | 3230 | 622 | 1441 | 135 | 523 | 38 | 0 | 0 | 74
1:30 | 3346 | 439.5 | 1477 | 135 | 522.5 | 38 | 0 | 0 | 75 | [7 empty] | Total Energy | 145.8168 | Total Energy Gen 145.817 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 145.817 MKWHr
2:00 | 3462 | 257 | 1513 | 135 | 522 | 38 | 0 | 0 | 76 | [7 empty] | Energy not Served | 0
2:30 | 3652.5 | 257 | 1624.5 | 136.5 | 521.5 | 37.5 | 0 | 0 | 83 | [7 empty] | Energy Requirement | 145.8168
3:00 | 3843 | 257 | 1736 | 138 | 521 | 37 | 0 | 0 | 90
3:30 | 3789 | 257.5 | 1665.5 | 134 | 521 | 36.5 | 0 | 0 | 91 | [6 empty] | Shortage
4:00 | 3735 | 258 | 1595 | 130 | 521 | 36 | 0 | 0 | 92
4:30 | 3317.5 | 257.5 | 1431 | 125 | 502 | 35.5 | 0 | 0 | 76
5:00 | 2900 | 257 | 1267 | 120 | 483 | 35 | 0 | 0 | 60
5:30 | 2810 | 257 | 1180 | 115 | 476.5 | 35 | 0 | 0 | 34
6:00 | 2720 | 257 | 1093 | 110 | 470 | 35 | 0 | 0 | 8
6:30 | 2721.5 | 257 | 1088 | 110 | 471 | 35.5 | 0 | 0 | 12 |  |  |  |  | Coal
7:00 | 2723 | 257 | 1083 | 110 | 472 | 36 | 0 | 0 | 16
7:30 | 2832.5 | 256 | 1123.5 | 121.5 | 471.5 | 36 | 0 | 0 | 25 |  |  |  | Oil |  |  |  | ,
8:00 | 2942 | 255 | 1164 | 133 | 471 | 36 | 0 | 0 | 34
8:30 | 3118.5 | 278.5 | 1231 | 136.5 | 481 | 36 | 0 | 0 | 38
9:00 | 3295 | 302 | 1298 | 140 | 491 | 36 | 0 | 0 | 42
9:30 | 3367.5 | 302 | 1337.5 | 150.5 | 505.5 | 36.5 | 0 | 0 | 49
10:00 | 3440 | 302 | 1377 | 161 | 520 | 37 | 0 | 0 | 56
10:30 | 3490.5 | 301.5 | 1402.5 | 162 | 520.5 | 37 | 0 | 0 | 59
11:00 | 3541 | 301 | 1428 | 163 | 521 | 37 | 0 | 0 | 62
11:30 | 3543 | 301.5 | 1428 | 164.5 | 521 | 36.5 | 0 | 0 | 65
12:00 | 3545 | 302 | 1428 | 166 | 521 | 36 | 0 | 0 | 68
12:30 | 3503 | 302 | 1430 | 171 | 522 | 36.5 | 0 | 0 | 76
13:00 | 3461 | 302 | 1432 | 176 | 523 | 37 | 0 | 0 | 84
13:30 | 3461 | 302 | 1432 | 176 | 523 | 37 | 0 | 0 | 84
14:00 | 3461 | 302 | 1432 | 176 | 523 | 37 | 0 | 0 | 84
14:30 | 3216 | 302 | 1312.5 | 148 | 521 | 53.5 | 0 | 0 | 76
15:00 | 2971 | 302 | 1193 | 120 | 519 | 70 | 0 | 0 | 68
15:30 | 2965.5 | 302 | 1252.5 | 120 | 520.5 | 52.5 | 0 | 0 | 69
16:00 | 2960 | 302 | 1312 | 120 | 522 | 35 | 0 | 0 | 70
16:30 | 3059.5 | 302 | 1362 | 122.5 | 521.5 | 35.5 | 0 | 0 | 72
17:00 | 3159 | 302 | 1412 | 125 | 521 | 36 | 0 | 0 | 74
17:30 | 3242 | 302 | 1483 | 140 | 521 | 35.5 | 0 | 0 | 77
18:00 | 3325 | 302 | 1554 | 155 | 521 | 35 | 0 | 0 | 80
18:30 | 3546.5 | 300 | 1692.5 | 225 | 539.5 | 35.5 | 25.5 | 0 | 83
19:00 | 3768 | 298 | 1831 | 295 | 558 | 36 | 51 | 0 | 86
19:30 | 3923 | 299 | 1859 | 375 | 601 | 36 | 51 | 0 | 88
20:00 | 3899 | 300 | 1912 | 294 | 600 | 37 | 34 | 0 | 86
20:30 | 3919 | 299.5 | 1952 | 285 | 610.5 | 37 | 17 | 0 | 89
21:00 | 3939 | 299 | 1992 | 276 | 621 | 37 | 0 | 0 | 92
21:30 | 3861 | 299.5 | 1948.5 | 246.5 | 620 | 37.5 | 0 | 0 | 86
22:00 | 3783 | 300 | 1905 | 217 | 619 | 38 | 0 | 0 | 80
22:30 | 3649.5 | 299.5 | 1707.5 | 204.5 | 580 | 38 | 0 | 0 | 80
23:00 | 3516 | 299 | 1510 | 192 | 541 | 38 | 0 | 0 | 80
23:30 | 3389 | 299 | 1443 | 192 | 509.5 | 38 | 0 | 0 | 77 | Max Temp. in Dhaka |  | 30.7° C
24:00 | 3262 | 299 | 1376 | 192 | 478 | 38 | 0 | 0 | 74
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
Total Energy Gen 145.817 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 145.817 MKWHr
Note on W13: Author:

## Generation
g | 2020-04-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 38 | 37 | 36 | 35 | 35 | 36 | 36 | 36 | 37 | 37 | 36 | 37 | 37 | 70 | 35 | 36 | 35 |  | 36 | 36 | 37 | 37 | 38 | 38 | 38 | 852245
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.6 | 2.5 | 8 | 2.7 | 9.2 | 15.7 |  |  | 16.6 | 11.7 | 5.6 | 3.2 | [9 empty] | 81810
6 | Sikalbaha 225MW CCPP (Gas) | 217 | 216 | 216 | 216 | 183 | 183 | 183 | 183 | 184 | 224 | 224 | 224 | 223 | 223 | 210 | 190 | 190 | 220 |  | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 5017290
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 94 | 97 | 139 | 139 | 70 | 70 | 70 | 70 | 113 | 107 | 107 | 104 | 104 | 104 | 70 | 70 | 70 | 70 |  | 145 | 139 | 139 | 139 | 139 | 70 | 71 | 2391316
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 34 |  |  |  |  | 89208
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 38 | 59 | 87 | 37 | 33 | 33 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 35 | 37 | 34 |  | 34 | 37 | 37 | 37 | 34 | 37 | 0 | 1014000
17 | Siddhirganj 335 MW CCPP | 140 | 140 | 170 | 170 | 80 | 60 | 60 | 80 | 80 | 130 | 160 | 160 | 160 | 100 | 50 | 50 | 80 | 100 |  | 160 | 218 | 180 | 180 | 180 | 180 | 140 | 3266838
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 334545
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 488000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 210 | 220 | 240 | 280 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 243 | 250 | 250 | 250 | 220 | 220 | 220 | 5127491
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 125 | 135 | 135 | 135 | 135 | 135 | 80 | 2194692
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 27 | 40 | 40 | 40 | 40 | 5 | 388872
33 | Ashuganj 225 MW CCPP | 170 | 183 | 192 | 177 | 142 | 129 | 129 | 166 | 183 | 183 | 183 | 183 | 174 | 164 | 150 | 152 | 150 | 150 |  | 181 | 181 | 180 | 186 | 180 | 180 | 180 | 4106000
34 | Ashuganj 450 MW CCPP(South) | 250 | 285 | 280 | 265 | 230 | 215 | 220 | 245 | 305 | 300 | 295 | 290 | 270 | 260 | 230 | 230 | 275 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6378000
| Ashuganj 450 MW CCPP(North) | 260 | 295 | 320 | 310 | 240 | 230 | 250 | 250 | 300 | 295 | 295 | 285 | 270 | 260 | 280 | 260 | 290 | 310 |  | 310 | 310 | 310 | 310 | 260 | 260 | 260 | 7082900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | [12 empty] | 10 |  | 20 | 20 | 20 | 20 | 20 | 5 | 0 | 153600
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 367 | 357 | 345 | 306 | 255 | 250 | 285 | 368 | 371 | 374 | 369 | 353 | 333 | 265 | 282 | 335 | 333 |  | 334 | 338 | 334 | 339 | 334 | 334 | 334 | 8017920
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 320 | 400 | 380 | 300 | 280 | 280 | 300 | 300 | 300 | 330 | 330 | 330 | 300 | 300 | 320 | 320 | 320 |  | 420 | 390 | 390 | 390 | 350 | 300 | 300 | 7961500
41 | Haripur 360MW CCPP(HPL) | 245 | 260 | 360 | 300 | 240 | 240 | 220 | 240 | 242 | 242 | 272 | 272 | 271 | 242 | 210 | 242 | 262 | 286 |  | 345 | 323 | 323 | 323 | 323 | 283 | 283 | 6481000
42 | RPCL 210MW CCPP | 184 | 183 | 211 | 213 | 167 | 168 | 167 | 208 | 204 | 204 | 204 | 204 | 207 | 181 | 179 | 180 | 179 | 165 |  | 184 | 187 | 187 | 198 | 200 | 214 | 213 | 4511800
43
44 | Fenchugonj CCPP Phase-1 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 59 | 58 | 58 | 58 |  | 58 | 58 | 58 | 57 | 59 | 58 | 58 | 1386000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 150 | 210 | 200 | 190 | 143 | 144 | 145 | 152 | 163 | 155 | 160 | 156 | 150 | 140 | 152 | 140 | 142 | 138 |  | 138 | 145 | 143 | 150 | 140 | 140 | 140 | 3548000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 64 | 64 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1010688
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 20 | 50 | 50 | 50 | 50 | 10 | 5 | 340800
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 100 | 110 | 150 | 150 | 80 | 50 | 50 | 50 | 50 | 50 | 79 | 100 | 100 | 100 | 49 | 70 | 99 | 120 |  | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 2384480
51 | Sylhet 20 MW GTPP | [17 empty] | 19 |  | 19 | 19 | 19 | 19 | 19 |  |  | 95000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [17 empty] | 7 |  | 10 | 10 | 10 | 10 | 10 |  | 0 | 49860
54 | Hobiganj 11MW PP Cofidence-E | [17 empty] | 11 |  | 11 | 11 | 11 | 11 | 11 |  | 0 | 63000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 28 | 31 | 5 | 2 | 165600
56 | Shahjahanulla 25 MW PP | [17 empty] | 24 |  | 24 | 24 | 24 | 24 | 24 |  | 0 | 120555
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 315 | 315 | 300 | 275 | 180 | 160 | 195 | 315 | 320 | 325 | 320 | 315 | 290 | 280 | 300 | 300 | 300 |  | 270 | 260 | 275 | 300 | 290 | 275 | 280 | 6978500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 102057
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 471408
61 | Narshingdi 22 MW PP (Doreen) | [20 empty] | 10 | 10 | 10 |  |  | 0 | 24948
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 |  |  |  |  | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 364428
63 | Impoprt (Tripura) | 74 | 76 | 90 | 92 | 60 | 8 | 16 | 34 | 42 | 56 | 62 | 68 | 84 | 68 | 68 | 70 | 74 | 80 |  | 86 | 88 | 86 | 92 | 80 | 80 | 74 | 1643520
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 42 | 42 | 39 | 20 |  | 18 | 10 | 15 | 22 | 11 | 21 | 40 | 40 | 40 |  | 40 | 42 | 42 | 42 | 42 | 42 | 12 | 879840
65 | Feni 22MW PP (Doreen) | [17 empty] | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 131256
66 | Feni 11 MW PP (Doreen) | [17 empty] | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 |  | 62460
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | [13 empty] | 33 |  | 33 | 33 | 33 | 33 | 33 | 8 | 0 | 216100
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 |  |  |  |  | 10 | 10 | 10 | 12 | 12 | 12 |  |  |  |  | 8 |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 199710
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 3 | 3 |  | 3 | 5 | 10 | 10 | 10 | 10 | 10 | 175140
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 788900
72 | Rupganj 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 14 | 14 | 14 | 20 |  | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 644000
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | [12 empty] | 14 |  | 83 | 91 | 99 | 107 | 107 | 42 | 0 | 480909
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [19 empty] | 36 | 36 |  |  |  |  | 0 | 49560
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi)
Gazipur 100 MW PP
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.2 | 0.3 | 0.7 | 0.2 | 0.4 | 0.5 | 0.2 | 0.1 | 0.1 | 0.6 | [10 empty] | 4680
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [10 empty] | 12 | 15 | 25 | 20 | [5 empty] | 10 | 15 | 15 | 15 | 15 |  | 0 | 160056
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 135 | 135 | 135 | 130 | 120 | 110 | 110 | 130 | 135 | 135 | 135 | 135 | 135 | 120 | 120 | 120 | 125 | 125 |  | 125 | 125 | 120 | 125 | 120 | 125 | 125 | 3022284
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 50 | 51 | 51 | 51 | 51 | 10 | 0 | 391176
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 20 | 51 | 51 | 51 | 51 | 5 | 0 | 375116
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 130 | 130 | 130 | 130 | 110 | 110 | 2911173
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.4 | 0.9 | 0.7 | 1 | 0.8 | 0.8 | 0.8 | 0.9 | 0.6 | 0.3 | 0.3 | [9 empty] | 8900
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) |  |  | 3 | [5 empty] | 5 | 16 | 16 | 16 | 16 | 16 |  |  |  | 14 |  | 32 | 50 | 53 | 65 | 65 | 50 | 0 | 458400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [19 empty] | 1 | 15 |  |  |  |  | 0 | 15840
115 | Juldah 100 MW PP Unit-3 (Acorn) | [25 empty] | 0 | 0
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [7 empty] | 3 | [11 empty] | 13 | 8 |  |  |  |  | 0 | 34800
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 | [9 empty] | 10 | [15 empty] | 0 | 8640
120 | Eastern Zone Total | 3879 | 4148 | 4595 | 4415 | 3509 | 3170.9 | 3142.1 | 3429.2 | 3841.1 | 3984.4 | 4119.9 | 4106.3 | 4073 | 3801.6 | 3522.4 | 3560.5 | 3772.5 | 4026 | 0 | 4782 | 4955 | 4880 | 4959 | 4786 | 4261 | 3831 | 98606811
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 49 | 49 | 32 | 16 |  |  | 0 | 113280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1413000
140 | Bhola 33 MW PP (Venture) | 15 | 15 | 17 | 18 | 13 | 11 | 10 | 11 | 13 | 13 | 8 | 8 | 11 | 11 | 14 | 15 | 17 | 13 |  | 19 | 20 | 20 | 20 | 20 | 16 | 15 | 334600
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 622 | 257 | 257 | 258 | 257 | 257 | 257 | 255 | 302 | 302 | 301 | 302 | 302 | 302 | 302 | 302 | 302 | 302 |  | 298 | 299 | 300 | 299 | 300 | 299 | 299 | 7369455
147 | Bheramara 410 MW CCPP | 240 | 255 | 320 | 320 | 220 | 225 | 225 | 260 | 290 | 365 | 375 | 360 | 335 | 285 | 240 | 235 | 235 | 235 |  | 335 | 335 | 330 | 330 | 330 | 290 | 290 | 7305984
148 | Payra 1320 MW | 301 | 302 | 301 | 301 | 264 | 250 | 252 | 250 | 270 | 299 | 300 | 302 | 298 | 298 | 298 | 301 | 300 | 301 |  | 337 | 380 | 379 | 401 | 398 | 320 | 257 | 7381500
149
150 | Barapukuria TPP Unit-1 | 72 | 70 | 70 | 71 | 70 | 70 | 70 | 71 | 71 | 71 | 71 | 69 | 75 | 73 | 71 | 71 | 71 | 71 |  | 71 | 70 | 71 | 70 | 71 | 71 | 71 | 1706181
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 |  | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 3654400
153 | Baghabari 71 MW GTPP | 40 | 40 | 70 | 70 | 40 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 70 | 70 | 71 | 70 | 70 | 30 | 30 | 1110000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 180 | 160 | 140 | 130 | 130 | 130 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 150 | 180 | 180 | 180 | 140 | 140 | 140 | 3866800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 165 | 155 | 140 | 130 | 130 | 130 | 130 | 130 | 147 | 172 | 177 | 177 | 178 | 186 | 200 | 183 |  | 169 | 192 | 191 | 198 | 192 | 140 | 140 | 4150000
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 388 | 410 | 421 | 374 | 252 | 212 | 246 | 270 | 300 | 348 | 347 | 347 | 347 | 343 | 232 | 259 | 337 | 403 |  | 388 | 375 | 405 | 429 | 389 | 378 | 361 | 8196782
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 5 | 0 | 97920
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | [13 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 85282
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 216846
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 12 | 25 | 25 |  |  |  |  | 51320
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [20 empty] | 35 | 32 | 38 |  |  | 0 | 104640
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.7 | 3 | 5.4 | 6.8 | 6.6 | 6.3 | 6.9 | 7.5 | 4.7 | 3.1 | 1.4 | 0.2 | [8 empty] | 52013
178
178