## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-04-29 | Wednesday
|  | Date (day): | 2020-04-29 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12209.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15152 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-04-28 | 2020-04-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 240 | 210 | 280 | 280 |  | 85 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 362 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 242 | 325 | 310 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 360 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 130 | 150 | 150 | 155 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 15 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 77 | 150 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 140 | 180 | 217 | 217 |  | 118 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 37 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 16 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 23 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1675 | 1880 | 3575 | 4325 | 446 | 1024
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.7 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 36 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 225 | 223 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 142 | 140 | 145
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 13 | 42 | 15 | 42
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 0 | 40 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 560.9 | 639 | 1581 | 1718 | 450 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 196 | 202 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 335 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 5 | 40 | 40
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 108 | 116 | 141
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 20 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 36 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1064 | 1158 | 1680 | 2305 | 485 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 204 | 199 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 20 | 20
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.9 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 40 | 170 | 170 |  | 30 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 221.9 | 257 | 611.6 | 610 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 67 | 87 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 30 | 30 |  | 60 | Machine problem
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 168 | 174 | 220 | 220 |  | 110 | ST Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 8 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 5 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 40 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 10 | 81 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 70 | 118 | 100 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 805 | 1009 | 1221 | 1271 | 0 | 570
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 298 | 833 | 299 | 842
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 370 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 648 | 1252 | 1084 | 2087 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 23 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 |  | 134 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 42 | 71 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 301 | 301 | 300 | 400 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 417 | 455 | 519 | 715 | 0 | 147
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 40 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 170 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 170 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 405 | 362 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 5 | 5 | 17 | 17
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 739 | 796 | 1617 | 1776 | 320 | 17
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 44 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 149 | 194 | 321 | 345 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 6279.8 | 7640 | 12209.6 | 15152 | 1871 | 2019
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5947.7268 | 7236 | 11563.9615 | 14350.7686
A. |  | 2020-04-28 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 7640 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5248.2 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7640 | MW
3 | Day peak Generation : |  |  | 6279.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7236 | MW
4 | Evening peak Generation : |  |  | 7640 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 155.7537 | MKWHr | By Solar | 0.18343 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 126.5508 | MKWHr |  | By Oil: | 4.9326 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 10.9657 | MKWHr |  | By Hydro: | 0.8082 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1871 | MW | Dhaka | 2191 | 2191 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2019 | MW | Chittagong | 765 | 765 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3890 | MW | Khulna | 1048 | 1048 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1034.22 | MMCFD |  |  | Rajshahi | 800 | 800 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 144251845.854 | ii) Oil : | Taka | 17297317.12 | Comilla | 771 | 771 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 51972053 | Total | Taka | 213521215.974 | Mymensingh | 580 | 580 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.134 | MKWHr. | Sylhet | 297 | 297 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -127 | MW (E to W) at | 21:00 | hrs | Barisal | 243 | 243 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -370 | MW at | 3:00 | hrs | Rangpur | 541 | 541 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.8° C |  |  | Total | 7236 | 7236 |  | 0
B. |  | 2020-04-29 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15152 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7300 | MW
4 | Reserve(Generation end) |  |  |  | 6152 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 183.4795 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4783.07 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.0618 | MKWHr. | ii) HVDC Flow at Peak Time |  | 833 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2512 | MKWHr. | iii) Maximum HVDC Flow : |  | 833 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.73 |  | (b) Today: | 78.84 |  | (c) Rule Curve: |  | 82.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-04-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 0 | 0 | 200 | 104 | 0 | 342 | 275 |  | 0 | 340 | 120 | 0 | 30 | 0 | 180 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 290 | 80 | 201 | 92 | 0 | 39 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 94 | 209 | 0 | 20 | 0 | 88 | 0 | 53 | 51 | 110 | 175 | 40 | 10 | 0 | 79 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 531 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 95 | 0 | 181 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 |  | 4635 | 2403 | 7038 | 3630 | 531 | 1974 | 220 | 552 | 37 | 0 | 94 | 0 | 0 | 78.73
2:00 | 24 | 0 | 0 | 0 | 210 | 106 | 0 | 371 | 275 |  | 0 | 340 | 120 | 0 | 30 | 0 | 180 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 310 | 95 | 195 | 92 | 0 | 39 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 94 | 209 | 0 | 20 | 0 | 88 | 0 | 53 | 51 | 110 | 172 | 50 | 10 | 0 | 100 | 19 | 0 | 10 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 254 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 95 | 0 | 184 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 |  | 4753 | 2158 | 6911 | 3719 | 254 | 2038 | 220 | 549 | 37 | 0 | 94 | 0 | 0 | 78.73
3:00 | 24 | 0 | 0 | 0 | 280 | 104 | 0 | 361 | 305 |  | 0 | 380 | 120 | 0 | 30 | 0 | 230 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 325 | 195 | 194 | 92 | 0 | 39 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 96 | 210 | 0 | 20 | 0 | 88 | 0 | 53 | 51 | 110 | 168 | 63 | 13 | 0 | 150 | 19 | 0 | 10 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  | 254 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 94 | 0 | 183 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 |  | 5166 | 2190 | 7356 | 4051 | 254 | 2115 | 232 | 571 | 37 | 0 | 96 | 0 | 0 | 78.73
4:00 | 24 | 0 | 0 | 0 | 280 | 42 | 0 | 346 | 275 |  | 0 | 350 | 120 | 0 | 15 | 0 | 231 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 295 | 285 | 152 | 45 | 0 | 39 | 30 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 22 | 20 | 98 | 210 | 0 | 20 | 0 | 88 | 0 | 5 | 5 | 110 | 167 | 50 | 13 | 0 | 149 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 254 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 94 | 0 | 180 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 |  | 4697 | 2149 | 6846 | 3941 | 254 | 1777 | 167 | 572 | 37 | 0 | 98 | 0 | 0 | 78.73
5:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 350 | 275 |  | 0 | 350 | 120 | 0 | 15 | 0 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 25 | 22 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 190 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 265 | 275 | 141 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 82 | 166 | 0 | 0 | 0 | 85 | 0 | 5 | 5 | 100 | 155 | 40 | 13 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 254 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 45 | 0 | 178 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 |  | 3937 | 1886 | 5823 | 3318 | 254 | 1568 | 135 | 431 | 35 | 0 | 82 | 0 | 0 | 78.73
6:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 308 | 245 |  | 0 | 300 | 120 | 0 | 0 | 0 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 25 | 22 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 190 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 230 | 240 | 142 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 74 | 165 | 0 | 0 | 0 | 64 | 0 | 5 | 5 | 100 | 171 | 40 | 13 | 0 | 49 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 254 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 42 | 0 | 170 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 |  | 3583.2 | 1738 | 5321.2 | 3032 | 254 | 1401 | 120 | 403 | 36 | 0 | 74 | 1.2 | 0 | 78.73
7:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 275 | 245 |  | 0 | 300 | 120 | 0 | 0 | 0 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 25 | 22 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 190 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 80 | 0 | 0 | 230 | 230 | 143 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 72 | 166 | 0 | 0 | 0.1 | 64 | 0 | 5 | 5 | 100 | 175 | 40 | 13 | 0 | 49 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 249 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 41 | 0 | 130 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 |  | 3542.2 | 1706 | 5248.2 | 2947 | 249 | 1410 | 120 | 408 | 36 | 0 | 72 | 6.2 | 0 | 78.73
8:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 352 | 245 |  | 0 | 300 | 145 | 0 | 7 | 0 | 140 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 80 | 0 | 0 | 280 | 230 | 140 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 80 | 166 | 0 | 0 | 0.3 | 64 | 0 | 5 | 5 | 100 | 173 | 40 | 13 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 250 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 3821.8 | 1748 | 5569.8 | 3202 | 250 | 1427 | 152 | 410 | 37 | 0 | 80 | 11.8 | 0 | 78.73
9:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 370 | 232 |  | 0 | 300 | 145 | 0 | 15 | 0 | 140 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 80 | 0 | 0 | 300 | 230 | 216 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 84 | 166 | 0 | 0 | 0.7 | 64 | 0 | 5 | 5 | 100 | 171 | 40 | 13 | 0 | 70 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 297 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 41 | 0 | 130 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 |  | 3996.4 | 1852 | 5848.4 | 3362 | 297 | 1480 | 160 | 409 | 37 | 0 | 84 | 19.4 | 0 | 78.73
10:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 367 | 222 |  | 0 | 360 | 140 | 0 | 15 | 0 | 140 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 22 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 80 | 0 | 0 | 310 | 290 | 201 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 92 | 209 | 0 | 0 | 0.7 | 66 | 0 | 5 | 5 | 130 | 170 | 40 | 13 | 0 | 70 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 41 | 0 | 130 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 |  | 4238.3 | 1940 | 6178.3 | 3581 | 298 | 1562 | 155 | 428 | 37 | 0 | 92 | 25.3 | 0 | 78.73
11:00 | 24 | 0 | 0 | 0 | 210 | 0 | 0 | 347 | 243 |  | 0 | 360 | 135 | 0 | 15 | 0 | 140 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 22 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 80 | 0 | 0 | 300 | 275 | 192 | 8 | 0 | 30 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 94 | 208 | 0 | 17 | 1.2 | 66 | 20 | 5 | 5 | 130 | 159 | 40 | 16 | 0 | 70 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 44 | 0 | 130 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4223.6 | 1950 | 6173.6 | 3546 | 298 | 1574 | 150 | 450 | 38 | 0 | 94 | 23.6 | 0 | 78.73
12:00 | 24 | 0 | 0 | 0 | 240 | 12 | 0 | 341 | 242 |  | 0 | 360 | 140 | 0 | 15 | 0 | 140 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 28 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 225 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 80 | 0 | 0 | 305 | 310 | 196 | 8 | 0 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 17 | 5 | 0 | 0 | 100 | 204 | 0 | 17 | 0.9 | 67 | 20 | 5 | 5 | 130 | 168 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4326.8 | 1953 | 6279.8 | 3655 | 298 | 1559 | 155 | 450 | 38 | 0 | 100 | 24.8 | 0 | 78.73
13:00 | 24 | 0 | 0 | 0 | 240 | 12 | 0 | 351 | 304 |  | 0 | 360 | 140 | 0 | 15 | 0 | 170 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 28 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 15 | 80 | 0 | 0 | 290 | 290 | 182 | 8 | 0 | 36 | 5 | 0 | 5 | 0 | 0 | 0 | 19 | 5 | 0 | 0 | 98 | 204 | 0 | 17 | 2.3 | 66 | 20 | 5 | 5 | 130 | 165 | 40 | 10 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 |  | 4414 | 1940 | 6354 | 3630 | 298 | 1642 | 155 | 453 | 38 | 17 | 98 | 23 | 0 | 78.73
14:00 | 24 | 0 | 0 | 0 | 240 | 12 | 0 | 356 | 304 |  | 0 | 360 | 140 | 0 | 15 | 0 | 170 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 28 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 16 | 80 | 0 | 0 | 315 | 290 | 202 | 8 | 0 | 36 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 188 | 0 | 17 | 1 | 67 | 20 | 5 | 5 | 130 | 171 | 40 | 10 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 302 |  | 4417.1 | 1967.5 | 6384.6 | 3664 | 298 | 1637 | 157 | 452 | 38 | 17 | 100 | 21.6 | 0 | 78.73
15:00 | 24 | 0 | 0 | 0 | 240 | 14 | 0 | 346 | 304 |  | 0 | 360 | 125 | 0 | 15 | 0 | 170 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 28 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 217 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 80 | 0 | 0 | 295 | 270 | 181 | 8 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 92 | 177 | 0 | 20 | 0.7 | 66 | 20 | 5 | 5 | 130 | 156 | 40 | 10 | 0 | 70 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 304 |  | 4243.6 | 1885.8 | 6129.4 | 3474 | 298 | 1575 | 164 | 454 | 38 | 17 | 92 | 17.4 | 0 | 78.73
16:00 | 24 | 0 | 0 | 0 | 200 | 14 | 0 | 335 | 274 |  | 0 | 320 | 130 | 0 | 0 | 0 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 19 | 80 | 0 | 0 | 270 | 260 | 150 | 8 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 176 | 0 | 20 | 0.5 | 65 | 20 | 5 | 5 | 130 | 155 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 252 |  | 3924.4 | 1803.2 | 5727.6 | 3232 | 298 | 1491 | 154 | 402 | 38 | 17 | 82 | 13.6 | 0 | 78.74
17:00 | 24 | 0 | 0 | 0 | 200 | 13 | 0 | 337 | 274 |  | 0 | 320 | 130 | 0 | 0 | 0 | 150 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 16 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 39 | 80 | 0 | 0 | 265 | 265 | 150 | 8 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 14 | 80 | 143 | 0 | 20 | 0.2 | 65 | 22 | 7 | 5 | 130 | 156 | 21 | 1 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 40 | 0 | 130 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 0 | 250 |  | 3961 | 1785.6 | 5746.6 | 3246 | 298 | 1527 | 137 | 400 | 37 | 17 | 80 | 4.6 | 0 | 78.74
18:00 | 24 | 0 | 0 | 0 | 210 | 14 | 0 | 353 | 274 |  | 0 | 320 | 140 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 115 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 305 | 305 | 150 | 8 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 14 | 94 | 143 | 0 | 20 | 0.1 | 66 | 32 | 8 | 5 | 130 | 179 | 21 | 1 | 0 | 70 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 298 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 43 | 0 | 130 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 246 |  | 4204.1 | 1809.9 | 6014 | 3448 | 298 | 1567 | 157 | 396 | 36 | 17 | 94 | 1 | 0 | 78.74
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 358 | 326 |  | 0 | 320 | 130 | 0 | 15 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 6 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 275 | 280 | 150 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 22 | 14 | 110 | 147 | 0 | 20 | 0 | 65 | 22 | 8 | 5 | 163 | 160 | 40 | 10 | 0 | 119 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 |  | 720 | 0 | 285 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 73 | 0 | 145 | 0 | 362 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 300 |  | 4509 | 2397 | 6906 | 3573 | 720 | 1661 | 305 | 450 | 36 | 51 | 110 | 0 | 0 | 78.75
19:30 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 336 | 323 |  | 0 | 360 | 130 | 0 | 30 | 0 | 180 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 6 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 305 | 260 | 180 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 110 | 187 | 0 | 20 | 0 | 87 | 22 | 8 | 5 | 163 | 161 | 40 | 10 | 0 | 119 | 19 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 40 |  | 832 | 0 | 335 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 71 | 0 | 170 | 0 | 362 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 302 |  | 4808 | 2659 | 7467 | 3880 | 832 | 1722 | 384 | 452 | 36 | 51 | 110 | 0 | 0 | 0
20:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 338 | 323 |  | 0 | 360 | 130 | 0 | 30 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 6 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 305 | 260 | 180 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 110 | 201 | 0 | 20 | 0 | 88 | 22 | 8 | 5 | 163 | 164 | 40 | 10 | 0 | 118 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 40 |  | 833 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 71 | 0 | 170 | 0 | 370 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 300 |  | 4813 | 2691 | 7504 | 3883 | 833 | 1738 | 403 | 450 | 36 | 51 | 110 | 0 | 0 | 78.75
21:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 362 | 325 |  | 0 | 360 | 130 | 0 | 15 | 0 | 180 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 12 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 142 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 335 | 300 | 202 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 108 | 199 | 0 | 18 | 0 | 87 | 30 | 8 | 5 | 163 | 174 | 40 | 10 | 0 | 118 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 40 |  | 833 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 71 | 0 | 170 | 0 | 362 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 301 |  | 4943 | 2697 | 7640 | 4075 | 833 | 1732 | 371 | 451 | 36 | 34 | 108 | 0 | 0 | 78.75
22:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 350 | 325 |  | 0 | 360 | 130 | 0 | 15 | 0 | 180 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 300 | 260 | 181 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 108 | 201 | 0 | 0 | 0 | 87 | 30 | 8 | 5 | 163 | 174 | 40 | 10 | 0 | 118 | 19 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 |  | 832 | 0 | 330 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 0 | 170 | 0 | 332 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 299 |  | 4704 | 2582 | 7286 | 3884 | 832 | 1680 | 262 | 449 | 37 | 34 | 108 | 0 | 0 | 78.76
23:00 | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 336 | 286 |  | 0 | 300 | 120 | 0 | 0 | 0 | 150 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 275 | 260 | 163 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 15 | 102 | 201 | 0 | 20 | 0 | 88 | 30 | 8 | 5 | 130 | 161 | 40 | 10 | 0 | 81 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 |  | 833 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 42 | 0 | 140 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4200 | 2430 | 6630 | 3551 | 833 | 1510 | 130 | 450 | 37 | 17 | 102 | 0 | 0 | 78.77
24:00 | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 335 | 286 |  | 0 | 300 | 120 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 260 | 260 | 142 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 94 | 214 | 0 | 20 | 0 | 88 | 30 | 8 | 5 | 100 | 156 | 40 | 5 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 733 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4016 | 2193 | 6209 | 3331 | 733 | 1443 | 120 | 450 | 38 | 0 | 94 | 0 | 0 | 78.78
KWH | 504000 | 0 | 0 | 0 | 5241264 | 557227 | 0 | 8414210 | 6655000 |  | 0 | 8050750 | 2983476 | 0 | 364920 | 0 | 4077938 | 0 | 2341000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64081 | 62460 | 600000 | 254700 | 617200 | 677600 | 0 | 0 | 808200 | 0 | 2400000 | 0 | 0 | 5166675 | 0 | 2853906 | 0 |  | 0 | 0 | 289795 | 0 | 0 | 0 | 380112 | 825600 | 2174920 | 0 | 0 | 7252000 | 6095000 | 4256000 | 535272 | 0 | 372456 | 250560 | 0 | 401724 | 0 | 0 | 0 | 242676 | 144720 | 304700 | 332310 | 2251200 | 4407280 | 0 | 306756 | 8200 | 1778000 | 321120 | 340800 | 372528 | 3187800 | 3964000 | 936384 | 307200 | 0 | 2097420 | 119000 | 0 | 79560 | 7483500 | 101125 | 44000 | 0 | 0 | 0 | 0 | 516000 | 0 | 0 | 143370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20640 | 0 | 0 | 0 | 0 | 100800 | 268800 |  | 10061818 | 0 | 8143488 | 0 | 179520 | 0 | 0 | 0 | 0 | 0 | 0 | 143900 | 381500 | 0 | 0 | 0 | 1175000 | 0 | 0 | 0 | 25010 | 0 | 0 | 0 | 0 | 187200 | 193896 | 216612 | 0 | 0 | 3721000 | 0 | 0 | 3854800 | 0 | 0 | 0 | 1356272 | 0 | 3922182 | 0 | 9087509 | 0 | 0 | 0 | 0 | 140160 | 0 | 11222 | 0 | 7244700 |  | 105707935 | 50045789 | 155753724 | 86296914 | 10061818 | 40253898 | 4642767 | 10965700 | 808200 | 289795 | 2251200 | 183432 | 0
Fuel Cost | 826560 | 0 | 0 | 0 | 5817803.04 | 735539.64 | 0 | 8498352.1 | 6854650 |  | 0 | 8775317.5 | 3311658.36 | 0 | 2514298.8 | 0 | 4241055.52 | 0 | 4049930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 631838.66 | 46845 | 450000 | 0 | 0 | 0 | 0 | 0 | 218214 | 0 | 4344000 | 0 | 0 | 5631675.75 | 0 | 4851640.2 | 0 |  | 0 | 0 | 2811011.5 | 0 | 0 | 0 | 478941.12 | 2452032 | 3218881.6 | 0 | 0 | 5366480 | 6095000 | 3915520 | 690500.88 | 0 | 420875.28 | 350784 | 0 | 686948.04 | 0 | 0 | 0 | 308198.52 | 108540 | 533225 | 249232.5 | 16884000 | 4671716.8 | 0 | 389580.12 | 130708 | 2915920 | 513792 | 606624 | 581143.68 | 3634092 | 4122560 | 1844676.48 | 586752 | 0 | 3628536.6 | 260610 | 0 | 162302.4 | 7558335 | 75843.75 | 33440 | 0 | 0 | 0 | 0 | 2683200 | 0 | 0 | 1675995.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 863856 | 1790208 |  | 57956071.68 | 0 | 8550662.4 | 0 | 1411027.2 | 0 | 0 | 0 | 0 | 0 | 0 | 162607 | 591325 | 0 | 0 | 0 | 2408750 | 0 | 0 | 0 | 192577 | 0 | 0 | 0 | 0 | 359424 | 300538.8 | 163975.284 | 0 | 0 | 20167820 | 0 | 0 | 4510116 | 0 | 0 | 0 | 2034408 | 0 | 4588952.94 | 0 | 8996633.91 | 0 | 0 | 0 | 0 | 1087641.6 | 0 | 124003.1 | 0 | 31804233 |  | 145099441.14 | 145410766.914 | 290510208.054 | 98294495.004 | 57956071.68 | 45957350.85 | 14486305.62 | 51972053 | 218214 | 2811011.5 | 16884000 | 1930706.4 | 0
Yesterday Day Peak | 24 | 0 | 0 | 0 | 240 | 12 | 0 | 341 | 242 |  | 0 | 360 | 140 | 0 | 15 | 0 | 140 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 28 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 225 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 13 | 80 | 0 | 0 | 305 | 310 | 196 | 8 | 0 | 33 | 5 | 0 | 5 | 0 | 0 | 0 | 17 | 5 | 0 | 0 | 100 | 204 | 0 | 17 | 0.9 | 67 | 20 | 5 | 5 | 130 | 168 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 42 | 0 | 130 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 6279.8 | DayPeak
Yesterday Evening Peak | 24 | 0 | 0 | 0 | 210 | 12 | 0 | 362 | 325 | 0 | 0 | 360 | 130 | 0 | 15 | 0 | 180 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 12 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 142 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 335 | 300 | 202 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 108 | 199 | 0 | 18 | 0 | 87 | 30 | 8 | 5 | 163 | 174 | 40 | 10 | 0 | 118 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 40 |  | 833 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 71 | 0 | 170 | 0 | 362 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 301 |  | 7640 | EvPeak
Forecast for Evening | 24 | 0 | 0 | 0 | 280 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 217 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 145 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 135 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 40 | 20 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 141 | 210 | 95 | 20 | 0 | 60 | 30 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 170 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 842 | 40 | 410 |  | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 60 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 0 | 0 | 200 | 17 | 15 | 210 | 0 | 0 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 400
Forecast for Day | 24 | 0 | 0 | 0 | 280 | 108 | 0 | 412 | 310 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 217 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 116 | 210 | 95 | 20 | 1.6 | 60 | 30 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 100 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 0 | 0 | 170 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 114 | 113 | 100 |  | 299 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 20 | 50 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 40 | 0 | 17 | 11 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 300
Generation at 08:00(Today) | 24 | 0 | 0 | 0 | 230 | 12 | 0 | 276 | 248 | 0 | 0 | 300 | 135 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 17 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 184 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 80 | 0 | 0 | 240 | 315 | 191 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 76 | 179 | 0 | 0 | 0.7 | 75 | 20 | 8 | 5 | 100 | 115 | 50 | 5 | 0 | 50 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 8 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0
199
| Minimum Generation |  | 5248.2 | 7:00
| Highest Generation |  | 7640 | 21:00
| Day Peak Generation |  | 6279.8 | 12:00
| Evening Peak Generation |  | 7640 | 21:00
| HVDC Max Flow |  | 833 | 20:00
| HVDC EvPeak Flow |  | 833 | 21:00
| Load factor L.F |  | 84.94%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-04-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-04-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6279.8 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 4783.07 | MW
Evening Peak Generation : |  | 7640 | MW Hour : | 21:00 | Available Max Generation : |  | 15152 | MW
E.P. Demand (at gen end) : |  | 7640 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9000 | MW
Maximum Generation : |  | 7640 | MW Hour : | 21:00 | Reserve(Generation end) |  | 6152 | MW
Total Gen. (MKWH) : |  | 155.7537 | System Load Factor : | 84.94% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -370 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-04-29
Actual : | 78.84 | Ft.(MSL) , | Rule curve : | 82.4 | Ft.( MSL )
Gas Consumed : | Total = | 1034.22 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144251845.854
: |  | Coal : | 51972053 | Oil : | 17297317.12 | Total : | 213521215.974
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3184.7554 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1077.4599 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 964.3825 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 871.0509 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 787.3491 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 635.3489 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 362.3761 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 163.7737 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 489.9785 |  |  | 0 | 0%
Total | 0 |  | 8536.4749 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-1,3,4 & 5.
4) Ashuganj unit-4,5
5) Siddirganj-335 MW ST
6) Kaptai-2,5
7) Raozan #1 & 2
8) Fenchuganj 3, 4
9) Chandpur 163 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Saidpur 132/33 kV T2 transformer was under shut down from 09:50 to 10:50 due to R/H at B-phase
isolator joint.
b) Shahajibazar 86 MW was under shut down from 11:10 to 12:43 due to R/H at P.T. joint.
c) Barishal(N) 230/132 kV T01 transformer was under shut down from 12:10 to 13:07 due to oil leakage.
d) Haripur-Ullon 132 kV Ckt tripped at 13:48 from both ends showing dist. R, Z1 and was switched on at
14:17.
e) B.Baria-Shahajibazar 132 kV both Ckts tripped at 15:17 from both ends showing dist. Z2 at B.Baria
end & dist. Z1, A-phase at Shahajibazar end and was switched on at 15:47.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-04-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 504000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 210 | 5241264
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 557227 | Low demand
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 8414210 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 325 | 6655000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8050750 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 130 | 2983476 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 15 | 364920 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 62460
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 2341000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 180 | 4077938 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 64081 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 854700 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 617200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 677600 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 0 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1880 | 41465826
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 143370
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 36 | 808200 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 223 | 5166675 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 142 | 2853906 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 289795 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 380112
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 825600
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20640
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 40 | 268800 | Low demand
| Chattogram area Total |  |  |  | 2166 | 639 | 13157098
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2174920 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 202 | 4256000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7252000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6095000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 372456 | Gas shortage.
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 250560 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 535272 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 401724 | Low demand
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 242676
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 144720 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2251200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 304700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 332310 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 36 | 100800 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1158 | 24714338
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 199 | 4407280
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 306756 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 40 | 516000 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 257 | 5238236
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 87 | 1778000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 321120
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3187800
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 174 | 3964000 | FGMO & GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 8 | 340800 | Low demand
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 5 | 372528 | Low demand
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 44000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 936384 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 10 | 307200 | Low demand
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 118 | 2097420
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 119000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 101125
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7483500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 79560
| Sylhet Area Total |  |  |  | 1949 | 1009 | 21132437
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 833 | 10061818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 179520 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8143488 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1252 | 18384826
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 23 | 381500 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 143900
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 71 | 1356272 | Low demand
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 301 | 7244700 | On test
| Barisal Area Total |  |  |  | 462 | 455 | 9126372
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1175000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 25010 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 3854800 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under S/D.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 3922182 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 362 | 9087509 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 5 | 187200 | Low demand
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 193896
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216612
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 796 | 18662209
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3721000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 44 | 140160 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11222
| Rangpur Area Total |  |  |  | 605 | 194 | 3872382
| Total |  |  |  | 19107 | 7640 | 155753724
| Eastern Grid Total |  |  |  | 13543 | 4943 | 105707935
| Western Grid Total |  |  |  | 5564 | 2697 | 50045789
| National Grid Total |  |  |  | 19107 | 7640 | 155753724
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-04-28
(a) ENTIRE EASTERN GRID : |  | 4604 | MW | (b) ENTIRE WESTERN GRID : |  | 2632 | MW
i) Dhaka area |  | 2191 | MW | i) Khulna area |  | 1048 | MW
ii) Chittagong area |  | 765 | MW | ii) Rajshahi area |  | 800 | MW
iii) Comilla area |  | 771 | MW | iii) Barisal area |  | 243 | MW
iv) Mymensingh area |  | 580 | MW | iv) Rangpur area |  | 541 | MW
v) Sylhet area |  | 297 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 7236 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 10:00 | Sherpur | 72 | 3:00 | Benapol | 32 | 19:30
Munsiganj | 86 | 19:30 | Srimongal | 25 | 14:00 | Jhenida | 91 | 19:30
Sonargaon | 49 | 19:30 | Shahjibazar | 60 | 19:00 | Bottail | 74 | 19:30
Shyampur | 150 | 2:00 | Fenchuganj | 23 | 17:00 | G.K Project | 36 | 19:30
Bhulta | 86 | 1:00 | Kulawara | 26 | 19:00 | Faridpur | 124 | 20:00
Madanganj | 47 | 1:00 | Sylhet | 84 | 19:00 | Madaripur | 68 | 21:00
Shitalakhya | 58 | 12:00 | Chatak | 19 | 20:00 | Sariatpur | 40 | 19:30
Rahim steel | 3 | 7:00 | Sunamganj | 25 | 19:00 | Gopalganj | 71 | 19:30
Matuail | 53 | 12:00 | Biani Bazar | 35 | 4:00 | Bagerhat | 65 | 20:00
Ghorasal | 46 | 18:30 | Comilla (S) | 110 | 19:00 | Mongla | 36 | 2:00
Narsingdi | 78 | 19:00 | Comilla(N) | 101 | 19:00 | Satkhira | 81 | 20:00
Haripur (SBU) | 37 | 20:00 | Chandpur | 67 | 19:00 | Gallamari | 32 | 4:00
Ullon | 38 | 19:30 | Feni | 83 | 19:00 | Magura | 40 | 19:30
Hasnabad | 116 | 19:30 | Chowmuhani | 124 | 19:00 | Norail | 28 | 19:00
Magbazar | 68 | 13:00 | Ashuganj | 42 | 13:00 | Chuadanga | 70 | 3:00
Maniknagar | 62 | 12:00 | Daudkandi | 90 | 19:30 | Barisal(N) | 30 | 20:00
Bangabhaban | 16 | 11:00 | B.Baria | 96 | 21:00 | Barisal (S) | 70 | 20:00
Narinda | 60 | 2:00 | Ramganj | 72 | 19:00 | Patuakhali | 78 | 21:00
Dhanmondi | 66 | 11:00 | Chaddagram | 22 | 18:30 | Bhandaria | 40 | 19:00
Lalbag | 49 | 13:00 | PHP | 10 | 17:00 | Borhan Uddin | 28 | 19:30
Madartek | 47 | 4:00 | Madunaghat | 48 | 9:00 | Ishurdi | 46 | 3:00
Dhaka University |  |  | Hathazari | 71 | 21:00 | Ruppur Paromanobik | 2 | 18:00
Mirpur | 68 | 13:00 | Khulshi | 119 | 14:00 | Natore | 86 | 3:00
Kalyanpur | 60 | 21:00 | Halishahar | 90 | 19:00 | Bogra | 118 | 1:00
Gulshan | 74 | 13:00 | Baraulia | 124 | 10:00 | Noagaon | 81 | 3:00
Uttara | 50 | 13:00 | Sikalbaha | 16 | 1:00 | Rajshahi | 107 | 3:00
Uttara New | 16 | 13:00 | Dohazari | 76 | 21:00 | Rajshahi New | 8 | 19:00
Kamrangirchar | 48 | 13:00 | Cox'sbazar | 82 | 20:00 | C.Nawabganj | 50 | 20:00
Savar | 85 | 14:00 | Chandraghona | 28 | 13:00 | Amnura | 30 | 20:00
Bhasantec | 92 | 13:00 | Kaptai | 3.5 | 17:00 | Pabna | 76 | 3:00
Agargaon | 34 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 81 | 3:00
Satmosjid | 66 | 13:00 | Bakulia | 69 | 12:00 | Serajganj | 63 | 3:00
Tongi | 90 | 14:00 | Julda | 16 | 1:00 | Niyamatpur | 36 | 19:30
Kabirpur | 116 | 14:00 | TK chemical | 11.6 | 21:00 | Joypurhat | 47 | 3:00
Basundhara | 75 | 14:00 | Modern Steel | 15 | 12:00 | Sherpur(Bogura) | 35 | 3:00
Manikganj | 54 | 1:00 | Shahmirpur | 23 | 22:00 | Mohastangor | 34 | 3:00
Joydevpur | 101 | 13:00 | Khagrachhari | 16 | 13:00 | Rangpur | 111 | 19:30
New Tongi | 63 | 12:00 | Matarbari | 28 | 20:00 | Lalmonirhat | 41 | 19:30
Kodda | 122 | 14:00 | Baroiar Hat | 26 | 18:00 | Saidpur | 79 | 19:30
Dhamrai | 50 | 14:00 | Rangamati | 8 | 14:00 | Purbasadipur | 74 | 20:00
Rajendrapur | 58 | 13:00 | Abul Khair 230 | 12 | 10:00 | Thakurgaon | 55 | 19:30
Valuka | 52 | 9:00 | BSRM | 1 | 1:00 | Palashbari | 86 | 20:00
Tangail | 143 | 3:00 | GPH Ispat | 7 | 13:00 | Barapukuria | 37 | 21:00
Mymensing | 151 | 3:00 | Goalpara | 17 | 19:30 | Panchagar | 34 | 19:30
Kishorganj | 76 | 1:00 | Central s/s | 63 | 19:30 | Joldhaka | 19 | 19:30
Netrokona | 74 | 19:30 | Noapara | 34 | 21:00 | Kurigram | 38 | 0.8125
Jamalpur | 88 | 20:00 | Jessore | 90 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-04-28 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 406 | 0.66667 | 398 | 0.58333 | Kaliakoir | 386 | #REF! | 377 | 0.875
Bheramara | 406 | 0.77083 | 396 | 0.875 | Bhulta | 399 | 0.66667 | 392 | 0.54167
Ashuganj(N) | 402 | 0.70833 | 397 | 0.625 | Gopalganj | 411 | 0.20833 | 396 | 0.875
Payra | 412 | 0.25 | 405 | 0.83333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 240 | 0.041667 | Comilla (N) | 238 | 0.66667 | 235 | 0.041667
Ishurdi | 238 | 0.25 | 228 | 0.8125 | Hathazari | 224 | 0.77083 | 218 | 0.375
Ashuganj | 242 | 0.66667 | 238 | 0.5 | Megnaghat | 240 | 0.75 | 236 | 0.125
Serajganj | 234 | 0.20833 | 230 | 0.875 | Fenchuganj | 243 | 0.625 | 239 | 0.16667
Baghabari | 245 | 0.25 | 238 | 0.83333 | Siddhirganj | 237 | 0.75 | 233 | 0.5
Barapukuria | 233 | 0.20833 | 227 | 0.8125 | Maniknagar | 236 | 0.70833 | 232 | 0.041667
Bogra | 234 | 0.25 | 225 | 0.8125 | Old Airport | 235 | 0.70833 | 230 | 0.5
Rajshahi | 229 | 0.20833 | 217 | 0.875 | Barisal | 246 | 0.16667 | 233 | 0.875
Khulna South | 234 | 0.20833 | 214 | 0.875 | AKSML | 220 | 0.91667 | 215 | 0.95833
Rampura | 232 | 0.625 | 230 | 0.041667 | BSRM | 226 | 0.77083 | 221 | 0.375
Haripur | 235 | 0.77083 | 231 | 0.041667 | Bibiyana | 242 | 0.625 | 237 | 0.20833
Hasnabad | 235 | 0.95833 | 230 | 0.041667 | Bhulta | 237 | 0.66667 | 233 | 0.41667
Shyampur | 233 | 0.66667 | 229 | 0.41667 | Ashuganj (S) | 239 | 0.66667 | 236 | 0.45833
Aminbazar | 236 | 24:00 | 232 | 0.33333 | Kaliakoir | 238 | 0.70833 | 231 | 0.5
Tongi | 234 | 0.625 | 227 | 0.58333 | GPH | 221 | 0.70833 | 216 | 0.375
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.77083 | 133 | 0.041667 | Hathazari | 132 | 0.77083 | 129 | 0.375
Munsiganj | 135 | 0.25 | 131 | 0.125 | Khulshi | 128 | 0.70833 | 124 | 0.375
Sonargaon | 136 | 0.20833 | 133 | 0.33333 | Halishahar | 130 | 0.75 | 125 | 0.41667
Shyampur | 138 | 0.25 | 135 | 0.45833 | Baraulia | 129 | 0.66667 | 126 | 0.375
Bhulta | 130 | 0.625 | 127 | 0.5 | Sikalbaha | 129 | 0.66667 | 126 | 0.33333
Madanganj | 138 | 0.77083 | 134 | 0.041667 | Dohazari | 128 | 0.66667 | 123 | 0.041667
Shitalakhya | 137 | 0.25 | 134 | 0.45833 | Cox'sbazar | 124 | 0.625 | 116 | 0.125
Rahim steal | 136 | 0.70833 | 134 | 0.041667 | Chandraghona | 131 | 0.70833 | 128 | 0.041667
Matuail | 136 | 0.77083 | 133 | 0.041667 | Kaptai | 132 | 0.041667 | 128 | 0.375
Ghorasal | 140 | 0.041667 | 140 | 0.041667 | A. Khaer Stl. | 130 | 0.625 | 126 | 0.041667
Narsinghdi | 135 | 0.77083 | 129 | 0.041667 | Bakulia | 128 | 0.66667 | 125 | 0.41667
Haripur (SBU) | 136 | 0.77083 | 133 | 0.45833 | Julda | 128 | 0.58333 | 126 | 0.29167
Ullon | 133 | 0.20833 | 131 | 0.041667 | TK Chemical | 131 | 0.75 | 126 | 0.375
Hasnabad | 136 | 0.70833 | 133 | 0.375 | Modern Steel | 129 | 0.66667 | 126 | 0.375
Magbazar | 134 | 0.70833 | 131 | 0.5 | Shahmirpur | 130 | 0.77083 | 126 | 0.375
Maniknagar | 138 | 0.29167 | 135 | 0.45833 | Khagrachhari | 130 | 0.66667 | 127 | 0.041667
Bangabhaban | 138 | 0.29167 | 135 | 0.45833 | Matarbari | 124 | 0.66667 | 118 | 0.95833
Narinda | 138 | 0.29167 | 135 | 0.45833 | Baroiar Hat | 130 | 0.75 | 127 | 1:00
Dhanmondi | 133 | 0.20833 | 131 | 0.041667 | Rangamati | 130 | 0.66667 | 127 | 9:00
Lalbag | 138 | 0.77083 | 133 | 0.5 | Goalpara | 141 | 0.20833 | 127 | 0.79167
Madartek | 133 | 0.25 | 131 | 0.041667 | Central s/s | 138 | 0.20833 | 124 | 0.875
Dhaka University |  |  |  |  | Noapara | 134 | 0.041667 | 124 | 0.875
Mirpur | 136 | 0.70833 | 133 | 0.58333 | Jessore | 135 | 0.20833 | 120 | 0.875
Kalyanpur | 137 | 0.77083 | 133 | 0.58333 | Benapol | 134 | 0.20833 | 120 | 0.875
Gulshan | 132 | 0.25 | 130 | 0.58333 | Jhenida | 133 | 0.20833 | 119 | 0.875
Uttara | 138 | 0.70833 | 132 | 0.58333 | Bottail | 137 | 0.25 | 128 | 0.875
Uttara New | 135 | 0.25 | 132 | 0.58333 | G.K Project | 141 | 0.70833 | 135 | 0.875
Kamrangirchar | 136 | 0.75 | 132 | 0.54167 | Faridpur | 139 | 0.25 | 132 | 0.8125
Savar | 136 | 0.77083 | 131 | 0.58333 | Madaripur | 140 | 0.125 | 133 | 0.875
Bhasantec | 135 | 0.77083 | 132 | 0.58333 | Sariatpur | 141 | 0.25 | 130 | 0.8125
Agargaon | 135 | 0.77083 | 133 | 0.58333 | Gopalganj | 145 | 0.25 | 134 | 0.875
Satmosjid | 136 | 0.77083 | 132 | 0.58333 | Bagerhat | 136 | 0.25 | 134 | 0.875
Tongi | 140 | 0.75 | 135 | 0.58333 | Mongla | 135 | 0.20833 | 122 | 0.875
Kabirpur | 135 | 0.75 | 128 | 0.58333 | Satkhira | 138 | 0.20833 | 123 | 0.875
Basundhara | 133 | 0.83333 | 130 | 0.58333 | Gallamari | 139 | 0.25 | 126 | 0.875
Manikganj | 140 | 0.77083 | 133 | 0.58333 | Magura | 133 | 0.25 | 120 | 0.875
Joydevpur | 143 | 0.75 | 139 | 0.54167 | Norail | 132 | 0.20833 | 115 | 0.875
New Tongi | 138 | 0.75 | 135 | 0.375 | Chuadanga | 130 | 0.20833 | 113 | 0.875
Kodda | 137 | 0.79167 | 128 | 0.58333 | Barisal(N) | 140 | 0.16667 | 132 | 0.8125
Dhamrai | 135 | 0.70833 | 128 | 0.58333 | Barisal (S) | 139 | 0.25 | 130 | 0.83333
Rajendrapur | 140 | 0.77083 | 135 | 0.54167 | Patuakhali | 137 | 0.25 | 125 | 0.875
Valuka | 131 | 0.77083 | 122 | 0.54167 | Bhandaria | 138 | 0.20833 | 128 | 0.83333
Tangail | 135 | 0.29167 | 127 | 0.58333 | Ishurdi | 139 | 0.25 | 133 | 0.79167
Mymensing | 133 | 0.29167 | 120 | 0.58333 | Ruppur Paromanobik | 138 | 0.16667 | 133 | 0.0625
Kishorganj | 134 | 0.66667 | 124 | 0.125 | Natore | 138 | 0.20833 | 132 | 0.8125
Netrokona | 131 | 0.33333 | 119 | 0.58333 | Bogra | 137 | 0.25 | 130 | 0.79167
Jamalpur | 129 | 0.33333 | 118 | 0.58333 | Noagaon | 133 | 0.20833 | 125 | 0.8125
Sherpur | 128 | 0.29167 | 118 | 0.58333 | Rajshahi | 138 | 0.625 | 131 | 0.79167
Srimongal | 140 | 0.25 | 137 | 0.41667 | Rajshahi New | 138 | 0.625 | 131 | 0.875
Shahjibazar | 139 | 0.16667 | 134 | 13:00 | C.Nawabganj | 135 | 0.58333 | 129 | 0.875
Fenchuganj | 138 | 0.33333 | 135 | 0.58333 | Amnura | 137 | 0.66667 | 128 | 0.83333
Khulawara | 138 | 0.75 | 135 | 0.375 | Pabna | 136 | 0.625 | 132 | 0.8125
Sylhet | 136 | 0.25 | 134 | 0.375 | Shahjadpur | 140 | 0.041667 | 138 | 0.77083
Chatak | 136 | 0.75 | 133 | 0.58333 | Serajganj | 135 | 0.041667 | 130 | 0.8125
Sunamganj | 136 | 0.75 | 132 | 0.54167 | Niyamatpur | 132 | 0.20833 | 124 | 0.8125
Biani Bazar | 136 | 0.75 | 132 | 0.58333 | Joypurhat | 135 | 0.45833 | 125 | 0.8125
Comilla(s) | 131 | 0.041667 | 127 | 0.33333 | Sherpur(Bogura) | 131 | 0.25 | 123 | 0.8125
Comilla(n) | 138 | 0.70833 | 135 | 0.79167 | Mohastangor | 135 | 0.29167 | 129 | 0.8125
Chandpur | 128 | 0.79167 | 127 | 0.29167 | Rangpur | 132 | 0.54167 | 124 | 0.875
Feni | 130 | 0.33333 | 127 | 0.41667 | Lalmonirhat | 128 | 0.25 | 120 | 0.75
Chowmuhani | 126 | 0.29167 | 121 | 0.79167 | Saidpur | 133 | 0.25 | 120 | 0.8125
Ashuganj | 140 | 0.375 | 138 | 0.083333 | Purbasadipur | 131 | 0.29167 | 120 | 0.8125
Daudkandi | 134 | 0.625 | 131 | 0.41667 | Thakurgaon | 130 | 0.25 | 120 | 0.79167
B.Baria | 137 | 0.625 | 135 | 0.41667 | Palashbari | 130 | 0.20833 | 125 | 0.041667
Ramganj | 128 | 0.70833 | 122 | 0.95833 | Barapukuria | 133 | 0.20833 | 127 | 0.8125
Chaddagram | 135 | 0.29167 | 130 | 0.75 | Panchagar | 129 | 0.25 | 114 | 0.8125
PHP | 129 | 0.8125 | 124 | 0.66667 | Joldhaka | 131 | 0.25 | 119 | 0.8125
Madanhat | 132 | 0.041667 | 128 | 0.41667 | Kurigram | 132 | 0.25 | 122 | 0.79167

## L-Curve
Date | 2020-04-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 180 | 4016 | 2193 | 6209 |  |  |  | QF-LDC-12
0:30 | 119.5 | 4325.5 | 2298 | 6623.5 | Date: | 2020-04-28
1:00 | 59 | 4635 | 2403 | 7038
1:30 | 126.5 | 4694 | 2280.5 | 6974.5
2:00 | 194 | 4753 | 2158 | 6911
2:30 | 282 | 4959.5 | 2174 | 7133.5 | [5 empty] | Gen. at Eve. Peak | 7640 | 7640 MW (21:00 )
3:00 | 370 | 5166 | 2190 | 7356 | [6 empty] | 21:00
3:30 | 235.5 | 4931.5 | 2169.5 | 7101 | [5 empty] | Gen. at Day Peak | 6279.8 | 6279.8 MW (12:00 )
4:00 | 101 | 4697 | 2149 | 6846 | [6 empty] | 12:00
4:30 | 80.5 | 4317 | 2017.5 | 6334.5 | [5 empty] | Highest Generation | 7640
5:00 | 60 | 3937 | 1886 | 5823 | [6 empty] | 21:00
5:30 | 78 | 3760.1 | 1812 | 5572.1
6:00 | 96 | 3583.2 | 1738 | 5321.2
6:30 | 83.5 | 3562.7 | 1722 | 5284.7
7:00 | 71 | 3542.2 | 1706 | 5248.2
7:30 | 53 | 3682 | 1727 | 5409
8:00 | 35 | 3821.8 | 1748 | 5569.8
8:30 | 62 | 3909.1 | 1800 | 5709.1
9:00 | 89 | 3996.4 | 1852 | 5848.4
9:30 | 95 | 4117.35 | 1896 | 6013.35
10:00 | 101 | 4238.3 | 1940 | 6178.3
10:30 | 120 | 4230.95 | 1945 | 6175.95
11:00 | 139 | 4223.6 | 1950 | 6173.6
11:30 | 128 | 4275.2 | 1951.5 | 6226.7
12:00 | 117 | 4326.8 | 1953 | 6279.8
12:30 | 108.5 | 4370.4 | 1946.5 | 6316.9
13:00 | 100 | 4414 | 1940 | 6354
13:30 | 125.5 | 4415.55 | 1953.75 | 6369.3
14:00 | 151 | 4417.1 | 1967.5 | 6384.6
14:30 | 97 | 4330.35 | 1926.65 | 6257
15:00 | 43 | 4243.6 | 1885.8 | 6129.4
15:30 | 37 | 4084 | 1844.5 | 5928.5
16:00 | 31 | 3924.4 | 1803.2 | 5727.6
16:30 | 66.5 | 3942.7 | 1794.4 | 5737.1
17:00 | 102 | 3961 | 1785.6 | 5746.6
17:30 | 175 | 4082.55 | 1797.75 | 5880.3
18:00 | 248 | 4204.1 | 1809.9 | 6014
18:30 | 170 | 4356.55 | 2103.45 | 6460
19:00 | 92 | 4509 | 2397 | 6906
19:30 | 140 | 4808 | 2659 | 7467
20:00 | 124 | 4813 | 2691 | 7504 |  |  |  | Executive Engineer
20:30 | 125.5 | 4878 | 2694 | 7572 |  |  |  | Network Operation Division
21:00 | 127 | 4943 | 2697 | 7640
21:30 | 74 | 4823.5 | 2639.5 | 7463
22:00 | 21 | 4704 | 2582 | 7286 |  |  |  |  | Page 6 of 7
22:30 | 115.5 | 4452 | 2506 | 6958
23:00 | 210 | 4200 | 2430 | 6630
23:30 | 195 | 4108 | 2311.5 | 6419.5
24:00 | 180 | 4016 | 2193 | 6209
7640 MW (21:00 )
6279.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-04-28 |  | Energy | 155753724
[10 empty] | 2020-04-28 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3331 | 733 | 1443 | 130 | 450 | 38 | 0 | 0 | 94
0:30 | 3480.5 | 632 | 1708.5 | 175 | 501 | 37.5 | 0 | 0 | 94 | Date: | 2020-04-28
1:00 | 3630 | 531 | 1974 | 220 | 552 | 37 | 0 | 0 | 94
1:30 | 3674.5 | 392.5 | 2006 | 220 | 550.5 | 37 | 0 | 0 | 94 | [7 empty] | Total Energy | 155.7537 | Total Energy Gen 155.754 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 155.754 MKWHr
2:00 | 3719 | 254 | 2038 | 220 | 549 | 37 | 0 | 0 | 94 | [7 empty] | Energy not Served | 0
2:30 | 3885 | 254 | 2076.5 | 226 | 560 | 37 | 0 | 0 | 95 | [7 empty] | Energy Requirement | 155.7537
3:00 | 4051 | 254 | 2115 | 232 | 571 | 37 | 0 | 0 | 96
3:30 | 3996 | 254 | 1946 | 199.5 | 571.5 | 37 | 0 | 0 | 97 | [6 empty] | Shortage
4:00 | 3941 | 254 | 1777 | 167 | 572 | 37 | 0 | 0 | 98
4:30 | 3629.5 | 254 | 1672.5 | 151 | 501.5 | 36 | 0 | 0 | 90
5:00 | 3318 | 254 | 1568 | 135 | 431 | 35 | 0 | 0 | 82
5:30 | 3175 | 254 | 1484.5 | 127.5 | 417 | 35.5 | 0 | 0 | 78
6:00 | 3032 | 254 | 1401 | 120 | 403 | 36 | 0 | 0 | 74
6:30 | 2989.5 | 251.5 | 1405.5 | 120 | 405.5 | 36 | 0 | 0 | 73 |  |  |  |  | Coal
7:00 | 2947 | 249 | 1410 | 120 | 408 | 36 | 0 | 0 | 72
7:30 | 3074.5 | 249.5 | 1418.5 | 136 | 409 | 36.5 | 0 | 0 | 76 |  |  |  | Oil |  |  |  | ,
8:00 | 3202 | 250 | 1427 | 152 | 410 | 37 | 0 | 0 | 80
8:30 | 3282 | 273.5 | 1453.5 | 156 | 409.5 | 37 | 0 | 0 | 82
9:00 | 3362 | 297 | 1480 | 160 | 409 | 37 | 0 | 0 | 84
9:30 | 3471.5 | 297.5 | 1521 | 157.5 | 418.5 | 37 | 0 | 0 | 88
10:00 | 3581 | 298 | 1562 | 155 | 428 | 37 | 0 | 0 | 92
10:30 | 3563.5 | 298 | 1568 | 152.5 | 439 | 37.5 | 0 | 0 | 93
11:00 | 3546 | 298 | 1574 | 150 | 450 | 38 | 0 | 0 | 94
11:30 | 3600.5 | 298 | 1566.5 | 152.5 | 450 | 38 | 0 | 0 | 97
12:00 | 3655 | 298 | 1559 | 155 | 450 | 38 | 0 | 0 | 100
12:30 | 3642.5 | 298 | 1600.5 | 155 | 451.5 | 38 | 8.5 | 0 | 99
13:00 | 3630 | 298 | 1642 | 155 | 453 | 38 | 17 | 0 | 98
13:30 | 3630 | 298 | 1642 | 155 | 453 | 38 | 17 | 0 | 98
14:00 | 3630 | 298 | 1642 | 155 | 453 | 38 | 17 | 0 | 98
14:30 | 3552 | 298 | 1608.5 | 159.5 | 453.5 | 38 | 17 | 0 | 95
15:00 | 3474 | 298 | 1575 | 164 | 454 | 38 | 17 | 0 | 92
15:30 | 3353 | 298 | 1533 | 159 | 428 | 38 | 17 | 0 | 87
16:00 | 3232 | 298 | 1491 | 154 | 402 | 38 | 17 | 0 | 82
16:30 | 3239 | 298 | 1509 | 145.5 | 401 | 37.5 | 17 | 0 | 81
17:00 | 3246 | 298 | 1527 | 137 | 400 | 37 | 17 | 0 | 80
17:30 | 3347 | 298 | 1547 | 147 | 398 | 36.5 | 17 | 0 | 87
18:00 | 3448 | 298 | 1567 | 157 | 396 | 36 | 17 | 0 | 94
18:30 | 3510.5 | 509 | 1614 | 231 | 423 | 36 | 34 | 0 | 102
19:00 | 3573 | 720 | 1661 | 305 | 450 | 36 | 51 | 0 | 110
19:30 | 3880 | 832 | 1722 | 384 | 452 | 36 | 51 | 0 | 110
20:00 | 3883 | 833 | 1738 | 403 | 450 | 36 | 51 | 0 | 110
20:30 | 3979 | 833 | 1735 | 387 | 450.5 | 36 | 42.5 | 0 | 109
21:00 | 4075 | 833 | 1732 | 371 | 451 | 36 | 34 | 0 | 108
21:30 | 3979.5 | 832.5 | 1706 | 316.5 | 450 | 36.5 | 34 | 0 | 108
22:00 | 3884 | 832 | 1680 | 262 | 449 | 37 | 34 | 0 | 108
22:30 | 3717.5 | 832.5 | 1595 | 196 | 449.5 | 37 | 25.5 | 0 | 105
23:00 | 3551 | 833 | 1510 | 130 | 450 | 37 | 17 | 0 | 102
23:30 | 3441 | 783 | 1476.5 | 130 | 450 | 37.5 | 8.5 | 0 | 98 | Max Temp. in Dhaka |  | 29.8° C
24:00 | 3331 | 733 | 1443 | 130 | 450 | 38 | 0 | 0 | 94
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 155.754 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 155.754 MKWHr
Note on W13: Author:

## Generation
g | 2020-04-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 37 | 37 | 37 | 37 | 35 | 36 | 36 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 36 |  | 36 | 36 | 36 | 36 | 37 | 37 | 38 | 808200
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.9 | 5.4 | 10.4 | 15.8 | 18.9 | 19.6 | 19.7 | 19.4 | 17.9 | 12.9 | 10.2 | 1.8 | [9 empty] | 143370
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 223 | 223 | 190 | 190 | 190 | 224 | 224 | 224 | 224 | 225 | 223 | 218 | 217 | 217 | 217 | 223 |  | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 5166675
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 145 | 100 | 50 | 50 | 50 | 100 | 139 | 139 | 139 | 139 | 139 | 139 | 104 | 104 | 115 |  | 104 | 139 | 139 | 142 | 139 | 139 | 139 | 2853906
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 51 | 51 | 51 | 34 | 34 | 17 |  | 289795
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 92 | 100 | 100 | 80 | 80 | 80 | 80 | 78 | 77 | 77 | 78 | 78 | 68 | 70 | 79 | 120 |  | 150 | 150 | 120 | 150 | 145 | 80 | 80 | 2341000
17 | Siddhirganj 335 MW CCPP | 180 | 180 | 230 | 231 | 70 | 70 | 70 | 140 | 140 | 140 | 140 | 140 | 170 | 170 | 170 | 150 | 150 | 150 |  | 150 | 180 | 180 | 180 | 180 | 150 | 80 | 4077938
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195MW PP (APSCL-United) | 92 | 92 | 92 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 535272
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 504000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 210 | 280 | 280 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 240 | 240 | 240 | 240 | 200 | 200 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 200 | 5241264
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2174920
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 39 | 39 | 39 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 33 | 36 | 36 |  | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 372456
33 | Ashuganj 225 MW CCPP | 201 | 195 | 194 | 152 | 141 | 142 | 143 | 140 | 216 | 201 | 192 | 196 | 182 | 202 | 181 | 150 | 150 | 150 |  | 150 | 180 | 180 | 202 | 181 | 163 | 142 | 4256000
34 | Ashuganj 450 MW CCPP(South) | 80 | 95 | 195 | 285 | 275 | 240 | 230 | 230 | 230 | 290 | 275 | 310 | 290 | 290 | 270 | 260 | 265 | 305 |  | 280 | 260 | 260 | 300 | 260 | 260 | 260 | 6095000
| Ashuganj 450 MW CCPP(North) | 290 | 310 | 325 | 295 | 265 | 230 | 230 | 280 | 300 | 310 | 300 | 305 | 290 | 315 | 295 | 270 | 265 | 305 |  | 275 | 305 | 305 | 335 | 300 | 275 | 260 | 7252000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 250560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 371 | 361 | 346 | 350 | 308 | 275 | 352 | 370 | 367 | 347 | 341 | 351 | 356 | 346 | 335 | 337 | 353 |  | 358 | 336 | 338 | 362 | 350 | 336 | 335 | 8414210
40 | Meghnaghat 450 MW CCPP(MPL) | 340 | 340 | 380 | 350 | 350 | 300 | 300 | 300 | 300 | 360 | 360 | 360 | 360 | 360 | 360 | 320 | 320 | 320 |  | 320 | 360 | 360 | 360 | 360 | 300 | 300 | 8050750
41 | Haripur 360MW CCPP(HPL) | 275 | 275 | 305 | 275 | 275 | 245 | 245 | 245 | 232 | 222 | 243 | 242 | 304 | 304 | 304 | 274 | 274 | 274 |  | 326 | 323 | 323 | 325 | 325 | 286 | 286 | 6655000
42 | RPCL 210MW CCPP | 209 | 209 | 210 | 210 | 166 | 165 | 166 | 166 | 166 | 209 | 208 | 204 | 204 | 188 | 177 | 176 | 143 | 143 |  | 147 | 187 | 201 | 199 | 201 | 201 | 214 | 4407280
43
44 | Fenchugonj CCPP Phase-1 | 88 | 88 | 88 | 88 | 85 | 64 | 64 | 64 | 64 | 66 | 66 | 67 | 66 | 67 | 66 | 65 | 65 | 66 |  | 65 | 87 | 88 | 87 | 87 | 88 | 88 | 1778000
45 | Fenchugonj CCPP Phase-2 | [10 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 32 |  | 22 | 22 | 22 | 30 | 30 | 30 | 30 | 321120
46 | Shajibazar 330 MW CCPP | 175 | 172 | 168 | 167 | 155 | 171 | 175 | 173 | 171 | 170 | 159 | 168 | 165 | 171 | 156 | 155 | 156 | 179 |  | 160 | 161 | 164 | 174 | 174 | 161 | 156 | 3964000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 50 | 63 | 50 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 21 | 21 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 936384
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 16 |  | 10 | 10 | 10 |  | 1 | 1 |  | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 307200
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 79 | 100 | 150 | 149 | 100 | 49 | 49 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 119 | 119 | 118 | 118 | 118 | 81 | 80 | 2097420
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | [17 empty] | 19 | 19 | 19 | 19 |  |  | 119000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | [16 empty] | 10 | 10 | 10 | 10 | 10 |  | 0 | 79560
54 | Hobiganj 11MW PP Cofidence-E | [19 empty] | 11 | 11 | 11 | 11 | 11 |  | 0 | 44000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 340800
56 | Shahjahanulla 25 MW PP | [19 empty] | 16 | 16 | 24 | 24 | 16 |  | 0 | 101125
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 320 | 315 | 310 | 315 | 300 | 315 | 310 | 320 | 320 | 305 | 300 | 310 | 300 | 290 | 270 | 300 | 310 |  | 280 | 305 | 310 | 310 | 290 | 270 | 290 | 7483500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 |  |  | 0 | 64081
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | [5 empty] | 22 | 22 | 22 | 21 | 21 |  | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 380112
61 | Narshingdi 22 MW PP (Doreen) | [19 empty] | 19 | 19 | 19 | 19 |  |  | 0 | 62460
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | [6 empty] | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 18 |  | 20 | 20 | 306756
63 | Impoprt (Tripura) | 94 | 94 | 96 | 98 | 82 | 74 | 72 | 80 | 84 | 92 | 94 | 100 | 98 | 100 | 92 | 82 | 80 | 94 |  | 110 | 110 | 110 | 108 | 108 | 102 | 94 | 2251200
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 20 | 14 | 12 | 11 | 11 | 13 | 15 | 16 | 16 | 19 | 39 | 40 |  | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 825600
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | [7 empty] | 17 | 19 | [6 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 242676
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  | 8 | 8 |  | 8 | 8 | 8 |  | 8 |  |  | 144720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 22 | [15 empty] | 22 | 33 | 33 | 33 | 33 | 33 | 8 | 304700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 7 | 10 | 14 | 14 |  | 14 | 17 | 18 | 20 | 20 | 15 | 15 | 332310
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 14 | 14 | 14 | 14 | 11 | 11 | 11 | 11 | 9 | 8 | 8 | 8 | 8 | 8 | 4 | 6 | 6 | 6 |  | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 254700
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 617200
72 | Rupganj 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 677600
73 | Ghorashal 108MW PP (Regent) | 104 | 106 | 104 | 42 | [7 empty] | 12 | 12 | 12 | 14 | 14 | 13 | 14 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 557227
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [19 empty] | 0 | 36 | 36 | 36 |  |  | 0 | 100800
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.7 | 1.1 | 2.9 | 5.7 | 2.8 | 4.2 | 1.3 | 0.2 | 1 | 0.7 | [10 empty] | 20640
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 30 | 30 | 15 | 15 |  |  | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 15 | 30 | 30 | 15 | 15 |  | 0 | 364920
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 | 145 | 140 | 135 | 140 | 140 | 140 | 125 | 130 | 130 | 140 |  | 130 | 130 | 130 | 130 | 130 | 120 | 120 | 2983476
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX) | [25 empty] | 0 | 0
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 372528
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 401724
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV)
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 3187800
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.1 | 0.3 | 0.7 | 0.7 | 1.2 | 0.9 | 2.3 | 1 | 0.7 | 0.5 | 0.2 | 0.1 | [8 empty] | 8200
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 50 | 50 | 62 | 32 | [9 empty] | 2 | 24 | 24 | 7 | 7 |  | 33 | 40 | 40 | 40 | 24 |  | 0 | 516000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit)
115 | Juldah 100 MW PP Unit-3 (Acorn) | [25 empty] | 0 | 0
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [25 empty] | 0 | 0
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 | 20 | 20 | 20 | [14 empty] | 10 |  | 40 | 40 | 40 | 40 | 40 | 10 | 0 | 268800
120 | Eastern Zone Total | 4635 | 4753 | 5166 | 4697 | 3937 | 3583.2 | 3542.2 | 3821.8 | 3996.4 | 4238.3 | 4223.6 | 4326.8 | 4414 | 4417.1 | 4243.6 | 3924.4 | 3961 | 4204.1 |  | 4509 | 4808 | 4813 | 4943 | 4704 | 4200 | 4016 | 105707935
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 38 | 49 | 49 | 49 | 43 |  | 0 | 179520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 95 | 94 | 94 | 45 | 42 | 41 | 40 | 41 | 41 | 44 | 42 | 42 | 40 | 40 | 40 | 40 | 43 |  | 73 | 71 | 71 | 71 | 70 | 42 | 32 | 1356272
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 143900
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 19 | 18 | 14 | 12 | 12 | 12 | 13 | 15 | 15 | 14 | 10 | 13 | 13 | 13 | 14 | 17 |  | 21 | 22 | 23 | 23 | 22 | 17 | 16 | 381500
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 531 | 254 | 254 | 254 | 254 | 254 | 249 | 250 | 297 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 |  | 720 | 832 | 833 | 833 | 832 | 833 | 733 | 10061818
147 | Bheramara 410 MW CCPP | 355 | 345 | 345 | 350 | 330 | 290 | 290 | 290 | 290 | 355 | 340 | 350 | 335 | 360 | 330 | 285 | 285 | 285 |  | 285 | 335 | 340 | 370 | 330 | 330 | 245 | 8143488
148 | Payra 1320 MW | 402 | 399 | 401 | 402 | 281 | 253 | 258 | 260 | 259 | 278 | 300 | 301 | 303 | 302 | 304 | 252 | 250 | 246 |  | 300 | 302 | 300 | 301 | 299 | 300 | 300 | 7244700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 170 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3721000
153 | Baghabari 71 MW GTPP | 70 | 70 | 70 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 70 | 70 | 70 | 70 | 40 | 40 | 1175000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 150 | 170 | 170 | 170 | 170 | 140 | 140 | 3854800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 181 | 184 | 183 | 180 | 178 | 170 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 145 | 170 | 170 | 170 | 170 | 140 | 140 | 3922182
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 367 | 410 | 421 | 420 | 373 | 306 | 323 | 352 | 408 | 409 | 409 | 405 | 408 | 411 | 357 | 375 | 358 | 379 |  | 362 | 362 | 370 | 362 | 332 | 357 | 318 | 9087509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 17 | 17 | 17 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 187200
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193896
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 8 |  | 8 | 11 | 11 | 11 | 11 | 8 | 8 | 216612
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 12 | 12 | 12 |  |  |  |  | 25010
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 20 | 30 | 49 | 44 | 10 |  | 0 | 140160
177 | Sympa Solar Power 8MW | [13 empty] | 2.5 | 2.8 | 2.2 | 2.6 | 0.9 | [8 empty] | 11222
178
178