## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-04-30 | Thursday
|  | Date (day): | 2020-04-30 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12093.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15032 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-04-29 | 2020-04-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 280 | 280 | 280 |  | 85 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 102 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 369 | 355 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 323 | 310 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 390 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 0 | 150 | 150 | 155 |  | Gas shortage & GT-1 S/D
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 14 | 48 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 78 | 120 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 130 | 180 | 217 | 217 |  | 118 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 43 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 23 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1762 | 1948 | 3575 | 4325 | 446 | 1024
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 36 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 217 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 42 | 15 | 42
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.9 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 53 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 40 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 451.4 | 720 | 1441 | 1573 | 450 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 100 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 197 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 315 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 290 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 39 | 40 | 40
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 48 | 5 | 20 | 35 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 55 | 8 | 8 | 187 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 10 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 76 | 124 | 116 | 141
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 26 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 22 | 22
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1079 | 1420 | 1680 | 2305 | 485 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 201 | 191 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 20 | 20
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 180 | 170 | 170 |  | 30 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 242.6 | 391 | 611.6 | 610 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 76 | 88 | 88 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 30 | 30 |  | 70 | Machine problem
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 193 | 188 | 220 | 220 |  | 110 | ST Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 8 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 51 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 49 | 53 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 80 | 81 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 120 | 150 | 100 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 320 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 916 | 1196 | 1249 | 1299 | 0 | 580
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 298 | 834 | 295 | 839
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 355 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 588 | 1328 | 1080 | 2084 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 28 | 20 | 20 |  | 13 | Engine problem
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 |  | 134 | GT-2 Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 31 | 96 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 303 | 454 | 300 | 400 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 410 | 638 | 519 | 715 | 0 | 147
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 70 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 180 | 210 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 178 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 407 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 5 | 16 | 17 | 17
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 896 | 917 | 1617 | 1776 | 320 | 17
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 156.4 | 185 | 321 | 345 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 6501.4 | 8743 | 12093.6 | 15032 | 1871 | 2029
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6174.2107 | 8303 | 11484.9778 | 14275.4999
A. |  | 2020-04-29 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 8743 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 4783.07 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8743 | MW
3 | Day peak Generation : |  |  | 6501.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8303 | MW
4 | Evening peak Generation : |  |  | 8743 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 161.4244 | MKWHr | By Solar | 0.19945 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 128.8746 | MKWHr |  | By Oil: | 7.5497 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 11.6002 | MKWHr |  | By Hydro: | 0.80502 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1871 | MW | Dhaka | 2529 | 2529 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2029 | MW | Chittagong | 821 | 821 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3900 | MW | Khulna | 1106 | 1106 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1083.45 | MMCFD |  |  | Rajshahi | 955 | 955 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 147281676.624 | ii) Oil : | Taka | 42175404.38 | Comilla | 948 | 948 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 54688910 | Total | Taka | 244145991.004 | Mymensingh | 779 | 779 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.034 | MKWHr. | Sylhet | 346 | 346 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -5 | MW (E to W) at | 21:00 | hrs | Barisal | 266 | 266 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -287 | MW at | 3:00 | hrs | Rangpur | 553 | 553 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.3° C |  |  | Total | 8303 | 8303 |  | 0
B. |  | 2020-04-30 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15032 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7000 | MW
4 | Reserve(Generation end) |  |  |  | 5832 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 169.8621 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5418.2 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.1164 | MKWHr. | ii) HVDC Flow at Peak Time |  | 834 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.279 | MKWHr. | iii) Maximum HVDC Flow : |  | 834 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.84 |  | (b) Today: | 78.89 |  | (c) Rule Curve: |  | 82.2
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-04-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 339 | 257 |  | 0 | 300 | 120 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 260 | 265 | 142 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 90 | 214 | 0 | 0 | 0 | 89 | 30 | 8 | 5 | 100 | 148 | 40 | 5 | 0 | 49 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 579 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 |  | 3899 | 2038 | 5937 | 3239 | 579 | 1422 | 120 | 449 | 38 | 0 | 90 | 0 | 0 | 78.79
2:00 | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 367 | 308 |  | 0 | 300 | 120 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 39 | 0 | 100 | 0 | 0 | 223 | 0 | 149 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 310 | 310 | 180 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 90 | 208 | 0 | 20 | 0 | 89 | 30 | 8 | 5 | 100 | 170 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4169 | 1696 | 5865 | 3447 | 251 | 1468 | 120 | 450 | 39 | 0 | 90 | 0 | 0 | 78.8
3:00 | 24 | 0 | 0 | 0 | 250 | 12 | 0 | 392 | 335 |  | 0 | 400 | 120 | 0 | 0 | 0 | 95 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 300 | 305 | 181 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 94 | 211 | 0 | 20 | 0 | 89 | 30 | 8 | 5 | 163 | 163 | 40 | 5 | 0 | 99 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 155 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 |  | 4615 | 1928 | 6543 | 3860 | 251 | 1729 | 120 | 451 | 38 | 0 | 94 | 0 | 0 | 78.81
4:00 | 24 | 0 | 0 | 0 | 250 | 12 | 0 | 363 | 345 |  | 0 | 370 | 120 | 0 | 0 | 0 | 95 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 80 | 0 | 0 | 310 | 265 | 158 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 15 | 94 | 215 | 0 | 20 | 0 | 88 | 30 | 8 | 5 | 130 | 141 | 40 | 5 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 0 | 0 | 31 | 0 | 167 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 4440 | 1882 | 6322 | 3710 | 251 | 1659 | 120 | 450 | 38 | 0 | 94 | 0 | 0 | 78.82
5:00 | 24 | 0 | 0 | 0 | 200 | 12 | 0 | 305 | 278 |  | 0 | 270 | 120 | 0 | 0 | 0 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 16 | 23 | 0 | 0 | 38 | 0 | 100 | 0 | 0 | 183 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 245 | 235 | 152 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 80 | 187 | 0 | 0 | 0 | 88 | 30 | 8 | 5 | 100 | 98 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 251 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 |  | 3609 | 1626 | 5235 | 2993 | 251 | 1303 | 120 | 450 | 38 | 0 | 80 | 0 | 0 | 78.83
6:00 | 24 | 0 | 0 | 0 | 180 | 12 | 0 | 258 | 248 |  | 0 | 270 | 120 | 0 | 0 | 0 | 40 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 240 | 235 | 142 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 72 | 147 | 0 | 0 | 0.1 | 73 | 20 | 8 | 5 | 100 | 103 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 248 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 31 | 0 | 140 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 249 |  | 3267.97 | 1515.1 | 4783.07 | 2751 | 248 | 1156 | 120 | 399 | 36 | 0 | 72 | 1.07 | 0 | 78.84
7:00 | 24 | 0 | 0 | 0 | 220 | 12 | 0 | 259 | 248 |  | 0 | 300 | 120 | 0 | 0 | 0 | 40 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 16 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 183 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 80 | 0 | 0 | 240 | 250 | 162 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 72 | 180 | 0 | 0 | 0.6 | 73 | 20 | 8 | 5 | 100 | 101 | 40 | 5 | 0 | 50 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 249 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 251 |  | 3385.65 | 1550.4 | 4936.05 | 2859 | 249 | 1191 | 120 | 401 | 36 | 0 | 72 | 8.05 | 0 | 78.85
8:00 | 24 | 0 | 0 | 0 | 230 | 12 | 0 | 276 | 248 |  | 0 | 300 | 135 | 0 | 0 | 0 | 40 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 17 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 184 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 80 | 0 | 0 | 240 | 315 | 191 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 76 | 179 | 0 | 0 | 0.7 | 75 | 20 | 8 | 5 | 100 | 115 | 50 | 5 | 0 | 50 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 249 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 8 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 |  | 3686.3 | 1574 | 5260.3 | 3041 | 249 | 1304 | 135 | 401 | 36 | 0 | 76 | 18.3 | 0 | 78.86
9:00 | 24 | 0 | 0 | 0 | 230 | 12 | 0 | 359 | 252 |  | 0 | 320 | 135 | 0 | 0 | 0 | 80 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 17 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 222 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 295 | 290 | 183 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 86 | 177 | 0 | 0 | 0.7 | 77 | 20 | 8 | 5 | 130 | 144 | 49 | 5 | 0 | 80 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 297 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 0 | 0 | 30 | 0 | 140 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 300 |  | 4004.1 | 1775.7 | 5779.8 | 3291 | 297 | 1467 | 135 | 450 | 37 | 0 | 86 | 16.8 | 0 | 78.87
10:00 | 24 | 0 | 0 | 0 | 230 | 12 | 0 | 372 | 302 |  | 0 | 350 | 140 | 0 | 0 | 0 | 80 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 24 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 310 | 300 | 202 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 9 | 82 | 207 | 0 | 0 | 1.5 | 76 | 20 | 8 | 5 | 130 | 190 | 49 | 5 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 297 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 0 | 0 | 30 | 0 | 163 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 301 |  | 4269.1 | 1763.9 | 6033 | 3534 | 297 | 1470 | 140 | 451 | 37 | 0 | 82 | 22 | 0 | 78.88
11:00 | 24 | 0 | 0 | 0 | 260 | 12 | 0 | 371 | 302 |  | 0 | 350 | 140 | 0 | 0 | 0 | 130 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 290 | 275 | 195 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 9 | 82 | 204 | 0 | 0 | 1 | 76 | 20 | 8 | 5 | 130 | 185 | 49 | 5 | 0 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 20 |  | 298 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 0 | 0 | 31 | 0 | 208 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 301 |  | 4231.2 | 1985.4 | 6216.6 | 3592 | 298 | 1571 | 165 | 451 | 35 | 0 | 82 | 22.6 | 0 | 78.89
12:00 | 24 | 0 | 0 | 0 | 260 | 12 | 0 | 369 | 302 |  | 0 | 350 | 140 | 0 | 14 | 0 | 130 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 80 | 0 | 0 | 340 | 300 | 203 | 16 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 16 | 12 | 76 | 201 | 0 | 0 | 1.6 | 76 | 20 | 8 | 5 | 130 | 193 | 49 | 5 | 0 | 120 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 40 |  | 298 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 214 | 0 | 0 | 0 | 31 | 0 | 211 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 303 |  | 4451 | 2050.4 | 6501.4 | 3756 | 298 | 1617 | 234 | 452 | 36 | 0 | 76 | 32.4 | 0 | 78.89
13:00 | 24 | 0 | 0 | 0 | 260 | 14 | 0 | 370 | 333 |  | 0 | 400 | 135 | 0 | 15 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 80 | 0 | 0 | 355 | 290 | 202 | 16 | 0 | 25 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 12 | 82 | 189 | 0 | 0 | 2 | 77 | 20 | 8 | 5 | 130 | 189 | 48 | 5 | 0 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 16 | 0 | 0 | 0 | 0 | 70 |  | 297 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 214 | 0 | 0 | 0 | 31 | 0 | 210 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0 | 306 |  | 4693.1 | 2134.2 | 6827.3 | 3927 | 297 | 1729 | 276 | 456 | 36 | 0 | 82 | 24.3 | 0 | 78.9
14:00 | 24 | 0 | 0 | 0 | 280 | 84 | 0 | 376 | 351 |  | 0 | 400 | 125 | 0 | 15 | 0 | 219 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 100 | 0 | 0 | 315 | 275 | 191 | 55 | 0 | 39 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 33 | 13 | 86 | 175 | 0 | 20 | 2.2 | 87 | 20 | 43 | 16 | 163 | 186 | 48 | 50 | 0 | 150 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 16 | 0 | 0 | 0 | 3 | 100 |  | 298 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 214 | 0 | 0 | 0 | 31 | 0 | 209 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 0 | 319 |  | 5086.3 | 2149.3 | 7235.6 | 4042 | 298 | 1974 | 307 | 469 | 36 | 0 | 86 | 23.6 | 0 | 78.9
15:00 | 24 | 0 | 0 | 0 | 280 | 100 | 0 | 340 | 352 |  | 0 | 400 | 0 | 0 | 15 | 0 | 221 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 24 | 23 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 100 | 0 | 0 | 310 | 265 | 181 | 55 | 0 | 39 | 30 | 0 | 28 | 0 | 0 | 0 | 21 | 0 | 33 | 16 | 100 | 157 | 0 | 20 | 1.7 | 89 | 20 | 53 | 51 | 130 | 182 | 48 | 80 | 0 | 150 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4 | 16 | 0 | 0 | 0 | 17 | 100 |  | 298 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 214 | 0 | 0 | 0 | 30 | 0 | 208 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0 | 353 |  | 4977.3 | 2172.2 | 7149.5 | 3915 | 298 | 2050 | 228 | 503 | 37 | 0 | 100 | 18.5 | 0 | 78.9
16:00 | 24 | 0 | 0 | 0 | 230 | 44 | 0 | 338 | 322 |  | 0 | 400 | 0 | 0 | 15 | 0 | 221 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 100 | 0 | 0 | 280 | 270 | 181 | 55 | 0 | 39 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 18 | 94 | 157 | 0 | 20 | 1.2 | 89 | 20 | 11 | 10 | 130 | 181 | 48 | 20 | 0 | 151 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 0 | 0 | 0 | 17 | 100 |  | 298 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 170 | 0 | 0 | 0 | 30 | 0 | 190 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 351 |  | 4662.2 | 2110.2 | 6772.4 | 3748 | 298 | 1862 | 222 | 501 | 36 | 0 | 94 | 11.4 | 0 | 78.9
17:00 | 24 | 0 | 0 | 0 | 200 | 44 | 0 | 336 | 282 |  | 0 | 320 | 0 | 0 | 15 | 0 | 170 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 280 | 270 | 182 | 55 | 0 | 39 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 14 | 92 | 158 | 0 | 20 | 0.4 | 89 | 20 | 11 | 10 | 100 | 187 | 48 | 20 | 0 | 101 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 50 | 0 | 0 | 0 | 17 | 100 |  | 298 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 0 | 0 | 30 | 0 | 184 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 348 |  | 4400.5 | 2086.9 | 6487.4 | 3608 | 298 | 1729 | 222 | 498 | 36 | 0 | 92 | 4.4 | 0 | 78.9
18:00 | 24 | 0 | 0 | 0 | 200 | 44 | 0 | 350 | 282 |  | 0 | 320 | 0 | 0 | 15 | 0 | 140 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 9 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 310 | 300 | 203 | 55 | 0 | 39 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 14 | 102 | 158 | 0 | 20 | 0 | 88 | 20 | 11 | 10 | 100 | 191 | 48 | 20 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 0 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 17 | 100 |  | 298 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 30 | 0 | 184 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 351 |  | 4495 | 2131.7 | 6626.7 | 3654 | 298 | 1755 | 281 | 501 | 35 | 0 | 102 | 0.7 | 0 | 78.9
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 0 | 0 | 230 | 97 | 0 | 362 | 323 |  | 0 | 360 | 0 | 0 | 24 | 0 | 140 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 16 | 25 | 9 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 42 | 100 | 0 | 0 | 310 | 295 | 202 | 55 | 0 | 39 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 19 | 120 | 158 | 0 | 20 | 0 | 89 | 20 | 38 | 25 | 130 | 190 | 48 | 77 | 0 | 129 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 115 | 0 | 17 | 0 | 100 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 50 | 100 |  | 796 | 0 | 365 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 33 | 0 | 181 | 0 | 408 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 416 |  | 5274 | 2767 | 8041 | 3854 | 796 | 2012 | 607 | 566 | 35 | 51 | 120 | 0 | 0 | 78.9
19:30 | 24 | 0 | 0 | 0 | 240 | 101 | 0 | 356 | 323 |  | 0 | 360 | 0 | 0 | 40 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 9 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 320 | 290 | 198 | 55 | 0 | 39 | 46 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 120 | 177 | 0 | 20 | 0 | 87 | 20 | 38 | 51 | 130 | 187 | 49 | 80 | 0 | 151 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 175 | 0 | 17 | 0 | 100 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 113 | 100 |  | 833 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 76 | 0 | 175 | 0 | 408 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 70 | 443 |  | 5620 | 2986 | 8606 | 3976 | 833 | 2140 | 857 | 593 | 36 | 51 | 120 | 0 | 0 | 0
20:00 | 24 | 0 | 0 | 0 | 240 | 100 | 0 | 356 | 323 |  | 0 | 360 | 0 | 0 | 48 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 17 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 300 | 285 | 188 | 55 | 0 | 39 | 47 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 120 | 176 | 0 | 20 | 0 | 88 | 20 | 53 | 51 | 130 | 186 | 63 | 80 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 175 | 0 | 17 | 0 | 100 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 103 | 100 |  | 834 | 0 | 330 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 24 | 60 | 27 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 95 | 0 | 175 | 0 | 405 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 35 | 452 |  | 5599 | 3015 | 8614 | 3946 | 834 | 2157 | 870 | 602 | 35 | 50 | 120 | 0 | 0 | 78.9
21:00 | 24 | 0 | 0 | 0 | 280 | 102 | 0 | 355 | 323 |  | 0 | 390 | 0 | 0 | 48 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 18 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 315 | 290 | 197 | 55 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 26 | 20 | 124 | 191 | 0 | 20 | 0 | 88 | 20 | 53 | 51 | 130 | 188 | 53 | 80 | 0 | 150 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 113 | 100 |  | 834 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 60 | 28 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 178 | 0 | 407 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 454 |  | 5675 | 3068 | 8743 | 4043 | 834 | 2210 | 842 | 604 | 36 | 50 | 124 | 0 | 0 | 78.9
22:00 | 24 | 0 | 0 | 0 | 280 | 101 | 0 | 340 | 324 |  | 0 | 390 | 25 | 0 | 30 | 0 | 180 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 18 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 38 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 295 | 270 | 182 | 55 | 0 | 39 | 49 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 28 | 20 | 124 | 204 | 0 | 20 | 0 | 86 | 30 | 53 | 51 | 100 | 180 | 53 | 40 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 100 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 113 | 100 |  | 833 | 0 | 330 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 192 | 0 | 401 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 447 |  | 5434 | 2881 | 8315 | 3905 | 833 | 2104 | 679 | 597 | 35 | 38 | 124 | 0 | 0 | 78.9
23:00 | 24 | 0 | 0 | 0 | 280 | 107 | 0 | 336 | 303 |  | 0 | 360 | 110 | 0 | 15 | 0 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 18 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 280 | 270 | 180 | 55 | 0 | 39 | 51 | 0 | 14 | 0 | 0 | 0 | 21 | 11 | 28 | 20 | 116 | 208 | 0 | 20 | 0 | 86 | 30 | 11 | 10 | 100 | 180 | 40 | 40 | 0 | 120 | 0 | 0 | 0 | 295 | 0 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 65 | 100 |  | 833 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 95 | 0 | 150 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 5110 | 2628 | 7738 | 3723 | 833 | 1892 | 555 | 550 | 35 | 34 | 116 | 0 | 0 | 78.9
24:00 | 24 | 0 | 0 | 0 | 240 | 52 | 0 | 335 | 304 |  | 0 | 360 | 130 | 0 | 14 | 0 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 24 | 24 | 23 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 260 | 260 | 180 | 55 | 0 | 39 | 51 | 0 | 14 | 0 | 0 | 0 | 21 | 11 | 28 | 20 | 110 | 209 | 0 | 20 | 0 | 88 | 30 | 11 | 10 | 100 | 140 | 40 | 20 | 0 | 100 | 0 | 0 | 0 | 270 | 0 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 65 | 100 |  | 734 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 140 | 0 | 0 | 0 | 41 | 0 | 140 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 |  | 4790 | 2428 | 7218 | 3545 | 734 | 1735 | 492 | 533 | 35 | 34 | 110 | 0 | 0 | 78.9
KWH | 492000 | 0 | 0 | 0 | 5669427 | 984818 | 0 | 8377660 | 7187000 |  | 0 | 8017250 | 1910255 | 0 | 323400 | 0 | 3253874 | 0 | 2327000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37800 | 0 | 104032 | 10228 | 600000 | 302580 | 540800 | 687500 | 0 | 0 | 805020 | 0 | 2400000 | 0 | 0 | 5088438 | 0 | 1113566 | 0 |  | 0 | 0 | 246148 | 0 | 0 | 0 | 430944 | 803040 | 2155148 | 0 | 0 | 7319000 | 6835000 | 4395000 | 719272 | 0 | 478656 | 504000 | 0 | 584252 | 0 | 0 | 0 | 391320 | 64260 | 485900 | 377070 | 2279040 | 4382280 | 0 | 297972 | 13800 | 1996000 | 571440 | 452400 | 480024 | 3140754 | 3711000 | 1108224 | 627840 | 0 | 2461780 | 92000 | 0 | 45720 | 7080250 | 101026 | 66000 | 0 | 0 | 0 | 0 | 1360800 | 0 | 38880 | 110970 | 504000 | 0 | 90327 | 0 | 0 | 0 | 0 | 29640 | 393927 | 0 | 0 | 0 | 614880 | 1200000 |  | 10116363 | 0 | 7555104 | 0 | 301440 | 0 | 0 | 0 | 0 | 0 | 40875 | 1448000 | 398252 | 0 | 0 | 0 | 1285000 | 0 | 0 | 0 | 50710 | 0 | 0 | 0 | 0 | 201840 | 192096 | 216162 | 0 | 0 | 3654400 | 0 | 0 | 4380773 | 0 | 0 | 0 | 1001838 | 0 | 4400536 | 0 | 8585273 | 0 | 0 | 0 | 0 | 144960 | 0 | 45039 | 187296 | 7945800 |  | 109272632 | 52151757 | 161424389 | 87868668 | 10116363 | 41005919 | 7303582 | 11600200 | 805020 | 246148 | 2279040 | 199449 | 0
Fuel Cost | 806880 | 0 | 0 | 0 | 6293063.97 | 1299959.76 | 0 | 8461436.6 | 7402610 |  | 0 | 8738802.5 | 2120383.05 | 0 | 2228226 | 0 | 3384028.96 | 0 | 4025710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275940 | 0 | 1025755.52 | 7671 | 450000 | 0 | 0 | 0 | 0 | 0 | 217355.4 | 0 | 4344000 | 0 | 0 | 5546397.42 | 0 | 1893062.2 | 0 |  | 0 | 0 | 2387635.6 | 0 | 0 | 0 | 542989.44 | 2385028.8 | 3189619.04 | 0 | 0 | 5416060 | 6835000 | 4043400 | 927860.88 | 0 | 540881.28 | 705600 | 0 | 999070.92 | 0 | 0 | 0 | 496976.4 | 48195 | 850325 | 282802.5 | 17092800 | 4645216.8 | 0 | 378424.44 | 219972 | 3273440 | 914304 | 805272 | 748837.44 | 3580459.56 | 3859440 | 2183201.28 | 1199174.4 | 0 | 4258879.4 | 201480 | 0 | 93268.8 | 7151052.5 | 75769.5 | 50160 | 0 | 0 | 0 | 0 | 7076160 | 0 | 382579.2 | 1297239.3 | 4107600 | 0 | 636805.35 | 0 | 0 | 0 | 0 | 0 | 2978088.12 | 0 | 0 | 0 | 5269521.6 | 7992000 |  | 58270250.88 | 0 | 7932859.2 | 0 | 2369318.4 | 0 | 0 | 0 | 0 | 0 | 425917.5 | 1636240 | 617290.6 | 0 | 0 | 0 | 2634250 | 0 | 0 | 0 | 390467 | 0 | 0 | 0 | 0 | 387532.8 | 297748.8 | 163634.634 | 0 | 0 | 19806848 | 0 | 0 | 5125504.41 | 0 | 0 | 0 | 1502757 | 0 | 5148627.12 | 0 | 8499420.27 | 0 | 0 | 0 | 0 | 1124889.6 | 0 | 497680.95 | 1384117.44 | 34882062 |  | 168643872.93 | 153097416.604 | 321741289.534 | 99939929.594 | 58270250.88 | 47341747.03 | 39787768.78 | 54688910 | 217355.4 | 2387635.6 | 17092800 | 2014892.25 | 0
Yesterday Day Peak | 24 | 0 | 0 | 0 | 260 | 12 | 0 | 369 | 302 |  | 0 | 350 | 140 | 0 | 14 | 0 | 130 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 80 | 0 | 0 | 340 | 300 | 203 | 16 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 16 | 12 | 76 | 201 | 0 | 0 | 1.6 | 76 | 20 | 8 | 5 | 130 | 193 | 49 | 5 | 0 | 120 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 40 |  | 298 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 214 | 0 | 0 | 0 | 31 | 0 | 211 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 303 |  | 6501.4 | DayPeak
Yesterday Evening Peak | 24 | 0 | 0 | 0 | 280 | 102 | 0 | 355 | 323 | 0 | 0 | 390 | 0 | 0 | 48 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 18 | 24 | 23 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 22 | 42 | 100 | 0 | 0 | 315 | 290 | 197 | 55 | 0 | 39 | 48 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 26 | 20 | 124 | 191 | 0 | 20 | 0 | 88 | 20 | 53 | 51 | 130 | 188 | 53 | 80 | 0 | 150 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 113 | 100 |  | 834 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 60 | 28 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 180 | 0 | 0 | 0 | 96 | 0 | 178 | 0 | 407 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 454 |  | 8743 | EvPeak
Forecast for Evening | 24 | 0 | 0 | 0 | 280 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 217 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 42 | 135 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 40 | 20 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 22 | 141 | 210 | 95 | 20 | 0 | 88 | 30 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 170 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 839 | 40 | 410 |  | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 60 | 20 | 110 | 30 | 0 | 70 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 0 | 0 | 200 | 17 | 15 | 210 | 0 | 0 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 400
Forecast for Day | 24 | 0 | 0 | 0 | 280 | 108 | 0 | 412 | 310 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 217 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 10 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 360 | 225 | 8 | 0 | 40 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 116 | 210 | 95 | 20 | 1.6 | 88 | 30 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 100 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 0 | 0 | 170 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 114 | 113 | 100 |  | 295 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 20 | 50 | 0 | 0 | 70 | 0 | 0 | 80 | 50 | 42 | 40 | 40 | 0 | 17 | 11 | 11 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 300
Generation at 08:00(Today) | 24 | 0 | 0 | 0 | 240 | 6 | 0 | 336 | 298 | 0 | 0 | 320 | 130 | 0 | 14 | 0 | 170 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 16 | 24 | 23 | 0 | 0 | 34 | 0 | 100 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 80 | 0 | 0 | 335 | 295 | 183 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 88 | 208 | 0 | 0 | 1.2 | 88 | 30 | 5 | 5 | 0 | 140 | 40 | 5 | 0 | 80 | 0 | 0 | 0 | 315 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 245 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 0 | 0 | 41 | 0 | 176 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 301 | 0
199
| Minimum Generation |  | 4783.07 | 6:00
| Highest Generation |  | 8743 | 21:00
| Day Peak Generation |  | 6501.4 | 12:00
| Evening Peak Generation |  | 8743 | 21:00
| HVDC Max Flow |  | 834 | 20:00
| HVDC EvPeak Flow |  | 834 | 21:00
| Load factor L.F |  | 76.93%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-04-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-04-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6501.4 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5418.2 | MW
Evening Peak Generation : |  | 8743 | MW Hour : | 21:00 | Available Max Generation : |  | 15032 | MW
E.P. Demand (at gen end) : |  | 8743 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9200 | MW
Maximum Generation : |  | 8743 | MW Hour : | 21:00 | Reserve(Generation end) |  | 5832 | MW
Total Gen. (MKWH) : |  | 161.4244 | System Load Factor : | 76.93% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -287 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-04-30
Actual : | 78.89 | Ft.(MSL) , | Rule curve : | 82.2 | Ft.( MSL )
Gas Consumed : | Total = | 1083.45 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147281676.624
: |  | Coal : | 54688910 | Oil : | 42175404.38 | Total : | 244145991.004
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3262.7466 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1104.5467 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 988.7521 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 893.1066 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 807.2608 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 651.4184 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 370.6338 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 167.8919 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 502.3756 |  |  | 0 | 0%
Total | 0 |  | 8748.7326 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-1,3,4 & 5.
4) Ashuganj unit-4,5
5) Siddirganj-335 MW ST
6) Kaptai-2,5
7) Raozan #1 & 2
8) Fenchuganj 3,
9) Chandpur 163 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sikalbaha 150 MW was under shut down since at 10:45 for maintenance work.
b) Savar 132/33 kV T3 transformer was under shut down since at 09:02 for oil leakage maintenance.
c) Madaripur 132/33 kV T3 transformer was under shut down from 07:10 to 12:43 for red hot maintenance |  |  |  |  | About 8 MW power interruption occurred under Madaripur S/S
at 33 kV Takerhat feeder. |  |  |  |  | areas from 07:10 to 12:43.
d) Summit Meghnaghat CCPP GT-2 with STG tripped at 14:33 showing low gas pressure and was
Synchronized at 21:18.
e) Siddhirganj-Maniknagar 230 kV Ckt-1 tripped at 17:01 showing differential relay ,gen trip at Siddhirganj
end & dist Z1,C phase relay at Maniknagar end and was switched on at 17:15
f) Siddhirganj GT-1 tripped at 17:01 due to tripping of Siddhirganj-Maniknagar 230 kV Ckt-1 and was
synchronized at 18:27.
g) Rangpur-Kurigram 132 kV Ckt was under shut down from 20:40 to 21:50 for red hot maintenance at |  |  |  |  | About 38 MW power interruption occurred under Kurigram S/S
Y phase CT clamp. |  |  |  |  | areas from 20:40 to 21:50.
h) Barishal(S)-Barishal(N) 132 kV Ckt-1 is under shut down since at 07:34 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-04-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 492000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 5669427 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 984818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 8377660 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 323 | 7187000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 390 | 8017250 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 1910255 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 323400 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 10228
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 120 | 2327000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 180 | 3253874 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 37800 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 104032 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 902580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 540800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 687500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 38880 | Reserve
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1948 | 40864504
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110970
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 36 | 805020 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 217 | 5088438 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 1113566 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 246148 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 504000 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 430944
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 803040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29640
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 53 | 393927 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 100 | 1200000
| Chattogram area Total |  |  |  | 2166 | 720 | 13125693
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2155148 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 197 | 4395000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7319000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6835000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 478656
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 48 | 504000
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 719272 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 584252
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 90327 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 391320
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 64260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2279040
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 26 | 485900
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 377070 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 614880
| Cumilla Area Total |  |  |  | 2980 | 1420 | 27293125
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 191 | 4382280
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 297972 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 1360800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 391 | 6054852
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 88 | 1996000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 571440
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3140754
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 188 | 3711000 | FGMO & GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 452400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 51 | 480024
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 66000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 53 | 1108224 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 627840
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 150 | 2461780
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 92000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 101026
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7080250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 45720
| Sylhet Area Total |  |  |  | 1949 | 1196 | 21934458
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 834 | 10116363
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 301440
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 7555104 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 40875 | Low demand
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1328 | 18013782
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 398252 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1448000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1001838
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 454 | 7945800 | On test
| Barisal Area Total |  |  |  | 462 | 638 | 10793890
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1285000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 50710 | Low demand
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4380773 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under S/D.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 4400536 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 407 | 8585273 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 16 | 201840 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 192096 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 216162
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 187296 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 917 | 19499686
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3654400
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 35 | 144960 | Low demand
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 45039
| Rangpur Area Total |  |  |  | 605 | 185 | 3844399
| Total |  |  |  | 19107 | 8743 | 161424389
| Eastern Grid Total |  |  |  | 13543 | 5675 | 109272632
| Western Grid Total |  |  |  | 5564 | 3068 | 52151757
| National Grid Total |  |  |  | 19107 | 8743 | 161424389
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-04-29
(a) ENTIRE EASTERN GRID : |  | 5423 | MW | (b) ENTIRE WESTERN GRID : |  | 2880 | MW
i) Dhaka area |  | 2529 | MW | i) Khulna area |  | 1106 | MW
ii) Chittagong area |  | 821 | MW | ii) Rajshahi area |  | 955 | MW
iii) Comilla area |  | 948 | MW | iii) Barisal area |  | 266 | MW
iv) Mymensingh area |  | 779 | MW | iv) Rangpur area |  | 553 | MW
v) Sylhet area |  | 346 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8303 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 98 | 11:00 | Sherpur | 92 | 21:00 | Benapol | 32 | 20:00
Munsiganj | 90 | 21:00 | Srimongal | 30 | 20:00 | Jhenida | 91 | 21:00
Sonargaon | 46 | 21:00 | Shahjibazar | 68 | 18:30 | Bottail | 84 | 21:00
Shyampur | 136 | 0:00 | Fenchuganj | 26 | 3:00 | G.K Project | 48 | 20:00
Bhulta | 99 | 0:00 | Kulawara | 32 | 19:30 | Faridpur | 128 | 19:30
Madanganj | 46 | 0:00 | Sylhet | 92 | 21:00 | Madaripur | 69 | 21:00
Shitalakhya | 58 | 14:00 | Chatak | 22 | 21:00 | Sariatpur | 46 | 21:00
Rahim steel | 0 | 1:00 | Sunamganj | 34 | 19:00 | Gopalganj | 63 | 19:30
Matuail | 52 | 11:00 | Biani Bazar | 52 | 19:00 | Bagerhat | 56 | 21:00
Ghorasal | 49 | 14:00 | Comilla (S) | 120 | 19:00 | Mongla | 36 | 15:00
Narsingdi | 103 | 19:00 | Comilla(N) | 110 | 21:00 | Satkhira | 84 | 20:00
Haripur (SBU) | 38 | 15:00 | Chandpur | 78 | 21:00 | Gallamari | 36 | 13:00
Ullon | 40 | 19:00 | Feni | 96 | 21:00 | Magura | 40 | 19:30
Hasnabad | 131 | 20:00 | Chowmuhani | 134 | 21:00 | Norail | 28 | 19:30
Magbazar | 68 | 14:00 | Ashuganj | 52 | 0:00 | Chuadanga | 79 | 20:00
Maniknagar | 64 | 21:00 | Daudkandi | 100 | 19:00 | Barisal(N) | 31 | 19:00
Bangabhaban | 16 | 11:00 | B.Baria | 131 | 21:00 | Barisal (S) | 76 | 21:00
Narinda | 60 | 14:00 | Ramganj | 86 | 20:00 | Patuakhali | 88 | 20:00
Dhanmondi | 68 | 14:00 | Chaddagram | 36 | 13:00 | Bhandaria | 44 | 19:30
Lalbag | 50 | 13:00 | PHP | 10 | 10:00 | Borhan Uddin | 30 | 21:00
Madartek | 54 | 22:00 | Madunaghat | 43 | 21:00 | Ishurdi | 50 | 19:30
Dhaka University |  |  | Hathazari | 78 | 19:30 | Ruppur Paromanobik | 2 | 13:00
Mirpur | 68 | 21:00 | Khulshi | 111 | 14:00 | Natore | 94 | 20:00
Kalyanpur | 66 | 21:00 | Halishahar | 101 | 19:30 | Bogra | 125 | 21:00
Gulshan | 72 | 13:00 | Baraulia | 124 | 5:00 | Noagaon | 85 | 21:00
Uttara | 51 | 14:00 | Sikalbaha | 14 | 19:00 | Rajshahi | 117 | 21:00
Uttara New | 16 | 14:00 | Dohazari | 82 | 21:00 | Rajshahi New | 8 | 19:00
Kamrangirchar | 49 | 14:00 | Cox'sbazar | 83 | 21:00 | C.Nawabganj | 59 | 21:00
Savar | 90 | 14:00 | Chandraghona | 26 | 19:00 | Amnura | 34 | 21:00
Bhasantec | 96 | 21:00 | Kaptai | 4 | 19:30 | Pabna | 89 | 19:30
Agargaon | 34 | 14:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 86 | 19:30
Satmosjid | 68 | 14:00 | Bakulia | 75 | 22:00 | Serajganj | 72 | 19:30
Tongi | 84 | 13:00 | Julda | 18 | 1:00 | Niyamatpur | 41 | 21:00
Kabirpur | 119 | 14:00 | TK chemical | 14.5 | 19:30 | Joypurhat | 51 | 20:00
Basundhara | 78 | 22:00 | Modern Steel | 14 | 1:00 | Sherpur(Bogura) | 36 | 21:00
Manikganj | 64 | 20:00 | Shahmirpur | 27 | 21:00 | Mohastangor | 39 | 19:30
Joydevpur | 107 | 21:00 | Khagrachhari | 18 | 18:30 | Rangpur | 115 | 21:00
New Tongi | 64 | 11:00 | Matarbari | 29 | 21:00 | Lalmonirhat | 45 | 19:30
Kodda | 131 | 16:00 | Baroiar Hat | 30 | 19:30 | Saidpur | 82 | 19:30
Dhamrai | 46 | 20:00 | Rangamati | 8 | 18:00 | Purbasadipur | 81 | 20:00
Rajendrapur | 64 | 21:00 | Abul Khair 230 | 11 | 18:00 | Thakurgaon | 58 | 19:30
Valuka | 50 | 19:30 | BSRM | 3 | 12:00 | Palashbari | 93 | 20:00
Tangail | 156 | 19:00 | GPH Ispat | 6 | 1:00 | Barapukuria | 40 | 21:00
Mymensing | 187 | 19:30 | Goalpara | 15 | 15:00 | Panchagar | 35 | 20:00
Kishorganj | 114 | 20:00 | Central s/s | 75 | 21:00 | Joldhaka | 20 | 19:30
Netrokona | 95 | 19:00 | Noapara | 36 | 20:00 | Kurigram | 39 | 0.8125
Jamalpur | 115 | 21:00 | Jessore | 91 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-04-29 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 408 | 0.25 | 396 | 0.66667 | Kaliakoir | 386 | 0.875 | 378 | 0.58333
Bheramara | 405 | 0.125 | 394 | 0.83333 | Bhulta | 401 | 0.25 | 390 | 0.58333
Ashuganj(N) | 403 | 0.25 | 395 | 0.45833 | Gopalganj | 412 | 0.25 | 391 | 0.8125
Payra | 413 | 0.25 | 402 | 0.79167
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 0.041667 | 238 | 0.41667 | Comilla (N) | 240 | 0.29167 | 232 | 0.54167
Ishurdi | 239 | 0.25 | 225 | 0.8125 | Hathazari | 223 | 0.25 | 213 | 0.5
Ashuganj | 242 | 0.041667 | 236 | 0.54167 | Megnaghat | 240 | 0.125 | 232 | 0.54167
Serajganj | 235 | 0.20833 | 229 | 0.8125 | Fenchuganj | 244 | 0.25 | 239 | 0.75
Baghabari | 245 | 0.20833 | 236 | 0.58333 | Siddhirganj | 238 | 0.29167 | 231 | 0.58333
Barapukuria | 234 | 0.29167 | 225 | 0.8125 | Maniknagar | 237 | 0.25 | 230 | 0.58333
Bogra | 235 | 0.20833 | 222 | 0.8125 | Agargaon | 237 | 0.25 | 228 | 0.54167
Rajshahi | 231 | 0.29167 | 217 | 0.875 | Barisal | 245 | 0.29167 | 224 | 0.79167
Khulna South | 232 | 0.20833 | 212 | 0.54167 | AKSML | 220 | 0.29167 | 212 | 0.5
Rampura | 232 | 0.041667 | 229 | 0.625 | BSRM | 226 | 0.77083 | 216 | 0.5
Haripur | 236 | 0.25 | 230 | 0.5 | Bibiyana | 241 | 0.20833 | 235 | 0.29167
Hasnabad | 238 | 0.16667 | 230 | 0.41667 | Bhulta | 239 | 0.25 | 231 | 0.58333
Shyampur | 235 | 0.25 | 226 | 0.58333 | Ashuganj (S) | 240 | 0.25 | 234 | 0.54167
Aminbazar | 238 | 0.25 | 229 | 0.58333 | Kaliakoir | 239 | 0.16667 | 230 | 0.5
Tongi | 235 | 0.16667 | 225 | 0.54167 | GPH | 221 | 0.16667 | 211 | 0.5
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 0.20833 | 132 | 0.58333 | Hathazari | 132 | 0.25 | 126 | 0.45833
Munsiganj | 135 | 0.16667 | 130 | 0.58333 | Khulshi | 130 | 0.77083 | 122 | 0.45833
Sonargaon | 134 | 0.041667 | 132 | 0.29167 | Halishahar | 130 | 0.25 | 123 | 0.5
Shyampur | 138 | 0.20833 | 133 | 0.58333 | Baraulia | 129 | 0.8125 | 123 | 0.45833
Bhulta | 130 | 0.125 | 127 | 0.875 | Sikalbaha | 131 | 0.77083 | 123 | 0.45833
Madanganj | 138 | 0.20833 | 130 | 0.75 | Dohazari | 127 | 0.77083 | 120 | 0.5
Shitalakhya | 139 | 0.25 | 132 | 0.625 | Cox'sbazar | 123 | 0.33333 | 115 | 0.91667
Rahim steal | 136 | 0.20833 | 133 | 0.45833 | Chandraghona | 131 | 0.77083 | 125 | 0.45833
Matuail | 136 | 0.20833 | 131 | 0.58333 | Kaptai | 132 | 0.29167 | 127 | 0.58333
Ghorasal | 142 | 0.041667 | 140 | 0.41667 | A. Khaer Stl. | 129 | 0.16667 | 124 | 0.45833
Narsinghdi | 133 | 0.20833 | 129 | 0.54167 | Bakulia | 128 | 0.20833 | 122 | 0.45833
Haripur (SBU) | 137 | 0.29167 | 132 | 0.54167 | Julda | 128 | 0.70833 | 122 | 0.5
Ullon | 134 | 0.125 | 129 | 0.58333 | TK Chemical | 129 | 0.20833 | 123 | 0.5
Hasnabad | 138 | 0.16667 | 132 | 0.54167 | Modern Steel | 129 | 0.20833 | 123 | 0.5
Magbazar | 135 | 0.20833 | 130 | 0.625 | Shahmirpur | 129 | 0.29167 | 123 | 0.45833
Maniknagar | 139 | 0.20833 | 134 | 0.58333 | Khagrachhari | 130 | 0.25 | 124 | 0.45833
Bangabhaban | 139 | 0.20833 | 134 | 0.58333 | Matarbari | 124 | 0.25 | 118 | 0.5
Narinda | 139 | 0.20833 | 134 | 0.58333 | Baroiar Hat | 130 | 0.041667 | 123 | 13:00
Dhanmondi | 134 | 0.125 | 129 | 0.58333 | Rangamati | 131 | 0.77083 | 124 | 11:00
Lalbag | 139 | 0.25 | 131 | 0.58333 | Goalpara | 137 | 0.75 | 123 | 0.54167
Madartek | 134 | 0.25 | 129 | 0.58333 | Central s/s | 136 | 0.125 | 125 | 0.5
Dhaka University |  |  |  |  | Noapara | 136 | 0.20833 | 124 | 0.5
Mirpur | 137 | 0.25 | 131 | 0.8125 | Jessore | 132 | 0.16667 | 118 | 0.54167
Kalyanpur | 137 | 0.25 | 132 | 0.58333 | Benapol | 134 | 0.041667 | 122 | 0.5
Gulshan | 134 | 0.25 | 129 | 0.58333 | Jhenida | 135 | 0.25 | 117 | 0.8125
Uttara | 139 | 0.25 | 131 | 0.58333 | Bottail | 138 | 0.20833 | 126 | 0.8125
Uttara New | 137 | 0.25 | 131 | 0.58333 | G.K Project | 142 | 0.20833 | 134 | 0.8125
Kamrangirchar | 137 | 0.25 | 130 | 0.58333 | Faridpur | 139 | 0.29167 | 130 | 0.79167
Savar | 137 | 0.25 | 130 | 0.58333 | Madaripur | 140 | 0.125 | 130 | 0.79167
Bhasantec | 136 | 0.25 | 130 | 0.58333 | Sariatpur | 140 | 0.25 | 129 | 0.79167
Agargaon | 137 | 0.25 | 131 | 0.58333 | Gopalganj | 144 | 0.25 | 132 | 0.79167
Satmosjid | 137 | 0.25 | 131 | 0.58333 | Bagerhat | 135 | 0.20833 | 120 | 0.54167
Tongi | 140 | 0.16667 | 134 | 0.54167 | Mongla | 134 | 0.25 | 121 | 0.5
Kabirpur | 135 | 0.16667 | 128 | 0.875 | Satkhira | 136 | 0.20833 | 122 | 0.54167
Basundhara | 134 | 0.20833 | 129 | 0.54167 | Gallamari | 138 | 0.25 | 124 | 0.54167
Manikganj | 140 | 0.29167 | 132 | 0.875 | Magura | 135 | 0.20833 | 116 | 0.8125
Joydevpur | 143 | 0.16667 | 137 | 0.875 | Norail | 132 | 0.16667 | 116 | 0.8125
New Tongi | 139 | 0.20833 | 133 | 0.58333 | Chuadanga | 132 | 0.25 | 110 | 0.8125
Kodda | 136 | 0.20833 | 127 | 0.58333 | Barisal(N) | 141 | 0.25 | 127 | 0.79167
Dhamrai | 135 | 0.20833 | 127 | 0.875 | Barisal (S) | 139 | 0.25 | 125 | 0.79167
Rajendrapur | 142 | 0.20833 | 133 | 0.875 | Patuakhali | 138 | 0.20833 | 120 | 0.79167
Valuka | 132 | 0.25 | 118 | 0.875 | Bhandaria | 138 | 0.29167 | 123 | 0.79167
Tangail | 135 | 0.083333 | 124 | 0.8125 | Ishurdi | 140 | 0.25 | 131 | 0.8125
Mymensing | 132 | 0.25 | 119 | 0.875 | Ruppur Paromanobik | 138 | 0.20833 | 132 | 0.79167
Kishorganj | 134 | 0.25 | 124 | 0.875 | Natore | 139 | 0.25 | 128 | 0.8125
Netrokona | 131 | 0.20833 | 116 | 0.875 | Bogra | 138 | 0.25 | 128 | 0.83333
Jamalpur | 130 | 0.95833 | 119 | 0.75 | Noagaon | 134 | 0.20833 | 123 | 0.875
Sherpur | 129 | 0.95833 | 117 | 0.75 | Rajshahi | 139 | 0.20833 | 128 | 0.8125
Srimongal | 140 | 0.25 | 137 | 0.54167 | Rajshahi New | 139 | 0.29167 | 129 | 0.875
Shahjibazar | 139 | 0.20833 | 135 | 13:00 | C.Nawabganj | 138 | 0.20833 | 127 | 0.8125
Fenchuganj | 139 | 0.25 | 136 | 0.41667 | Amnura | 139 | 0.25 | 128 | 0.8125
Khulawara | 138 | 0.20833 | 135 | 0.54167 | Pabna | 136 | 0.041667 | 128 | 0.8125
Sylhet | 137 | 0.29167 | 134 | 0.54167 | Shahjadpur | 141 | 0.16667 | 136 | 0.8125
Chatak | 136 | 0.25 | 133 | 0.54167 | Serajganj | 136 | 0.20833 | 128 | 0.875
Sunamganj | 135 | 0.16667 | 131 | 0.875 | Niyamatpur | 134 | 0.20833 | 121 | 0.875
Biani Bazar | 136 | 0.20833 | 131 | 0.79167 | Joypurhat | 135 | 0.16667 | 124 | 0.8125
Comilla(s) | 131 | 0.29167 | 127 | 0.625 | Sherpur(Bogura) | 138 | 0.20833 | 127 | 0.77083
Comilla(n) | 137 | 0.29167 | 132 | 0.5 | Mohastangor | 137 | 0.25 | 127 | 0.8125
Chandpur | 130 | 0.33333 | 125 | 0.625 | Rangpur | 132 | 0.29167 | 120 | 0.8125
Feni | 133 | 0.33333 | 125 | 0.45833 | Lalmonirhat | 130 | 0.29167 | 115 | 0.8125
Chowmuhani | 126 | 0.29167 | 120 | 0.58333 | Saidpur | 132 | 0.25 | 116 | 0.8125
Ashuganj | 140 | 0.041667 | 136 | 0.875 | Purbasadipur | 131 | 0.25 | 116 | 0.8125
Daudkandi | 136 | 0.29167 | 128 | 0.58333 | Thakurgaon | 128 | 0.20833 | 116 | 0.8125
B.Baria | 138 | 0.29167 | 133 | 0.875 | Palashbari | 134 | 0.20833 | 122 | 0.54167
Ramganj | 124 | 0.33333 | 117 | 0.58333 | Barapukuria | 134 | 0.29167 | 125 | 0.8125
Chaddagram | 134 | 0.29167 | 125 | 0.58333 | Panchagar | 126 | 0.20833 | 112 | 0.8125
PHP | 127 | 0.33333 | 122 | 0.54167 | Joldhaka | 131 | 0.20833 | 115 | 0.8125
Madanhat | 132 | 0.25 | 127 | 0.45833 | Kurigram | 132 | 0.20833 | 119 | 0.8125

## L-Curve
Date | 2020-04-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 135 | 4790 | 2428 | 7218 |  |  |  | QF-LDC-12
0:30 | 104.5 | 4344.5 | 2233 | 6577.5 | Date: | 2020-04-29
1:00 | 74 | 3899 | 2038 | 5937
1:30 | 135.5 | 4034 | 1867 | 5901
2:00 | 197 | 4169 | 1696 | 5865
2:30 | 242 | 4392 | 1812 | 6204 | [5 empty] | Gen. at Eve. Peak | 8743 | 8743 MW (21:00 )
3:00 | 287 | 4615 | 1928 | 6543 | [6 empty] | 21:00
3:30 | 210.5 | 4527.5 | 1905 | 6432.5 | [5 empty] | Gen. at Day Peak | 6501.4 | 6501.4 MW (12:00 )
4:00 | 134 | 4440 | 1882 | 6322 | [6 empty] | 12:00
4:30 | 89 | 4024.5 | 1754 | 5778.5 | [5 empty] | Highest Generation | 8743
5:00 | 44 | 3609 | 1626 | 5235 | [6 empty] | 21:00
5:30 | 42 | 3438.485 | 1570.55 | 5009.035
6:00 | 40 | 3267.97 | 1515.1 | 4783.07
6:30 | 27 | 3326.81 | 1532.75 | 4859.56
7:00 | 14 | 3385.65 | 1550.4 | 4936.05
7:30 | 8 | 3535.975 | 1562.2 | 5098.175
8:00 | 2 | 3686.3 | 1574 | 5260.3
8:30 | 8 | 3845.2 | 1674.85 | 5520.05
9:00 | 14 | 4004.1 | 1775.7 | 5779.8
9:30 | 20 | 4136.6 | 1769.8 | 5906.4
10:00 | 26 | 4269.1 | 1763.9 | 6033
10:30 | 57.5 | 4250.15 | 1874.65 | 6124.8
11:00 | 89 | 4231.2 | 1985.4 | 6216.6
11:30 | 45.5 | 4341.1 | 2017.9 | 6359
12:00 | 2 | 4451 | 2050.4 | 6501.4
12:30 | 9.5 | 4572.05 | 2092.3 | 6664.35
13:00 | 17 | 4693.1 | 2134.2 | 6827.3
13:30 | 67 | 4889.7 | 2141.75 | 7031.45
14:00 | 117 | 5086.3 | 2149.3 | 7235.6
14:30 | 112 | 5031.8 | 2160.75 | 7192.55
15:00 | 107 | 4977.3 | 2172.2 | 7149.5
15:30 | 80.5 | 4819.75 | 2141.2 | 6960.95
16:00 | 54 | 4662.2 | 2110.2 | 6772.4
16:30 | 44 | 4531.35 | 2098.55 | 6629.9
17:00 | 34 | 4400.5 | 2086.9 | 6487.4
17:30 | 57.5 | 4447.75 | 2109.3 | 6557.05
18:00 | 81 | 4495 | 2131.7 | 6626.7
18:30 | 59 | 4884.5 | 2449.35 | 7333.85
19:00 | 37 | 5274 | 2767 | 8041
19:30 | 87 | 5620 | 2986 | 8606
20:00 | 43 | 5599 | 3015 | 8614 |  |  |  | Executive Engineer
20:30 | 24 | 5637 | 3041.5 | 8678.5 |  |  |  | Network Operation Division
21:00 | 5 | 5675 | 3068 | 8743
21:30 | 24 | 5554.5 | 2974.5 | 8529
22:00 | 43 | 5434 | 2881 | 8315 |  |  |  |  | Page 6 of 7
22:30 | 89.5 | 5272 | 2754.5 | 8026.5
23:00 | 136 | 5110 | 2628 | 7738
23:30 | 135.5 | 4950 | 2528 | 7478
24:00 | 135 | 4790 | 2428 | 7218
8743 MW (21:00 )
6501.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-04-29 |  | Energy | 161424389
[10 empty] | 2020-04-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3545 | 734 | 1735 | 555 | 533 | 35 | 34 | 0 | 110
0:30 | 3392 | 656.5 | 1578.5 | 337.5 | 491 | 36.5 | 17 | 0 | 100 | Date: | 2020-04-29
1:00 | 3239 | 579 | 1422 | 120 | 449 | 38 | 0 | 0 | 90
1:30 | 3343 | 415 | 1445 | 120 | 449.5 | 38.5 | 0 | 0 | 90 | [7 empty] | Total Energy | 161.4244 | Total Energy Gen 161.424 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.424 MKWHr
2:00 | 3447 | 251 | 1468 | 120 | 450 | 39 | 0 | 0 | 90 | [7 empty] | Energy not Served | 0
2:30 | 3653.5 | 251 | 1598.5 | 120 | 450.5 | 38.5 | 0 | 0 | 92 | [7 empty] | Energy Requirement | 161.4244
3:00 | 3860 | 251 | 1729 | 120 | 451 | 38 | 0 | 0 | 94
3:30 | 3785 | 251 | 1694 | 120 | 450.5 | 38 | 0 | 0 | 94 | [6 empty] | Shortage
4:00 | 3710 | 251 | 1659 | 120 | 450 | 38 | 0 | 0 | 94
4:30 | 3351.5 | 251 | 1481 | 120 | 450 | 38 | 0 | 0 | 87
5:00 | 2993 | 251 | 1303 | 120 | 450 | 38 | 0 | 0 | 80
5:30 | 2872 | 249.5 | 1229.5 | 120 | 424.5 | 37 | 0 | 0 | 76
6:00 | 2751 | 248 | 1156 | 120 | 399 | 36 | 0 | 0 | 72
6:30 | 2805 | 248.5 | 1173.5 | 120 | 400 | 36 | 0 | 0 | 72 |  |  |  |  | Coal
7:00 | 2859 | 249 | 1191 | 120 | 401 | 36 | 0 | 0 | 72
7:30 | 2950 | 249 | 1247.5 | 127.5 | 401 | 36 | 0 | 0 | 74 |  |  |  | Oil |  |  |  | ,
8:00 | 3041 | 249 | 1304 | 135 | 401 | 36 | 0 | 0 | 76
8:30 | 3166 | 273 | 1385.5 | 135 | 425.5 | 36.5 | 0 | 0 | 81
9:00 | 3291 | 297 | 1467 | 135 | 450 | 37 | 0 | 0 | 86
9:30 | 3412.5 | 297 | 1468.5 | 137.5 | 450.5 | 37 | 0 | 0 | 84
10:00 | 3534 | 297 | 1470 | 140 | 451 | 37 | 0 | 0 | 82
10:30 | 3563 | 297.5 | 1520.5 | 152.5 | 451 | 36 | 0 | 0 | 82
11:00 | 3592 | 298 | 1571 | 165 | 451 | 35 | 0 | 0 | 82
11:30 | 3674 | 298 | 1594 | 199.5 | 451.5 | 35.5 | 0 | 0 | 79
12:00 | 3756 | 298 | 1617 | 234 | 452 | 36 | 0 | 0 | 76
12:30 | 3841.5 | 297.5 | 1673 | 255 | 454 | 36 | 0 | 0 | 79
13:00 | 3927 | 297 | 1729 | 276 | 456 | 36 | 0 | 0 | 82
13:30 | 3927 | 297 | 1729 | 276 | 456 | 36 | 0 | 0 | 82
14:00 | 3927 | 297 | 1729 | 276 | 456 | 36 | 0 | 0 | 82
14:30 | 3921 | 297.5 | 1889.5 | 252 | 479.5 | 36.5 | 0 | 0 | 91
15:00 | 3915 | 298 | 2050 | 228 | 503 | 37 | 0 | 0 | 100
15:30 | 3831.5 | 298 | 1956 | 225 | 502 | 36.5 | 0 | 0 | 97
16:00 | 3748 | 298 | 1862 | 222 | 501 | 36 | 0 | 0 | 94
16:30 | 3678 | 298 | 1795.5 | 222 | 499.5 | 36 | 0 | 0 | 93
17:00 | 3608 | 298 | 1729 | 222 | 498 | 36 | 0 | 0 | 92
17:30 | 3631 | 298 | 1742 | 251.5 | 499.5 | 35.5 | 0 | 0 | 97
18:00 | 3654 | 298 | 1755 | 281 | 501 | 35 | 0 | 0 | 102
18:30 | 3754 | 547 | 1883.5 | 444 | 533.5 | 35 | 25.5 | 0 | 111
19:00 | 3854 | 796 | 2012 | 607 | 566 | 35 | 51 | 0 | 120
19:30 | 3976 | 833 | 2140 | 857 | 593 | 36 | 51 | 0 | 120
20:00 | 3946 | 834 | 2157 | 870 | 602 | 35 | 50 | 0 | 120
20:30 | 3994.5 | 834 | 2183.5 | 856 | 603 | 35.5 | 50 | 0 | 122
21:00 | 4043 | 834 | 2210 | 842 | 604 | 36 | 50 | 0 | 124
21:30 | 3974 | 833.5 | 2157 | 760.5 | 600.5 | 35.5 | 44 | 0 | 124
22:00 | 3905 | 833 | 2104 | 679 | 597 | 35 | 38 | 0 | 124
22:30 | 3814 | 833 | 1998 | 617 | 573.5 | 35 | 36 | 0 | 120
23:00 | 3723 | 833 | 1892 | 555 | 550 | 35 | 34 | 0 | 116
23:30 | 3634 | 783.5 | 1813.5 | 555 | 541.5 | 35 | 34 | 0 | 113 | Max Temp. in Dhaka |  | 31.3° C
24:00 | 3545 | 734 | 1735 | 555 | 533 | 35 | 34 | 0 | 110
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 161.424 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.424 MKWHr
Note on W13: Author:

## Generation
g | 2020-04-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 38 | 39 | 38 | 38 | 38 | 36 | 36 | 36 | 37 | 37 | 35 | 36 | 36 | 36 | 37 | 36 | 36 | 35 |  | 35 | 36 | 35 | 36 | 35 | 35 | 35 | 805020
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.67 | 5.55 | 14.3 | 13.7 | 13.9 | 12.5 | 18.5 | 15.2 | 13.3 | 6.2 | 5 | 1.5 | [9 empty] | 110970
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 223 | 223 | 183 | 183 | 183 | 184 | 222 | 224 | 218 | 218 | 218 | 218 | 218 | 217 | 217 | 217 |  | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 5088438
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 149 | 146 | 104 | 104 | 70 | 70 | 70 | 70 | 70 | [16 empty] | 1113566
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 50 | 50 | 38 | 34 | 34 | 246148
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 80 | 80 | 160 | 155 | 80 | 75 | 73 | 80 | 80 | 78 | 78 | 78 | 75 | 145 | 99 | 75 | 75 | 35 |  | 120 | 120 | 120 | 120 | 78 | 70 | 70 | 2327000
17 | Siddhirganj 335 MW CCPP | 40 | 40 | 95 | 95 | 70 | 40 | 40 | 40 | 80 | 80 | 130 | 130 | 180 | 219 | 221 | 221 | 170 | 140 |  | 140 | 180 | 180 | 180 | 180 | 180 | 150 | 3253874
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 719272
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 492000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 200 | 200 | 250 | 250 | 200 | 180 | 220 | 230 | 230 | 230 | 260 | 260 | 260 | 280 | 280 | 230 | 200 | 200 |  | 230 | 240 | 240 | 280 | 280 | 280 | 240 | 5669427
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2155148
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 478656
33 | Ashuganj 225 MW CCPP | 142 | 180 | 181 | 158 | 152 | 142 | 162 | 191 | 183 | 202 | 195 | 203 | 202 | 191 | 181 | 181 | 182 | 203 |  | 202 | 198 | 188 | 197 | 182 | 180 | 180 | 4395000
34 | Ashuganj 450 MW CCPP(South) | 265 | 310 | 305 | 265 | 235 | 235 | 250 | 315 | 290 | 300 | 275 | 300 | 290 | 275 | 265 | 270 | 270 | 300 |  | 295 | 290 | 285 | 290 | 270 | 270 | 260 | 6835000
| Ashuganj 450 MW CCPP(North) | 260 | 310 | 300 | 310 | 245 | 240 | 240 | 240 | 295 | 310 | 290 | 340 | 355 | 315 | 310 | 280 | 280 | 310 |  | 310 | 320 | 300 | 315 | 295 | 280 | 260 | 7319000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 25 | 25 | 25 |  | 25 | 46 | 47 | 48 | 49 | 51 | 51 | 504000
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 367 | 392 | 363 | 305 | 258 | 259 | 276 | 359 | 372 | 371 | 369 | 370 | 376 | 340 | 338 | 336 | 350 |  | 362 | 356 | 356 | 355 | 340 | 336 | 335 | 8377660
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 400 | 370 | 270 | 270 | 300 | 300 | 320 | 350 | 350 | 350 | 400 | 400 | 400 | 400 | 320 | 320 |  | 360 | 360 | 360 | 390 | 390 | 360 | 360 | 8017250
41 | Haripur 360MW CCPP(HPL) | 257 | 308 | 335 | 345 | 278 | 248 | 248 | 248 | 252 | 302 | 302 | 302 | 333 | 351 | 352 | 322 | 282 | 282 |  | 323 | 323 | 323 | 323 | 324 | 303 | 304 | 7187000
42 | RPCL 210MW CCPP | 214 | 208 | 211 | 215 | 187 | 147 | 180 | 179 | 177 | 207 | 204 | 201 | 189 | 175 | 157 | 157 | 158 | 158 |  | 158 | 177 | 176 | 191 | 204 | 208 | 209 | 4382280
43
44 | Fenchugonj CCPP Phase-1 | 89 | 89 | 89 | 88 | 88 | 73 | 73 | 75 | 77 | 76 | 76 | 76 | 77 | 87 | 89 | 89 | 89 | 88 |  | 89 | 87 | 88 | 88 | 86 | 86 | 88 | 1996000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 571440
46 | Shajibazar 330 MW CCPP | 148 | 170 | 163 | 141 | 98 | 103 | 101 | 115 | 144 | 190 | 185 | 193 | 189 | 186 | 182 | 181 | 187 | 191 |  | 190 | 187 | 186 | 188 | 180 | 180 | 140 | 3711000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 49 | 63 | 53 | 53 | 40 | 40 | 1108224
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 80 | 20 | 20 | 20 |  | 77 | 80 | 80 | 80 | 40 | 40 | 20 | 627840
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 49 | 50 | 99 | 150 | 50 | 50 | 50 | 50 | 80 | 80 | 80 | 120 | 150 | 150 | 150 | 151 | 101 | 100 |  | 129 | 151 | 150 | 150 | 150 | 120 | 100 | 2461780
51 | Sylhet 20 MW GTPP | [19 empty] | 18 | 18 | 18 | 18 | 18 |  |  | 92000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [19 empty] | 10 | 10 | 10 | 10 | 10 |  |  | 45720
54 | Hobiganj 11MW PP Cofidence-E | [19 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 66000
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 | 53 | 11 | 11 | 11 |  | 38 | 38 | 53 | 53 | 53 | 11 | 11 | 452400
56 | Shahjahanulla 25 MW PP | [19 empty] | 24 | 24 | 24 | 24 | 24 |  |  | 101026
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 305 | 320 | 300 | 260 | 175 | 180 | 275 | 290 | 310 | 310 | 310 | 320 | 315 | 290 | 300 | 300 | 315 |  | 290 | 320 | 305 | 320 | 290 | 295 | 270 | 7080250
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 104032
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 430944
61 | Narshingdi 22 MW PP (Doreen) | [19 empty] | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 10228
62 | Tangail 22 MW PP (Doreen) |  | 20 | 20 | 20 | [9 empty] | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 297972
63 | Impoprt (Tripura) | 90 | 90 | 94 | 94 | 80 | 72 | 72 | 76 | 86 | 82 | 82 | 76 | 82 | 86 | 100 | 94 | 92 | 102 |  | 120 | 120 | 120 | 124 | 124 | 116 | 110 | 2279040
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 13 | 12 | 10 | 10 | 10 | 12 | 18 | 14 | 14 | 18 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 803040
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 391320
66 | Feni 11 MW PP (Doreen) | [19 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 64260
67 | Jangalia 33MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 26 | 28 | 28 | 28 | 485900
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 12 | 13 | 16 | 18 | 14 | 14 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 377070
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 12 | 12 | 12 | 7 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 10 | 9 | 10 | 10 | 10 | 9 |  | 9 | 9 | 17 | 18 | 18 | 18 | 24 | 302580
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 540800
72 | Rupganj 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 687500
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 84 | 100 | 44 | 44 | 44 |  | 97 | 101 | 100 | 102 | 101 | 107 | 52 | 984818
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | [13 empty] | 3 | 17 | 17 | 17 | 17 |  | 50 | 113 | 103 | 113 | 113 | 65 | 65 | 614880
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0.2 | 1.5 | 3.3 | 1.7 | 4.7 | 2.7 | 4.9 | 0.9 | 2.8 | 4.4 | 1 | 0.6 | [9 empty] | 29640
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | [10 empty] | 0 | 14 | 15 | 15 | 15 | 15 | 15 | 15 |  | 24 | 40 | 48 | 48 | 30 | 15 | 14 | 323400
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 135 | 135 | 140 | 140 | 140 | 135 | 125 | [9 empty] | 25 | 110 | 130 | 1910255
87 | Meghnaghat 100 MW(IEL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 | 51 | 10 | 10 | 10 |  | 25 | 51 | 51 | 51 | 51 | 10 | 10 | 480024
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 14 | 14 | 584252
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV)
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern)
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 163 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 100 | 100 |  | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 3140754
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.6 | 0.7 | 0.7 | 1.5 | 1 | 1.6 | 2 | 2.2 | 1.7 | 1.2 | 0.4 | [9 empty] | 13800
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 17 | 17 |  |  |  |  | 37800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [10 empty] | 5 | 40 | 40 | 48 | 80 | 40 | 40 | 40 |  | 115 | 175 | 175 | 180 | 182 | 182 | 100 | 1360800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [17 empty] | 2 |  | 17 | 17 | 17 |  |  |  |  | 38880
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 40 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 504000
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 2 |  | 26 | 40 | 38 | 10 | 6 |  |  | 90327
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [26 empty] | 0
| Anwara 300 MW PP (United) | [12 empty] | 16 | 16 | 16 | 50 | 50 | 53 |  | 52 | 52 | 52 | 53 | 16 | 16 | 16 | 393927
| Juldah unit-2 | [10 empty] | 20 | 40 | 70 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1200000
120 | Eastern Zone Total | 3899 | 4169 | 4615 | 4440 | 3609 | 3267.97 | 3385.65 | 3686.3 | 4004.1 | 4269.1 | 4231.2 | 4451 | 4693.1 | 5086.3 | 4977.3 | 4662.2 | 4400.5 | 4495 |  | 5274 | 5620 | 5599 | 5675 | 5434 | 5110 | 4790 | 109272632
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [19 empty] | 17 | 66 | 92 | 115 | 60 |  |  | 301440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 |  | 33 | 76 | 95 | 96 | 96 | 95 | 41 | 1001838
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1448000
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 17 | 17 | 13 | 11 | 11 | 11 | 12 | 13 | 15 | 16 | 16 | 16 | 13 | 16 | 15 | 19 |  | 25 | 26 | 27 | 28 | 26 | 22 | 21 | 398252
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [21 empty] | 24 | 24 |  |  |  | 40875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 579 | 251 | 251 | 251 | 251 | 248 | 249 | 249 | 297 | 297 | 298 | 298 | 297 | 298 | 298 | 298 | 298 | 298 |  | 796 | 833 | 834 | 834 | 833 | 833 | 734 | 10116363
147 | Bheramara 410 MW CCPP | 245 | 245 | 375 | 285 | 235 | 220 | 220 | 225 | 225 | 260 | 290 | 290 | 360 | 340 | 335 | 330 | 335 | 375 |  | 365 | 345 | 330 | 355 | 330 | 330 | 330 | 7555104
148 | Payra 1320 MW | 299 | 300 | 301 | 300 | 300 | 249 | 251 | 250 | 300 | 301 | 301 | 303 | 306 | 319 | 353 | 351 | 348 | 351 |  | 416 | 443 | 452 | 454 | 447 | 400 | 384 | 7945800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3654400
153 | Baghabari 71 MW GTPP | 40 | 40 | 70 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 40 | 40 | 40 | 1285000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 155 | 200 | 140 | 130 | 130 | 130 | 135 | 160 | 190 | 214 | 214 | 214 | 214 | 170 | 160 | 140 |  | 140 | 180 | 180 | 180 | 180 | 150 | 140 | 4380773
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 167 | 140 | 140 | 140 | 140 | 140 | 163 | 208 | 211 | 210 | 209 | 208 | 190 | 184 | 184 |  | 181 | 175 | 175 | 178 | 192 | 150 | 140 | 4400536
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 322 | 307 | 362 | 365 | 250 | 220 | 250 | 269 | 364 | 266 | 362 | 397 | 410 | 410 | 402 | 408 | 402 | 409 |  | 408 | 408 | 405 | 407 | 401 | 362 | 359 | 8585273
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 8 | 14 | 14 | 14 | 14 |  | 15 | 15 | 15 | 16 | 17 | 17 | 17 | 201840
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192096
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 216162
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 12 | 12 | 12 |  |  |  | 50710
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 30 | 70 | 35 | 35 |  |  |  | 187296
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 30 | 38 | 40 | 35 | 30 |  |  | 144960
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.4 |  | 0.7 | 1.9 | 6.4 | 7.4 | 6.2 | 5.3 | 6.2 | 4.2 | 1.9 | 0.7 | [8 empty] | 45039
178
178