## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-05-05 | Tuesday
|  | Date (day): | 2020-05-05 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12023.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15360 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-05-04 | 2020-05-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 24 | 24 | 24 | 24 |  | 61 | Unit-1 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 280 | 280 | 280 | 280 |  | 85 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 30 | 71 | 78 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 107 | 110 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 342 | 0 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 322 | 200 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 380 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 140 | 135 | 150 | 150 | 155 |  | Gas shortage & GT-1 S/D
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 16 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 179 | 140 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 47 | 45 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 27 | 20 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 200 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 132 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2005 | 2508 | 2917 | 4188 | 446 | 1227
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 38 | 40 | 40 | 190 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 224 | 221 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 140 | 140
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 40 | 15 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.5 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 210 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 664.3 | 1056 | 1581 | 1711 | 450 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 216 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 280 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 285 | 360 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 42 | 42 | 40 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 48 | 5 | 52 | 52 | 3 |  | Gas shortage
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 26 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 128 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 134 | 116 | 141
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 20 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 36 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1309 | 1533 | 1772 | 2349 | 441 | 163
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 156 | 210 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.7 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 74 | 176 | 176 | 176 |  | 24 | Machine problem
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 104 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 247.7 | 456 | 617.6 | 616 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 41 | 42 | 42 |  |  | GT-1 under maint.
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 32 | 29 | 32 | 32 |  | 61 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 83 | 247 | 220 | 220 |  | 110 | ST Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 61 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 80 | 81 | 81
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 150 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 295 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1095 | 1200 | 1255 | 1255 | 0 | 571
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 409 | 799 | 401 | 797
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 24 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 330 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 803 | 1334 | 1186 | 2042 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 32 | 30 | 30
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 83 | 83 | 83 |  | 111 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 32 | 98 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 380 | 670 | 525 | 660 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 514 | 915 | 777 | 1008 | 0 | 111
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 50 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 45 | 50 | 70 | 30 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 150 | 145 | 0 | 0 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 150 | 220 | 220 |  | Gas shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 176 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 397 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 14 | 16 | 17 | 17 |  | 5 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 911 | 1007 | 1597 | 1846 | 250 | 22
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 151 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.9 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 157.9 | 264 | 321 | 345 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 7706.9 | 10273 | 12023.6 | 15360 | 1757 | 2192
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7211.7619 | 9613 | 11251.1308 | 14373.1802
A. |  | 2020-05-04 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10273 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5911.59 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10273 | MW
3 | Day peak Generation : |  |  | 7706.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9613 | MW
4 | Evening peak Generation : |  |  | 10273 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 193.2139 | MKWHr | By Solar | 0.22301 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 143.3415 | MKWHr |  | By Oil: | 20.7124 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.6378 | MKWHr |  | By Hydro: | 0.80142 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1757 | MW | Dhaka | 3024 | 3024 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2192 | MW | Chittagong | 872 | 872 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3949 | MW | Khulna | 1326 | 1326 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1183.81 | MMCFD |  |  | Rajshahi | 1134 | 1134 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 168906289.794 | ii) Oil : | Taka | 133416047.57 | Comilla | 1029 | 1029 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 68046428 | Total | Taka | 370368765.364 | Mymensingh | 872 | 872 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.1695 | MKWHr. | Sylhet | 419 | 419 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -148 | MW (E to W) at | 21:00 | hrs | Barisal | 266 | 266 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -331 | MW at | 3:00 | hrs | Rangpur | 671 | 671 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 9613 | 9613 |  | 0
B. |  | 2020-05-05 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15360 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 4560 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 203.1256 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7080.3 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.8625 | MKWHr. | ii) HVDC Flow at Peak Time |  | 799 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6352 | MKWHr. | iii) Maximum HVDC Flow : |  | 799 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.94 |  | (b) Today: | 79.03 |  | (c) Rule Curve: |  | 81.24
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-05-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 24 | 0 | 0 | 0 | 280 | 110 | 0 | 338 | 360 |  | 0 | 420 | 135 | 0 | 30 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 20 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 100 | 0 | 0 | 300 | 270 | 181 | 8 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 106 | 158 | 0 | 20 | 0 | 41 | 32 | 53 | 44 | 130 | 170 | 62 | 80 | 0 | 150 | 19 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 100 |  | 455 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 21 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 195 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 |  | 5345 | 2450 | 7795 | 4024 | 455 | 2174 | 501 | 500 | 35 | 0 | 106 | 0 | 0 | 78.89
2:00 | 24 | 0 | 0 | 0 | 280 | 110 | 0 | 340 | 360 |  | 0 | 420 | 130 | 0 | 30 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 223 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 100 | 0 | 0 | 315 | 290 | 198 | 8 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 102 | 158 | 0 | 20 | 0 | 42 | 32 | 53 | 50 | 163 | 179 | 62 | 80 | 0 | 150 | 19 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 100 |  | 263 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 21 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 0 | 0 | 96 | 0 | 196 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 |  | 5383 | 2264 | 7647 | 4096 | 263 | 2213 | 437 | 500 | 36 | 0 | 102 | 0 | 0 | 78.9
3:00 | 24 | 0 | 0 | 0 | 280 | 110 | 0 | 377 | 360 |  | 0 | 450 | 135 | 0 | 30 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 22 | 25 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 135 | 0 | 0 | 310 | 290 | 193 | 80 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 106 | 158 | 0 | 20 | 0 | 41 | 32 | 53 | 47 | 163 | 175 | 63 | 80 | 0 | 149 | 19 | 0 | 10 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 45 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 65 | 100 |  | 263 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 21 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 205 | 0 | 0 | 0 | 96 | 0 | 205 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 438 |  | 5721 | 2353 | 8074 | 4161 | 263 | 2324 | 596 | 588 | 36 | 0 | 106 | 0 | 0 | 78.91
4:00 | 24 | 0 | 0 | 0 | 280 | 110 | 0 | 335 | 284 |  | 0 | 400 | 125 | 0 | 64 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 13 | 20 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 135 | 0 | 0 | 260 | 250 | 181 | 83 | 0 | 42 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 104 | 160 | 0 | 20 | 0 | 41 | 32 | 53 | 47 | 130 | 165 | 63 | 80 | 0 | 100 | 19 | 0 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 65 | 30 |  | 263 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 23 | 0 | 0 | 50 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 200 | 0 | 0 | 0 | 96 | 0 | 177 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 |  | 5390 | 2229 | 7619 | 3787 | 263 | 2104 | 748 | 576 | 37 | 0 | 104 | 0 | 0 | 78.92
5:00 | 24 | 0 | 0 | 0 | 200 | 55 | 0 | 334 | 284 |  | 0 | 370 | 125 | 0 | 30 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 13 | 20 | 10 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 135 | 0 | 0 | 270 | 250 | 181 | 8 | 0 | 42 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 90 | 160 | 0 | 20 | 0 | 39 | 32 | 5 | 5 | 130 | 165 | 40 | 10 | 0 | 101 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 |  | 263 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 96 | 0 | 153 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 |  | 4334 | 2020 | 6354 | 3525 | 263 | 1619 | 315 | 505 | 37 | 0 | 90 | 0 | 0 | 78.93
6:00 | 24 | 0 | 0 | 0 | 200 | 15 | 0 | 335 | 284 |  | 0 | 370 | 125 | 0 | 15 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 20 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 223 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 35 | 80 | 0 | 0 | 270 | 250 | 180 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 20 | 86 | 160 | 0 | 20 | 0.1 | 39 | 32 | 5 | 5 | 130 | 162 | 40 | 10 | 0 | 99 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 10 |  | 262 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 15 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 63 | 0 | 140 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 319 |  | 3986.39 | 1925.2 | 5911.59 | 3339 | 262 | 1559 | 158 | 469 | 37 | 0 | 86 | 1.59 | 0 | 78.94
7:00 | 24 | 0 | 0 | 0 | 200 | 13 | 0 | 359 | 314 |  | 0 | 340 | 140 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 20 | 27 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 190 | 0 | 115 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 80 | 0 | 0 | 305 | 290 | 150 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 12 | 88 | 156 | 0 | 20 | 0.6 | 40 | 32 | 5 | 5 | 130 | 178 | 63 | 10 | 0 | 101 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 10 |  | 262 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 14 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 8 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 32 | 0 | 140 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 282 |  | 4081.7 | 1928.8 | 6010.5 | 3474 | 262 | 1554 | 158 | 432 | 37 | 0 | 88 | 5.5 | 0 | 78.95
8:00 | 24 | 0 | 0 | 0 | 250 | 13 | 0 | 373 | 356 |  | 0 | 390 | 140 | 0 | 4 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 20 | 27 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 222 | 0 | 112 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 6 | 80 | 0 | 0 | 315 | 300 | 202 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 90 | 156 | 0 | 20 | 1.2 | 42 | 32 | 5 | 5 | 130 | 188 | 40 | 10 | 0 | 121 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 10 |  | 262 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 14 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 8 | 0 | 0 | 150 | 0 | 0 | 165 | 0 | 0 | 0 | 31 | 0 | 165 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 | 283 |  | 4426.2 | 2043.4 | 6469.6 | 3758 | 262 | 1711 | 162 | 433 | 37 | 0 | 90 | 16.6 | 0 | 78.79
9:00 | 24 | 0 | 0 | 0 | 250 | 60 | 0 | 379 | 352 |  | 0 | 390 | 135 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 20 | 27 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 224 | 0 | 110 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 100 | 0 | 0 | 315 | 300 | 202 | 36 | 0 | 36 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 96 | 155 | 0 | 20 | 1.8 | 42 | 32 | 5 | 5 | 163 | 178 | 59 | 10 | 0 | 150 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 10 |  | 383 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 185 | 0 | 0 | 0 | 31 | 0 | 194 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 0 | 304 |  | 4702.4 | 2258.2 | 6960.6 | 3944 | 383 | 1826 | 200 | 454 | 37 | 0 | 96 | 20.6 | 0 | 78.79
10:00 | 24 | 0 | 0 | 0 | 250 | 98 | 0 | 372 | 351 |  | 0 | 390 | 135 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 24 | 27 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 225 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 100 | 0 | 0 | 310 | 295 | 202 | 36 | 0 | 36 | 30 | 0 | 15 | 0 | 0 | 0 | 21 | 8 | 33 | 0 | 102 | 151 | 0 | 20 | 0.8 | 42 | 32 | 48 | 25 | 163 | 102 | 61 | 10 | 0 | 150 | 0 | 0 | 10 | 320 | 24 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 40 |  | 409 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 17 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 149 | 0 | 0 | 190 | 0 | 0 | 0 | 32 | 0 | 206 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 303 |  | 4915.2 | 2345.8 | 7261 | 3989 | 409 | 1981 | 264 | 452 | 37 | 0 | 102 | 27 | 0 | 78.79
11:00 | 24 | 0 | 0 | 0 | 250 | 107 | 0 | 366 | 349 |  | 0 | 420 | 135 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 28 | 27 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 225 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 100 | 0 | 0 | 350 | 305 | 203 | 36 | 0 | 42 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 104 | 150 | 0 | 20 | 2.5 | 42 | 32 | 48 | 50 | 163 | 86 | 59 | 40 | 0 | 150 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 40 |  | 409 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 16 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 190 | 0 | 0 | 0 | 32 | 0 | 206 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 317 |  | 5149.5 | 2359.4 | 7508.9 | 4084 | 409 | 2116 | 264 | 467 | 37 | 0 | 104 | 27.9 | 0 | 78.79
12:00 | 24 | 0 | 0 | 0 | 280 | 107 | 0 | 375 | 348 |  | 0 | 420 | 140 | 0 | 15 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 28 | 27 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 135 | 0 | 0 | 335 | 290 | 203 | 45 | 0 | 42 | 48 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 100 | 151 | 0 | 20 | 2.7 | 42 | 32 | 48 | 50 | 163 | 83 | 58 | 80 | 0 | 150 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 16 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 370 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 18 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 32 | 0 | 198 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0 | 380 |  | 5321 | 2385.9 | 7706.9 | 4058 | 409 | 2169 | 369 | 530 | 36 | 0 | 100 | 35.9 | 0 | 78.79
13:00 | 24 | 0 | 0 | 0 | 280 | 107 | 0 | 369 | 347 |  | 0 | 420 | 140 | 0 | 20 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 28 | 27 | 0 | 0 | 34 | 0 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 135 | 0 | 0 | 330 | 285 | 201 | 45 | 0 | 42 | 48 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 0 | 92 | 151 | 0 | 20 | 0.9 | 42 | 32 | 50 | 50 | 163 | 82 | 58 | 80 | 0 | 150 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 18.8 | 30 | 0 | 8 | 0 | 0 | 0 | 0 | 5.4 | 82 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 365 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 19 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 136 | 0 | 0 | 0 | 33 | 0 | 198 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 453 |  | 5449.1 | 2503.8 | 7952.9 | 4011 | 409 | 2168 | 604 | 603 | 34 | 0 | 92 | 31.9 | 0 | 78.98
14:00 | 24 | 0 | 0 | 0 | 280 | 107 | 0 | 375 | 346 |  | 0 | 420 | 140 | 0 | 30 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 33 | 10 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 135 | 0 | 0 | 340 | 295 | 182 | 45 | 0 | 42 | 48 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 19 | 110 | 151 | 0 | 20 | 2.1 | 42 | 32 | 53 | 50 | 163 | 90 | 57 | 80 | 0 | 150 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 17.3 | 100 | 0 | 23 | 0 | 0 | 0 | 0 | 2.6 | 123 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 375 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 22 | 0 | 0 | 50 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 139 | 0 | 0 | 0 | 50 | 0 | 199 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 0 | 550 |  | 5654 | 2637.2 | 8291.2 | 4040 | 409 | 2187 | 782 | 700 | 35 | 0 | 110 | 28.2 | 0 | 78.99
15:00 | 24 | 0 | 0 | 0 | 280 | 107 | 30 | 371 | 347 |  | 0 | 420 | 140 | 0 | 40 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 33 | 27 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 135 | 0 | 0 | 320 | 280 | 177 | 45 | 0 | 42 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 19 | 112 | 150 | 0 | 20 | 1.4 | 42 | 32 | 53 | 50 | 163 | 89 | 57 | 80 | 0 | 144 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 13.7 | 100 | 0 | 60 | 0 | 0 | 0 | 0 | 2.6 | 174 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 0 | 0 | 50 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 139 | 0 | 0 | 0 | 72 | 0 | 215 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 547 |  | 5756.7 | 2656 | 8412.7 | 4004 | 409 | 2220 | 912 | 697 | 35 | 0 | 112 | 23.7 | 0 | 78.99
16:00 | 24 | 0 | 0 | 0 | 240 | 106 | 30 | 343 | 322 |  | 0 | 380 | 140 | 0 | 64 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 20 | 33 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 28 | 135 | 0 | 0 | 315 | 270 | 176 | 45 | 0 | 42 | 25 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 110 | 151 | 0 | 20 | 0.3 | 42 | 30 | 14 | 50 | 130 | 106 | 58 | 30 | 0 | 78 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 4 | 10.4 | 100 | 0 | 60 | 0 | 0 | 0 | 0 | 1.2 | 174 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 340 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 20 | 0 | 0 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 137 | 0 | 0 | 0 | 72 | 0 | 201 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 550 |  | 5389.9 | 2600.6 | 7990.5 | 3790 | 409 | 2040 | 890 | 700 | 36 | 2 | 110 | 13.5 | 0 | 79
17:00 | 24 | 0 | 0 | 0 | 240 | 107 | 30 | 360 | 322 |  | 0 | 380 | 130 | 0 | 64 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 20 | 33 | 20 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 218 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 135 | 0 | 0 | 290 | 265 | 208 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 104 | 151 | 0 | 20 | 0.5 | 42 | 29 | 14 | 50 | 130 | 116 | 58 | 30 | 0 | 80 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 140 | 0 | 16 | 1.5 | 50 | 0 | 60 | 0 | 0 | 0 | 0 | 0.9 | 107 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 0 | 0 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 72 | 0 | 184 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 550 |  | 5229.9 | 2474.1 | 7704 | 3676 | 409 | 2021 | 750 | 700 | 36 | 4 | 104 | 4 | 0 | 79
18:00 | 24 | 0 | 0 | 0 | 240 | 110 | 30 | 341 | 323 |  | 0 | 340 | 140 | 1 | 64 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 20 | 28 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 6 | 221 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 285 | 270 | 192 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 17 | 118 | 151 | 0 | 20 | 0.1 | 42 | 29 | 14 | 50 | 130 | 162 | 59 | 30 | 0 | 80 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 2 | 0 | 0 | 140 | 0 | 16 | 0.2 | 50 | 0 | 60 | 0 | 2 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 8 | 100 |  | 408 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 22 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 12 | 0 | 5 | 0 | 0 | 15 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 52 | 0 | 0 | 0 | 72 | 0 | 185 | 0 | 409 | 0 | 0 | 0 | 0 | 5 | 0 | 0.5 | 20 | 600 |  | 5228.3 | 2563.5 | 7791.8 | 3670 | 408 | 1987 | 816 | 750 | 37 | 5 | 118 | 0.8 | 0 | 79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 24 | 0 | 0 | 0 | 240 | 110 | 30 | 347 | 283 |  | 0 | 340 | 120 | 14 | 82 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 19 | 25 | 12 | 28 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 8 | 221 | 0 | 147 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 315 | 300 | 210 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 132 | 151 | 0 | 20 | 0 | 42 | 29 | 53 | 50 | 100 | 172 | 59 | 80 | 0 | 80 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 74 | 0 | 0 | 193 | 0 | 43 | 0 | 100 | 0 | 75 | 0 | 40 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 113 | 100 |  | 781 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 30 | 0 | 0 | 50 | 55 | 0 | 0 | 0 | 50 | 0 | 6 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 93 | 0 | 0 | 0 | 80 | 0 | 175 | 0 | 408 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 50 | 640 |  | 5975 | 3214 | 9189 | 3833 | 781 | 2012 | 1530 | 790 | 37 | 74 | 132 | 0 | 0 | 79.01
19:30 | 24 | 0 | 0 | 0 | 240 | 110 | 30 | 335 | 283 |  | 0 | 380 | 120 | 50 | 97 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 14 | 28 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 8 | 220 | 0 | 145 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 280 | 265 | 211 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 130 | 153 | 0 | 20 | 0 | 42 | 29 | 53 | 50 | 100 | 174 | 59 | 80 | 0 | 140 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 180 | 0 | 0 | 175 | 0 | 75 | 0 | 100 | 0 | 114 | 0 | 104 | 0 | 0 | 0 | 208 | 0 | 0 | 36 | 113 | 100 |  | 799 | 0 | 335 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 31 | 32 | 0 | 50 | 55 | 0 | 0 | 0 | 50 | 0 | 7 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 0 | 0 | 97 | 50 | 180 | 0 | 407 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 663 |  | 6363 | 3459 | 9822 | 3832 | 799 | 2089 | 2047 | 813 | 37 | 75 | 130 | 0 | 0 | 0
20:00 | 24 | 0 | 0 | 0 | 240 | 109 | 30 | 347 | 323 |  | 0 | 380 | 125 | 45 | 96 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 20 | 28 | 20 | 0 | 0 | 38 | 0 | 100 | 0 | 8 | 220 | 0 | 145 | 0 |  | 0 | 0 | 68 | 0 | 4 | 0 | 22 | 40 | 135 | 0 | 0 | 280 | 280 | 214 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 130 | 155 | 0 | 20 | 0 | 42 | 29 | 53 | 50 | 100 | 184 | 61 | 80 | 0 | 150 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 189 | 0 | 0 | 176 | 0 | 124 | 0 | 100 | 0 | 118 | 0 | 94 | 0 | 0 | 0 | 210 | 0 | 0 | 36 | 113 | 100 |  | 798 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 31 | 32 | 0 | 45 | 50 | 0 | 0 | 0 | 50 | 0 | 8 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 142 | 0 | 0 | 0 | 97 | 41 | 180 | 0 | 380 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 90 | 667 |  | 6509 | 3438 | 9947 | 3879 | 798 | 2089 | 2120 | 817 | 38 | 76 | 130 | 0 | 0 | 79.01
21:00 | 24 | 0 | 0 | 0 | 280 | 110 | 30 | 342 | 322 |  | 0 | 380 | 135 | 50 | 96 | 15 | 0 | 0 | 140 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 16 | 25 | 22 | 28 | 20 | 0 | 0 | 38 | 0 | 100 | 0 | 8 | 221 | 0 | 139 | 0 |  | 0 | 0 | 68 | 0 | 10 | 0 | 22 | 40 | 135 | 0 | 0 | 280 | 285 | 216 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 134 | 156 | 0 | 20 | 0 | 41 | 29 | 53 | 50 | 130 | 247 | 61 | 80 | 0 | 150 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 200 | 0 | 0 | 176 | 0 | 132 | 0 | 100 | 0 | 128 | 0 | 104 | 0 | 0 | 0 | 210 | 0 | 0 | 36 | 113 | 100 |  | 799 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 32 | 32 | 0 | 45 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 151 | 0 | 0 | 145 | 0 | 0 | 0 | 98 | 50 | 176 | 0 | 397 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 670 |  | 6753 | 3520 | 10273 | 4017 | 799 | 2133 | 2247 | 821 | 38 | 84 | 134 | 0 | 0 | 79.01
22:00 | 24 | 0 | 0 | 0 | 280 | 110 | 30 | 344 | 322 |  | 0 | 420 | 134 | 0 | 96 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 22 | 28 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 8 | 221 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 40 | 0 | 0 | 0 | 315 | 290 | 215 | 45 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 136 | 154 | 0 | 20 | 0 | 42 | 29 | 53 | 50 | 130 | 235 | 61 | 80 | 0 | 149 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 120 | 0 | 0 | 176 | 0 | 128 | 0 | 100 | 0 | 135 | 0 | 110 | 0 | 0 | 0 | 216 | 0 | 0 | 36 | 113 | 100 |  | 799 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 32 | 32 | 0 | 45 | 50 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 97 | 50 | 172 | 0 | 416 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 666 |  | 6530 | 3492 | 10022 | 3949 | 799 | 2205 | 2030 | 816 | 37 | 50 | 136 | 0 | 0 | 79.02
23:00 | 24 | 0 | 0 | 0 | 280 | 110 | 35 | 342 | 322 |  | 0 | 420 | 130 | 0 | 97 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 22 | 28 | 20 | 0 | 0 | 37 | 0 | 100 | 0 | 8 | 223 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 40 | 0 | 0 | 0 | 310 | 285 | 214 | 83 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 128 | 156 | 0 | 20 | 0 | 42 | 29 | 53 | 50 | 163 | 243 | 61 | 80 | 0 | 150 | 19 | 0 | 10 | 285 | 24 | 11 | 0 | 15 | 0 | 0 | 176 | 0 | 48 | 0 | 100 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 113 | 100 |  | 799 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 29 | 16 | 0 | 45 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 0 | 0 | 96 | 50 | 177 | 0 | 383 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 109 | 663 |  | 6156 | 3414 | 9570 | 3909 | 799 | 2240 | 1610 | 813 | 37 | 34 | 128 | 0 | 0 | 79.02
24:00 | 24 | 0 | 0 | 0 | 280 | 110 | 73 | 350 | 322 |  | 0 | 420 | 140 | 0 | 97 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 25 | 22 | 28 | 25 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 40 | 0 | 0 | 0 | 300 | 280 | 215 | 83 | 0 | 42 | 55 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 124 | 156 | 0 | 20 | 0 | 41 | 29 | 53 | 50 | 163 | 237 | 61 | 80 | 0 | 150 | 19 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 195 | 0 | 15 | 0 | 100 | 0 | 70 | 0 | 24 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 113 | 100 |  | 652 | 0 | 335 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 40 | 60 | 27 | 16 | 0 | 45 | 40 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 0 | 0 | 97 | 0 | 175 | 0 | 407 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 600 |  | 6111 | 3072 | 9183 | 3868 | 652 | 2366 | 1353 | 750 | 36 | 34 | 124 | 0 | 0 | 79.02
KWH | 480000 | 0 | 0 | 0 | 6210400 | 2165136 | 393568 | 8646660 | 7884000 |  | 0 | 8873000 | 3261818 | 128640 | 1203024 | 50977 | 0 | 0 | 3808000 | 0 | 0 | 0 | 22560 | 0 | 0 | 0 | 0 | 309240 | 187722 | 108765 | 293400 | 600000 | 431460 | 683700 | 617900 | 0 | 0 | 801420 | 0 | 2400000 | 0 | 49072 | 5192475 | 0 | 3195178 | 0 |  | 0 | 0 | 306337 | 0 | 21192 | 0 | 519504 | 688320 | 2629676 | 0 | 0 | 7723100 | 6879000 | 4749000 | 853090 | 0 | 837648 | 550560 | 0 | 1024712 | 0 | 0 | 0 | 493920 | 156960 | 710200 | 377180 | 2635200 | 3633520 | 0 | 444672 | 14400 | 980000 | 738461 | 900600 | 972576 | 3517118 | 3529000 | 1361568 | 1368960 | 0 | 3120000 | 307000 | 0 | 186300 | 7489500 | 372192 | 154000 | 0 | 664909 | 0 | 0 | 3240000 | 0 | 535680 | 123930 | 1153920 | 0 | 1030400 | 0 | 490800 | 0 | 0 | 31680 | 2039891 | 0 | 0 | 131100 | 853440 | 1824000 |  | 10862545 | 0 | 8692704 | 0 | 1171200 | 0 | 0 | 0 | 0 | 0 | 201750 | 2019816 | 507290 | 140544 | 0 | 1247000 | 1295000 | 0 | 0 | 0 | 196540 | 0 | 20367 | 0 | 0 | 315360 | 172548 | 243882 | 0 | 0 | 3676200 | 0 | 0 | 3894382 | 0 | 0 | 0 | 1688142 | 240000 | 4656636 | 0 | 9465545 | 0 | 0 | 0 | 0 | 512640 | 0 | 53003 | 615840 | 10961600 |  | 130363331 | 62850534 | 193213865 | 94325194 | 10862545 | 49016325 | 20363104 | 14637800 | 801420 | 349264 | 2635200 | 223013 | 0
Fuel Cost | 787200 | 0 | 0 | 0 | 6893544 | 2857979.52 | 669065.6 | 8733126.6 | 8120520 |  | 0 | 9671570 | 3620617.98 | 976377.6 | 8288835.36 | 431265.42 | 0 | 0 | 6587840 | 0 | 0 | 0 | 221990.4 | 0 | 0 | 0 | 0 | 2257452 | 1451091.06 | 1072422.9 | 220050 | 450000 | 0 | 0 | 0 | 0 | 0 | 216383.4 | 0 | 4344000 | 0 | 455878.88 | 5659797.75 | 0 | 5431802.6 | 0 |  | 0 | 0 | 2971468.9 | 0 | 184370.4 | 0 | 654575.04 | 2044310.4 | 3891920.48 | 0 | 0 | 5715094 | 6879000 | 4369080 | 1100486.1 | 0 | 946542.24 | 770784 | 0 | 1752257.52 | 0 | 0 | 0 | 627278.4 | 117720 | 1242850 | 282885 | 19764000 | 3851531.2 | 0 | 564733.44 | 229536 | 1607200 | 1181537.6 | 1603068 | 1517218.56 | 4009514.52 | 3670160 | 2682288.96 | 2614713.6 | 0 | 5397600 | 672330 | 0 | 380052 | 7564395 | 279144 | 117040 | 0 | 5026712.04 | 0 | 0 | 16848000 | 0 | 5271091.2 | 1448741.7 | 9404448 | 0 | 7264320 | 0 | 4476096 | 0 | 0 | 0 | 15421575.96 | 0 | 0 | 1308378 | 7313980.8 | 12147840 |  | 62568259.2 | 0 | 9127339.2 | 0 | 9205632 | 0 | 0 | 0 | 0 | 0 | 2102235 | 2282392.08 | 786299.5 | 1371709.44 | 0 | 2556350 | 2654750 | 0 | 0 | 0 | 1513358 | 0 | 197356.23 | 0 | 0 | 605491.2 | 267449.4 | 184618.674 | 0 | 0 | 19925004 | 0 | 0 | 4556426.94 | 0 | 0 | 0 | 2532213 | 4082400 | 5448264.12 | 0 | 9370889.55 | 0 | 0 | 0 | 0 | 3978086.4 | 0 | 585683.15 | 4551057.6 | 48121424 |  | 256606680.13 | 198574688.684 | 455181368.814 | 110668012.324 | 62568259.2 | 58238277.47 | 130025232.04 | 68046428 | 216383.4 | 3390815.53 | 19764000 | 2263960.85 | 0
Yesterday Day Peak | 24 | 0 | 0 | 0 | 280 | 107 | 0 | 375 | 348 |  | 0 | 420 | 140 | 0 | 15 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 18 | 28 | 27 | 0 | 0 | 36 | 0 | 100 | 0 | 0 | 224 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 135 | 0 | 0 | 335 | 290 | 203 | 45 | 0 | 42 | 48 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 0 | 100 | 151 | 0 | 20 | 2.7 | 42 | 32 | 48 | 50 | 163 | 83 | 58 | 80 | 0 | 150 | 19 | 0 | 10 | 325 | 24 | 11 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 16 | 0 | 0 | 0 | 0 | 100 |  | 409 | 0 | 370 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 18 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 32 | 0 | 198 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0 | 380 |  | 7706.9 | DayPeak
Yesterday Evening Peak | 24 | 0 | 0 | 0 | 280 | 110 | 30 | 342 | 322 | 0 | 0 | 380 | 135 | 50 | 96 | 15 | 0 | 0 | 140 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 16 | 25 | 22 | 28 | 20 | 0 | 0 | 38 | 0 | 100 | 0 | 8 | 221 | 0 | 139 | 0 | 0 | 0 | 0 | 68 | 0 | 10 | 0 | 22 | 40 | 135 | 0 | 0 | 280 | 285 | 216 | 26 | 0 | 42 | 5 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 134 | 156 | 0 | 20 | 0 | 41 | 29 | 53 | 50 | 130 | 247 | 61 | 80 | 0 | 150 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 200 | 0 | 0 | 176 | 0 | 132 | 0 | 100 | 0 | 128 | 0 | 104 | 0 | 0 | 0 | 210 | 0 | 0 | 36 | 113 | 100 |  | 799 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 83 | 32 | 32 | 0 | 45 | 50 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 8 | 11 | 0 | 0 | 151 | 0 | 0 | 145 | 0 | 0 | 0 | 98 | 50 | 176 | 0 | 397 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 670 |  | 10273 | EvPeak
Forecast for Evening | 24 | 0 | 0 | 0 | 280 | 108 | 78 | 400 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 40 | 100 | 0 | 0 | 360 | 360 | 225 | 55 | 0 | 42 | 52 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 20 | 141 | 210 | 95 | 20 | 0 | 42 | 32 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 176 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 797 | 40 | 410 |  | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 83 | 30 | 110 | 30 | 70 | 60 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 0 | 0 | 200 | 17 | 15 | 0 | 0 | 220 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 660
Forecast for Day | 24 | 0 | 0 | 0 | 280 | 108 | 71 | 0 | 200 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 20 | 33 | 33 | 52 | 0 | 40 | 0 | 100 | 0 | 25 | 225 | 0 | 140 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 360 | 225 | 55 | 0 | 40 | 52 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 116 | 210 | 95 | 20 | 1.6 | 42 | 32 | 51 | 44 | 163 | 220 | 66 | 81 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 0 | 0 | 176 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 114 | 113 | 100 |  | 401 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 83 | 30 | 50 | 0 | 50 | 60 | 0 | 0 | 80 | 50 | 42 | 40 | 40 | 0 | 17 | 11 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 150 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 525
Generation at 08:00(Today) | 24 | 0 | 0 | 0 | 280 | 104 | 71 | 0 | 0 | 0 | 0 | 450 | 130 | 14 | 36 | 20 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 19 | 25 | 20 | 28 | 25 | 0 | 0 | 37 | 0 | 100 | 0 | 0 | 221 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 100 | 0 | 0 | 315 | 310 | 189 | 55 | 0 | 39 | 52 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 20 | 102 | 156 | 0 | 20 | 0.7 | 42 | 29 | 50 | 47 | 163 | 236 | 40 | 80 | 0 | 150 | 19 | 0 | 10 | 290 | 8 | 0 | 0 | 27 | 0 | 0 | 173 | 0 | 25 | 6.5 | 100 | 0 | 82 | 0 | 8 | 0 | 0 | 1.9 | 100 | 0 | 0 | 0 | 8 | 100 | 0 | 252 | 0 | 335 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 19 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 17 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 13 | 0 | 93 | 0 | 175 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 35 | 525 | 0
199
| Minimum Generation |  | 5911.59 | 6:00
| Highest Generation |  | 10273 | 21:00
| Day Peak Generation |  | 7706.9 | 12:00
| Evening Peak Generation |  | 10273 | 21:00
| HVDC Max Flow |  | 799 | 19:30
| HVDC EvPeak Flow |  | 799 | 21:00
| Load factor L.F |  | 78.37%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-05-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-05-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7706.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7080.3 | MW
Evening Peak Generation : |  | 10273 | MW Hour : | 21:00 | Available Max Generation : |  | 15360 | MW
E.P. Demand (at gen end) : |  | 10273 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10800 | MW
Maximum Generation : |  | 10273 | MW Hour : | 21:00 | Reserve(Generation end) |  | 4560 | MW
Total Gen. (MKWH) : |  | 193.2139 | System Load Factor : | 78.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -331 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-05-05
Actual : | 79.03 | Ft.(MSL) , | Rule curve : | 81.24 | Ft.( MSL )
Gas Consumed : | Total = | 1183.81 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168906289.794
: |  | Coal : | 68046428 | Oil : | 133416047.57 | Total : | 370368765.364
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3767.0477 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1279.6932 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1146.329 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1035.722 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 936.0127 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 755.3258 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 424.0287 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 194.5208 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 582.5367 |  |  | 0 | 0%
Total | 0 |  | 10121.2166 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 11) Siddirganj-210 MW TPP
|  |  |  | 2) Bibiyana #3 | 12) Megnaghat Summit-305 MW GT-1
3) Ghorasal Unit-1,3,4 & 5.
4) Ashuganj unit-4,5
5) Siddirganj-335 MW
6) Kaptai-2,5
7) Raozan # 2
9) Chandpur 163 MW
10) Bhola-225 MW GT-2 & ST.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sirajganj #01 ST tripped at 11:46 due to Shaft vibration.
b) Madunaghat 132/33 kVT-1 transformer was under shut down from 10:44 to 12:10 for 33 kV
feeder maintenance by PDB.
c) Naogaon-Santaher P/S 132 kV line shut down from 11:00 to 12:20 for P/P work.
d) Polashbari-Mahastanghor 132 kV Ckt -1 was under shut down from 14:24 to 16:20 due to
corrective maintenance.
e) Haripur 360 MW tripped at 00:01 due to gas line problem and was synchronized at 10:36.
f) After maintenance Ashuganj # 03 was synchronized at 03:46.
g) Hasnabad-Shyampur 230 kV Ckt is under shut down from 07:40 to 10:07 for C/M.
h) After maintenance Sirajganj # 02 was synchronized at 06:39
i) Sirajganj #01 GT was under shut down at 00:44 for ST maintenance work.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-05-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 24 | 480000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 280 | 6210400 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 30 | 393568 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 110 | 2165136
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8646660 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 322 | 7884000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8873000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 128640 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 135 | 3261818 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 1203024
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 50977 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 293400
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 140 | 3808000 | Frequency control
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under S/D.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 309240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 22560 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 187722
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 108765 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1031460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 683700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 617900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 200 | 664909 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 535680 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2508 | 47560559
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 49072 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 123930
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 801420 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 221 | 5192475 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3195178 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 306337 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1153920
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 519504
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 688320
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 21192 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31680
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 210 | 2039891 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 100 | 1824000
| Chattogram area Total |  |  |  | 2166 | 1056 | 18346919
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2629676
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4749000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7723100 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6879000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 837648
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 550560 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 853090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1024712
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 1030400 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 493920
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 156960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 2635200
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 710200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 377180 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 36 | 131100 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 853440
| Cumilla Area Total |  |  |  | 2980 | 1533 | 31635186
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3633520 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 444672 | Engine problem
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14400
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 176 | 3240000 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 104 | 490800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 456 | 7823392
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 980000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 738461
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3517118
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 247 | 3529000 | FGMO & GT-1 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 900600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 972576
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 154000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1361568 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1368960
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 150 | 3120000
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 307000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 372192
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7489500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 186300
| Sylhet Area Total |  |  |  | 1949 | 1200 | 24997275
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 799 | 10862545
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1171200
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8692704 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 201750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 240000 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1334 | 21168199
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 140544 | Low demand
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 507290
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 83 | 2019816
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 1688142
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 670 | 10961600 | On test
| Barisal Area Total |  |  |  | 462 | 915 | 15317392
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1295000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 45 | 1247000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 196540
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 20367 | Low demand
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3894382 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under S/D.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4656636 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 397 | 9465545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 16 | 315360 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 172548 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243882
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 615840
| Rajshahi Area Total |  |  |  | 2183 | 1007 | 22123100
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 151 | 3676200 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 512640
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53003
| Rangpur Area Total |  |  |  | 605 | 264 | 4241843
| Total |  |  |  | 19107 | 10273 | 193213865
| Eastern Grid Total |  |  |  | 13543 | 6753 | 130363331
| Western Grid Total |  |  |  | 5564 | 3520 | 62850534
| National Grid Total |  |  |  | 19107 | 10273 | 193213865
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-05-04
(a) ENTIRE EASTERN GRID : |  | 6216 | MW | (b) ENTIRE WESTERN GRID : |  | 3397 | MW
i) Dhaka area |  | 3024 | MW | i) Khulna area |  | 1326 | MW
ii) Chittagong area |  | 872 | MW | ii) Rajshahi area |  | 1134 | MW
iii) Comilla area |  | 1029 | MW | iii) Barisal area |  | 266 | MW
iv) Mymensingh area |  | 872 | MW | iv) Rangpur area |  | 671 | MW
v) Sylhet area |  | 419 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9613 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 14:00 | Sherpur | 100 | 19:30 | Benapol | 40 | 19:30
Munsiganj | 114 | 21:00 | Srimongal | 39 | 18:30 | Jhenida | 106 | 21:00
Sonargaon | 51 | 12:00 | Shahjibazar | 90 | 21:00 | Bottail | 100 | 20:00
Shyampur | 148 | 0:00 | Fenchuganj | 30 | 19:00 | G.K Project | 53 | 21:00
Bhulta | 109 | 23:00 | Kulawara | 33 | 21:00 | Faridpur | 160 | 20:00
Madanganj | 45 | 0:00 | Sylhet | 106 | 22:00 | Madaripur | 93 | 21:00
Shitalakhya | 74 | 14:00 | Chatak | 26 | 21:00 | Sariatpur | 56 | 21:00
Rahim steel | 0 | 1:00 | Sunamganj | 42 | 21:00 | Gopalganj | 90 | 20:00
Matuail | 61 | 15:00 | Biani Bazar | 58 | 21:00 | Bagerhat | 81 | 20:00
Ghorasal | 61 | 20:00 | Comilla (S) | 136 | 22:00 | Mongla | 34 | 1:00
Narsingdi | 119 | 20:00 | Comilla(N) | 111 | 22:00 | Satkhira | 92 | 22:00
Haripur (SBU) | 67 | 9:00 | Chandpur | 95 | 21:00 | Gallamari | 43 | 23:00
Ullon | 43 | 19:00 | Feni | 104 | 21:00 | Magura | 48 | 19:30
Hasnabad | 164 | 21:00 | Chowmuhani | 152 | 20:00 | Norail | 37 | 19:30
Magbazar | 77 | 13:00 | Ashuganj | 56 | 23:00 | Chuadanga | 84 | 21:00
Maniknagar | 68 | 12:00 | Daudkandi | 132 | 21:00 | Barisal(N) | 41 | 19:30
Bangabhaban | 16 | 10:00 | B.Baria | 143 | 21:00 | Barisal (S) | 86 | 19:30
Narinda | 62 | 21:00 | Ramganj | 102 | 21:00 | Patuakhali | 96 | 20:00
Dhanmondi | 74 | 14:00 | Chaddagram | 30 | 19:00 | Bhandaria | 46 | 20:00
Lalbag | 57 | 14:00 | PHP | 10 | 16:00 | Borhan Uddin | 32 | 21:00
Madartek | 61 | 22:00 | Madunaghat | 57 | 19:00 | Ishurdi | 60 | 20:00
Dhaka University |  |  | Hathazari | 74 | 19:00 | Ruppur Paromanobik | 2 | 9:00
Mirpur | 80 | 21:00 | Khulshi | 114 | 14:00 | Natore | 115 | 21:00
Kalyanpur | 75 | 21:00 | Halishahar | 101 | 19:30 | Bogra | 139 | 21:00
Gulshan | 82 | 13:00 | Baraulia | 129 | 1:00 | Noagaon | 98 | 21:00
Uttara | 59 | 21:00 | Sikalbaha | 16 | 19:00 | Rajshahi | 137 | 21:00
Uttara New | 19 | 21:00 | Dohazari | 84 | 21:00 | Rajshahi New | 10 | 19:00
Kamrangirchar | 57 | 13:00 | Cox'sbazar | 89 | 21:00 | C.Nawabganj | 64 | 21:00
Savar | 104 | 14:00 | Chandraghona | 28 | 18:30 | Amnura | 40 | 20:00
Bhasantec | 113 | 21:00 | Kaptai | 4 | 19:00 | Pabna | 104 | 21:00
Agargaon | 40 | 21:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 102 | 21:00
Satmosjid | 78 | 21:00 | Bakulia | 83 | 11:00 | Serajganj | 85 | 20:00
Tongi | 106 | 13:00 | Julda | 15 | 1:00 | Niyamatpur | 46 | 21:00
Kabirpur | 153 | 14:00 | TK chemical | 19.9 | 22:00 | Joypurhat | 55 | 21:00
Basundhara | 89 | 21:00 | Modern Steel | 13 | 3:00 | Sherpur(Bogura) | 38 | 19:30
Manikganj | 82 | 19:30 | Shahmirpur | 28 | 22:00 | Mohastangor | 44 | 20:00
Joydevpur | 133 | 15:00 | Khagrachhari | 20 | 19:30 | Rangpur | 135 | 21:00
New Tongi | 79 | 14:00 | Matarbari | 29.5 | 21:00 | Lalmonirhat | 50 | 20:00
Kodda | 156 | 14:00 | Baroiar Hat | 32 | 19:00 | Saidpur | 98 | 20:00
Dhamrai | 56 | 15:00 | Rangamati | 10 | 19:00 | Purbasadipur | 73 | 18:00
Rajendrapur | 74 | 19:30 | Abul Khair 230 | 7 | 21:00 | Thakurgaon | 68 | 19:30
Valuka | 78 | 20:00 | BSRM | 109 | 3:00 | Palashbari | 108 | 21:00
Tangail | 186 | 21:00 | GPH Ispat | 15 | 13:00 | Barapukuria | 44 | 21:00
Mymensing | 193 | 20:00 | Goalpara | 22 | 21:00 | Panchagar | 43 | 21:00
Kishorganj | 128 | 22:00 | Central s/s | 75 | 19:30 | Joldhaka | 23 | 21:00
Netrokona | 102 | 19:30 | Noapara | 51 | 20:00 | Kurigram | 50 | 0.83333
Jamalpur | 115 | 19:30 | Jessore | 108 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-05-04 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 403 | 0.16667 | 391 | 0.625 | Kaliakoir | 387 | 0.20833 | 370 | 0.58333
Bheramara | 404 | 0.125 | 391 | 0.875 | Bhulta | 395 | 0.16667 | 385 | 0.58333
Ashuganj(N) | 401 | 0.16667 | 390 | 0.58333 | Gopalganj | 408 | 0.25 | 372 | 0.875
Payra | 411 | 0.25 | 388 | 0.875
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 234 | 0.041667 | 232 | 0.625 | Comilla (N) | 237 | 0.16667 | 231 | 0.58333
Ishurdi | 237 | 0.25 | 224 | 0.875 | Hathazari | 224 | 0.77083 | 215 | 0.41667
Ashuganj | 242 | 0.125 | 236 | 0.41667 | Megnaghat | 235 | 0.25 | 228 | 0.45833
Serajganj | 235 | 0.20833 | 228 | 0.625 | Fenchuganj | 242 | 0.16667 | 237 | 0.5
Baghabari | 241 | 0.25 | 235 | 0.91667 | Siddhirganj | 235 | 0.16667 | 228 | 0.58333
Barapukuria | 232 | 0.25 | 223 | 0.79167 | Maniknagar | 233 | 0.16667 | 226 | 0.58333
Bogra | 233 | 0.16667 | 220 | 0.58333 | Agargaon | 232 | 0.16667 | 223 | 0.58333
Rajshahi | 227 | 0.25 | 213 | 0.58333 | Barisal | 245 | 0.20833 | 226 | 0.79167
Khulna South | 231 | 0.25 | 210 | 0.79167 | AKSML | 219 | 0.16667 | 212 | 0.45833
Rampura | 232 | 0.16667 | 228 | 0.33333 | BSRM | 224 | 0.77083 | 215 | 0.45833
Haripur | 232 | 0.125 | 229 | 0.375 | Bibiyana | 240 | 0.16667 | 233 | 0.5
Hasnabad | 232 | 0.125 | 225 | 0.58333 | Bhulta | 235 | 0.16667 | 227 | 0.58333
Shyampur | 230 | 0.16667 | 222 | 0.58333 | Ashuganj (S) | 238 | 0.16667 | 233 | 0.375
Aminbazar | 233 | 0.125 | 225 | 0.5 | Kaliakoir | 236 | 0.16667 | 225 | 0.45833
Tongi | 233 | 0.125 | 220 | 0.54167 | GPH | 219 | 0.16667 | 212 | 0.45833
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 0.16667 | 130 | 0.41667 | Hathazari | 132 | 0.8125 | 128 | 0.41667
Munsiganj | 136 | 0.16667 | 128 | 0.45833 | Khulshi | 129 | 0.83333 | 124 | 0.375
Sonargaon | 131 | 0.79167 | 127 | 0.375 | Halishahar | 131 | 0.77083 | 124 | 0.41667
Shyampur | 134 | 0.16667 | 130 | 0.45833 | Baraulia | 131 | 0.16667 | 125 | 0.41667
Bhulta | 130 | 0.125 | 125 | 0.41667 | Sikalbaha | 131 | 0.79167 | 124 | 0.375
Madanganj | 133 | 0.16667 | 126 | 0.5 | Dohazari | 128 | 0.77083 | 122 | 0.041667
Shitalakhya | 136 | 0.20833 | 127 | 0.58333 | Cox'sbazar | 124 | 0.77083 | 116 | 0.041667
Rahim steal | 135 | 0.16667 | 130 | 0.45833 | Chandraghona | 131 | 0.83333 | 127 | 0.375
Matuail | 135 | 0.16667 | 128 | 0.58333 | Kaptai | 130 | 0.25 | 127 | 0.41667
Ghorasal | 140 | 0.041667 | 138 | 0.625 | A. Khaer Stl. | 130 | 0.70833 | 126 | 0.41667
Narsinghdi | 131 | 0.16667 | 124 | 0.58333 | Bakulia | 130 | 0.77083 | 124 | 0.41667
Haripur (SBU) | 135 | 0.16667 | 130 | 0.5 | Julda | 131 | 0.77083 | 125 | 0.375
Ullon | 132 | 0.125 | 127 | 0.45833 | TK Chemical | 131 | 0.75 | 125 | 0.375
Hasnabad | 135 | 0.16667 | 128 | 0.54167 | Modern Steel | 130 | 0.83333 | 125 | 0.41667
Magbazar | 132 | 0.16667 | 127 | 0.5 | Shahmirpur | 130 | 0.79167 | 125 | 0.41667
Maniknagar | 137 | 0.16667 | 133 | 0.58333 | Khagrachhari | 130 | 0.16667 | 126 | 0.41667
Bangabhaban | 137 | 0.16667 | 133 | 0.58333 | Matarbari | 123 | 0.77083 | 119 | 0.041667
Narinda | 137 | 0.16667 | 133 | 0.58333 | Baroiar Hat | 130 | 0.041667 | 123 | 13:00
Dhanmondi | 132 | 0.125 | 127 | 0.45833 | Rangamati | 132 | 0.77083 | 126 | 10:00
Lalbag | 135 | 0.20833 | 127 | 0.54167 | Goalpara S/S | 136 | 0.20833 | 126 | 0.45833
Madartek | 132 | 0.20833 | 126 | 0.54167 | Central s/s | 135 | 0.25 | 124 | 0.45833
Dhaka University |  |  |  |  | Noapara | 132 | 0.25 | 123 | 0.45833
Mirpur | 136 | 0.083333 | 131 | 0.5 | Jessore | 130 | 0.25 | 118 | 0.58333
Kalyanpur | 135 | 0.125 | 129 | 0.58333 | Benapol | 132 | 0.25 | 118 | 0.79167
Gulshan | 132 | 0.20833 | 127 | 0.5 | Jhenida | 131 | 0.25 | 112 | 0.875
Uttara | 135 | 0.125 | 129 | 0.5 | Bottail | 135 | 0.16667 | 123 | 0.875
Uttara New | 135 | 0.20833 | 128 | 0.5 | G.K Project | 140 | 0.20833 | 133 | 0.8125
Kamrangirchar | 135 | 0.29167 | 127 | 0.5 | Faridpur | 137 | 0.29167 | 120 | 0.875
Savar | 134 | 0.20833 | 128 | 0.5 | Madaripur | 140 | 0.29167 | 126 | 0.875
Bhasantec | 134 | 0.25 | 128 | 0.5 | Sariatpur | 139 | 0.25 | 122 | 0.66667
Agargaon | 134 | 0.16667 | 128 | 0.58333 | Gopalganj | 142 | 0.25 | 120 | 0.875
Satmosjid | 134 | 0.20833 | 128 | 0.54167 | Bagerhat | 133 | 0.75 | 122 | 0.45833
Tongi | 139 | 0.875 | 130 | 0.54167 | Mongla | 132 | 0.77083 | 120 | 0.45833
Kabirpur | 132 | 0.20833 | 124 | 0.95833 | Satkhira | 134 | 0.20833 | 123 | 0.45833
Basundhara | 132 | 0.083333 | 127 | 0.54167 | Gallamari | 137 | 0.25 | 126 | 0.45833
Manikganj | 136 | 0.20833 | 128 | 0.95833 | Magura | 132 | 0.25 | 111 | 0.875
Joydevpur | 140 | 0.083333 | 135 | 0.54167 | Norail | 129 | 0.20833 | 107 | 0.875
New Tongi | 138 | 0.875 | 128 | 0.58333 | Chuadanga | 127 | 0.25 | 101 | 0.875
Kodda | 139 | 0.875 | 122 | 0.625 | Barisal(N) | 140 | 0.20833 | 126 | 0.79167
Dhamrai | 132 | 0.83333 | 123 | 0.125 | Barisal (S) | 137 | 0.25 | 124 | 0.79167
Rajendrapur | 138 | 0.16667 | 129 | 0.58333 | Patuakhali | 134 | 0.20833 | 118 | 0.79167
Valuka | 130 | 0.16667 | 114 | 0.79167 | Bhandaria | 135 | 0.041667 | 121 | 0.79167
Tangail | 134 | 0.20833 | 124 | 0.79167 | Ishurdi | 137 | 0.16667 | 130 | 0.875
Mymensing | 132 | 0.16667 | 117 | 0.79167 | Ruppur Paromanobik | 137 | 0.25 | 130 | 0.875
Kishorganj | 133 | 0.125 | 123 | 0.041667 | Natore | 137 | 0.25 | 127 | 0.875
Netrokona | 130 | 0.16667 | 114 | 0.79167 | Bogra | 136 | 0.25 | 127 | 0.875
Jamalpur | 134 | 0.16667 | 118 | 0.33333 | Noagaon | 133 | 0.25 | 122 | 0.58333
Sherpur | 134 | 0.16667 | 120 | 0.33333 | Rajshahi | 136 | 0.20833 | 127 | 0.875
Srimongal | 140 | 0.16667 | 135 | 0.70833 | Rajshahi New | 137 | 0.77083 | 127 | 0.58333
Shahjibazar | 138 | 0.16667 | 134 | 15:00 | C.Nawabganj | 134 | 0.16667 | 125 | 0.58333
Fenchuganj | 136 | 0.083333 | 135 | 0.041667 | Amnura | 136 | 0.25 | 126 | 0.58333
Khulawara | 137 | 0.16667 | 134 | 0.33333 | Pabna | 135 | 0.20833 | 126 | 0.875
Sylhet | 136 | 0.16667 | 133 | 0.79167 | Shahjadpur | 139 | 0.041667 | 136 | 0.29167
Chatak | 135 | 0.125 | 131 | 0.79167 | Serajganj | 135 | 0.20833 | 128 | 0.45833
Sunamganj | 134 | 0.16667 | 129 | 0.875 | Niyamatpur | 133 | 0.25 | 120 | 0.875
Biani Bazar | 134 | 0.16667 | 129 | 0.79167 | Joypurhat | 135 | 0.20833 | 120 | 0.875
Comilla(s) | 129 | 0.29167 | 125 | 0.58333 | Sherpur(Bogura) | 136 | 0.20833 | 127 | 0.58333
Comilla(n) | 136 | 0.29167 | 131 | 0.58333 | Mohastangor | 135 | 0.20833 | 124 | 0.58333
Chandpur | 125 | 0.33333 | 120 | 0.58333 | Rangpur | 130 | 0.25 | 119 | 0.54167
Feni | 128 | 0.29167 | 123 | 0.58333 | Lalmonirhat | 127 | 0.25 | 115 | 0.5
Chowmuhani | 125 | 0.29167 | 117 | 0.625 | Saidpur | 131 | 0.20833 | 118 | 0.58333
Ashuganj | 140 | 0.16667 | 135 | 0.8125 | Purbasadipur | 130 | 0.20833 | 113 | 0.79167
Daudkandi | 131 | 0.29167 | 127 | 0.54167 | Thakurgaon | 128 | 0.20833 | 115 | 0.54167
B.Baria | 134 | 0.29167 | 131 | 0.83333 | Palashbari | 132 | 0.20833 | 116 | 0.875
Ramganj | 124 | 0.77083 | 119 | 0.41667 | Barapukuria | 132 | 0.25 | 123 | 0.79167
Chaddagram | 132 | 0.16667 | 123 | 0.58333 | Panchagar | 125 | 0.041667 | 112 | 0.58333
PHP | 130 | 0.16667 | 122 | 0.58333 | Joldhaka | 129 | 0.20833 | 116 | 0.54167
Madanhat | 134 | 0.77083 | 128 | 0.375 | Kurigram | 131 | 0.25 | 117 | 0.54167

## L-Curve
Date | 2020-05-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 44 | 6111 | 3072 | 9183 |  |  |  | QF-LDC-12
0:30 | 64.5 | 5728 | 2761 | 8489 | Date: | 2020-05-04
1:00 | 85 | 5345 | 2450 | 7795
1:30 | 178.5 | 5364 | 2357 | 7721
2:00 | 272 | 5383 | 2264 | 7647
2:30 | 301.5 | 5552 | 2308.5 | 7860.5 | [5 empty] | Gen. at Eve. Peak | 10273 | 10273 MW (21:00 )
3:00 | 331 | 5721 | 2353 | 8074 | [6 empty] | 21:00
3:30 | 257 | 5555.5 | 2291 | 7846.5 | [5 empty] | Gen. at Day Peak | 7706.9 | 7706.9 MW (12:00 )
4:00 | 183 | 5390 | 2229 | 7619 | [6 empty] | 12:00
4:30 | 102.5 | 4862 | 2124.5 | 6986.5 | [5 empty] | Highest Generation | 10273
5:00 | 22 | 4334 | 2020 | 6354 | [6 empty] | 21:00
5:30 | 64 | 4160.195 | 1972.6 | 6132.795
6:00 | 106 | 3986.39 | 1925.2 | 5911.59
6:30 | 101 | 4034.045 | 1927 | 5961.045
7:00 | 96 | 4081.7 | 1928.8 | 6010.5
7:30 | 102 | 4253.95 | 1986.1 | 6240.05
8:00 | 108 | 4426.2 | 2043.4 | 6469.6
8:30 | 119 | 4564.3 | 2150.8 | 6715.1
9:00 | 130 | 4702.4 | 2258.2 | 6960.6
9:30 | 110 | 4808.8 | 2302 | 7110.8
10:00 | 90 | 4915.2 | 2345.8 | 7261
10:30 | 75.5 | 5032.35 | 2352.6 | 7384.95
11:00 | 61 | 5149.5 | 2359.4 | 7508.9
11:30 | 46.5 | 5235.25 | 2372.65 | 7607.9
12:00 | 32 | 5321 | 2385.9 | 7706.9
12:30 | 23.5 | 5385.05 | 2444.85 | 7829.9
13:00 | 15 | 5449.1 | 2503.8 | 7952.9
13:30 | 8 | 5551.55 | 2570.5 | 8122.05
14:00 | 1 | 5654 | 2637.2 | 8291.2
14:30 | 13 | 5705.35 | 2646.6 | 8351.95
15:00 | 25 | 5756.7 | 2656 | 8412.7
15:30 | 20 | 5573.3 | 2628.3 | 8201.6
16:00 | 15 | 5389.9 | 2600.6 | 7990.5
16:30 | 42 | 5309.9 | 2537.35 | 7847.25
17:00 | 69 | 5229.9 | 2474.1 | 7704
17:30 | 51.5 | 5229.1 | 2518.8 | 7747.9
18:00 | 34 | 5228.3 | 2563.5 | 7791.8
18:30 | 49 | 5601.65 | 2888.75 | 8490.4
19:00 | 64 | 5975 | 3214 | 9189
19:30 | 117 | 6363 | 3459 | 9822
20:00 | 145 | 6509 | 3438 | 9947 |  |  |  | Executive Engineer
20:30 | 146.5 | 6631 | 3479 | 10110 |  |  |  | Network Operation Division
21:00 | 148 | 6753 | 3520 | 10273
21:30 | 99.5 | 6641.5 | 3506 | 10147.5
22:00 | 51 | 6530 | 3492 | 10022 |  |  |  |  | Page 6 of 7
22:30 | 81.5 | 6343 | 3453 | 9796
23:00 | 112 | 6156 | 3414 | 9570
23:30 | 78 | 6133.5 | 3243 | 9376.5
24:00 | 44 | 6111 | 3072 | 9183
10273 MW (21:00 )
7706.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-05-04 |  | Energy | 193213865
[10 empty] | 2020-05-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3868 | 652 | 2366 | 1610 | 750 | 36 | 34 | 0 | 124
0:30 | 3946 | 553.5 | 2270 | 1055.5 | 625 | 35.5 | 17 | 0 | 115 | Date: | 2020-05-04
1:00 | 4024 | 455 | 2174 | 501 | 500 | 35 | 0 | 0 | 106
1:30 | 4060 | 359 | 2193.5 | 469 | 500 | 35.5 | 0 | 0 | 104 | [7 empty] | Total Energy | 193.2139 | Total Energy Gen 193.214 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.214 MKWHr
2:00 | 4096 | 263 | 2213 | 437 | 500 | 36 | 0 | 0 | 102 | [7 empty] | Energy not Served | 0
2:30 | 4128.5 | 263 | 2268.5 | 516.5 | 544 | 36 | 0 | 0 | 104 | [7 empty] | Energy Requirement | 193.2139
3:00 | 4161 | 263 | 2324 | 596 | 588 | 36 | 0 | 0 | 106
3:30 | 3974 | 263 | 2214 | 672 | 582 | 36.5 | 0 | 0 | 105 | [6 empty] | Shortage
4:00 | 3787 | 263 | 2104 | 748 | 576 | 37 | 0 | 0 | 104
4:30 | 3656 | 263 | 1861.5 | 531.5 | 540.5 | 37 | 0 | 0 | 97
5:00 | 3525 | 263 | 1619 | 315 | 505 | 37 | 0 | 0 | 90
5:30 | 3432 | 262.5 | 1589 | 236.5 | 487 | 37 | 0 | 0 | 88
6:00 | 3339 | 262 | 1559 | 158 | 469 | 37 | 0 | 0 | 86
6:30 | 3406.5 | 262 | 1556.5 | 158 | 450.5 | 37 | 0 | 0 | 87 |  |  |  |  | Coal
7:00 | 3474 | 262 | 1554 | 158 | 432 | 37 | 0 | 0 | 88
7:30 | 3616 | 262 | 1632.5 | 160 | 432.5 | 37 | 0 | 0 | 89 |  |  |  | Oil |  |  |  | ,
8:00 | 3758 | 262 | 1711 | 162 | 433 | 37 | 0 | 0 | 90
8:30 | 3851 | 322.5 | 1768.5 | 181 | 443.5 | 37 | 0 | 0 | 93
9:00 | 3944 | 383 | 1826 | 200 | 454 | 37 | 0 | 0 | 96
9:30 | 3966.5 | 396 | 1903.5 | 232 | 453 | 37 | 0 | 0 | 99
10:00 | 3989 | 409 | 1981 | 264 | 452 | 37 | 0 | 0 | 102
10:30 | 4036.5 | 409 | 2048.5 | 264 | 459.5 | 37 | 0 | 0 | 103
11:00 | 4084 | 409 | 2116 | 264 | 467 | 37 | 0 | 0 | 104
11:30 | 4071 | 409 | 2142.5 | 316.5 | 498.5 | 36.5 | 0 | 0 | 102
12:00 | 4058 | 409 | 2169 | 369 | 530 | 36 | 0 | 0 | 100
12:30 | 4034.5 | 409 | 2168.5 | 486.5 | 566.5 | 35 | 0 | 0 | 96
13:00 | 4011 | 409 | 2168 | 604 | 603 | 34 | 0 | 0 | 92
13:30 | 4011 | 409 | 2168 | 604 | 603 | 34 | 0 | 0 | 92
14:00 | 4011 | 409 | 2168 | 604 | 603 | 34 | 0 | 0 | 92
14:30 | 4007.5 | 409 | 2194 | 758 | 650 | 34.5 | 0 | 0 | 102
15:00 | 4004 | 409 | 2220 | 912 | 697 | 35 | 0 | 0 | 112
15:30 | 3897 | 409 | 2130 | 901 | 698.5 | 35.5 | 1 | 0 | 111
16:00 | 3790 | 409 | 2040 | 890 | 700 | 36 | 2 | 0 | 110
16:30 | 3733 | 409 | 2030.5 | 820 | 700 | 36 | 3 | 0 | 107
17:00 | 3676 | 409 | 2021 | 750 | 700 | 36 | 4 | 0 | 104
17:30 | 3673 | 408.5 | 2004 | 783 | 725 | 36.5 | 4.5 | 0 | 111
18:00 | 3670 | 408 | 1987 | 816 | 750 | 37 | 5 | 0 | 118
18:30 | 3751.5 | 594.5 | 1999.5 | 1173 | 770 | 37 | 39.5 | 0 | 125
19:00 | 3833 | 781 | 2012 | 1530 | 790 | 37 | 74 | 0 | 132
19:30 | 3832 | 799 | 2089 | 2047 | 813 | 37 | 75 | 0 | 130
20:00 | 3879 | 798 | 2089 | 2120 | 817 | 38 | 76 | 0 | 130
20:30 | 3948 | 798.5 | 2111 | 2183.5 | 819 | 38 | 80 | 0 | 132
21:00 | 4017 | 799 | 2133 | 2247 | 821 | 38 | 84 | 0 | 134
21:30 | 3983 | 799 | 2169 | 2138.5 | 818.5 | 37.5 | 67 | 0 | 135
22:00 | 3949 | 799 | 2205 | 2030 | 816 | 37 | 50 | 0 | 136
22:30 | 3929 | 799 | 2222.5 | 1820 | 814.5 | 37 | 42 | 0 | 132
23:00 | 3909 | 799 | 2240 | 1610 | 813 | 37 | 34 | 0 | 128
23:30 | 3888.5 | 725.5 | 2303 | 1610 | 781.5 | 36.5 | 34 | 0 | 126 | Max Temp. in Dhaka |  | 34.5° C
24:00 | 3868 | 652 | 2366 | 1610 | 750 | 36 | 34 | 0 | 124
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 193.214 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.214 MKWHr
Note on W13: Author:

## Generation
g | 2020-05-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 34 | 35 | 35 | 36 | 36 | 37 |  | 37 | 37 | 38 | 38 | 37 | 37 | 36 | 801420
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 6 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 49072
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.89 | 3 | 10.4 | 8.7 | 16.9 | 12.3 | 19.8 | 18.8 | 17.3 | 13.7 | 10.4 | 1.5 | 0.2 | [8 empty] | 123930
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 224 | 223 | 223 | 223 | 190 | 222 | 224 | 225 | 225 | 224 | 218 | 218 | 218 | 218 | 218 | 221 |  | 221 | 220 | 220 | 221 | 221 | 223 | 224 | 5192475
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 104 | 104 | 104 | 115 | 112 | 110 | 139 | 146 | 139 | 139 | 139 | 139 | 139 | 145 | 139 |  | 147 | 145 | 145 | 139 | 139 | 139 | 139 | 3195178
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 68 | 68 | 68 | 68 | 34 | 34 | 34 | 306337
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 198 | 195 | 198 | 124 | 123 | 78 | 78 | 150 | 180 | 180 | 180 | 179 | 179 | 191 | 191 | 150 | 100 | 100 |  | 100 | 100 | 100 | 140 | 180 | 149 | 150 | 3808000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 2 |  | 74 | 180 | 189 | 200 | 120 | 15 |  | 664909
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 80 | 83 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 45 | 45 | 45 | 45 | 45 | 26 | 26 |  | 26 | 26 | 26 | 26 | 45 | 83 | 83 | 853090
20 | Ghorasal TPP (Unit-1&2) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 480000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 280 | 280 | 280 | 280 | 200 | 200 | 200 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 240 | 240 | 240 |  | 240 | 240 | 240 | 280 | 280 | 280 | 280 | 6210400
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 135 | 135 | 135 | 80 | 80 | 80 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 |  |  |  | 2629676
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 5 | 5 | 5 | 36 | 36 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 837648
33 | Ashuganj 225 MW CCPP | 181 | 198 | 193 | 181 | 181 | 180 | 150 | 202 | 202 | 202 | 203 | 203 | 201 | 182 | 177 | 176 | 208 | 192 |  | 210 | 211 | 214 | 216 | 215 | 214 | 215 | 4749000
34 | Ashuganj 450 MW CCPP(South) | 270 | 290 | 290 | 250 | 250 | 250 | 290 | 300 | 300 | 295 | 305 | 290 | 285 | 295 | 280 | 270 | 265 | 270 |  | 300 | 265 | 280 | 285 | 290 | 285 | 280 | 6879000
| Ashuganj 450 MW CCPP(North) | 300 | 315 | 310 | 260 | 270 | 270 | 305 | 315 | 315 | 310 | 350 | 335 | 330 | 340 | 320 | 315 | 290 | 285 |  | 315 | 280 | 280 | 280 | 315 | 310 | 300 | 7723100
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 55 | 5 | 5 | 5 | 5 | 5 | 30 | 50 | 48 | 48 | 48 | 25 | 25 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 55 | 550560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 340 | 377 | 335 | 334 | 335 | 359 | 373 | 379 | 372 | 366 | 375 | 369 | 375 | 371 | 343 | 360 | 341 |  | 347 | 335 | 347 | 342 | 344 | 342 | 350 | 8646660
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 450 | 400 | 370 | 370 | 340 | 390 | 390 | 390 | 420 | 420 | 420 | 420 | 420 | 380 | 380 | 340 |  | 340 | 380 | 380 | 380 | 420 | 420 | 420 | 8873000
41 | Haripur 360MW CCPP(HPL) | 360 | 360 | 360 | 284 | 284 | 284 | 314 | 356 | 352 | 351 | 349 | 348 | 347 | 346 | 347 | 322 | 322 | 323 |  | 283 | 283 | 323 | 322 | 322 | 322 | 322 | 7884000
42 | RPCL 210MW CCPP | 158 | 158 | 158 | 160 | 160 | 160 | 156 | 156 | 155 | 151 | 150 | 151 | 151 | 151 | 150 | 151 | 151 | 151 |  | 151 | 153 | 155 | 156 | 154 | 156 | 156 | 3633520
43
44 | Fenchugonj CCPP Phase-1 | 41 | 42 | 41 | 41 | 39 | 39 | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 41 | 42 | 42 | 41 | 980000
45 | Fenchugonj CCPP Phase-2 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 738461
46 | Shajibazar 330 MW CCPP | 170 | 179 | 175 | 165 | 165 | 162 | 178 | 188 | 178 | 102 | 86 | 83 | 82 | 90 | 89 | 106 | 116 | 162 |  | 172 | 174 | 184 | 247 | 235 | 243 | 237 | 3529000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 63 | 63 | 40 | 40 | 63 | 40 | 59 | 61 | 59 | 58 | 58 | 57 | 57 | 58 | 58 | 59 |  | 59 | 59 | 61 | 61 | 61 | 61 | 61 | 1361568
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 80 | 80 | 80 | 80 | 30 | 30 | 30 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1368960
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 150 | 150 | 149 | 100 | 101 | 99 | 101 | 121 | 150 | 150 | 150 | 150 | 150 | 150 | 144 | 78 | 80 | 80 |  | 80 | 140 | 150 | 150 | 149 | 150 | 150 | 3120000
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 307000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 186300
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | [7 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 154000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 48 | 48 | 48 | 50 | 53 | 53 | 14 | 14 | 14 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 900600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | [5 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 372192
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 320 | 280 | 265 | 285 | 300 | 320 | 325 | 320 | 315 | 325 | 315 | 315 | 320 | 300 | 310 | 300 |  | 290 | 310 | 300 | 295 | 290 | 285 | 300 | 7489500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 108765
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 519504
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | [6 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 16 | 19 | 19 |  | 293400
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 444672
63 | Impoprt (Tripura) | 106 | 102 | 106 | 104 | 90 | 86 | 88 | 90 | 96 | 102 | 104 | 100 | 92 | 110 | 112 | 110 | 104 | 118 |  | 132 | 130 | 130 | 134 | 136 | 128 | 124 | 2635200
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 35 | 35 | 22 | 6 | 3 | 3 | 2 | 2 | 7 | 3 | 4 | 28 | 40 | 42 |  | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 688320
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493920
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 8 |  |  |  |  | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 156960
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 710200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 0 | [5 empty] | 19 | 19 | 20 | 20 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 377180
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 13 | 13 | 10 | 16 | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 |  | 12 | 14 | 20 | 22 | 22 | 22 | 22 | 431460
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 24 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 683700
72 | Rupganj 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 10 | 20 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 10 | 27 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 617900
73 | Ghorashal 108MW PP (Regent) | 110 | 110 | 110 | 110 | 55 | 15 | 13 | 13 | 60 | 98 | 107 | 107 | 107 | 107 | 107 | 106 | 107 | 110 |  | 110 | 110 | 109 | 110 | 110 | 110 | 110 | 2165136
| Feni Lanka Power | [20 empty] | 36 | 36 | 36 | 36 |  |  | 131100
| Chowmuhani 113 MW | 26 | 17 | 65 | 65 | [13 empty] | 8 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 853440
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [22 empty] | 16 | 16 |  |  | 22560
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0.4 | 1.1 | 1.6 | 4.9 | 2.5 | 5.7 | 5.5 | 5.4 | 2.6 | 2.6 | 1.2 | 0.9 | [9 empty] | 31680
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 30 | 30 | 30 | 64 | 30 | 15 |  | 4 | 15 | 15 | 15 | 15 | 20 | 30 | 40 | 64 | 64 | 64 |  | 82 | 97 | 96 | 96 | 96 | 97 | 97 | 1203024
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 135 | 130 | 135 | 125 | 125 | 125 | 140 | 140 | 135 | 135 | 135 | 140 | 140 | 140 | 140 | 140 | 130 | 140 |  | 120 | 120 | 125 | 135 | 134 | 130 | 140 | 3261818
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 1 |  | 14 | 50 | 45 | 50 |  |  |  | 128640
88 | Ghorashal 78.5 MW PP(MAX) | [14 empty] | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 35 | 73 | 393568
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 44 | 50 | 47 | 47 | 5 | 5 | 5 | 5 | 5 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 972576
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 15 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1024712
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [21 empty] | 4 | 10 |  |  |  | 21192
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 15 | 15 | 15 | 15 |  |  |  | 50977
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 35 | 55 | 55 | 55 | 17 |  |  | 187722
101 | Kushiara 163 MW CCPP (KP) | 130 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 |  | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 3517118
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.6 | 1.2 | 1.8 | 0.8 | 2.5 | 2.7 | 0.9 | 2.1 | 1.4 | 0.3 | 0.5 | 0.1 | [8 empty] | 14400
103 | Kamalaghat 54 MW PP(Banco Energy) |  |  |  | 17 | [11 empty] | 17 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 35 |  | 309240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 160 | 170 | 200 | 90 | 8 | 8 | 8 | 40 | 74 | 74 | 74 | 141 | 163 | 183 | 140 | 140 | 140 |  | 193 | 175 | 176 | 176 | 176 | 176 | 195 | 3240000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [15 empty] | 4 | 16 | 16 |  | 43 | 75 | 124 | 132 | 128 | 48 | 15 | 535680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 |  | 45 | 100 | 40 | [7 empty] | 30 | 100 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1153920
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) |  |  | 3 | 50 | [8 empty] | 8 | 23 | 60 | 60 | 60 | 60 |  | 75 | 114 | 118 | 128 | 135 | 70 | 70 | 1030400
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | [17 empty] | 2 |  | 40 | 104 | 94 | 104 | 110 | 70 | 24 | 490800
| Anwara 300 MW PP (United) |  |  | 48 | 97 | [7 empty] | 16 | 82 | 123 | 174 | 174 | 107 | 107 |  | 190 | 208 | 210 | 210 | 216 | 190 | 180 | 2039891
| Juldah unit-2 | 100 | 100 | 100 | 30 | 30 | 10 | 10 | 10 | 10 | 40 | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1824000
120 | Eastern Zone Total | 5345 | 5383 | 5721 | 5390 | 4334 | 3986.39 | 4081.7 | 4426.2 | 4702.4 | 4915.2 | 5149.5 | 5321 | 5449.1 | 5654 | 5756.7 | 5389.9 | 5229.9 | 5228.3 |  | 5975 | 6363 | 6509 | 6753 | 6530 | 6156 | 6111 | 130363331
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | [11 empty] | 24 | 83 | 103 | 115 | 91 | 66 | 66 |  | 115 | 115 | 115 | 115 | 115 | 115 | 94 | 1171200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [20 empty] | 32 | 32 | 32 | 32 | 16 | 16 | 140544
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 96 | 96 | 96 | 96 | 63 | 32 | 31 | 31 | 32 | 32 | 32 | 33 | 50 | 72 | 72 | 72 | 72 |  | 80 | 97 | 97 | 98 | 97 | 96 | 97 | 1688142
| Bhola 225 MW CCPP | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 60 | 2019816
140 | Bhola 33 MW PP (Venture) | 21 | 21 | 21 | 23 | 17 | 15 | 14 | 14 | 16 | 17 | 16 | 18 | 19 | 22 | 20 | 20 | 19 | 22 |  | 30 | 31 | 31 | 32 | 32 | 29 | 27 | 507290
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 50 | 41 | 50 | 50 | 50 |  | 240000
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 201750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 455 | 263 | 263 | 263 | 263 | 262 | 262 | 262 | 383 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 408 |  | 781 | 799 | 798 | 799 | 799 | 799 | 652 | 10862545
147 | Bheramara 410 MW CCPP | 335 | 355 | 335 | 330 | 335 | 330 | 375 | 375 | 375 | 365 | 380 | 370 | 365 | 375 | 350 | 340 | 340 | 340 |  | 370 | 335 | 330 | 330 | 330 | 325 | 335 | 8692704
148 | Payra 1320 MW | 350 | 350 | 438 | 426 | 355 | 319 | 282 | 283 | 304 | 303 | 317 | 380 | 453 | 550 | 547 | 550 | 550 | 600 |  | 640 | 663 | 667 | 670 | 666 | 663 | 600 | 10961600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 3676200
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 70 | 65 | 65 | 65 | 60 | 60 | 50 |  | 55 | 55 | 50 | 50 | 50 | 40 | 40 | 1295000
156 | Baghabari 100 MW GTPP | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 70 | 60 | 60 | 60 | 50 | 50 | 45 | 45 | 50 |  | 50 | 50 | 45 | 45 | 45 | 45 | 45 | 1247000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 190 | 190 | 205 | 200 | 140 | 140 | 140 | 165 | 185 | 190 | 190 | 150 | 136 | 139 | 139 | 137 | 55 | 52 |  | 93 | 140 | 142 | 145 | 146 | 147 | 146 | 3894382
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 195 | 196 | 205 | 177 | 153 | 140 | 140 | 165 | 194 | 206 | 206 | 198 | 198 | 199 | 215 | 201 | 184 | 185 |  | 175 | 180 | 180 | 176 | 172 | 177 | 175 | 4656636
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 416 | 413 | 337 | 316 | 311 | 343 | 405 | 410 | 410 | 404 | 400 | 409 | 402 | 401 | 405 | 402 | 409 |  | 408 | 407 | 380 | 397 | 416 | 383 | 407 | 9465545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 17 | 17 | 17 | 17 | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 315360
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 3 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172548
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243882
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 196540
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | [15 empty] | 2 | 4 | 5 |  | 6 | 7 | 8 |  |  |  |  | 20367
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 20 |  | 50 | 70 | 90 | 109 | 109 | 109 | 70 | 615840
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [17 empty] | 5 |  | 35 | 70 | 74 | 113 | 113 | 99 | 70 | 512640
177 | Sympa Solar Power 8MW | [5 empty] | 0.2 | 0.8 | 3.4 | 5.2 | 6.8 | 7.4 | 7.9 | 6.8 | 6.2 | 6 | 1.6 | 1.1 | 0.5 | [8 empty] | 53003
178
178