## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-05-08 | Friday
|  | Date (day): | 2020-05-08 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12270.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15014 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-05-07 | 2020-05-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Unit-1 & 2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 235 | 100 | 0 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 40 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 14 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 305 | 360 | 200
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 32 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 300 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 2 | 7 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 150 | 130 | 150 | 150 | 155 |  | Gas shortage & GT-1 S/D
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 75 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 70 | 150 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 50 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 17 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 37 | 45 | 53 |  | 27 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 20 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 18 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 19 | 76 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 28 | 60 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 1744 | 1459 | 3069 | 3871 | 368 | 1364
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 77 | 73 | 80 | 80 | 150 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 225 | 217 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 80 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 105 | 105
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 40 | 15 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.5 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 49 | 107 | 230 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 90 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 689 | 940 | 1631 | 1761 | 410 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 140 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 181 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 275 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 42 | 41 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 50 | 52 | 52
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 8 | 100 | 120 | 75 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 25 | 51 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 60 | 10 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 0 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 122 | 116 | 141
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 21
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1279 | 1111 | 1558 | 2190 | 238 | 523
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 110 | 160 | 210
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 110 | 45 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 289.4 | 175 | 591.6 | 640 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 86 | 84 | 87 | 87
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 27 | 30 | 30 |  | 63 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 252 | 204 | 220 | 244 |  | 86 | ST Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 40 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 40 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 80 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 150 | 70 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 20 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 250 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 1286 | 1012 | 1297 | 1321 | 0 | 549
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 40
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 397 | 785 | 742 | 938
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 16 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 37
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 215 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 50 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 816 | 1016 | 1527 | 2185 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 26 | 30 | 30
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 |  | 134 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 97 | 89 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 503 | 400 | 400 | 550 |  |  | on test
| Barisal Area Total |  |  |  |  | 472 | 462 | 672 | 583 | 629 | 875 | 0 | 134
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 60 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 0 | 60 | 60 | 40 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 0 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 163 | 140 | 200 | 220 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 193 | 140 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 305 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 14 | 17 | 17 |  | 5 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 908 | 667 | 1647 | 1826 | 271 | 22
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 151 | 140 | 200 | 200
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 154.7 | 140 | 321 | 345 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 7838.1 | 7103 | 12270.6 | 15014 | 1457 | 2690
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7460.7059 | 6761 | 11679.7869 | 14291.0959
A. |  | 2020-05-07 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8644 | MW at | 15:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5802.6 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7103 | MW
3 | Day peak Generation : |  |  | 7838.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6761 | MW
4 | Evening peak Generation : |  |  | 7103 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 170.9665 | MKWHr | By Solar | 0.25385 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 124.475 | MKWHr |  | By Oil: | 18.1456 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.5826 | MKWHr |  | By Hydro: | 1.6732 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1457 | MW | Dhaka | 2557 | 2557 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2690 | MW | Chittagong | 970 | 970 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4147 | MW | Khulna | 787 | 787 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1006.241 | MMCFD |  |  | Rajshahi | 252 | 252 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 150890450.452 | ii) Oil : | Taka | 114327005.31 | Comilla | 1024 | 1024 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 67774333 | Total | Taka | 332991788.762 | Mymensingh | 268 | 268 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.1955 | MKWHr. | Sylhet | 394 | 394 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 730 | MW (E to W) at | 19:00 | hrs | Barisal | 300 | 300 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -97 | MW at | 2:00 | hrs | Rangpur | 209 | 209 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 6761 | 6761 |  | 0
B. |  | 2020-05-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 37.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15014 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6200 | MW
4 | Reserve(Generation end) |  |  |  | 6514 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 168.1184 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4921.7 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.2916 | MKWHr. | ii) HVDC Flow at Peak Time |  | 785 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5446 | MKWHr. | iii) Maximum HVDC Flow : |  | 786 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.94 |  | (b) Today: | 78.49 |  | (c) Rule Curve: |  | 80.67
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-05-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 0 | 110 | 71 | 335 | 0 |  | 0 | 380 | 140 | 0 | 48 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 24 | 25 | 0 | 0 | 36 | 37 | 100 | 0 | 0 | 225 | 0 | 100 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 40 | 135 | 100 | 0 | 310 | 0 | 180 | 130 | 0 | 38 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 0 | 159 | 16 | 20 | 0 | 86 | 27 | 53 | 50 | 130 | 240 | 50 | 20 | 0 | 150 | 19 | 0 | 10 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 124 | 0 | 0 | 54 | 113 | 100 |  | 417 | 0 | 335 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 98 | 0 | 164 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 |  | 5200 | 2503 | 7703 | 3633 | 417 | 1901 | 948 | 680 | 73 | 51 | 0 | 0 | 0 | 78.99
2:00 | 0 | 0 | 200 | 0 | 0 | 110 | 71 | 328 | 0 |  | 0 | 380 | 140 | 0 | 48 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 24 | 25 | 0 | 0 | 35 | 37 | 100 | 0 | 0 | 224 | 0 | 100 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 42 | 135 | 100 | 0 | 320 | 0 | 193 | 130 | 0 | 38 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 0 | 158 | 0 | 20 | 0 | 87 | 27 | 53 | 50 | 130 | 252 | 50 | 20 | 0 | 149 | 19 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 124 | 0 | 0 | 54 | 113 | 100 |  | 252 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 148 | 0 | 96 | 0 | 163 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 |  | 5209 | 2363 | 7572 | 3659 | 252 | 1923 | 935 | 680 | 72 | 51 | 0 | 0 | 0 | 78.98
3:00 | 0 | 0 | 241 | 0 | 0 | 110 | 71 | 360 | 0 |  | 0 | 380 | 140 | 0 | 48 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 24 | 24 | 25 | 0 | 0 | 34 | 37 | 100 | 0 | 0 | 225 | 0 | 100 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 22 | 42 | 135 | 100 | 0 | 345 | 0 | 201 | 130 | 0 | 38 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 0 | 157 | 0 | 20 | 0 | 87 | 27 | 53 | 50 | 130 | 257 | 50 | 80 | 0 | 150 | 19 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 124 | 0 | 0 | 54 | 113 | 100 |  | 252 | 0 | 375 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 98 | 0 | 193 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529 |  | 5428 | 2441 | 7869 | 3924 | 252 | 1974 | 918 | 679 | 71 | 51 | 0 | 0 | 0 | 78.97
4:00 | 0 | 0 | 243 | 0 | 0 | 110 | 72 | 346 | 0 |  | 0 | 420 | 140 | 0 | 45 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 17 | 24 | 25 | 0 | 0 | 34 | 37 | 100 | 0 | 0 | 222 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 42 | 135 | 100 | 0 | 310 | 0 | 180 | 130 | 0 | 38 | 30 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 15 | 0 | 160 | 0 | 20 | 0 | 86 | 27 | 53 | 50 | 163 | 236 | 63 | 77 | 0 | 150 | 19 | 0 | 10 | 295 | 24 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 85 | 0 | 0 | 36 | 113 | 100 |  | 252 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 195 | 0 | 98 | 0 | 206 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528 |  | 5277 | 2297 | 7574 | 3812 | 252 | 1974 | 770 | 678 | 71 | 17 | 0 | 0 | 0 | 78.96
5:00 | 0 | 0 | 150 | 0 | 0 | 52 | 40 | 340 | 0 |  | 0 | 380 | 140 | 0 | 15 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 17 | 24 | 25 | 0 | 0 | 35 | 37 | 100 | 0 | 0 | 220 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 100 | 100 | 0 | 310 | 0 | 182 | 83 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 0 | 159 | 0 | 20 | 0 | 85 | 27 | 11 | 10 | 163 | 238 | 50 | 30 | 0 | 150 | 19 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 100 |  | 252 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 56 | 0 | 189 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 |  | 4293 | 2070 | 6363 | 3522 | 252 | 1520 | 397 | 600 | 72 | 0 | 0 | 0 | 0 | 78.95
6:00 | 0 | 0 | 150 | 0 | 0 | 13 | 40 | 343 | 0 |  | 0 | 350 | 140 | 0 | 15 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 17 | 20 | 25 | 0 | 0 | 35 | 37 | 100 | 0 | 0 | 224 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 100 | 100 | 0 | 310 | 0 | 152 | 45 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 0 | 159 | 0 | 20 | 0.1 | 85 | 27 | 11 | 10 | 130 | 249 | 50 | 10 | 0 | 100 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 26 | 10 |  | 252 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 53 | 0 | 176 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 397 |  | 3878.4 | 1924.2 | 5802.6 | 3369 | 252 | 1355 | 206 | 547 | 72 | 0 | 0 | 1.6 | 0 | 78.94
7:00 | 0 | 0 | 200 | 0 | 0 | 13 | 40 | 368 | 0 |  | 0 | 350 | 140 | 0 | 15 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 17 | 20 | 25 | 0 | 0 | 37 | 37 | 100 | 0 | 0 | 225 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 100 | 100 | 0 | 270 | 0 | 191 | 45 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 0 | 159 | 0 | 17 | 0.5 | 87 | 27 | 11 | 10 | 130 | 244 | 63 | 10 | 0 | 100 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5.5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 26 | 10 |  | 252 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 12 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 53 | 0 | 182 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 415 |  | 4036.7 | 2090.2 | 6126.9 | 3632 | 252 | 1390 | 206 | 565 | 74 | 0 | 0 | 7.9 | 0 | 78.93
8:00 | 0 | 0 | 200 | 0 | 0 | 32 | 40 | 358 | 0 |  | 0 | 350 | 150 | 0 | 15 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 25 | 0 | 0 | 37 | 38 | 100 | 0 | 0 | 226 | 0 | 149 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 100 | 100 | 0 | 320 | 0 | 208 | 83 | 0 | 27 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 52 | 157 | 0 | 17 | 1 | 87 | 27 | 11 | 10 | 163 | 256 | 61 | 10 | 0 | 150 | 19 | 0 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10.9 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 22 |  | 253 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 52 | 0 | 191 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 399 |  | 4301 | 2202.9 | 6503.9 | 3828 | 253 | 1526 | 205 | 548 | 75 | 0 | 52 | 16.9 | 0 | 78.92
9:00 | 0 | 0 | 237 | 0 | 0 | 104 | 68 | 361 | 0 |  | 0 | 350 | 145 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 25 | 0 | 0 | 38 | 39 | 100 | 0 | 0 | 224 | 0 | 148 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 100 | 140 | 0 | 310 | 0 | 202 | 83 | 0 | 39 | 30 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 90 | 155 | 0 | 17 | 1.5 | 88 | 27 | 50 | 30 | 163 | 246 | 60 | 77 | 0 | 151 | 19 | 0 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 15.6 | 30 | 0 | 0 | 0 | 8 | 0 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 95 |  | 252 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 204 | 0 | 93 | 0 | 212 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0 | 400 |  | 4859.4 | 2265.8 | 7125.2 | 3972 | 252 | 1794 | 363 | 550 | 77 | 0 | 90 | 27.2 | 0 | 78.91
10:00 | 0 | 0 | 237 | 0 | 0 | 104 | 67 | 351 | 0 |  | 0 | 350 | 145 | 0 | 28 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 20 | 33 | 25 | 0 | 0 | 38 | 39 | 100 | 0 | 0 | 225 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 100 | 140 | 0 | 320 | 0 | 199 | 83 | 0 | 39 | 52 | 0 | 40 | 0 | 0 | 0 | 21 | 8 | 25 | 11 | 98 | 155 | 0 | 17 | 1.1 | 86 | 27 | 51 | 50 | 130 | 247 | 60 | 77 | 0 | 149 | 19 | 0 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 79 | 0 | 4 | 18.5 | 50 | 0 | 11 | 0 | 8 | 0 | 0 | 5.1 | 16 | 0 | 0 | 0 | 0 | 100 |  | 396 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 95 | 0 | 204 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 404 |  | 4998.7 | 2351.8 | 7350.5 | 3900 | 396 | 1836 | 458 | 554 | 77 | 0 | 98 | 31.5 | 0 | 78.9
11:00 | 0 | 0 | 237 | 0 | 0 | 104 | 67 | 339 | 0 |  | 0 | 380 | 145 | 0 | 64 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 20 | 33 | 25 | 0 | 0 | 38 | 39 | 100 | 0 | 0 | 226 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 100 | 140 | 0 | 310 | 0 | 187 | 83 | 0 | 42 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 25 | 11 | 104 | 154 | 0 | 17 | 1.9 | 87 | 28 | 50 | 50 | 163 | 250 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 14 | 0 | 0 | 100 | 0 | 17 | 19.6 | 100 | 0 | 35 | 0 | 8 | 0 | 0 | 5.4 | 16 | 0 | 0 | 0 | 0 | 100 |  | 396 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 95 | 0 | 201 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 0 | 454 |  | 5214.9 | 2370.4 | 7585.3 | 3840 | 396 | 1897 | 633 | 604 | 77 | 0 | 104 | 34.3 | 0 | 78.89
12:00 | 0 | 0 | 235 | 0 | 0 | 104 | 66 | 356 | 0 |  | 0 | 380 | 150 | 2 | 80 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 20 | 33 | 25 | 0 | 0 | 38 | 39 | 100 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 100 | 140 | 0 | 345 | 0 | 200 | 83 | 0 | 39 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 104 | 152 | 0 | 17 | 2.4 | 86 | 29 | 48 | 50 | 163 | 252 | 58 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 19 | 0 | 0 | 110 | 0 | 28 | 19.5 | 100 | 0 | 60 | 0 | 8 | 0 | 0 | 5.5 | 49 | 0 | 0 | 0 | 27 | 90 |  | 397 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 16 | 8 | 8 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 163 | 0 | 92 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 503 |  | 5287.4 | 2550.7 | 7838.1 | 3804 | 397 | 1929 | 842 | 654 | 77 | 0 | 104 | 31.1 | 0 | 78.88
13:00 | 0 | 0 | 236 | 0 | 0 | 109 | 65 | 347 | 0 |  | 0 | 420 | 145 | 32 | 95 | 13 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 20 | 33 | 29 | 0 | 0 | 37 | 39 | 100 | 0 | 0 | 217 | 0 | 40 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 100 | 140 | 0 | 325 | 0 | 194 | 83 | 0 | 42 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 112 | 151 | 0 | 17 | 2.1 | 86 | 28 | 50 | 50 | 163 | 237 | 59 | 80 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 64 | 0 | 0 | 134 | 0 | 57 | 19.5 | 100 | 0 | 83 | 0 | 8 | 0 | 0 | 4.3 | 100 | 0 | 0 | 0 | 45 | 100 |  | 397 | 0 | 340 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 45 | 45 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 16 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 94 | 0 | 206 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 20 | 553 |  | 5632.9 | 2647.4 | 8280.3 | 3835 | 397 | 2000 | 1126 | 703 | 76 | 0 | 112 | 31.3 | 0 | 78.87
14:00 | 5 | 0 | 235 | 0 | 0 | 110 | 65 | 341 | 0 |  | 0 | 420 | 143 | 41 | 96 | 40 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 20 | 33 | 29 | 0 | 0 | 36 | 36 | 100 | 0 | 0 | 219 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 120 | 140 | 0 | 335 | 0 | 199 | 83 | 0 | 42 | 49 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 122 | 151 | 0 | 17 | 1.9 | 87 | 29 | 53 | 50 | 163 | 246 | 58 | 80 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 134 | 0 | 82 | 17.4 | 100 | 0 | 100 | 0 | 8 | 0 | 0 | 3 | 158 | 0 | 0 | 0 | 45 | 100 |  | 397 | 0 | 360 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 45 | 40 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 15 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 91 | 0 | 202 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 35 | 555 |  | 5958.3 | 2666.5 | 8624.8 | 3998 | 397 | 1964 | 1338 | 705 | 72 | 0 | 122 | 28.8 | 0 | 78.86
15:00 | 20 | 0 | 235 | 0 | 0 | 110 | 64 | 351 | 0 |  | 0 | 420 | 130 | 41 | 96 | 40 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 19 | 25 | 17 | 33 | 29 | 0 | 0 | 35 | 35 | 100 | 0 | 0 | 218 | 0 | 139 | 0 |  | 0 | 0 | 14 | 0 | 0 | 0 | 21 | 4 | 120 | 140 | 0 | 310 | 0 | 196 | 8 | 0 | 42 | 47 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 122 | 185 | 0 | 17 | 1.5 | 84 | 29 | 50 | 50 | 163 | 238 | 59 | 80 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 95 | 0 | 0 | 134 | 0 | 99 | 13.9 | 100 | 0 | 120 | 0 | 22 | 0 | 0 | 2.4 | 207 | 0 | 0 | 0 | 45 | 100 |  | 398 | 0 | 335 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 40 | 35 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 15 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 202 | 0 | 96 | 0 | 199 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 35 | 553 |  | 5973.8 | 2670.2 | 8644 | 3950 | 398 | 1906 | 1459 | 703 | 70 | 14 | 122 | 22 | 0 | 78.85
16:00 | 0 | 0 | 130 | 0 | 0 | 54 | 64 | 326 | 0 |  | 0 | 420 | 135 | 24 | 97 | 55 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 17 | 33 | 12 | 0 | 0 | 35 | 35 | 100 | 0 | 0 | 217 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 19 | 120 | 140 | 0 | 275 | 0 | 198 | 8 | 0 | 42 | 48 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 102 | 157 | 0 | 20 | 0.2 | 87 | 26 | 50 | 47 | 130 | 236 | 59 | 80 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 143 | 0 | 139 | 8.8 | 100 | 0 | 100 | 0 | 45 | 0 | 0 | 1.6 | 180 | 0 | 0 | 0 | 36 | 100 |  | 398 | 0 | 335 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 40 | 30 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 15 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 97 | 0 | 185 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 546 |  | 5536.6 | 2531.8 | 8068.4 | 3652 | 398 | 1809 | 1311 | 696 | 70 | 17 | 102 | 13.4 | 0 | 78.83
17:00 | 0 | 0 | 100 | 0 | 0 | 14 | 65 | 325 | 0 |  | 0 | 320 | 125 | 7 | 97 | 40 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 17 | 33 | 20 | 0 | 0 | 35 | 36 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 38 | 100 | 110 | 0 | 275 | 0 | 181 | 8 | 0 | 41 | 49 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 98 | 151 | 0 | 20 | 0.1 | 87 | 27 | 53 | 50 | 100 | 235 | 60 | 20 | 0 | 100 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 45 | 0 | 0 | 144 | 0 | 100 | 3.3 | 100 | 0 | 100 | 0 | 45 | 0 | 0 | 0.8 | 104 | 0 | 0 | 0 | 36 | 100 |  | 397 | 0 | 335 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 98 | 0 | 179 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 |  | 4892.2 | 2383 | 7275.2 | 3385 | 397 | 1482 | 1121 | 700 | 71 | 17 | 98 | 4.2 | 0 | 78.81
18:00 | 0 | 0 | 100 | 0 | 0 | 14 | 40 | 324 | 32 |  | 0 | 300 | 140 | 7 | 75 | 40 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 25 | 17 | 33 | 20 | 0 | 0 | 36 | 36 | 100 | 0 | 0 | 217 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 40 | 100 | 100 | 0 | 275 | 0 | 184 | 8 | 0 | 42 | 49 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 106 | 152 | 0 | 20 | 0 | 87 | 27 | 25 | 20 | 100 | 205 | 40 | 20 | 0 | 100 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 52 | 0 | 0 | 144 | 0 | 89 | 0.3 | 100 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 36 | 100 |  | 395 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 97 | 0 | 140 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 |  | 4602.3 | 2158 | 6760.3 | 3166 | 395 | 1420 | 961 | 623 | 72 | 17 | 106 | 0.3 | 0 | 78.79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 100 | 0 | 0 | 14 | 40 | 305 | 32 |  | 0 | 300 | 130 | 7 | 75 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 12 | 33 | 18 | 0 | 0 | 36 | 37 | 100 | 0 | 0 | 217 | 0 | 80 | 0 |  | 0 | 0 | 102 | 0 | 0 | 0 | 21 | 40 | 100 | 100 | 0 | 275 | 0 | 181 | 8 | 0 | 42 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 122 | 110 | 0 | 20 | 0 | 84 | 27 | 53 | 40 | 100 | 204 | 40 | 80 | 0 | 70 | 19 | 0 | 10 | 250 | 24 | 11 | 0 | 76 | 0 | 0 | 45 | 0 | 60 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 113 | 100 |  | 785 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 140 | 0 | 97 | 0 | 140 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 4697 | 2406 | 7103 | 3007 | 785 | 1492 | 966 | 540 | 73 | 118 | 122 | 0 | 0 | 78.77
19:30 | 0 | 0 | 100 | 0 | 0 | 14 | 40 | 285 | 58 |  | 0 | 300 | 120 | 0 | 48 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 12 | 8 | 18 | 0 | 0 | 37 | 37 | 100 | 0 | 0 | 218 | 0 | 80 | 0 |  | 0 | 0 | 70 | 0 | 0 | 0 | 21 | 40 | 80 | 80 | 0 | 255 | 0 | 140 | 8 | 0 | 41 | 5 | 0 | 15 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 122 | 111 | 0 | 0 | 0 | 87 | 27 | 53 | 50 | 100 | 201 | 40 | 80 | 0 | 70 | 19 | 0 | 10 | 240 | 24 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 57 | 113 | 100 |  | 785 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 140 | 0 | 96 | 0 | 140 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 |  | 3983 | 2310 | 6293 | 2788 | 785 | 1426 | 537 | 491 | 74 | 70 | 122 | 0 | 0 | 0
20:00 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 281 | 58 |  | 0 | 280 | 120 | 0 | 15 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 37 | 38 | 100 | 0 | 0 | 217 | 0 | 70 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 40 | 50 | 80 | 0 | 240 | 0 | 130 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 120 | 110 | 0 | 0 | 0 | 87 | 26 | 5 | 5 | 100 | 183 | 40 | 10 | 0 | 50 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 113 | 100 |  | 685 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 32 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 88 | 0 | 130 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 |  | 3323 | 2008 | 5331 | 2470 | 685 | 1067 | 470 | 410 | 75 | 34 | 120 | 0 | 0 | 78.75
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 60 |  | 0 | 320 | 140 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 36 | 38 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 32 | 0 | 80 | 0 | 295 | 0 | 196 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 20 | 74 | 0 | 0 | 0 | 87 | 26 | 5 | 5 | 100 | 148 | 40 | 10 | 0 | 80 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 100 |  | 684 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 130 | 0 | 34 | 0 | 130 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 |  | 3095 | 1896 | 4991 | 2397 | 684 | 1064 | 305 | 413 | 74 | 34 | 20 | 0 | 0 | 78.73
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 143 |  | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 10 | 24 | 16 | 0 | 0 | 37 | 38 | 100 | 0 | 0 | 204 | 0 | 139 | 0 |  | 0 | 0 | 35 | 0 | 0 | 0 | 21 | 42 | 0 | 80 | 0 | 260 | 0 | 180 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 74 | 0 | 0 | 0 | 84 | 27 | 5 | 5 | 130 | 195 | 62 | 10 | 0 | 100 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 |  | 680 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 166 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 |  | 3425 | 1918 | 5343 | 2643 | 680 | 1215 | 240 | 411 | 75 | 35 | 44 | 0 | 0 | 78.7
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 283 |  | 0 | 320 | 140 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 24 | 25 | 0 | 0 | 37 | 38 | 100 | 0 | 0 | 218 | 0 | 146 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 12 | 0 | 80 | 0 | 305 | 0 | 200 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 74 | 0 | 0 | 0 | 86 | 27 | 5 | 5 | 110 | 203 | 63 | 10 | 0 | 50 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 |  | 786 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 175 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 |  | 3560 | 2079 | 5639 | 2689 | 786 | 1357 | 210 | 411 | 75 | 51 | 60 | 0 | 0 | 78.69
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 296 |  | 0 | 360 | 125 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 24 | 25 | 0 | 0 | 37 | 38 | 100 | 0 | 0 | 217 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 25 | 0 | 80 | 0 | 310 | 0 | 180 | 8 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 76 | 106 | 0 | 0 | 0 | 86 | 27 | 5 | 5 | 110 | 193 | 64 | 10 | 0 | 101 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 737 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 175 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 |  | 3614 | 2201 | 5815 | 2852 | 737 | 1523 | 125 | 410 | 75 | 17 | 76 | 0 | 0 | 78.67
KWH | 18000 | 0 | 3807000 | 0 | 0 | 1432272 | 1133664 | 8309520 | 802000 |  | 0 | 8524000 | 3350807 | 173760 | 1165800 | 294277 | 0 | 0 | 3092000 | 0 | 0 | 0 | 10560 | 0 | 0 | 0 | 0 | 369720 | 227318 | 63269 | 313524 | 550000 | 454680 | 653000 | 596200 | 0 | 0 | 785160 | 888000 | 2400000 | 0 | 0 | 5149600 | 0 | 2644382 | 0 |  | 0 | 0 | 543102 | 0 | 0 | 0 | 470832 | 650880 | 2263894 | 2582595 | 0 | 7624000 | 0 | 4521000 | 1421818 | 0 | 721008 | 721440 | 0 | 793488 | 0 | 0 | 0 | 430452 | 195120 | 704100 | 339290 | 1544640 | 3294040 | 18240 | 328068 | 13650 | 2046000 | 652560 | 834600 | 838296 | 3389154 | 5201000 | 1325760 | 1107840 | 0 | 3004060 | 356000 | 0 | 196920 | 7253500 | 431190 | 209000 | 0 | 594654 | 0 | 0 | 2150400 | 0 | 696960 | 154035 | 1298880 | 0 | 754400 | 0 | 398400 | 0 | 0 | 38040 | 1530545 | 0 | 0 | 323760 | 1259160 | 2072640 |  | 10291636 | 0 | 7681536 | 0 | 561600 | 0 | 0 | 0 | 0 | 0 | 0 | 1390000 | 393682 | 43200 | 0 | 822000 | 950000 | 0 | 0 | 0 | 124190 | 0 | 0 | 0 | 0 | 252480 | 144432 | 110646 | 0 | 0 | 3647300 | 0 | 0 | 0 | 0 | 4152245 | 0 | 1804480 | 0 | 4592864 | 0 | 8392909 | 0 | 0 | 0 | 0 | 0 | 0 | 48124 | 120000 | 10935300 |  | 114507924 | 56458624 | 170966548 | 84387166 | 10291636 | 40087855 | 17591980 | 14582600 | 1673160 | 553662 | 1544640 | 253849 | 0
Fuel Cost | 29520 | 0 | 5558220 | 0 | 0 | 1890599.04 | 1927228.8 | 8392615.2 | 826060 |  | 0 | 9291160 | 3719395.77 | 1318838.4 | 8032362 | 2489583.42 | 0 | 0 | 5349160 | 0 | 0 | 0 | 103910.4 | 0 | 0 | 0 | 0 | 2698956 | 1757168.14 | 623832.34 | 235143 | 412500 | 0 | 0 | 0 | 0 | 0 | 211993.2 | 239760 | 4344000 | 0 | 0 | 5613064 | 0 | 4495449.4 | 0 |  | 0 | 0 | 5268089.4 | 0 | 0 | 0 | 593248.32 | 1933113.6 | 3350563.12 | 3822240.6 | 0 | 5641760 | 0 | 4159320 | 1834145.22 | 0 | 814739.04 | 1010016 | 0 | 1356864.48 | 0 | 0 | 0 | 546674.04 | 146340 | 1232175 | 254467.5 | 11584800 | 3491682.4 | 165619.2 | 416646.36 | 217581 | 3355440 | 1044096 | 1485588 | 1307741.76 | 3863635.56 | 5409040 | 2611747.2 | 2115974.4 | 0 | 5197023.8 | 779640 | 0 | 401716.8 | 7326035 | 323392.5 | 158840 | 0 | 4495584.24 | 0 | 0 | 11182080 | 0 | 6858086.4 | 1800669.15 | 10585872 | 0 | 5318520 | 0 | 3633408 | 0 | 0 | 0 | 11570920.2 | 0 | 0 | 3231124.8 | 10791001.2 | 13803782.4 |  | 59279823.36 | 0 | 8065612.8 | 0 | 4414176 | 0 | 0 | 0 | 0 | 0 | 0 | 1570700 | 610207.1 | 421632 | 0 | 1685100 | 1947500 | 0 | 0 | 0 | 956263 | 0 | 0 | 0 | 0 | 484761.6 | 223869.6 | 83759.022 | 0 | 0 | 19768366 | 0 | 0 | 0 | 0 | 5480963.4 | 0 | 2706720 | 0 | 5373650.88 | 0 | 8308979.91 | 0 | 0 | 0 | 0 | 0 | 0 | 531770.2 | 886800 | 48005967 |  | 236051563.8 | 170806621.872 | 406858185.672 | 101986033.582 | 59279823.36 | 48904416.87 | 108955005.51 | 67774333 | 451753.2 | 5371999.8 | 11584800 | 2550020.35 | 0
Yesterday Day Peak | 0 | 0 | 235 | 0 | 0 | 104 | 66 | 356 | 0 |  | 0 | 380 | 150 | 2 | 80 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 19 | 25 | 20 | 33 | 25 | 0 | 0 | 38 | 39 | 100 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 100 | 140 | 0 | 345 | 0 | 200 | 83 | 0 | 39 | 50 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 104 | 152 | 0 | 17 | 2.4 | 86 | 29 | 48 | 50 | 163 | 252 | 58 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 19 | 0 | 0 | 110 | 0 | 28 | 19.5 | 100 | 0 | 60 | 0 | 8 | 0 | 0 | 5.5 | 49 | 0 | 0 | 0 | 27 | 90 |  | 397 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 16 | 8 | 8 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 163 | 0 | 92 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 0 | 503 |  | 7838.1 | DayPeak
Yesterday Evening Peak | 0 | 0 | 100 | 0 | 0 | 14 | 40 | 305 | 32 | 0 | 0 | 300 | 130 | 7 | 75 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 19 | 25 | 12 | 33 | 18 | 0 | 0 | 36 | 37 | 100 | 0 | 0 | 217 | 0 | 80 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 21 | 40 | 100 | 100 | 0 | 275 | 0 | 181 | 8 | 0 | 42 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 122 | 110 | 0 | 20 | 0 | 84 | 27 | 53 | 40 | 100 | 204 | 40 | 80 | 0 | 70 | 19 | 0 | 10 | 250 | 24 | 11 | 0 | 76 | 0 | 0 | 45 | 0 | 60 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 113 | 100 |  | 785 | 0 | 215 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 140 | 0 | 97 | 0 | 140 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 |  | 7103 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 108 | 78 | 200 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 28 | 24 | 25 | 52 | 0 | 40 | 40 | 100 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 40 | 135 | 100 | 0 | 360 | 0 | 225 | 120 | 0 | 42 | 52 | 0 | 51 | 0 | 50 | 50 | 22 | 11 | 33 | 21 | 141 | 210 | 95 | 20 | 0 | 87 | 30 | 51 | 44 | 163 | 244 | 66 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 938 | 40 | 410 |  | 115 | 225 | 0 | 0 | 37 | 70 | 40 | 60 | 30 | 110 | 30 | 60 | 50 | 50 | 45 | 100 | 50 | 42 | 46 | 43 | 35 | 17 | 11 | 11 | 0 | 0 | 200 | 17 | 15 | 0 | 0 | 220 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 200 | 113 | 105 | 113 | 0 |  | 113 | 550
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 108 | 78 | 360 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 0 | 0 | 150 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 50 | 54 | 35 | 55 | 22 | 25 | 20 | 20 | 25 | 52 | 0 | 40 | 40 | 100 | 0 | 25 | 225 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 15 | 100 | 100 | 0 | 360 | 0 | 225 | 100 | 0 | 41 | 52 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 116 | 160 | 95 | 20 | 1.6 | 87 | 30 | 51 | 44 | 163 | 220 | 66 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 0 | 100 | 0 | 115 | 100 | 105 | 5 | 230 | 54 | 50 | 114 | 113 | 100 |  | 742 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 30 | 40 | 60 | 30 | 50 | 0 | 60 | 50 | 0 | 0 | 80 | 50 | 42 | 40 | 40 | 0 | 17 | 11 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 200 |  | 89 | 50 | 210 | 0 | 410 | 90 | 100 | 113 | 50 | 113 | 0 | 8 | 113 | 400
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 355 | 304 | 0 | 0 | 350 | 140 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 24 | 25 | 0 | 0 | 36 | 38 | 100 | 0 | 0 | 218 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 80 | 0 | 320 | 0 | 192 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 130 | 0 | 0 | 1.2 | 86 | 27 | 5 | 5 | 110 | 196 | 52 | 10 | 0 | 50 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 212 | 0
199
| Minimum Generation |  | 5802.6 | 6:00
| Highest Generation |  | 8644 | 15:00
| Day Peak Generation |  | 7838.1 | 12:00
| Evening Peak Generation |  | 7103 | 19:00
| HVDC Max Flow |  | 786 | 23:00
| HVDC EvPeak Flow |  | 785 | 19:00
| Load factor L.F |  | 82.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-05-08
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-05-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7838.1 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 4921.7 | MW
Evening Peak Generation : |  | 7103 | MW Hour : | 19:00 | Available Max Generation : |  | 15014 | MW
E.P. Demand (at gen end) : |  | 7103 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8500 | MW
Maximum Generation : |  | 8644 | MW Hour : | 15:00 | Reserve(Generation end) |  | 6514 | MW
Total Gen. (MKWH) : |  | 170.9665 | System Load Factor : | 82.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -97 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-05-08
Actual : | 78.49 | Ft.(MSL) , | Rule curve : | 80.67 | Ft.( MSL )
Gas Consumed : | Total = | 1006.241 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 150890450.452
: |  | Coal : | 67774333 | Oil : | 114327005.31 | Total : | 332991788.762
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3025.109 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1022.0139 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 914.4984 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 825.9032 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 746.5902 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 602.455 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 345.4729 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 155.3438 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 464.602 |  |  | 0 | 0%
Total | 0 |  | 8101.9882 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 11) Ashuganj 450 MW South
2) Bibiyana #3
3) Ghorasal Unit-1,2,3,5 & 7.
4) Ashuganj unit-5
5) Siddirganj-335 MW
6) Kaptai-2,5
7) Raozan # 2
9) Chandpur 163 MW
10) Bhola-225 MW GT-2 & ST.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Jamalpur-Mymensingh 132 kV Ckt-2 was under shut down from 08:12 to 12:53 for CB maintenance at
Mymensingh.
b) Naogaon 132/33 kV T-1 transformer was under shut down from 09:15 to 10:10 for R/H maintenance at |  |  |  |  | About 09 MW power interruption occurred under Naogaon S/S area
33 kV side. |  |  |  |  | from 09:15 to 10:10.
c) Kabirpur 132/33 kV T-2 & T-3 transformer were under shut down from 10:28 to 11:48 for R/H maintenance
at 33 kV side.
d) Sikalbaha 150 MW GT tripped at 11:03 due to IGV problem and was synchronized at 12:53.
e) Rampura-Ullon 132 kV Ckt-1 was under shut down from 11:53 to 15:16 for Ullon S/S work.
f) Ullon-Haripur 132 kV Ckt tripped at 13:25 showing Dist. Z1,B-phase on both ends and was switched on at
13:53.
g) Ghorashal-Ashuganj 132 kV Ckt-1 was switched on at 16:06.
h) Haripur 360 MW GT was synchronized at 17:05 and ST was synchronized at 21:22.
i) Baghabari 100 MW was forced shut down at 17:37 for gas shortage.
j) Bogura-Sherpur 132 kV Ckt-1 tripped at 16:38 showing Dist. Z1,A-phase at Bogura end and was switched
on at 12:14.
k) Barishal-Patuakhali 132 kV Ckt tripped at 21:11 showing Dist Z1, A,B & C phase at Barishal end and was |  |  |  |  | About 77 MW power interruption occurred under Patuakhali S/S area
switched on at 21:56. |  |  |  |  | from 21:11 to 21:56.
l) Mongla-Bagerhat 132 kV Ckt tripped at 20:37 showing Dist. A-B-C phase at Mongla end and was |  |  |  |  | About 8 MW power interruption occurred under Mongla S/S area
switched on at 20:49. |  |  |  |  | from 20:37 20:49.
m) Barishal -Bhandaria 132 kV Ckt tripped at 21:03 showing Dist. Z1,A-phase at Barishal end and
was switched on at 23:18.
n) Juldah-Shahmirpur 132 kV Ckt-1 tripped at 23:20 from both ends showing Dist. Z1 at both ends and
was switched on at 00:27(08/05/2020).
o) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 00:25(08/05/2020) to 09:29 to remove
GI wire on the line.
p) Madanganj 132/33 kV T-1 transformer tripped at 00:26(08/05/2020) from both sides showing O/C, B-phase
due to Mondalpara feeder fault and was switched on at 00:45.
q) Madaripur-Gopalganj 132 kV Ckt-2 was under shut down from 06:50(08/05/2020) to 09:18 for R/H
maintenance at Madaripur end.
r) Halishahar 132/33 kV T-3 transformer was shut down at 07:39(08/05/2020) for R/H maintenance at
33 kV breaker.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-05-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 18000 | Unit-1 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 3807000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 40 | 1133664 | Low demand
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 14 | 1432272 | Low demand
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 305 | 8309520 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 32 | 802000 | machine syn at 17:05
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 8524000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 173760 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 130 | 3350807 | Gas shortage.
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 75 | 1165800 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 294277 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 313524
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 70 | 3092000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under S/D.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 369720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 10560 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 227318 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 63269 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 1004680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 653000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 18 | 596200 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 76 | 594654 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 60 | 696960 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 1459 | 36632985
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 154035
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 73 | 1673160 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 217 | 5149600 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 80 | 2644382 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 543102
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1298880
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 470832
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 650880
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 38040
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 107 | 1530545 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 100 | 2072640
| Chattogram area Total |  |  |  | 2166 | 940 | 18626096
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2263894 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2582595 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4521000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7624000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 721008
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 721440
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1421818 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 793488 | Low demand
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 754400 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 430452
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 195120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 1544640
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 704100
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 339290 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 323760 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1259160
| Cumilla Area Total |  |  |  | 2980 | 1111 | 26200165
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 110 | 3294040 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 328068
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 18240 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13650
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 45 | 2150400 | Low demand
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 0 | 398400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 175 | 6202798
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 84 | 2046000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 27 | 652560
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3389154
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 204 | 5201000 | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 834600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 40 | 838296
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 209000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1325760 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1107840
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 70 | 3004060
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 356000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 431190
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 250 | 7253500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 196920
| Sylhet Area Total |  |  |  | 1949 | 1012 | 26845880
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 785 | 10291636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 561600 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 7681536 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Reserve
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2314 | 1016 | 18534772
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 43200 | Reserve
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 393682 | Engine problem
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1390000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1804480
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 400 | 10935300 | On test
| Barisal Area Total |  |  |  | 462 | 583 | 14566662
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 950000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 822000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 124190 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under S/D.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 4152245 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 140 | 4592864 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 305 | 8392909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 14 | 252480 | Engine problem
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 144432 | Engine problem
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 110646 | Engine problem
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 120000 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 667 | 19661766
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 140 | 3647300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48124
| Rangpur Area Total |  |  |  | 605 | 140 | 3695424
| Total |  |  |  | 19107 | 7103 | 170966548
| Eastern Grid Total |  |  |  | 13543 | 4697 | 114507924
| Western Grid Total |  |  |  | 5564 | 2406 | 56458624
| National Grid Total |  |  |  | 19107 | 7103 | 170966548
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-05-07
(a) ENTIRE EASTERN GRID : |  | 5213 | MW | (b) ENTIRE WESTERN GRID : |  | 1548 | MW
i) Dhaka area |  | 2557 | MW | i) Khulna area |  | 787 | MW
ii) Chittagong area |  | 970 | MW | ii) Rajshahi area |  | 252 | MW
iii) Comilla area |  | 1024 | MW | iii) Barisal area |  | 300 | MW
iv) Mymensingh area |  | 268 | MW | iv) Rangpur area |  | 209 | MW
v) Sylhet area |  | 394 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 6761 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 14:00 | Sherpur | 72 | 1:00 | Benapol | 28 | 14:00
Munsiganj | 106 | 19:00 | Srimongal | 42 | 19:00 | Jhenida | 70 | 2:00
Sonargaon | 56 | 2:00 | Shahjibazar | 87 | 19:00 | Bottail | 90 | 2:00
Shyampur | 138 | 2:00 | Fenchuganj | 30 | 20:00 | G.K Project | 35 | 1:00
Bhulta | 107 | 12:00 | Kulawara | 40 | 19:00 | Faridpur | 120 | 18:00
Madanganj | 46 | 15:00 | Sylhet | 104 | 21:00 | Madaripur | 74 | 19:00
Shitalakhya | 89 | 15:00 | Chatak | 19 | 19:00 | Sariatpur | 58 | 19:30
Rahim steel | 16 | 10:00 | Sunamganj | 42 | 19:30 | Gopalganj | 80 | 19:00
Matuail | 68 | 12:00 | Biani Bazar | 57 | 21:00 | Bagerhat | 60 | 18:30
Ghorasal | 57 | 16:00 | Comilla (S) | 122 | 19:00 | Mongla | 34 | 10:00
Narsingdi | 113 | 19:30 | Comilla(N) | 117 | 19:30 | Satkhira | 76 | 15:00
Haripur (SBU) | 75 | 13:00 | Chandpur | 93 | 19:30 | Gallamari | 46 | 19:30
Ullon | 42 | 14:00 | Feni | 114 | 21:00 | Magura | 38 | 18:30
Hasnabad | 178 | 19:30 | Chowmuhani | 144 | 18:30 | Norail | 30 | 19:00
Magbazar | 84 | 14:00 | Ashuganj | 55 | 19:30 | Chuadanga | 66 | 1:00
Maniknagar | 76 | 14:00 | Daudkandi | 130 | 19:00 | Barisal(N) | 43 | 20:00
Bangabhaban | 20 | 11:00 | B.Baria | 139 | 20:00 | Barisal (S) | 98 | 20:00
Narinda | 66 | 13:00 | Ramganj | 108 | 18:30 | Patuakhali | 106 | 21:00
Dhanmondi | 84 | 13:00 | Chaddagram | 32 | 20:00 | Bhandaria | 48 | 20:00
Lalbag | 62 | 13:00 | PHP | 9 | 8:00 | Borhan Uddin | 40 | 21:00
Madartek | 61 | 19:30 | Madunaghat | 50 | 15:00 | Ishurdi | 45 | 14:00
Dhaka University |  |  | Hathazari | 86 | 19:00 | Ruppur Paromanobik | 2 | 17:00
Mirpur | 80 | 15:00 | Khulshi | 124 | 14:00 | Natore | 75 | 3:00
Kalyanpur | 72 | 14:00 | Halishahar | 112 | 19:00 | Bogra | 104 | 1:00
Gulshan | 86 | 13:00 | Baraulia | 123 | 11:00 | Noagaon | 72 | 4:00
Uttara | 59 | 14:00 | Sikalbaha | 20 | 15:00 | Rajshahi | 112 | 3:00
Uttara New | 20 | 14:00 | Dohazari | 86 | 19:30 | Rajshahi New | 8 | 3:00
Kamrangirchar | 60 | 14:00 | Cox'sbazar | 86 | 21:00 | C.Nawabganj | 59 | 3:00
Savar | 100 | 13:00 | Chandraghona | 28 | 19:00 | Amnura | 28 | 3:00
Bhasantec | 116 | 14:00 | Kaptai | 4 | 18:30 | Pabna | 81 | 15:00
Agargaon | 36 | 14:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 79 | 12:00
Satmosjid | 78 | 14:00 | Bakulia | 82 | 22:00 | Serajganj | 64 | 15:00
Tongi | 118 | 12:00 | Julda | 18 | 4:00 | Niyamatpur | 29 | 1:00
Kabirpur | 180 | 18:00 | TK chemical | 18.3 | 22:00 | Joypurhat | 45 | 2:00
Basundhara | 90 | 13:00 | Modern Steel | 13 | 15:00 | Sherpur(Bogura) | 34 | 3:00
Manikganj | 58 | 18:00 | Shahmirpur | 28 | 14:00 | Mohastangor | 28 | 3:00
Joydevpur | 146 | 15:00 | Khagrachhari | 22 | 19:30 | Rangpur | 95 | 15:00
New Tongi | 84 | 12:00 | Matarbari | 30 | 21:00 | Lalmonirhat | 35 | 13:00
Kodda | 182 | 15:00 | Baroiar Hat | 34 | 19:00 | Saidpur | 74 | 17:00
Dhamrai | 62 | 13:00 | Rangamati | 10 | 19:00 | Purbasadipur | 65 | 13:00
Rajendrapur | 72 | 14:00 | Abul Khair 230 | 146 | 2:00 | Thakurgaon | 46 | 16:00
Valuka | 68 | 14:00 | BSRM | 107 | 13:00 | Palashbari | 76 | 3:00
Tangail | 143 | 15:00 | GPH Ispat | 110 | 11:00 | Barapukuria | 32 | 12:00
Mymensing | 169 | 18:00 | Goalpara | 25 | 19:30 | Panchagar | 27 | 14:00
Kishorganj | 108 | 19:00 | Central s/s | 72 | 19:00 | Joldhaka | 14 | 16:00
Netrokona | 90 | 18:30 | Noapara | 46 | 19:30 | Kurigram | 36 | 0.77083
Jamalpur | 89 | 17:00 | Jessore | 102 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2020-05-07 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV |  |  | KV |  | KV
Bibiyana | 408 | 0.83333 | 392 | 0.375 | Kaliakoir | 397 | 0.83333 | 370 | 0.41667
Bheramara | 407 | 0.75 | 399 | 0.83333 | Bhulta | 399 | 0.875 | 378 | 0.375
Ashuganj(N) | 405 | 0.875 | 385 | 0.375 | Gopalganj | 423 | 0.875 | 389 | 0.58333
Payra | 419 | 0.875 | 400 | 0.58333
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 245 | 0.8125 | 230 | 0.041667 | Comilla (N) | 240 | 0.875 | 226 | 0.5
Ishurdi | 243 | 0.875 | 225 | 0.58333 | Hathazari | 224 | 24:00 | 216 | 0.5
Ashuganj | 241 | 0.83333 | 234 | 0.45833 | Megnaghat | 241 | 0.83333 | 225 | 0.41667
Serajganj | 235 | 0.25 | 230 | 0.041667 | Fenchuganj | 243 | 0.83333 | 236 | 0.625
Baghabari | 246 | 0.77083 | 238 | 0.041667 | Siddhirganj | 239 | 0.83333 | 224 | 0.41667
Barapukuria | 237 | 0.77083 | 227 | 0.54167 | Maniknagar | 238 | 0.83333 | 223 | 0.41667
Bogra | 240 | 0.79167 | 225 | 0.125 | Agargaon | 239 | 0.83333 | 222 | 0.41667
Rajshahi | 240 | 0.75 | 219 | 0.58333 | Barisal | 249 | 0.875 | 224 | 0.16667
Khulna South | 226 | 0.16667 | 215 | 0.58333 | AKSML | 221 | 0.16667 | 214 | 0.54167
Rampura | 233 | 0.83333 | 223 | 0.45833 | BSRM | 226 | 0.91667 | 216 | 0.375
Haripur | 237 | 0.83333 | 222 | 0.41667 | Bibiyana | 241 | 0.8125 | 232 | 0.41667
Hasnabad | 235 | 0.8125 | 224 | 0.41667 | Bhulta | 237 | 0.875 | 224 | 0.41667
Shyampur | 237 | 0.83333 | 221 | 0.41667 | Ashuganj (S) | 237 | 0.041667 | 227 | 0.16667
Aminbazar | 240 | 0.83333 | 224 | 0.5 | Kaliakoir | 242 | 0.83333 | 224 | 0.41667
Tongi | 234 | 0.875 | 220 | 0.375 | GPH | 221 | 0.83333 | 214 | 0.375
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 0.83333 | 128 | 0.375 | Hathazari | 133 | 0.125 | 128 | 0.5
Munsiganj | 138 | 0.83333 | 129 | 0.375 | Khulshi | 131 | 0 | 125 | 0.45833
Sonargaon | 135 | 0.83333 | 128 | 0.33333 | Halishahar | 132 | 0.77083 | 126 | 0.29167
Shyampur | 139 | 0.83333 | 128 | 0.41667 | Baraulia | 132 | 0.95833 | 127 | 0.33333
Bhulta | 131 | 0.83333 | 123 | 0.41667 | Sikalbaha | 132 | 0.041667 | 126 | 0.875
Madanganj | 136 | 0.83333 | 125 | 0.375 | Dohazari | 129 | 0 | 121 | 0.875
Shitalakhya | 142 | 0.83333 | 127 | 0.41667 | Cox'sbazar | 128 | 0 | 112 | 0.875
Rahim steal | 137 | 0.83333 | 129 | 0.41667 | Chandraghona | 132 | 0 | 128 | 0.875
Matuail | 136 | 0.875 | 128 | 0.33333 | Kaptai | 131 | 0.041667 | 128 | 0.45833
Ghorasal | 145 | 0.83333 | 135 | 0.54167 | A. Khaer Stl. | 130 | 0.041667 | 126 | 0.41667
Narsinghdi | 139 | 0.875 | 126 | 0.375 | Bakulia | 130 | 0.041667 | 126 | 0.33333
Haripur (SBU) | 137 | 0.83333 | 128 | 0.41667 | Julda | 133 | 0.125 | 127 | 0.33333
Ullon | 136 | 0.83333 | 126 | 0.45833 | TK Chemical | 131 | 0.041667 | 126 | 0.83333
Hasnabad | 140 | 0.83333 | 128 | 0.375 | Modern Steel | 131 | 0.041667 | 126 | 0.45833
Magbazar | 136 | 0.83333 | 126 | 0.41667 | Shahmirpur | 132 | 0.16667 | 123 | 0.083333
Maniknagar | 139 | 0.83333 | 131 | 0.41667 | Khagrachhari | 131 | 0.041667 | 127 | 0.5
Bangabhaban | 139 | 0.83333 | 131 | 0.41667 | Matarbari | 129 | 0 | 114 | 0.875
Narinda | 139 | 0.83333 | 131 | 0.41667 | Baroiar Hat | 135 | 0.91667 | 124 | 14:00
Dhanmondi | 136 | 0.83333 | 126 | 0.45833 | Rangamati | 132 | 0.083333 | 127 | 21:00
Lalbag | 140 | 0.83333 | 126 | 0.41667 | Goalpara S/S | 143 | 0.83333 | 129 | 0.45833
Madartek | 135 | 0.83333 | 125 | 0.41667 | Central s/s | 140 | 0.83333 | 124 | 0.58333
Dhaka University |  |  |  |  | Noapara | 143 | 0.83333 | 123 | 0.58333
Mirpur | 137 | 0.83333 | 127 | 0.41667 | Jessore | 140 | 0.83333 | 120 | 0.58333
Kalyanpur | 138 | 0.83333 | 128 | 0.41667 | Benapol | 141 | 0.83333 | 119 | 0.58333
Gulshan | 136 | 0.83333 | 125 | 0.41667 | Jhenida | 141 | 0.83333 | 117 | 0.58333
Uttara | 141 | 0.8125 | 128 | 0.375 | Bottail | 141 | 0.8125 | 126 | 0.58333
Uttara New | 137 | 0.83333 | 126 | 0.41667 | G.K Project | 143 | 0.8125 | 133 | 0.58333
Kamrangirchar | 139 | 0.83333 | 125 | 0.41667 | Faridpur | 142 | 0.875 | 127 | 0.58333
Savar | 138 | 0.83333 | 126 | 0.41667 | Madaripur | 145 | 0.875 | 132 | 0.58333
Bhasantec | 137 | 0.83333 | 126 | 0.41667 | Sariatpur | 146 | 0.875 | 128 | 0.041667
Agargaon | 138 | 0.83333 | 127 | 0.41667 | Gopalganj | 149 | 0.875 | 129 | 0.58333
Satmosjid | 138 | 0.83333 | 127 | 0.41667 | Bagerhat | 144 | 0.875 | 120 | 0.54167
Tongi | 142 | 0.8125 | 131 | 0.375 | Mongla | 142 | 0.875 | 118 | 0.58333
Kabirpur | 140 | 0.83333 | 120 | 0.45833 | Satkhira | 145 | 0.83333 | 121 | 0.58333
Basundhara | 135 | 0.83333 | 125 | 0.41667 | Gallamari | 143 | 0.83333 | 125 | 0.58333
Manikganj | 144 | 0.83333 | 129 | 0.54167 | Magura | 140 | 0.8125 | 115 | 0.58333
Joydevpur | 143 | 0.875 | 133 | 0.41667 | Norail | 140 | 0.83333 | 121 | 0.58333
New Tongi | 142 | 0.83333 | 129 | 0.375 | Chuadanga | 138 | 0.8125 | 111 | 0.58333
Kodda | 140 | 0.8125 | 124 | 0.375 | Barisal(N) | 142 | 0.875 | 129 | 0.625
Dhamrai | 139 | 0.8125 | 124 | 0.54167 | Barisal (S) | 144 | 0.91667 | 124 | 0.77083
Rajendrapur | 145 | 0.83333 | 128 | 0.45833 | Patuakhali | 140 | 0.95833 | 122 | 0.79167
Valuka | 139 | 0.8125 | 120 | 0.54167 | Bhandaria | 137 | 0.25 | 124 | 0.625
Tangail | 143 | 0.8125 | 124 | 0.54167 | Ishurdi | 143 | 0.875 | 131 | 0.58333
Mymensing | 140 | 0.83333 | 122 | 0.58333 | Ruppur Paromanobik | 140 | 0.83333 | 131 | 0.58333
Kishorganj | 140 | 0.83333 | 125 | 0.54167 | Natore | 142 | 0.75 | 128 | 0.58333
Netrokona | 140 | 0.83333 | 121 | 0.54167 | Bogra | 142 | 0.83333 | 129 | 0.58333
Jamalpur | 137 | 0.77083 | 128 | 0.54167 | Noagaon | 140 | 0.75 | 126 | 0.58333
Sherpur | 139 | 0.77083 | 123 | 0.95833 | Rajshahi | 141 | 0.75 | 127 | 0.58333
Srimongal | 140 | 0.875 | 135 | 0.79167 | Rajshahi New | 141 | 0.8125 | 129 | 0.58333
Shahjibazar | 139 | 0.875 | 134 | 1:00 | C.Nawabganj | 141 | 0.83333 | 127 | 0.58333
Fenchuganj | 136 | 0.83333 | 135 | 0.041667 | Amnura | 141 | 0.75 | 128 | 0.45833
Khulawara | 136 | 0.25 | 134 | 0.79167 | Pabna | 142 | 0.77083 | 128 | 0.58333
Sylhet | 135 | 0.041667 | 133 | 0.79167 | Shahjadpur | 145 | 0.79167 | 136 | 0.58333
Chatak | 134 | 0.125 | 131 | 0.8125 | Serajganj | 142 | 0.79167 | 130 | 0.625
Sunamganj | 135 | 0.125 | 129 | 0.8125 | Niyamatpur | 141 | 0.75 | 125 | 0.58333
Biani Bazar | 134 | 0.083333 | 130 | 0.8125 | Joypurhat | 141 | 0.75 | 126 | 0.083333
Comilla(s) | 134 | 0.875 | 122 | 0.54167 | Sherpur(Bogura) | 142 | 0.75 | 130 | 0.58333
Comilla(n) | 138 | 0.95833 | 128 | 0.5 | Mohastangor | 140 | 0.79167 | 128 | 0.58333
Chandpur | 138 | 0.91667 | 124 | 0.79167 | Rangpur | 136 | 0.83333 | 122 | 0.625
Feni | 138 | 0.91667 | 125 | 0.58333 | Lalmonirhat | 134 | 0.79167 | 117 | 0.25
Chowmuhani | 136 | 0.91667 | 120 | 0.29167 | Saidpur | 137 | 0.79167 | 119 | 0.58333
Ashuganj | 147 | 0.875 | 135 | 0.041667 | Purbasadipur | 136 | 0.79167 | 118 | 0.58333
Daudkandi | 138 | 0.875 | 126 | 0.83333 | Thakurgaon | 134 | 0.77083 | 119 | 0.58333
B.Baria | 139 | 0.875 | 131 | 0.58333 | Palashbari | 137 | 0.79167 | 120 | 0.625
Ramganj | 136 | 0.91667 | 116 | 0.79167 | Barapukuria | 137 | 0.83333 | 127 | 0.625
Chaddagram | 136 | 0.91667 | 125 | 0.625 | Panchagar | 136 | 0.77083 | 112 | 0.58333
PHP | 136 | 0.91667 | 122 | 0.625 | Joldhaka | 137 | 0.79167 | 119 | 0.58333
Madanhat | 134 | 0.083333 | 129 | 0.875 | Kurigram | 137 | 0.79167 | 118 | 0.58333

## L-Curve
Date | 2020-05-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 546 | 3614 | 2201 | 5815 |  |  |  | QF-LDC-12
0:30 | 335 | 4407 | 2352 | 6759 | Date: | 2020-05-07
1:00 | 124 | 5200 | 2503 | 7703
1:30 | 110.5 | 5204.5 | 2433 | 7637.5
2:00 | 97 | 5209 | 2363 | 7572
2:30 | 63.5 | 5318.5 | 2402 | 7720.5 | [5 empty] | Gen. at Eve. Peak | 7103 | 7103 MW (19:00 )
3:00 | 30 | 5428 | 2441 | 7869 | [6 empty] | 19:00
3:30 | 18.5 | 5352.5 | 2369 | 7721.5 | [5 empty] | Gen. at Day Peak | 7838.1 | 7838.1 MW (12:00 )
4:00 | 7 | 5277 | 2297 | 7574 | [6 empty] | 12:00
4:30 | 46 | 4785 | 2183.5 | 6968.5 | [5 empty] | Highest Generation | 8644
5:00 | 85 | 4293 | 2070 | 6363 | [6 empty] | 15:00
5:30 | 176.5 | 4085.7 | 1997.1 | 6082.8
6:00 | 268 | 3878.4 | 1924.2 | 5802.6
6:30 | 281.5 | 3957.55 | 2007.2 | 5964.75
7:00 | 295 | 4036.7 | 2090.2 | 6126.9
7:30 | 315.5 | 4168.85 | 2146.55 | 6315.4
8:00 | 336 | 4301 | 2202.9 | 6503.9
8:30 | 309 | 4580.2 | 2234.35 | 6814.55
9:00 | 282 | 4859.4 | 2265.8 | 7125.2
9:30 | 264 | 4929.05 | 2308.8 | 7237.85
10:00 | 246 | 4998.7 | 2351.8 | 7350.5
10:30 | 210 | 5106.8 | 2361.1 | 7467.9
11:00 | 174 | 5214.9 | 2370.4 | 7585.3
11:30 | 178 | 5251.15 | 2460.55 | 7711.7
12:00 | 182 | 5287.4 | 2550.7 | 7838.1
12:30 | 197 | 5460.15 | 2599.05 | 8059.2
13:00 | 212 | 5632.9 | 2647.4 | 8280.3
13:30 | 132.5 | 5795.6 | 2656.95 | 8452.55
14:00 | 53 | 5958.3 | 2666.5 | 8624.8
14:30 | 29 | 5966.05 | 2668.35 | 8634.4
15:00 | 5 | 5973.8 | 2670.2 | 8644
15:30 | 86.5 | 5755.2 | 2601 | 8356.2
16:00 | 168 | 5536.6 | 2531.8 | 8068.4
16:30 | 305 | 5214.4 | 2457.4 | 7671.8
17:00 | 442 | 4892.2 | 2383 | 7275.2
17:30 | 507 | 4747.25 | 2270.5 | 7017.75
18:00 | 572 | 4602.3 | 2158 | 6760.3
18:30 | 651 | 4649.65 | 2282 | 6931.65
19:00 | 730 | 4697 | 2406 | 7103
19:30 | 652 | 3983 | 2310 | 6293
20:00 | 409 | 3323 | 2008 | 5331 |  |  |  | Executive Engineer
20:30 | 419.5 | 3209 | 1952 | 5161 |  |  |  | Network Operation Division
21:00 | 430 | 3095 | 1896 | 4991
21:30 | 415 | 3260 | 1907 | 5167
22:00 | 400 | 3425 | 1918 | 5343 |  |  |  |  | Page 6 of 7
22:30 | 453.5 | 3492.5 | 1998.5 | 5491
23:00 | 507 | 3560 | 2079 | 5639
23:30 | 526.5 | 3587 | 2140 | 5727
24:00 | 546 | 3614 | 2201 | 5815
7103 MW (19:00 )
7838.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-05-07 |  | Energy | 170966548
[10 empty] | 2020-05-07 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2852 | 737 | 1523 | 210 | 410 | 75 | 17 | 0 | 76
0:30 | 3242.5 | 577 | 1712 | 579 | 545 | 74 | 34 | 0 | 38 | Date: | 2020-05-07
1:00 | 3633 | 417 | 1901 | 948 | 680 | 73 | 51 | 0 | 0
1:30 | 3646 | 334.5 | 1912 | 941.5 | 680 | 72.5 | 51 | 0 | 0 | [7 empty] | Total Energy | 170.9665 | Total Energy Gen 170.967 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.967 MKWHr
2:00 | 3659 | 252 | 1923 | 935 | 680 | 72 | 51 | 0 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3791.5 | 252 | 1948.5 | 926.5 | 679.5 | 71.5 | 51 | 0 | 0 | [7 empty] | Energy Requirement | 170.9665
3:00 | 3924 | 252 | 1974 | 918 | 679 | 71 | 51 | 0 | 0
3:30 | 3868 | 252 | 1974 | 844 | 678.5 | 71 | 34 | 0 | 0 | [6 empty] | Shortage
4:00 | 3812 | 252 | 1974 | 770 | 678 | 71 | 17 | 0 | 0
4:30 | 3667 | 252 | 1747 | 583.5 | 639 | 71.5 | 8.5 | 0 | 0
5:00 | 3522 | 252 | 1520 | 397 | 600 | 72 | 0 | 0 | 0
5:30 | 3445.5 | 252 | 1437.5 | 301.5 | 573.5 | 72 | 0 | 0 | 0
6:00 | 3369 | 252 | 1355 | 206 | 547 | 72 | 0 | 0 | 0
6:30 | 3500.5 | 252 | 1372.5 | 206 | 556 | 73 | 0 | 0 | 0 |  |  |  |  | Coal
7:00 | 3632 | 252 | 1390 | 206 | 565 | 74 | 0 | 0 | 0
7:30 | 3730 | 252.5 | 1458 | 205.5 | 556.5 | 74.5 | 0 | 0 | 26 |  |  |  | Oil |  |  |  | ,
8:00 | 3828 | 253 | 1526 | 205 | 548 | 75 | 0 | 0 | 52
8:30 | 3900 | 252.5 | 1660 | 284 | 549 | 76 | 0 | 0 | 71
9:00 | 3972 | 252 | 1794 | 363 | 550 | 77 | 0 | 0 | 90
9:30 | 3936 | 324 | 1815 | 410.5 | 552 | 77 | 0 | 0 | 94
10:00 | 3900 | 396 | 1836 | 458 | 554 | 77 | 0 | 0 | 98
10:30 | 3870 | 396 | 1866.5 | 545.5 | 579 | 77 | 0 | 0 | 101
11:00 | 3840 | 396 | 1897 | 633 | 604 | 77 | 0 | 0 | 104
11:30 | 3822 | 396.5 | 1913 | 737.5 | 629 | 77 | 0 | 0 | 104
12:00 | 3804 | 397 | 1929 | 842 | 654 | 77 | 0 | 0 | 104
12:30 | 3819.5 | 397 | 1964.5 | 984 | 678.5 | 76.5 | 0 | 0 | 108
13:00 | 3835 | 397 | 2000 | 1126 | 703 | 76 | 0 | 0 | 112
13:30 | 3835 | 397 | 2000 | 1126 | 703 | 76 | 0 | 0 | 112
14:00 | 3835 | 397 | 2000 | 1126 | 703 | 76 | 0 | 0 | 112
14:30 | 3892.5 | 397.5 | 1953 | 1292.5 | 703 | 73 | 7 | 0 | 117
15:00 | 3950 | 398 | 1906 | 1459 | 703 | 70 | 14 | 0 | 122
15:30 | 3801 | 398 | 1857.5 | 1385 | 699.5 | 70 | 15.5 | 0 | 112
16:00 | 3652 | 398 | 1809 | 1311 | 696 | 70 | 17 | 0 | 102
16:30 | 3518.5 | 397.5 | 1645.5 | 1216 | 698 | 70.5 | 17 | 0 | 100
17:00 | 3385 | 397 | 1482 | 1121 | 700 | 71 | 17 | 0 | 98
17:30 | 3275.5 | 396 | 1451 | 1041 | 661.5 | 71.5 | 17 | 0 | 102
18:00 | 3166 | 395 | 1420 | 961 | 623 | 72 | 17 | 0 | 106
18:30 | 3086.5 | 590 | 1456 | 963.5 | 581.5 | 72.5 | 67.5 | 0 | 114
19:00 | 3007 | 785 | 1492 | 966 | 540 | 73 | 118 | 0 | 122
19:30 | 2788 | 785 | 1426 | 537 | 491 | 74 | 70 | 0 | 122
20:00 | 2470 | 685 | 1067 | 470 | 410 | 75 | 34 | 0 | 120
20:30 | 2433.5 | 684.5 | 1065.5 | 387.5 | 411.5 | 74.5 | 34 | 0 | 70
21:00 | 2397 | 684 | 1064 | 305 | 413 | 74 | 34 | 0 | 20
21:30 | 2520 | 682 | 1139.5 | 272.5 | 412 | 74.5 | 34.5 | 0 | 32
22:00 | 2643 | 680 | 1215 | 240 | 411 | 75 | 35 | 0 | 44
22:30 | 2666 | 733 | 1286 | 225 | 411 | 75 | 43 | 0 | 52
23:00 | 2689 | 786 | 1357 | 210 | 411 | 75 | 51 | 0 | 60
23:30 | 2770.5 | 761.5 | 1440 | 210 | 410.5 | 75 | 34 | 0 | 68 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 2852 | 737 | 1523 | 210 | 410 | 75 | 17 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 170.967 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 170.967 MKWHr
Note on W13: Author:

## Generation
g | 2020-05-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 36 | 35 | 34 | 34 | 35 | 35 | 37 | 37 | 38 | 38 | 38 | 38 | 37 | 36 | 35 | 35 | 35 | 36 |  | 36 | 37 | 37 | 36 | 37 | 37 | 37 | 785160
2 | Karnaphuli Hydro PP Unit-4 & 5 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 39 | 39 | 39 | 39 | 39 | 36 | 35 | 35 | 36 | 36 |  | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 888000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5.5 | 10.9 | 15.6 | 18.5 | 19.6 | 19.5 | 19.5 | 17.4 | 13.9 | 8.8 | 3.3 | 0.3 | [8 empty] | 154035
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 224 | 225 | 222 | 220 | 224 | 225 | 226 | 224 | 225 | 226 | 225 | 217 | 219 | 218 | 217 | 217 | 217 |  | 217 | 218 | 217 | 203 | 204 | 218 | 217 | 5149600
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 149 | 148 | 146 | 147 |  | 40 | 140 | 139 | 139 | 104 | 104 |  | 80 | 80 | 70 | 110 | 139 | 146 | 139 | 2644382
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | [10 empty] | 14 | 17 | 17 | 17 |  | 102 | 70 | 34 | 34 | 35 | 51 | 17 | 543102
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 100 | 100 | 145 | 145 | 120 | 100 | 130 | 129 | 180 | 150 | 150 | 150 | 189 | 189 | 158 | 158 | 71 | 74 |  | 70 | 70 | 32 | 32 | 87 | 87 | 85 | 3092000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 14 | 19 | 64 | 95 | 95 | 45 | 45 | 52 |  | 76 | [6 empty] | 594654
19 | Ashuganj 195MW PP (APSCL-United) | 130 | 130 | 130 | 130 | 83 | 45 | 45 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1421818
20 | Ghorasal TPP (Unit-1&2) | [13 empty] | 5 | 20 | [11 empty] | 18000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 241 | 243 | 150 | 150 | 200 | 200 | 237 | 237 | 237 | 235 | 236 | 235 | 235 | 130 | 100 | 100 |  | 100 | 100 | 100 |  |  |  |  | 3807000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 100 | 100 |  | 100 | 80 | 50 | 0 |  |  |  | 2263894
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 110 | 100 |  | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 2582595
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 10 | 10 | 10 | 27 | 39 | 39 | 42 | 39 | 42 | 42 | 42 | 42 | 41 | 42 |  | 42 | 41 | 10 | 10 | 10 | 10 | 10 | 721008
33 | Ashuganj 225 MW CCPP | 180 | 193 | 201 | 180 | 182 | 152 | 191 | 208 | 202 | 199 | 187 | 200 | 194 | 199 | 196 | 198 | 181 | 184 |  | 181 | 140 | 130 | 196 | 180 | 200 | 180 | 4521000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 320 | 345 | 310 | 310 | 310 | 270 | 320 | 310 | 320 | 310 | 345 | 325 | 335 | 310 | 275 | 275 | 275 |  | 275 | 255 | 240 | 295 | 260 | 305 | 310 | 7624000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 30 | 52 | 51 | 50 | 49 | 49 | 47 | 48 | 49 | 49 |  | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 721440
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 335 | 328 | 360 | 346 | 340 | 343 | 368 | 358 | 361 | 351 | 339 | 356 | 347 | 341 | 351 | 326 | 325 | 324 |  | 305 | 285 | 281 | 314 | 350 | 353 | 358 | 8309520
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 420 | 380 | 350 | 350 | 350 | 350 | 350 | 380 | 380 | 420 | 420 | 420 | 420 | 320 | 300 |  | 300 | 300 | 280 | 320 | 350 | 320 | 360 | 8524000
41 | Haripur 360MW CCPP(HPL) | [17 empty] | 32 |  | 32 | 58 | 58 | 60 | 143 | 283 | 296 | 802000
42 | RPCL 210MW CCPP | 159 | 158 | 157 | 160 | 159 | 159 | 159 | 157 | 155 | 155 | 154 | 152 | 151 | 151 | 185 | 157 | 151 | 152 |  | 110 | 111 | 110 | 74 | 74 | 74 | 106 | 3294040
43
44 | Fenchugonj CCPP Phase-1 | 86 | 87 | 87 | 86 | 85 | 85 | 87 | 87 | 88 | 86 | 87 | 86 | 86 | 87 | 84 | 87 | 87 | 87 |  | 84 | 87 | 87 | 87 | 84 | 86 | 86 | 2046000
45 | Fenchugonj CCPP Phase-2 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 29 | 28 | 29 | 29 | 26 | 27 | 27 |  | 27 | 27 | 26 | 26 | 27 | 27 | 27 | 652560
46 | Shajibazar 330 MW CCPP | 240 | 252 | 257 | 236 | 238 | 249 | 244 | 256 | 246 | 247 | 250 | 252 | 237 | 246 | 238 | 236 | 235 | 205 |  | 204 | 201 | 183 | 148 | 195 | 203 | 193 | 5201000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 63 | 50 | 50 | 63 | 61 | 60 | 60 | 61 | 58 | 59 | 58 | 59 | 59 | 60 | 40 |  | 40 | 40 | 40 | 40 | 62 | 63 | 64 | 1325760
48 | Shahjibazar 86MW PP (Shahjibazar) | 20 | 20 | 80 | 77 | 30 | 10 | 10 | 10 | 77 | 77 | 77 | 77 | 80 | 80 | 80 | 80 | 20 | 20 |  | 80 | 80 | 10 | 10 | 10 | 10 | 10 | 1107840
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 150 | 149 | 150 | 150 | 150 | 100 | 100 | 150 | 151 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 100 |  | 70 | 70 | 50 | 80 | 100 | 50 | 101 | 3004060
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | [5 empty] | 356000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | [5 empty] | 196920
54 | Hobiganj 11MW PP Cofidence-E | [5 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | [5 empty] | 209000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 11 | 50 | 51 | 50 | 48 | 50 | 53 | 50 | 50 | 53 | 25 |  | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 834600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | [5 empty] | 431190
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 300 | 295 | 280 | 290 | 320 | 320 | 310 | 315 | 300 | 310 | 315 | 290 | 305 | 280 | 270 | 270 |  | 250 | 240 | 220 | 240 | 280 | 300 | 310 | 7253500
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | [17 empty] | 17 | [6 empty] | 63269
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 |  | 21 | 470832
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | [6 empty] | 313524
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 |  | 20 | [6 empty] | 328068
63 | Impoprt (Tripura) | [7 empty] | 52 | 90 | 98 | 104 | 104 | 112 | 122 | 122 | 102 | 98 | 106 |  | 122 | 122 | 120 | 20 | 44 | 60 | 76 | 1544640
64 | Malancha, Ctg. EPZ (United) | 40 | 42 | 42 | 42 | 42 | 42 | 17 | 7 | 2 | 2 | 2 | 2 | 8 | 2 | 4 | 19 | 38 | 40 |  | 40 | 40 | 40 | 32 | 42 | 12 | 25 | 650880
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 |  |  |  | 430452
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 |  |  |  | 195120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 8 |  |  |  | 704100
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 8 | 8 | 11 | 11 | 18 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 |  |  | 5 | 11 | 339290
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 |  |  |  | 25 | 25 | 25 | 550000
70 | Summit Madhabdi | 24 | 24 | 24 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 12 | 12 | 0 |  | 10 | 20 | 20 | 454680
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 20 | 20 | 20 | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 8 | 8 | 16 | 24 | 24 | 24 | 653000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 29 | 29 | 29 | 12 | 20 | 20 |  | 18 | 18 | 0 |  | 16 | 25 | 25 | 596200
73 | Ghorashal 108MW PP (Regent) | 110 | 110 | 110 | 110 | 52 | 13 | 13 | 32 | 104 | 104 | 104 | 104 | 109 | 110 | 110 | 54 | 14 | 14 |  | 14 | 14 | 0 |  |  |  |  | 1432272
| Feni Lanka Power | 54 | 54 | 54 | 36 | [16 empty] | 57 | 90 |  |  |  |  | 323760
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 84 | 26 | 26 |  |  |  |  | 27 | 45 | 45 | 45 | 36 | 36 | 36 |  | 113 | 113 | 113 | 65 |  |  |  | 1259160
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [19 empty] | 16 | [6 empty] | 10560
80 | Jamalpur 95 MW PP(Powerpac) | 16 | [25 empty] | 18240
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 1.7 | 3.1 | 4.3 | 5.1 | 5.4 | 5.5 | 4.3 | 3 | 2.4 | 1.6 | 0.8 | [9 empty] | 38040
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 48 | 48 | 48 | 45 | 15 | 15 | 15 | 15 | 15 | 28 | 64 | 80 | 95 | 96 | 96 | 97 | 97 | 75 |  | 75 | 48 | 15 |  |  |  |  | 1165800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 150 | 145 | 145 | 145 | 150 | 145 | 143 | 130 | 135 | 125 | 140 |  | 130 | 120 | 120 | 140 | 140 | 140 | 125 | 3350807
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 2 | 32 | 41 | 41 | 24 | 7 | 7 |  | 7 | [6 empty] | 173760
88 | Ghorashal 78.5 MW PP(MAX) | 71 | 71 | 71 | 72 | 40 | 40 | 40 | 40 | 68 | 67 | 67 | 66 | 65 | 65 | 64 | 64 | 65 | 40 |  | 40 | 40 | [5 empty] | 1133664
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 20 |  | 40 | 50 | 5 | 5 | 5 | 5 | 5 | 838296
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 10 | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 |  | 25 | 15 | 5 | 5 | 5 | 5 | 5 | 793488
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV)
97 | Katpotti 52 MW PP (Sinha) | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 13 | 40 | 40 | 55 | 40 | 40 |  | 40 | [6 empty] | 294277
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 |  | 17 | [6 empty] | 227318
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 163 | 163 | 130 | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 100 |  | 100 | 100 | 100 | 100 | 130 | 110 | 110 | 3389154
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.5 | 1 | 1.5 | 1.1 | 1.9 | 2.4 | 2.1 | 1.9 | 1.5 | 0.2 | 0.1 | [9 empty] | 13650
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | [6 empty] | 17 | 17 | 17 | 17 | 53 | 53 | 17 | 17 | 17 |  | 53 | 17 | [5 empty] | 369720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 173 | 173 | 173 | 50 | 7 | 7 | 10 | 70 | 79 | 100 | 110 | 134 | 134 | 134 | 143 | 144 | 144 |  | 45 | 8 | [5 empty] | 2150400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 4 | 17 | 28 | 57 | 82 | 99 | 139 | 100 | 89 |  | 60 | [6 empty] | 696960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 70 | 70 | 70 | 70 |  |  |  |  | 30 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 50 | [5 empty] | 1298880
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 11 | 35 | 60 | 83 | 100 | 120 | 100 | 100 | 50 |  | 10 | 2 | [5 empty] | 754400
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 30 | 30 | 30 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 22 | 45 | 45 | 8 | [8 empty] | 398400
| Anwara 300 MW PP (United) | 124 | 124 | 124 | 85 | [5 empty] | 16 | 16 | 49 | 100 | 158 | 207 | 180 | 104 | 70 |  | 107 | 6 | [5 empty] | 1530545
| Juldah unit-2 | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 22 | 95 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 70 |  | 2072640
120 | Eastern Zone Total | 5200 | 5209 | 5428 | 5277 | 4293 | 3878.4 | 4036.7 | 4301 | 4859.4 | 4998.7 | 5214.9 | 5287.4 | 5632.9 | 5958.3 | 5973.8 | 5536.6 | 4892.2 | 4602.3 |  | 4697 | 3983 | 3323 | 3095 | 3425 | 3560 | 3614 | 114507924
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | 49 | 49 | [8 empty] | 49 | 54 | 49 | 83 | 66 | 32 | 16 |  | 16 | [6 empty] | 561600
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [20 empty] | 16 | 32 |  |  |  |  | 43200
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 98 | 96 | 98 | 98 | 56 | 53 | 53 | 52 | 93 | 95 | 95 | 92 | 94 | 91 | 96 | 97 | 98 | 97 |  | 97 | 96 | 88 | 34 |  |  |  | 1804480
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 50 | 50 | 40 | 40 | 1390000
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 20 | 18 | 15 | 13 | 12 | 13 | 14 | 14 | 16 | 17 | 19 | 20 | 21 | 20 | 17 | 20 |  | 26 | 29 | 29 | 29 | 1 | 1 | 7 | 393682
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [26 empty] | 0
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 417 | 252 | 252 | 252 | 252 | 252 | 252 | 253 | 252 | 396 | 396 | 397 | 397 | 397 | 398 | 398 | 397 | 395 |  | 785 | 785 | 685 | 684 | 680 | 786 | 737 | 10291636
147 | Bheramara 410 MW CCPP | 335 | 340 | 375 | 330 | 290 | 260 | 340 | 400 | 370 | 350 | 330 | 370 | 340 | 360 | 335 | 335 | 335 | 240 |  | 215 | 205 | 200 | 215 | 215 | 215 | 285 | 7681536
148 | Payra 1320 MW | 530 | 530 | 529 | 528 | 450 | 397 | 415 | 399 | 400 | 404 | 454 | 503 | 553 | 555 | 553 | 546 | 550 | 473 |  | 400 | 351 | 270 | 273 | 261 | 261 | 260 | 10935300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 |  | 140 | 140 | 140 | 140 | 150 | 150 | 150 | 3647300
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 40 | 35 | 30 | 30 | 60 |  | 60 | 60 | 30 |  |  |  |  | 950000
156 | Baghabari 100 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 45 | 40 | 40 | 30 | [9 empty] | 822000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 152 | 148 | 191 | 195 | 165 | 130 | 162 | 164 | 204 | 168 | 155 | 163 | 193 | 197 | 202 | 151 | 166 | 142 |  | 140 | 140 | 130 | 130 | 164 | 158 | 170 | 4152245
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 164 | 163 | 193 | 206 | 189 | 176 | 182 | 191 | 212 | 204 | 201 | 193 | 206 | 202 | 199 | 185 | 179 | 140 |  | 140 | 140 | 130 | 130 | 166 | 175 | 175 | 4592864
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 398 | 426 | 394 | 330 | 325 | 315 | 346 | 402 | 375 | 373 | 373 | 402 | 410 | 404 | 404 | 408 | 313 | 341 |  | 305 | 266 | 214 | 211 | 231 | 293 | 377 | 8392909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 17 | 17 | 17 | 17 | 5 | 5 | 5 | 5 | 17 | 17 | 17 | 16 | 16 | 15 | 15 | 15 |  | 16 |  | 14 | 14 | 0 | 0 |  |  |  | 252480
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 8 |  | 8 | 8 | [5 empty] | 144432
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 110646
165 | Amnura 50 MW PP(Sinha) | [11 empty] | 18 | 24 | 24 | 24 | 12 | 12 |  |  | 0 | 0 | [5 empty] | 124190
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 20 | 35 | 35 | [11 empty] | 120000
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [26 empty] | 0
177 | Sympa Solar Power 8MW | [5 empty] | 0.2 | 0.2 | 1.9 | 5.8 | 6.8 | 7.4 | 3.7 | 5.4 | 6.5 | 4.2 | 2.8 | [10 empty] | 48124
178
178