## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-05-30 | Saturday
|  | Date (day): | 2020-05-30 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11839.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14976 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-05-29 | 2020-05-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | #02-Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 220 | 150 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 68 | 50 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 104 | 108 | 108 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 329 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 361 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 50 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 135 | 125 | 150 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 140 | 180 | 100 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 88 | 50 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 219 | 218 | 200 | 230 |  | 105
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 50 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 43 | 48 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 20 | 30 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 95 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 6047 | 5811 | 2117 | 2729 | 3494 | 4549 | 213 | 1066
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 60 | 60 | 170 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 145 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 20 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 36 | 42 | 35 | 40
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.2 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 200 | 230 | 230
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
| Juldah unit-2 |  | HFO | IPP | 0 | 0 | 0 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 477.2 | 652 | 1257 | 1441 | 430 | 98
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 135 | 110 | 110 | 35 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 194 | 184 | 225 | 225 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 310 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 270 | 200 | 360 |  |  | FGMO
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 41 | 42 | 42
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 51 | 55 | 55
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 55 | 63 | 63 | 132 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 50 | 51
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 100 | 150
64 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 82 | 90 | 90 |  | 73
66 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
67 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
68 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 126 | 154 | 173
69 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20
72 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1259 | 1396 | 1914 | 2494 | 430 | 73
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 199 | 205 | 202 | 202 | 0
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 50 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 90 | 170 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 12 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 235 | 432 | 560.6 | 634 | 0 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 72 | 73 | 88 | 88
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 91 | 245 | 240 | 245 |  | 85 | ST Under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 66 | 66 |  | 0
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 77 | 80 | 80
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 119 | 120 | 120 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 20
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1994 | 1949 | 709 | 937 | 1286 | 1323 | 0 | 545
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 45
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 604 | 846 | 807 | 955
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 99 | 99 |  | 16 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 37
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 0 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 335 | 340 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 6 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 67 | 100 | 105
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 959 | 1423 | 1486 | 2191 | 0 | 16
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 50 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 28 | 30 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 91 | 96 | 95 | 95
| Payra 1320 MW |  | Coal | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maintenance
| Barisal Area Total |  |  |  |  | 472 | 462 | 129 | 234 | 175 | 268 | 0 | 194
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 70 | 70 | 70 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 65 | 60 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 34
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 70
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 40 | 50 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 46 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 187 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 214 | 202 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 150 | 392 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 34
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 19 | 20 | 20
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 8 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 40 | 40 |  | 12 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 50 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 50 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 109 | 50 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 729 | 1098 | 1459 | 1773 | 331 | 20
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 104 | 50 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.9 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 157.9 | 254 | 208 | 303 | 170 | 0
| Total |  |  |  |  | 19630 | 19107 | 6772.1 | 9155 | 11839.6 | 14976 | 1574 | 2012
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6405.9406 | 8660 | 11199.4469 | 14166.2654
A. |  | 2020-05-29 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 9155 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5800 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9155 | MW
3 | Day peak Generation : |  |  | 6772.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8660 | MW
4 | Evening peak Generation : |  |  | 9155 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 172.3033 | MKWHr | By Solar | 0.15952 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.0238 | MKWHr |  | By Oil: | 18.6192 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.662 | MKWHr |  | By Hydro: | 0.744 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1574 | MW | Dhaka | 2593 | 2593 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2012 | MW | Chittagong | 919 | 919 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3586 | MW | Khulna | 1155 | 1155 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1168.43 | MMCFD |  |  | Rajshahi | 1064 | 1064 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 160969123.318 | ii) Oil : | Taka | 126678331.43 | Comilla | 855 | 855 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19848040 | Total | Taka | 307495494.748 | Mymensingh | 778 | 778 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.4905 | MKWHr. | Sylhet | 384 | 384 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -332 | MW (E to W) at | 21:00 | hrs | Barisal | 251 | 251 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -332 | MW at | 21:00 | hrs | Rangpur | 661 | 661 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 8660 | 8660 |  | 0
B. |  | 2020-05-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14976 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 5176 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 184.4427 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6027.2 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.6036 | MKWHr. | ii) HVDC Flow at Peak Time |  | 846 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4912 | MKWHr. | iii) Maximum HVDC Flow : |  | 847 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.73 |  | (b) Today: | 77.96 |  | (c) Rule Curve: |  | 76.4
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-05-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 160 | 0 | 0 | 109 | 73 | 340 | 324 |  | 0 | 420 | 130 | 0 | 96 | 0 | 218 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 13 | 25 | 15 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 330 | 120 | 220 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 120 | 194 | 0 | 22 | 0 | 72 | 30 | 53 | 50 | 130 | 199 | 50 | 74 | 0 | 119 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 14 | 0 | 0 | 0 | 0 | 120 | 0 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 46 | 50 |  | 504 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 110 | 0 | 0 | 55 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 96 | 0 | 205 | 0 | 225 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 0 | 0 |  | 5334 | 2078 | 7412 | 3841 | 504 | 1720 | 1013 | 150 | 30 | 34 | 120 | 0 | 0 | 76.63
2:00 | 35 | 0 | 170 | 0 | 0 | 109 | 73 | 347 | 324 |  | 0 | 420 | 135 | 0 | 96 | 0 | 219 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 13 | 25 | 15 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 315 | 45 | 221 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 116 | 207 | 0 | 22 | 0 | 72 | 30 | 52 | 50 | 163 | 187 | 50 | 74 | 0 | 119 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 14 | 0 | 0 | 0 | 0 | 120 | 0 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 46 | 50 |  | 456 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 110 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 97 | 0 | 210 | 0 | 226 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 |  | 5313 | 1935 | 7248 | 3762 | 456 | 1754 | 946 | 150 | 30 | 34 | 116 | 0 | 0 | 76.65
3:00 | 35 | 0 | 170 | 0 | 0 | 109 | 74 | 339 | 324 |  | 0 | 420 | 135 | 0 | 96 | 0 | 219 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 13 | 25 | 15 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 320 | 25 | 221 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 112 | 208 | 0 | 22 | 0 | 72 | 30 | 53 | 50 | 163 | 190 | 50 | 74 | 0 | 120 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 14 | 0 | 0 | 0 | 0 | 64 | 0 | 10 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 46 | 50 |  | 456 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 97 | 0 | 209 | 0 | 224 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 |  | 5156 | 1905 | 7061 | 3699 | 456 | 1753 | 827 | 150 | 30 | 34 | 112 | 0 | 0 | 76.67
4:00 | 35 | 0 | 173 | 0 | 0 | 109 | 74 | 330 | 324 |  | 0 | 420 | 130 | 0 | 30 | 0 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 25 | 15 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 315 | 70 | 221 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 108 | 211 | 0 | 22 | 0 | 72 | 30 | 53 | 50 | 163 | 192 | 50 | 74 | 0 | 120 | 19 | 0 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 10 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 46 | 50 |  | 456 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 48 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 97 | 0 | 210 | 0 | 223 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 4947 | 1841 | 6788 | 3723 | 456 | 1753 | 551 | 150 | 30 | 17 | 108 | 0 | 0 | 76.69
5:00 | 35 | 0 | 170 | 0 | 0 | 106 | 74 | 341 | 323 |  | 0 | 420 | 130 | 0 | 15 | 0 | 221 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 25 | 13 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 148 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 315 | 90 | 221 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 20 | 104 | 209 | 0 | 22 | 0 | 72 | 30 | 11 | 10 | 163 | 184 | 50 | 30 | 0 | 120 | 19 | 0 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 26 | 100 |  | 456 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 97 | 0 | 208 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4711 | 1795 | 6506 | 3710 | 456 | 1624 | 415 | 150 | 30 | 17 | 104 | 0 | 0 | 76.71
6:00 | 35 | 0 | 140 | 0 | 0 | 54 | 74 | 335 | 283 |  | 0 | 380 | 135 | 0 | 15 | 0 | 184 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 25 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 270 | 100 | 181 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 94 | 209 | 0 | 22 | 0 | 72 | 30 | 11 | 10 | 130 | 192 | 50 | 10 | 0 | 120 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 70 |  | 457 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 73 | 0 | 194 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4136 | 1716 | 5852 | 3416 | 457 | 1410 | 294 | 150 | 30 | 0 | 94 | 1 | 0 | 76.73
7:00 | 35 | 0 | 140 | 0 | 0 | 54 | 74 | 346 | 283 |  | 0 | 380 | 135 | 0 | 15 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 25 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 285 | 100 | 180 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 88 | 209 | 0 | 22 | 0 | 72 | 30 | 11 | 10 | 130 | 190 | 63 | 10 | 0 | 120 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0 | 70 |  | 459 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 73 | 0 | 183 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 4156 | 1773 | 5929 | 3424 | 459 | 1478 | 294 | 150 | 30 | 0 | 88 | 6 | 0 | 76.75
8:00 | 35 | 0 | 140 | 0 | 0 | 54 | 73 | 347 | 304 |  | 0 | 360 | 135 | 0 | 15 | 0 | 150 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 100 | 0 | 0 | 295 | 100 | 181 | 8 | 50 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 10 | 84 | 207 | 0 | 22 | 0 | 72 | 30 | 11 | 10 | 110 | 185 | 50 | 10 | 0 | 120 | 18 | 0 | 10 | 0 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 53 | 0 | 0 | 0 | 0 | 70 |  | 459 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 73 | 0 | 179 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 |  | 4092 | 1708 | 5800 | 3328 | 459 | 1438 | 296 | 150 | 30 | 0 | 84 | 15 | 0 | 76.77
9:00 | 35 | 0 | 140 | 0 | 0 | 95 | 72 | 353 | 354 |  | 0 | 360 | 140 | 0 | 15 | 0 | 220 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 12 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 100 | 0 | 0 | 290 | 125 | 190 | 8 | 90 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 10 | 82 | 206 | 0 | 22 | 0 | 72 | 30 | 11 | 10 | 130 | 185 | 50 | 10 | 0 | 121 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 13 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 100 |  | 459 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 87 | 0 | 210 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 |  | 4444 | 1761 | 6205 | 3628 | 459 | 1524 | 312 | 150 | 30 | 0 | 82 | 20 | 0 | 76.79
10:00 | 35 | 0 | 140 | 0 | 0 | 106 | 70 | 334 | 352 |  | 0 | 360 | 130 | 0 | 22 | 0 | 190 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 330 | 140 | 198 | 8 | 90 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 84 | 207 | 0 | 20 | 2 | 72 | 30 | 11 | 10 | 110 | 90 | 50 | 10 | 0 | 119 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 34 | 0 | 0 | 0 | 0 | 100 |  | 577 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 80 | 0 | 210 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 |  | 4334 | 1862 | 6196 | 3517 | 577 | 1500 | 321 | 150 | 30 | 0 | 84 | 17 | 0 | 76.81
11:00 | 35 | 0 | 140 | 0 | 0 | 104 | 70 | 336 | 320 |  | 0 | 330 | 135 | 0 | 48 | 0 | 219 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 100 | 0 | 0 | 335 | 220 | 200 | 8 | 90 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 86 | 202 | 0 | 20 | 2 | 72 | 30 | 47 | 40 | 110 | 92 | 50 | 10 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 2 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 93 | 0 | 210 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 |  | 4488 | 1848 | 6336 | 3641 | 604 | 1460 | 355 | 149 | 30 | 0 | 86 | 11 | 0 | 76.83
12:00 | 35 | 0 | 140 | 0 | 0 | 104 | 68 | 352 | 335 |  | 0 | 420 | 135 | 0 | 48 | 0 | 219 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 100 | 0 | 0 | 325 | 280 | 194 | 8 | 91 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 92 | 199 | 0 | 22 | 2 | 72 | 30 | 50 | 50 | 163 | 91 | 61 | 10 | 0 | 119 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 5 | 52 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 65 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 91 | 0 | 214 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 |  | 4797 | 1974 | 6771 | 3889 | 604 | 1599 | 393 | 150 | 30 | 0 | 92 | 14 | 0 | 76.86
13:00 | 35 | 0 | 220 | 0 | 0 | 109 | 68 | 361 | 346 |  | 0 | 420 | 140 | 0 | 60 | 0 | 219 | 0 | 150 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 345 | 305 | 200 | 53 | 90 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 5 | 33 | 15 | 98 | 187 | 0 | 22 | 2 | 72 | 30 | 50 | 50 | 163 | 100 | 61 | 74 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 3 | 105 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 355 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 32 | 0 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 204 | 0 | 95 | 0 | 212 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 |  | 5265 | 1996 | 7261 | 4070 | 604 | 1733 | 564 | 150 | 30 | 0 | 98 | 12 | 0 | 76.89
14:00 | 35 | 0 | 220 | 0 | 0 | 109 | 68 | 347 | 346 |  | 0 | 420 | 142 | 0 | 96 | 0 | 216 | 0 | 120 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 13 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 345 | 305 | 205 | 55 | 91 | 40 | 52 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 106 | 180 | 0 | 22 | 1.2 | 71 | 30 | 50 | 50 | 163 | 103 | 59 | 74 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 1.7 | 107 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 375 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 80 | 0 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 95 | 0 | 186 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 35 | 0 |  | 5395.9 | 2032.8 | 7428.7 | 3975 | 604 | 1785 | 769 | 150 | 30 | 0 | 106 | 9.7 | 0 | 76.92
15:00 | 35 | 0 | 220 | 0 | 0 | 105 | 68 | 357 | 346 |  | 0 | 420 | 130 | 0 | 90 | 0 | 221 | 0 | 175 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 13 | 0 | 0 | 0 | 32 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 38 | 135 | 0 | 0 | 315 | 350 | 185 | 55 | 85 | 40 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 90 | 182 | 0 | 22 | 1.5 | 72 | 30 | 50 | 50 | 163 | 101 | 61 | 74 | 0 | 120 | 18 | 0 | 9 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 13.1 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0.2 | 156 | 0 | 0 | 0 | 0 | 100 |  | 605 | 0 | 330 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 110 | 0 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 138 | 0 | 95 | 0 | 181 | 0 | 234 | 0 | 0 | 0 | 15 | 0 | 0 | 4.8 | 0 | 0 |  | 5504.8 | 2062.8 | 7567.6 | 3973 | 605 | 1858 | 824 | 149 | 32 | 17 | 90 | 19.6 | 0 | 76.97
16:00 | 35 | 0 | 102 | 0 | 0 | 105 | 40 | 335 | 352 |  | 0 | 420 | 125 | 0 | 48 | 0 | 224 | 0 | 120 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 17 | 0 | 0 | 0 | 32 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 38 | 135 | 0 | 0 | 310 | 365 | 184 | 8 | 86 | 40 | 50 | 0 | 51 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 92 | 182 | 0 | 22 | 0.9 | 71 | 30 | 50 | 50 | 163 | 142 | 61 | 74 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 1.8 | 81 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 96 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 65 | 0 | 176 | 0 | 296 | 0 | 0 | 0 | 15 | 0 | 0 | 1.2 | 0 | 0 |  | 5035.7 | 2052.2 | 7087.9 | 3815 | 604 | 1819 | 550 | 150 | 32 | 17 | 92 | 8.9 | 0 | 77.02
17:00 | 35 | 0 | 100 | 0 | 0 | 30 | 40 | 330 | 352 |  | 0 | 380 | 130 | 0 | 48 | 0 | 225 | 0 | 78 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 17 | 0 | 0 | 0 | 31 | 95 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 40 | 100 | 0 | 0 | 265 | 275 | 192 | 8 | 90 | 40 | 10 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 90 | 187 | 0 | 22 | 0.5 | 70 | 30 | 14 | 10 | 130 | 197 | 40 | 10 | 0 | 110 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 3.9 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0.9 | 32 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 47 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 65 | 0 | 179 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 |  | 4368.3 | 2092.1 | 6460.4 | 3569 | 604 | 1563 | 430 | 150 | 31 | 17 | 90 | 6.4 | 0 | 77.07
18:00 | 35 | 0 | 100 | 0 | 0 | 30 | 40 | 334 | 272 |  | 0 | 300 | 133 | 0 | 48 | 0 | 155 | 0 | 78 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 7 | 25 | 17 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 265 | 250 | 190 | 8 | 90 | 40 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 86 | 187 | 0 | 22 | 0.1 | 71 | 30 | 14 | 10 | 130 | 196 | 40 | 10 | 0 | 71 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0.5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 100 |  | 602 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 32 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 160 | 0 | 67 | 0 | 183 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0 |  | 4077.6 | 2031.6 | 6109.2 | 3441 | 602 | 1344 | 422 | 151 | 30 | 32 | 86 | 1.2 | 0 | 77.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 100 | 0 | 0 | 26 | 40 | 337 | 320 |  | 0 | 350 | 144 | 36 | 87 | 0 | 222 | 0 | 77 | 0 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 7 | 25 | 17 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 20 | 42 | 100 | 0 | 0 | 325 | 300 | 206 | 8 | 88 | 40 | 10 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 118 | 200 | 0 | 22 | 0 | 76 | 30 | 23 | 17 | 130 | 237 | 61 | 77 | 0 | 109 | 19 | 0 | 10 | 0 | 24 | 11 | 0 | 36 | 0 | 0 | 9 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 25 | 100 |  | 837 | 0 | 390 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 21 | 80 | 0 | 60 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 75 | 0 | 184 | 0 | 398 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 |  | 5147 | 2578 | 7725 | 3923 | 837 | 1593 | 976 | 150 | 30 | 98 | 118 | 0 | 0 | 77.17
19:30 | 35 | 0 | 150 | 0 | 0 | 70 | 40 | 328 | 358 |  | 0 | 420 | 130 | 50 | 96 | 0 | 229 | 0 | 120 | 0 | 40 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 7 | 25 | 20 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 310 | 270 | 185 | 8 | 85 | 41 | 10 | 0 | 40 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 124 | 201 | 0 | 22 | 0 | 73 | 30 | 53 | 50 | 163 | 238 | 61 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 36 | 100 |  | 847 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 25 | 110 | 0 | 60 | 65 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 94 | 10 | 207 | 0 | 420 | 0 | 0 | 0 | 32 | 100 | 0 | 0 | 70 | 0 |  | 5857 | 2973 | 8830 | 4003 | 847 | 1906 | 1667 | 150 | 30 | 103 | 124 | 0 | 0 | 0
20:00 | 35 | 0 | 150 | 0 | 0 | 104 | 40 | 337 | 358 |  | 0 | 420 | 130 | 50 | 97 | 0 | 219 | 0 | 120 | 0 | 70 | 58 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 22 | 25 | 11 | 25 | 20 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 310 | 270 | 184 | 8 | 88 | 41 | 45 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 120 | 204 | 0 | 22 | 0 | 72 | 30 | 52 | 50 | 130 | 245 | 63 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 92 | 0 | 0 | 88 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 36 | 100 |  | 847 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 55 | 40 | 0 | 23 | 110 | 0 | 60 | 65 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 19 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 95 | 10 | 206 | 0 | 400 | 0 | 0 | 0 | 40 | 91 | 0 | 0 | 70 | 0 |  | 5991 | 2959 | 8950 | 4006 | 847 | 1932 | 1742 | 150 | 30 | 123 | 120 | 0 | 0 | 77.32
21:00 | 35 | 0 | 220 | 0 | 0 | 108 | 50 | 329 | 361 |  | 0 | 420 | 125 | 50 | 97 | 0 | 218 | 0 | 180 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 22 | 25 | 18 | 25 | 20 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 20 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 310 | 270 | 184 | 55 | 82 | 41 | 51 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 205 | 0 | 22 | 0 | 73 | 30 | 53 | 50 | 163 | 245 | 63 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 95 | 0 | 0 | 90 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 8 | 100 |  | 846 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 28 | 110 | 0 | 60 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 19 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 96 | 6 | 202 | 0 | 392 | 0 | 0 | 0 | 67 | 104 | 0 | 0 | 109 | 0 |  | 6146 | 3009 | 9155 | 4133 | 846 | 2034 | 1786 | 150 | 30 | 50 | 126 | 0 | 0 | 77.27
22:00 | 35 | 0 | 220 | 0 | 0 | 109 | 72 | 329 | 303 |  | 0 | 420 | 130 | 40 | 97 | 0 | 218 | 0 | 195 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 15 | 25 | 20 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 40 | 135 | 0 | 0 | 310 | 270 | 190 | 112 | 91 | 41 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 128 | 201 | 0 | 22 | 0 | 72 | 30 | 53 | 50 | 130 | 240 | 62 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 45 | 0 | 0 | 57 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 8 | 100 |  | 846 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 27 | 110 | 0 | 60 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 19 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 98 | 30 | 199 | 0 | 424 | 0 | 0 | 0 | 105 | 35 | 0 | 0 | 109 | 0 |  | 6051 | 3006 | 9057 | 4142 | 846 | 2054 | 1663 | 150 | 30 | 44 | 128 | 0 | 0 | 76.35
23:00 | 35 | 0 | 180 | 0 | 0 | 109 | 72 | 329 | 304 |  | 0 | 420 | 140 | 16 | 97 | 0 | 218 | 0 | 145 | 0 | 92 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 15 | 25 | 20 | 0 | 0 | 0 | 32 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 135 | 0 | 0 | 310 | 270 | 183 | 112 | 81 | 41 | 51 | 0 | 51 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 120 | 207 | 5 | 22 | 0 | 72 | 30 | 53 | 50 | 130 | 234 | 50 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 14 | 0 | 0 | 140 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 8 | 100 |  | 847 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 110 | 0 | 55 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 98 | 15 | 203 | 0 | 349 | 0 | 0 | 0 | 105 | 35 | 0 | 0 | 109 | 0 |  | 5894 | 2896 | 8790 | 4007 | 847 | 1980 | 1654 | 150 | 32 | 0 | 120 | 0 | 0 | 77.42
24:00 | 35 | 0 | 180 | 0 | 0 | 109 | 72 | 329 | 304 |  | 0 | 420 | 130 | 0 | 97 | 0 | 218 | 0 | 150 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 15 | 25 | 20 | 0 | 0 | 0 | 33 | 95 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 135 | 0 | 0 | 310 | 270 | 189 | 112 | 80 | 38 | 49 | 0 | 51 | 0 | 0 | 0 | 21 | 0 | 33 | 20 | 118 | 207 | 8 | 22 | 0 | 72 | 30 | 53 | 50 | 130 | 133 | 50 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 100 |  | 847 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 25 | 110 | 0 | 45 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 189 | 0 | 375 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 |  | 5648 | 2648 | 8296 | 3889 | 847 | 2003 | 1256 | 150 | 33 | 0 | 118 | 0 | 0 | 76.33
KWH | 828000 | 0 | 3882000 | 0 | 0 | 2070000 | 1524096 | 8270850 | 7799000 |  | 0 | 9057250 | 3187549 | 209280 | 1570584 | 0 | 5118129 | 0 | 3323000 | 0 | 613440 | 182592 | 0 | 0 | 0 | 0 | 0 | 201240 | 0 | 110499 | 484632 | 600000 | 259560 | 646900 | 508000 | 0 | 0 | 0 | 744000 | 2300000 | 0 | 0 | 0 | 0 | 3103026 | 0 |  | 0 | 0 | 422366 | 0 | 0 | 0 | 470880 | 1018080 | 2985572 | 0 | 0 | 7733900 | 4921000 | 4781000 | 585454 | 1763110 | 924120 | 527040 | 0 | 1162624 | 0 | 0 | 0 | 423396 | 196920 | 811800 | 461300 | 2491200 | 4684360 | 13440 | 458856 | 13700 | 1710000 | 720960 | 909600 | 912096 | 3507709 | 3893000 | 1277280 | 1212480 | 0 | 2810900 | 436000 | 0 | 241200 | 0 | 561120 | 264000 | 0 | 386400 | 0 | 0 | 508800 | 0 | 1416960 | 69795 | 54720 | 0 | 0 | 0 | 1560000 | 0 | 0 | 25199 | 2898000 | 0 | 0 | 0 | 353640 | 2104320 |  | 14603636 | 0 | 8233344 | 0 | 563520 | 0 | 0 | 0 | 230 | 130944 | 192000 | 0 | 499800 | 143328 | 0 | 737000 | 1415000 | 0 | 0 | 0 | 268690 | 0 | 0 | 0 | 0 | 440880 | 196560 | 148284 | 0 | 0 | 3662000 | 0 | 0 | 0 | 0 | 4524873 | 0 | 2111551 | 94080 | 5002045 | 0 | 6574236 | 0 | 0 | 0 | 443088 | 441600 | 0 | 50828 | 547872 | 0 |  | 121277924 | 51025389 | 172303313 | 91674117 | 14603636 | 40349656 | 18065642 | 3662000 | 744000 | 553540 | 2491200 | 159522 | 0
Fuel Cost | 1357920 | 0 | 5667720 | 0 | 0 | 2732400 | 2590963.2 | 8353558.5 | 8032970 |  | 0 | 9872402.5 | 3538179.39 | 1588435.2 | 10821323.76 | 0 | 5322854.16 | 0 | 5748790 | 0 | 4619203.2 | 1665239.04 | 0 | 0 | 0 | 0 | 0 | 1469052 | 0 | 1089520.14 | 363474 | 450000 | 0 | 0 | 0 | 0 | 0 | 0 | 200880 | 4163000 | 0 | 0 | 0 | 0 | 5275144.2 | 0 |  | 0 | 0 | 4096950.2 | 0 | 0 | 0 | 593308.8 | 3023697.6 | 4418646.56 | 0 | 0 | 5723086 | 4921000 | 4398520 | 755235.66 | 2027576.5 | 1044255.6 | 737856 | 0 | 1988087.04 | 0 | 0 | 0 | 537712.92 | 147690 | 1420650 | 345975 | 18684000 | 4965421.6 | 122035.2 | 582747.12 | 218378 | 2804400 | 1153536 | 1619088 | 1422869.76 | 3998788.26 | 4048720 | 2516241.6 | 2315836.8 | 0 | 4862857 | 954840 | 0 | 492048 | 0 | 420840 | 200640 | 0 | 2921184 | 0 | 0 | 2645760 | 0 | 13942886.4 | 815903.55 | 445968 | 0 | 0 | 0 | 14227200 | 0 | 0 | 0 | 21908880 | 0 | 0 | 0 | 3030694.8 | 14014771.2 |  | 84116943.36 | 0 | 8645011.2 | 0 | 4429267.2 | 0 | 0 | 0 | 2412.7 | 1372293.12 | 2000640 | 0 | 774690 | 1398881.28 | 0 | 1510850 | 2900750 | 0 | 0 | 0 | 2068913 | 0 | 0 | 0 | 0 | 846489.6 | 304668 | 112250.988 | 0 | 0 | 19848040 | 0 | 0 | 0 | 0 | 5972832.36 | 0 | 3167326.5 | 1600300.8 | 5852392.65 | 0 | 6508493.64 | 0 | 0 | 0 | 4182750.72 | 3426816 | 0 | 561649.4 | 4048774.08 | 0 |  | 246439812.46 | 165653436.598 | 412093249.058 | 109785212.758 | 84116943.36 | 51183910.56 | 121206675.41 | 19848040 | 200880 | 5471656.02 | 18684000 | 1595930.95 | 0
Yesterday Day Peak | 35 | 0 | 140 | 0 | 0 | 104 | 68 | 352 | 335 |  | 0 | 420 | 135 | 0 | 48 | 0 | 219 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 10 | 20 | 14 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 100 | 0 | 0 | 325 | 280 | 194 | 8 | 91 | 41 | 5 | 0 | 51 | 0 | 0 | 0 | 16 | 8 | 33 | 15 | 92 | 199 | 0 | 22 | 2 | 72 | 30 | 50 | 50 | 163 | 91 | 61 | 10 | 0 | 119 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 5.2 | 52 | 0 | 0 | 0 | 0 | 100 |  | 604 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 0 | 65 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 91 | 0 | 214 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9 | 0 | 0 |  | 6772.1 | DayPeak
Yesterday Evening Peak | 35 | 0 | 220 | 0 | 0 | 108 | 50 | 329 | 361 | 0 | 0 | 420 | 125 | 50 | 97 | 0 | 218 | 0 | 180 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 22 | 25 | 18 | 25 | 20 | 0 | 0 | 0 | 30 | 95 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 20 | 42 | 135 | 0 | 0 | 310 | 270 | 184 | 55 | 82 | 41 | 51 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 126 | 205 | 0 | 22 | 0 | 73 | 30 | 53 | 50 | 163 | 245 | 63 | 77 | 0 | 120 | 18 | 0 | 10 | 0 | 24 | 11 | 0 | 95 | 0 | 0 | 90 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 8 | 100 |  | 846 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 28 | 110 | 0 | 60 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 19 | 8 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 96 | 6 | 202 | 0 | 392 | 0 | 0 | 0 | 67 | 104 | 0 | 0 | 109 | 0 |  | 9155 | EvPeak
Forecast for Evening | 35 | 0 | 220 | 0 | 0 | 108 | 78 | 412 | 360 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 230 | 0 | 200 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 30 | 30 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 40 | 110 | 0 | 0 | 360 | 360 | 225 | 63 | 90 | 42 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 173 | 202 | 95 | 22 | 0 | 88 | 30 | 51 | 44 | 163 | 245 | 66 | 80 | 0 | 150 | 20 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 230 | 54 | 110 | 114 | 113 | 100 |  | 955 | 45 | 410 | 0 | 99 | 225 | 0 | 0 | 37 | 70 | 40 | 0 | 33 | 110 | 30 | 0 | 70 | 34 | 70 | 100 | 50 | 42 | 46 | 40 | 34 | 20 | 10 | 11 | 0 | 0 | 150 | 20 | 20 | 0 | 0 | 200 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 0
Forecast for Day | 35 | 0 | 150 | 0 | 0 | 108 | 78 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 200 | 0 | 100 | 0 | 50 | 50 | 100 | 50 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 23 | 33 | 30 | 52 | 0 | 30 | 30 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 50 | 50 | 50 | 22 | 35 | 110 | 0 | 0 | 360 | 200 | 225 | 63 | 90 | 42 | 55 | 0 | 50 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 202 | 50 | 22 | 1.6 | 88 | 30 | 51 | 44 | 163 | 240 | 66 | 80 | 0 | 120 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 100 | 50 | 170 | 50 | 149 | 20 | 100 | 100 | 100 | 0 | 115 | 100 | 100 | 5 | 230 | 10 | 50 | 114 | 113 | 100 |  | 807 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 50 | 0 | 0 | 70 | 0 | 0 | 50 | 50 | 42 | 46 | 40 | 0 | 20 | 10 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 95 | 50 | 210 | 0 | 410 | 50 | 0 | 50 | 100 | 50 | 0 | 8 | 50 | 0
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 0 | 13 | 45 | 334 | 283 | 0 | 0 | 370 | 140 | 0 | 15 | 0 | 190 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 16 | 20 | 0 | 0 | 30 | 31 | 95 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 80 | 0 | 0 | 290 | 275 | 199 | 63 | 90 | 30 | 10 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 8 | 12 | 96 | 209 | 0 | 22 | 0.1 | 72 | 30 | 5 | 5 | 130 | 239 | 40 | 5 | 0 | 121 | 18 | 0 | 10 | 0 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1.4 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 557 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 97 | 0 | 164 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0
199
| Minimum Generation |  | 5800 | 8:00
| Highest Generation |  | 9155 | 21:00
| Day Peak Generation |  | 6772.1 | 12:00
| Evening Peak Generation |  | 9155 | 21:00
| HVDC Max Flow |  | 847 | 19:30
| HVDC EvPeak Flow |  | 846 | 21:00
| Load factor L.F |  | 78.42%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-05-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-05-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6772.1 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6027.2 | MW
Evening Peak Generation : |  | 9155 | MW Hour : | 21:00 | Available Max Generation : |  | 14976 | MW
E.P. Demand (at gen end) : |  | 9155 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 9155 | MW Hour : | 21:00 | Reserve(Generation end) |  | 5176 | MW
Total Gen. (MKWH) : |  | 172.3033 | System Load Factor : | 78.42% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -332 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-05-30
Actual : | 77.96 | Ft.(MSL) , | Rule curve : | 76.4 | Ft.( MSL )
Gas Consumed : | Total = | 1168.43 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160969123.318
: |  | Coal : | 19848040 | Oil : | 126678331.43 | Total : | 307495494.748
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3458.9604 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1172.6928 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1050.0622 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 948.5955 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 857.3557 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 691.8468 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 391.4087 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 178.2527 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 533.5647 |  |  | 0 | 0%
Total | 0 |  | 9282.7395 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,5 & 7.
4) Ashuganj unit-5
5) Bhola-225 MW
6) Kaptai-1,2,4
7) Raozan # 2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Faridpur 132/33 T1 & T2 transformer tripped at 09:25 due to 33 kV Rajbari feeder fault and were switched |  |  |  |  | About 90 MW power interruption occurred under Faridpur S/S areas
on at 09:36. |  |  |  |  | from 09:25 to 09:36.
b) Barishal(N)-Bhola 230 kV Ckt-2 tripped at 09:30 from both end showing dist Z1 block, gen trip
and was switched on at 11:08.
c) Baghabari 100 MW was synchronized at 11:08.
d) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 11:19 to 12:42 due to kite removing.
e) Sirajganj-230 kV bus-2 was shut down from 11:32 to 14:02 due to red hot maintenance at Sirajganj #04
bus isolator.
f) Ramganj-Chowmuhoni 132 kV Ckt-2 tripped at 15:56 showing dist Z1 and was switched on at 00:45.
g) Barishal-Madaripur 132 kV Ckt-2 tripped at 16:44 from Madaripur end showing dist trip at end Madaripur
and was switched on at 16:51.
h) Hathazari-Baraulia 132 kV Ckt-2 was under shut down from 21:02 to 22:23 due to red hot maintenance at
R-phase line insulator top head of Baroaulia.
i) Kodda-Rajendrapur 132 kV Ckt-1 tripped at 06:35 from Kodda end showing distance relay
and was switched on at 06:59.
j) Tangail-RPCL 132 kV Ckt-2 tripped at 03:45 from both end showing distance Z1 at Tangail end &
distance R-phase at RPCL end and was switched on at 10:50(30-05-2020).
j) Narshingdi-B.Baria 132 kV Ckt-2 tripped at 07:15 from Narshingdi end showing distance relay
and was switched on at 07:36(30-05-2020).
k) Kabirpur 132/33 kV T-3 transformer is under shut down from 07:22 to 10:22 for isolator maintenance work. |  |  |  |  | About 28 MW power interruption occurred under Kabirpur S/S areas
from 07:22 to 10:22(30-05-2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-05-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 828000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 3882000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 50 | 1524096 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 108 | 2070000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8270850 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 361 | 7799000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9057250 | Frequency Control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 209280 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 125 | 3187549 | FGMO & GT-1 S/D D/T Low demmand
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1570584
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 484632
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3323000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 88 | 613440 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 218 | 5118129 | Engine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 182592 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 201240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 110499 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 859560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 646900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 508000 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 386400 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1416960
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5811 | 2729 | 52249961
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2300000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 69795
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 744000 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3103026 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 20 | 422366 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 54720 | Reserve
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 470880
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1018080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25199
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 200 | 2898000 | Transformer O/L
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 |  | IPP | 0 | 0 | 100 | 2104320
| Chattogram area Total |  |  |  | 2166 | 652 | 13210386
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2985572
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4781000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7733900 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 4921000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 924120
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 527040
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 585454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1162624
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 82 | 1763110
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 423396
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 196920
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2491200 | Low demand
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 811800
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 461300
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 353640 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1396 | 30122076
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4684360
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 458856
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 13440 | Reserve
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13700
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 90 | 508800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1560000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 432 | 7239156
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 73 | 1710000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720960
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3507709
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 245 | 3893000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 909600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 912096
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1277280 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1212480
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 120 | 2810900 | Frequency Control
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 436000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 561120
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Gas shortage.
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 241200
| Sylhet Area Total |  |  |  | 1949 | 937 | 18456345
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 846 | 14603636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 563520 | Engine problem
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 230 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 130944 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 335 | 8233344 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 192000
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 6 | 94080 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 67 | 443088 | Low demand
| Khulna Area Total |  |  |  | 2314 | 1423 | 24260842
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 143328
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 499800
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2111551
| Payra 1320 MW |  | NWPGCL | 0 | 0 | 0 | 0 | Under maint.
| Barisal Area Total |  |  |  | 462 | 234 | 2754679
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1415000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 60 | 737000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 268690 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4524873 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 202 | 5002045 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 6574236 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 440880
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 8 | 196560
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 148284
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 547872
| Rajshahi Area Total |  |  |  | 2183 | 1098 | 19855440
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3662000 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 104 | 441600
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50828
| Rangpur Area Total |  |  |  | 605 | 254 | 4154428
| Total |  |  |  | 19107 | 9155 | 172303313
| Eastern Grid Total |  |  |  | 13543 | 6146 | 121277924
| Western Grid Total |  |  |  | 5564 | 3009 | 51025389
| National Grid Total |  |  |  | 19107 | 9155 | 172303313
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-05-29
(a) ENTIRE EASTERN GRID : |  | 5529 | MW | (b) ENTIRE WESTERN GRID : |  | 3131 | MW
i) Dhaka area |  | 2593 | MW | i) Khulna area |  | 1155 | MW
ii) Chittagong area |  | 919 | MW | ii) Rajshahi area |  | 1064 | MW
iii) Comilla area |  | 855 | MW | iii) Barisal area |  | 251 | MW
iv) Mymensingh area |  | 778 | MW | iv) Rangpur area |  | 661 | MW
v) Sylhet area |  | 384 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8660 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 72 | 20:00 | Sherpur | 90 | 23:00 | Benapol | 22 | 21:00
Munsiganj | 106 | 21:00 | Srimongal | 35 | 19:30 | Jhenida | 100 | 19:30
Sonargaon | 41 | 4:00 | Shahjibazar | 91 | 21:00 | Bottail | 90 | 19:30
Shyampur | 100 | 0:00 | Fenchuganj | 34 | 18:30 | G.K Project | 52 | 22:00
Bhulta | 82 | 21:00 | Kulawara | 41 | 19:30 | Faridpur | 150 | 19:30
Madanganj | 30 | 1:00 | Sylhet | 92 | 19:00 | Madaripur | 76 | 21:00
Shitalakhya | 58 | 1:00 | Chatak | 26 | 21:00 | Sariatpur | 46 | 15:00
Rahim steel | 0 | 1:00 | Sunamganj | 37 | 19:30 | Gopalganj | 81 | 19:30
Matuail | 58 | 23:00 | Biani Bazar | 44 | 19:00 | Bagerhat | 76 | 21:00
Ghorasal | 51 | 22:00 | Comilla (S) | 128 | 22:00 | Mongla | 28 | 1:00
Narsingdi | 112 | 22:00 | Comilla(N) | 79 | 19:30 | Satkhira | 76 | 23:00
Haripur (SBU) | 47 | 14:00 | Chandpur | 72 | 21:00 | Gallamari | 37 | 21:00
Ullon | 54 | 19:00 | Feni | 96 | 19:30 | Magura | 50 | 19:30
Hasnabad | 137 | 19:00 | Chowmuhani | 112 | 22:00 | Norail | 35 | 22:00
Magbazar | 65 | 15:00 | Ashuganj | 56 | 23:00 | Chuadanga | 96 | 20:00
Maniknagar | 56 | 19:00 | Daudkandi | 112 | 19:30 | Barisal(N) | 33 | 21:00
Bangabhaban | 13 | 18:00 | B.Baria | 136 | 22:00 | Barisal (S) | 76 | 21:00
Narinda | 60 | 12:00 | Ramganj | 68 | 19:30 | Patuakhali | 93 | 22:00
Dhanmondi | 66 | 14:00 | Chaddagram | 32 | 19:00 | Bhandaria | 38 | 22:00
Lalbag | 42 | 15:00 | PHP | 9 | 20:00 | Borhan Uddin | 32 | 22:00
Madartek | 54 | 20:00 | Madunaghat | 50 | 20:00 | Ishurdi | 59 | 21:00
Dhaka University |  |  | Hathazari | 73 | 19:30 | Ruppur Paromanobik | 2 | 16:00
Mirpur | 77 | 13:00 | Khulshi | 155 | 15:00 | Natore | 119 | 22:00
Kalyanpur | 69 | 21:00 | Halishahar | 106 | 20:00 | Bogra | 140 | 20:00
Gulshan | 68 | 13:00 | Baraulia | 87 | 9:00 | Noagaon | 108 | 22:00
Uttara | 55 | 21:00 | Sikalbaha | 16 | 19:30 | Rajshahi | 125 | 21:00
Uttara New | 14 | 21:00 | Dohazari | 84 | 20:00 | Rajshahi New | 10 | 21:00
Kamrangirchar | 51 | 19:00 | Cox'sbazar | 79 | 20:00 | C.Nawabganj | 62 | 21:00
Savar | 85 | 16:00 | Chandraghona | 26 | 21:00 | Amnura | 38 | 22:00
Bhasantec | 104 | 15:00 | Kaptai | 4 | 19:00 | Pabna | 99 | 20:00
Agargaon | 39 | 21:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 85 | 20:00
Satmosjid | 70 | 13:00 | Bakulia | 78 | 19:30 | Serajganj | 77 | 20:00
Tongi | 80 | 15:00 | Julda | 14 | 1:00 | Niyamatpur | 48 | 20:00
Kabirpur | 132 | 21:00 | TK chemical | 14.1 | 21:00 | Joypurhat | 40 | 20:00
Basundhara | 87 | 22:00 | Modern Steel | 0.2 | 1:00 | Sherpur(Bogura) | 42 | 20:00
Manikganj | 66 | 20:00 | Shahmirpur | 22 | 1:00 | Mohastangor | 34 | 22:00
Joydevpur | 111 | 15:00 | Khagrachhari | 20 | 19:00 | Rangpur | 130 | 20:00
New Tongi | 57 | 21:00 | Matarbari | 28.5 | 19:30 | Lalmonirhat | 46 | 19:30
Kodda | 120 | 21:00 | Baroiar Hat | 32 | 19:00 | Saidpur | 88 | 20:00
Dhamrai | 54 | 22:00 | Rangamati | 10 | 19:00 | Purbasadipur | 96 | 19:30
Rajendrapur | 64 | 23:00 | Abul Khair 230 | 144 | 3:00 | Thakurgaon | 70 | 19:30
Valuka | 56 | 21:00 | BSRM | 105 | 7:00 | Palashbari | 112 | 19:30
Tangail | 170 | 19:30 | GPH Ispat | 65 | 19:30 | Barapukuria | 41 | 22:00
Mymensing | 172 | 21:00 | Goalpara | 25 | 19:30 | Panchagar | 46 | 20:00
Kishorganj | 103 | 21:00 | Central s/s | 66 | 19:30 | Joldhaka | 23 | 20:00
Netrokona | 97 | 20:00 | Noapara | 42 | 20:00 | Kurigram | 50 | 19:30
Jamalpur | 114 | 20:00 | Jessore | 102 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-05-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 400 | 7:00 | 393 | 12:00 | Kaliakoir | 390 | 0.77083 | 381 | 0.5
| Bheramara | 410 | 6:00 | 394 | 20:00 | Bhulta | 397 | 0.77083 | 392 | 0.5
| Ashuganj(N) | 401 | 23:00 | 397 | 17:00 | Gopalganj | 414 | 0.66667 | 375 | 0.5
| Payra | 418 | 5:00 | 380 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 240 | 1:00 | Comilla (N) | 239 | 18:30 | 233 | 13:00
| Ishurdi | 239 | 5:00 | 224 | 21:00 | Hathazari | 227 | 19:30 | 218 | 11:00
| Ashuganj | 240 | 6:00 | 234 | 10:00 | Megnaghat | 238 | 19:00 | 234 | 10:00
| Serajganj | 235 | 5:00 | 226 | 21:00 | Fenchuganj | 242 | 2:00 | 237 | 22:00
| Baghabari | 241 | 4:00 | 234 | 22:00 | Siddhirganj | 238 | 5:00 | 235 | 12:00
| Barapukuria | 236 | 4:00 | 227 | 21:00 | Maniknagar | 237 | 18:30 | 233 | 12:00
| Bogra | 235 | 6:00 | 222 | 21:00 | Agargaon | 236 | 18:30 | 230 | 13:00
| Rajshahi | 237 | 5:00 | 219 | 21:00 | Barisal | 247 | 5:00 | 223 | 11:00
| Khulna South | 237 | 5:00 | 213 | 21:00 | AKSML | 224 | 20:00 | 216 | 6:00
| Rampura | 233 | 18:30 | 231 | 12:00 | BSRM | 228 | 20:00 | 217 | 7:00
| Haripur | 235 | 5:00 | 232 | 10:00 | Bibiyana | 239 | 1:00 | 234 | 20:00
| Hasnabad | 234 | 7:00 | 230 | 12:00 | Bhulta | 238 | 18:30 | 233 | 12:00
| Shyampur | 233 | 2:00 | 230 | 13:00 | Ashuganj (S) | 238 | 5:00 | 232 | 23:00
| Aminbazar | 235 | 19:30 | 230 | 1:00 | Kaliakoir | 237 | 18:30 | 232 | 12:00
| Tongi | 233 | 1:00 | 226 | 10:00 | GPH | 224 | 18:30 | 215 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 18:30 | 134 | 12:00 | Hathazari | 134 | 19:30 | 129 | 11:00
| Munsiganj | 138 | 20:00 | 133 | 12:00 | Khulshi | 133 | 20:00 | 126 | 9:00
| Sonargaon | 134 | 18:00 | 132 | 1:00 | Halishahar | 133 | 20:00 | 127 | 9:00
| Shyampur | 134 | 18:30 | 131 | 12:00 | Baraulia | 133 | 18:30 | 127 | 7:00
| Bhulta | 130 | 2:00 | 129 | 1:00 | Sikalbaha | 134 | 19:30 | 128 | 6:00
| Madanganj | 135 | 20:00 | 131 | 12:00 | Dohazari | 130 | 19:30 | 124 | 8:00
| Shitalakhya | 140 | 20:00 | 135 | 1:00 | Cox'sbazar | 126 | 7:00 | 118 | 3:00
| Rahim steal | 137 | 18:00 | 134 | 12:00 | Chandraghona | 134 | 20:00 | 129 | 5:00
| Matuail | 137 | 18:30 | 134 | 12:00 | Kaptai | 134 | 19:00 | 128 | 4:00
| Ghorasal | 142 | 1:00 | 142 | 1:00 | A. Khaer Stl. | 131 | 18:30 | 128 | 10:00
| Narsinghdi | 134 | 7:00 | 131 | 1:00 | Bakulia | 132 | 19:30 | 126 | 9:00
| Haripur (SBU) | 137 | 18:00 | 134 | 1:00 | Julda | 132 | 18:00 | 129 | 7:00
| Ullon | 133 | 3:00 | 130 | 11:00 | TK Chemical | 133 | 19:30 | 128 | 6:00
| Hasnabad | 138 | 21:00 | 135 | 1:00 | Modern Steel | 132 | 19:30 | 127 | 6:00
| Magbazar | 134 | 4:00 | 130 | 15:00 | Shahmirpur | 133 | 19:30 | 129 | 4:00
| Maniknagar | 138 | 4:00 | 136 | 1:00 | Khagrachhari | 132 | 18:30 | 128 | 7:00
| Bangabhaban | 138 | 4:00 | 136 | 1:00 | Matarbari | 128 | 15:00 | 120 | 3:00
| Narinda | 138 | 4:00 | 136 | 1:00 | Baroiar Hat | 133 | 18:30 | 127 | 7:00
| Dhanmondi | 133 | 3:00 | 130 | 11:00 | Rangamati | 133 | 18:30 | 128 | 9:00
| Lalbag | 138 | 6:00 | 134 | 12:00 | Goalpara S/S | 135 | 5:00 | 125 | 13:00
| Madartek | 133 | 18:30 | 130 | 12:00 | Khulna Central S/S | 135 | 3:00 | 121 | 19:30
| Dhaka University |  |  |  |  | Noapara | 133 | 5:00 | 123 | 13:00
| Mirpur | 136 | 18:00 | 133 | 13:00 | Jessore | 131 | 5:00 | 119 | 21:00
| Kalyanpur | 137 | 18:30 | 133 | 13:00 | Benapol | 134 | 5:00 | 116 | 19:00
| Gulshan | 132 | 18:30 | 130 | 13:00 | Jhenida | 131 | 5:00 | 113 | 21:00
| Uttara | 136 | 18:30 | 132 | 13:00 | Bottail | 136 | 5:00 | 123 | 21:00
| Uttara New | 136 | 19:30 | 132 | 15:00 | G.K Project | 141 | 6:00 | 132 | 21:00
| Kamrangirchar | 136 | 6:00 | 132 | 12:00 | Faridpur | 137 | 3:00 | 128 | 12:00
| Savar | 135 | 18:30 | 131 | 13:00 | Madaripur | 139 | 3:00 | 125 | 12:00
| Bhasantec | 130 | 18:30 | 127 | 14:00 | Shariyatpur S/S | 139 | 16:00 | 127 | 13:00
| Agargaon | 131 | 6:00 | 128 | 13:00 | Gopalganj | 144 | 5:00 | 130 | 12:00
| Satmosjid | 131 | 18:30 | 127 | 13:00 | Bagerhat | 134 | 5:00 | 122 | 12:00
| Tongi | 138 | 18:00 | 135 | 15:00 | Mongla | 134 | 18:30 | 121 | 13:00
| Kabirpur | 131 | 18:00 | 127 | 21:00 | Satkhira | 134 | 5:00 | 123 | 13:00
| Basundhara | 133 | 3:00 | 130 | 13:00 | Gallamari | 136 | 18:30 | 124 | 19:00
| Manikganj | 140 | 1:00 | 134 | 15:00 | Magura | 130 | 5:00 | 110 | 19:00
| Joydevpur | 144 | 18:30 | 141 | 13:00 | Norail | 130 | 6:00 | 108 | 22:00
| New Tongi | 137 | 19:00 | 134 | 14:00 | Chuadanga | 127 | 5:00 | 100 | 21:00
| Kodda | 135 | 1:00 | 127 | 13:00 | Barisal(N) | 143 | 18:30 | 128 | 11:00
| Dhamrai | 130 | 8:00 | 126 | 21:00 | Barisal (S) | 141 | 3:00 | 127 | 11:00
| Rajendrapur | 133 | 23:00 | 126 | 4:00 | Patuakhali | 138 | 5:00 | 123 | 11:00
| Valuka | 131 | 3:00 | 122 | 22:00 | Bhandaria | 137 | 18:30 | 125 | 11:00
| Tangail | 134 | 5:00 | 126 | 21:00 | Ishurdi | 139 | 5:00 | 131 | 21:00
| Mymensing | 133 | 18:30 | 123 | 21:00 | Ruppur Paromanobik | 138 | 5:00 | 132 | 20:00
| Kishorganj | 134 | 6:00 | 127 | 21:00 | Natore | 137 | 6:00 | 127 | 21:00
| Netrokona | 131 | 4:00 | 120 | 21:00 | Bogra | 138 | 6:00 | 130 | 19:30
| Jamalpur | 137 | 23:00 | 124 | 7:00 | Noagaon | 135 | 6:00 | 124 | 21:00
| Sherpur | 135 | 23:00 | 126 | 17:00 | Rajshahi | 135 | 5:00 | 126 | 21:00
| Srimongal | 139 | 9:00 | 137 | 21:00 | Rajshahi New | 137 | 5:00 | 126 | 21:00
| Shahjibazar | 138 | 6:00 | 135 | 21:00 | C.Nawabganj | 135 | 5:00 | 125 | 21:00
| Fenchuganj | 138 | 1:00 | 135 | 22:00 | Amnura | 136 | 18:30 | 124 | 21:00
| Khulawara | 137 | 1:00 | 134 | 23:00 | Pabna | 137 | 7:00 | 127 | 21:00
| Sylhet | 136 | 1:00 | 134 | 21:00 | Shahjadpur | 142 | 3:00 | 135 | 19:00
| Chatak | 135 | 1:00 | 132 | 23:00 | Serajganj | 136 | 4:00 | 130 | 20:00
| Sunamganj | 135 | 6:00 | 131 | 22:00 | Niyamatpur | 135 | 4:00 | 121 | 21:00
| Biani Bazar | 136 | 3:00 | 131 | 21:00 | Joypurhat | 136 | 5:00 | 124 | 20:00
| Comilla(s) | 126 | 7:00 | 122 | 14:00 | Sherpur(Bogura) | 138 | 6:00 | 129 | 21:00
| Comilla(n) | 138 | 18:30 | 131 | 15:00 | Mohastangor | 137 | 5:00 | 126 | 21:00
| Chandpur | 130 | 7:00 | 127 | 15:00 | Rangpur | 135 | 2:00 | 123 | 20:00
| Feni | 134 | 18:00 | 127 | 13:00 | Lalmonirhat | 130 | 5:00 | 118 | 21:00
| Chowmuhani | 130 | 18:00 | 124 | 13:00 | Saidpur | 133 | 3:00 | 122 | 20:00
| Ashuganj | 141 | 14:00 | 137 | 21:00 | Purbasadipur | 132 | 4:00 | 117 | 20:00
| Daudkandi | 136 | 18:30 | 131 | 13:00 | Thakurgaon | 131 | 5:00 | 117 | 21:00
| B.Baria | 137 | 7:00 | 133 | 22:00 | Palashbari | 133 | 4:00 | 119 | 19:30
| Ramganj | 125 | 19:00 | 118 | 22:00 | Barapukuria | 136 | 4:00 | 127 | 21:00
| Chaddagram | 135 | 18:00 | 130 | 13:00 | Panchagar | 130 | 5:00 | 115 | 20:00
| PHP | 132 | 18:00 | 125 | 0:00 | Joldhaka | 132 | 6:00 | 117 | 21:00
| Madanhat | 135 | 19:30 | 130 | 4:00 | Kurigram | 133 | 3:00 | 121 | 20:00

## L-Curve
Date | 2020-05-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 220 | 5648 | 2648 | 8296 |  |  |  | QF-LDC-12
0:30 | 230 | 5491 | 2363 | 7854 | Date: | 2020-05-29
1:00 | 240 | 5334 | 2078 | 7412
1:30 | 235 | 5323.5 | 2006.5 | 7330
2:00 | 230 | 5313 | 1935 | 7248
2:30 | 215 | 5234.5 | 1920 | 7154.5 | [5 empty] | Gen. at Eve. Peak | 9155 | 9155 MW (21:00 )
3:00 | 200 | 5156 | 1905 | 7061 | [6 empty] | 21:00
3:30 | 182 | 5051.5 | 1873 | 6924.5 | [5 empty] | Gen. at Day Peak | 6772.1 | 6772.1 MW (12:00 )
4:00 | 164 | 4947 | 1841 | 6788 | [6 empty] | 12:00
4:30 | 122 | 4829 | 1818 | 6647 | [5 empty] | Highest Generation | 9155
5:00 | 80 | 4711 | 1795 | 6506 | [6 empty] | 21:00
5:30 | 59.5 | 4423.5 | 1755.5 | 6179
6:00 | 39 | 4136 | 1716 | 5852
6:30 | 46.5 | 4146 | 1744.5 | 5890.5
7:00 | 54 | 4156 | 1773 | 5929
7:30 | 60 | 4124 | 1740.5 | 5864.5
8:00 | 66 | 4092 | 1708 | 5800
8:30 | 64.5 | 4268 | 1734.5 | 6002.5
9:00 | 63 | 4444 | 1761 | 6205
9:30 | 83.5 | 4389 | 1811.5 | 6200.5
10:00 | 104 | 4334 | 1862 | 6196
10:30 | 55 | 4411 | 1855 | 6266
11:00 | 6 | 4488 | 1848 | 6336
11:30 | 35.5 | 4642.5 | 1911 | 6553.5
12:00 | 65 | 4797 | 1974 | 6771
12:30 | 182.5 | 5031 | 1985 | 7016
13:00 | 300 | 5265 | 1996 | 7261
13:30 | 303 | 5330.45 | 2014.4 | 7344.85
14:00 | 306 | 5395.9 | 2032.8 | 7428.7
14:30 | 278 | 5450.35 | 2047.8 | 7498.15
15:00 | 250 | 5504.8 | 2062.8 | 7567.6
15:30 | 184 | 5270.25 | 2057.5 | 7327.75
16:00 | 118 | 5035.7 | 2052.2 | 7087.9
16:30 | 86.5 | 4702 | 2072.15 | 6774.15
17:00 | 55 | 4368.3 | 2092.1 | 6460.4
17:30 | 44.5 | 4222.95 | 2061.85 | 6284.8
18:00 | 34 | 4077.6 | 2031.6 | 6109.2
18:30 | 70.5 | 4612.3 | 2304.8 | 6917.1
19:00 | 107 | 5147 | 2578 | 7725
19:30 | 318 | 5857 | 2973 | 8830
20:00 | 313 | 5991 | 2959 | 8950 |  |  |  | Executive Engineer
20:30 | 322.5 | 6068.5 | 2984 | 9052.5 |  |  |  | Network Operation Division
21:00 | 332 | 6146 | 3009 | 9155
21:30 | 258 | 6098.5 | 3007.5 | 9106
22:00 | 184 | 6051 | 3006 | 9057 |  |  |  |  | Page 6 of 7
22:30 | 204 | 5972.5 | 2951 | 8923.5
23:00 | 224 | 5894 | 2896 | 8790
23:30 | 222 | 5771 | 2772 | 8543
24:00 | 220 | 5648 | 2648 | 8296
9155 MW (21:00 )
6772.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-05-29 |  | Energy | 172303313
[10 empty] | 2020-05-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3889 | 847 | 2003 | 1654 | 150 | 33 | 0 | 0 | 118
0:30 | 3865 | 675.5 | 1861.5 | 1333.5 | 150 | 31.5 | 17 | 0 | 119 | Date: | 2020-05-29
1:00 | 3841 | 504 | 1720 | 1013 | 150 | 30 | 34 | 0 | 120
1:30 | 3801.5 | 480 | 1737 | 979.5 | 150 | 30 | 34 | 0 | 118 | [7 empty] | Total Energy | 172.3033 | Total Energy Gen 172.303 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.303 MKWHr
2:00 | 3762 | 456 | 1754 | 946 | 150 | 30 | 34 | 0 | 116 | [7 empty] | Energy not Served | 0
2:30 | 3730.5 | 456 | 1753.5 | 886.5 | 150 | 30 | 34 | 0 | 114 | [7 empty] | Energy Requirement | 172.3033
3:00 | 3699 | 456 | 1753 | 827 | 150 | 30 | 34 | 0 | 112
3:30 | 3711 | 456 | 1753 | 689 | 150 | 30 | 25.5 | 0 | 110 | [6 empty] | Shortage
4:00 | 3723 | 456 | 1753 | 551 | 150 | 30 | 17 | 0 | 108
4:30 | 3716.5 | 456 | 1688.5 | 483 | 150 | 30 | 17 | 0 | 106
5:00 | 3710 | 456 | 1624 | 415 | 150 | 30 | 17 | 0 | 104
5:30 | 3563 | 456.5 | 1517 | 354.5 | 150 | 30 | 8.5 | 0 | 99
6:00 | 3416 | 457 | 1410 | 294 | 150 | 30 | 0 | 0 | 94
6:30 | 3420 | 458 | 1444 | 294 | 150 | 30 | 0 | 0 | 91 |  |  |  |  | Coal
7:00 | 3424 | 459 | 1478 | 294 | 150 | 30 | 0 | 0 | 88
7:30 | 3376 | 459 | 1458 | 295 | 150 | 30 | 0 | 0 | 86 |  |  |  | Oil |  |  |  | ,
8:00 | 3328 | 459 | 1438 | 296 | 150 | 30 | 0 | 0 | 84
8:30 | 3478 | 459 | 1481 | 304 | 150 | 30 | 0 | 0 | 83
9:00 | 3628 | 459 | 1524 | 312 | 150 | 30 | 0 | 0 | 82
9:30 | 3572.5 | 518 | 1512 | 316.5 | 150 | 30 | 0 | 0 | 83
10:00 | 3517 | 577 | 1500 | 321 | 150 | 30 | 0 | 0 | 84
10:30 | 3579 | 590.5 | 1480 | 338 | 149.5 | 30 | 0 | 0 | 85
11:00 | 3641 | 604 | 1460 | 355 | 149 | 30 | 0 | 0 | 86
11:30 | 3765 | 604 | 1529.5 | 374 | 149.5 | 30 | 0 | 0 | 89
12:00 | 3889 | 604 | 1599 | 393 | 150 | 30 | 0 | 0 | 92
12:30 | 3979.5 | 604 | 1666 | 478.5 | 150 | 30 | 0 | 0 | 95
13:00 | 4070 | 604 | 1733 | 564 | 150 | 30 | 0 | 0 | 98
13:30 | 4070 | 604 | 1733 | 564 | 150 | 30 | 0 | 0 | 98
14:00 | 4070 | 604 | 1733 | 564 | 150 | 30 | 0 | 0 | 98
14:30 | 4021.5 | 604.5 | 1795.5 | 694 | 149.5 | 31 | 8.5 | 0 | 94
15:00 | 3973 | 605 | 1858 | 824 | 149 | 32 | 17 | 0 | 90
15:30 | 3894 | 604.5 | 1838.5 | 687 | 149.5 | 32 | 17 | 0 | 91
16:00 | 3815 | 604 | 1819 | 550 | 150 | 32 | 17 | 0 | 92
16:30 | 3692 | 604 | 1691 | 490 | 150 | 31.5 | 17 | 0 | 91
17:00 | 3569 | 604 | 1563 | 430 | 150 | 31 | 17 | 0 | 90
17:30 | 3505 | 603 | 1453.5 | 426 | 150.5 | 30.5 | 24.5 | 0 | 88
18:00 | 3441 | 602 | 1344 | 422 | 151 | 30 | 32 | 0 | 86
18:30 | 3682 | 719.5 | 1468.5 | 699 | 150.5 | 30 | 65 | 0 | 102
19:00 | 3923 | 837 | 1593 | 976 | 150 | 30 | 98 | 0 | 118
19:30 | 4003 | 847 | 1906 | 1667 | 150 | 30 | 103 | 0 | 124
20:00 | 4006 | 847 | 1932 | 1742 | 150 | 30 | 123 | 0 | 120
20:30 | 4069.5 | 846.5 | 1983 | 1764 | 150 | 30 | 86.5 | 0 | 123
21:00 | 4133 | 846 | 2034 | 1786 | 150 | 30 | 50 | 0 | 126
21:30 | 4137.5 | 846 | 2044 | 1724.5 | 150 | 30 | 47 | 0 | 127
22:00 | 4142 | 846 | 2054 | 1663 | 150 | 30 | 44 | 0 | 128
22:30 | 4074.5 | 846.5 | 2017 | 1658.5 | 150 | 31 | 22 | 0 | 124
23:00 | 4007 | 847 | 1980 | 1654 | 150 | 32 | 0 | 0 | 120
23:30 | 3948 | 847 | 1991.5 | 1654 | 150 | 32.5 | 0 | 0 | 119 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3889 | 847 | 2003 | 1654 | 150 | 33 | 0 | 0 | 118
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 172.303 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 172.303 MKWHr
Note on W13: Author:

## Generation
g | 2020-05-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 32 | 31 | 30 |  | 30 | 30 | 30 | 30 | 30 | 32 | 33 | 744000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 10 | 13 | 6 |  |  |  |  | 13.1 | 5 | 3.9 | 0.5 | [8 empty] | 69795
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 147 | 146 | 147 | 147 | 148 | 100 | 100 | 100 | 100 | 143 | 139 | 139 | 141 | 147 | 145 | 139 | 70 | 70 |  | 145 | 145 | 145 | 145 | 145 | 140 | 147 | 3103026
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 |  | 68 | 68 | 68 | 20 | 34 |  | 0 | 422366
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 180 | 190 | 158 | 150 | 109 | 75 | 75 | 76 | 158 | 95 | 100 | 140 | 150 | 120 | 175 | 120 | 78 | 78 |  | 77 | 120 | 120 | 180 | 195 | 145 | 150 | 3323000
17 | Siddhirganj 335 MW CCPP | 218 | 219 | 219 | 220 | 221 | 184 | 180 | 150 | 220 | 190 | 219 | 219 | 219 | 216 | 221 | 224 | 225 | 155 |  | 222 | 229 | 219 | 218 | 218 | 218 | 218 | 5118129
18 | Kodda 300 MW PP Unit-2 (Summit) | 14 | 14 | 14 | [16 empty] | 36 | 95 | 92 | 95 | 45 | 14 | 0 | 386400
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 53 | 55 | 55 | 8 | 8 | 8 |  | 8 | 8 | 8 | 55 | 112 | 112 | 112 | 585454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 828000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 160 | 170 | 170 | 173 | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 220 | 220 | 220 | 102 | 100 | 100 |  | 100 | 150 | 150 | 220 | 220 | 180 | 180 | 3882000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 100 | 100 |  | 100 | 135 | 135 | 135 | 135 | 135 | 135 | 2985572
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 | 40 |  | 40 | 41 | 41 | 41 | 41 | 41 | 38 | 924120
33 | Ashuganj 225 MW CCPP | 220 | 221 | 221 | 221 | 221 | 181 | 180 | 181 | 190 | 198 | 200 | 194 | 200 | 205 | 185 | 184 | 192 | 190 |  | 206 | 185 | 184 | 184 | 190 | 183 | 189 | 4781000
34 | Ashuganj 450 MW CCPP(South) | 120 | 45 | 25 | 70 | 90 | 100 | 100 | 100 | 125 | 140 | 220 | 280 | 305 | 305 | 350 | 365 | 275 | 250 |  | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 4921000
| Ashuganj 450 MW CCPP(North) | 330 | 315 | 320 | 315 | 315 | 270 | 285 | 295 | 290 | 330 | 335 | 325 | 345 | 345 | 315 | 310 | 265 | 265 |  | 325 | 310 | 310 | 310 | 310 | 310 | 310 | 7733900
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 52 | 50 | 50 | 10 | 10 |  | 10 | 10 | 45 | 51 | 51 | 51 | 49 | 527040
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 90 | 90 | 91 | 90 | 91 | 85 | 86 | 90 | 90 |  | 88 | 85 | 88 | 82 | 91 | 81 | 80 | 1763110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 347 | 339 | 330 | 341 | 335 | 346 | 347 | 353 | 334 | 336 | 352 | 361 | 347 | 357 | 335 | 330 | 334 |  | 337 | 328 | 337 | 329 | 329 | 329 | 329 | 8270850
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 380 | 380 | 360 | 360 | 360 | 330 | 420 | 420 | 420 | 420 | 420 | 380 | 300 |  | 350 | 420 | 420 | 420 | 420 | 420 | 420 | 9057250
41 | Haripur 360MW CCPP(HPL) | 324 | 324 | 324 | 324 | 323 | 283 | 283 | 304 | 354 | 352 | 320 | 335 | 346 | 346 | 346 | 352 | 352 | 272 |  | 320 | 358 | 358 | 361 | 303 | 304 | 304 | 7799000
42 | RPCL 210MW CCPP | 194 | 207 | 208 | 211 | 209 | 209 | 209 | 207 | 206 | 207 | 202 | 199 | 187 | 180 | 182 | 182 | 187 | 187 |  | 200 | 201 | 204 | 205 | 201 | 207 | 207 | 4684360
43
44 | Fenchugonj CCPP Phase-1 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 71 | 70 | 71 |  | 76 | 73 | 72 | 73 | 72 | 72 | 72 | 1710000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720960
46 | Shajibazar 330 MW CCPP | 199 | 187 | 190 | 192 | 184 | 192 | 190 | 185 | 185 | 90 | 92 | 91 | 100 | 103 | 101 | 142 | 197 | 196 |  | 237 | 238 | 245 | 245 | 240 | 234 | 133 | 3893000
47 | Shahjibazar GTPP Unit- 8 & 9 | 50 | 50 | 50 | 50 | 50 | 50 | 63 | 50 | 50 | 50 | 50 | 61 | 61 | 59 | 61 | 61 | 40 | 40 |  | 61 | 61 | 63 | 63 | 62 | 50 | 50 | 1277280
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 74 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 74 | 74 | 74 | 74 | 10 | 10 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1212480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 150 MW CCPP | 119 | 119 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 119 | 120 | 119 | 120 | 120 | 120 | 120 | 110 | 71 |  | 109 | 120 | 120 | 120 | 120 | 120 | 120 | 2810900
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 436000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241200
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 52 | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 47 | 50 | 50 | 50 | 50 | 50 | 14 | 14 |  | 23 | 53 | 52 | 53 | 53 | 53 | 53 | 909600
56 | Shahjahanulla 25 MW PP | 16 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 561120
57 | Bibiana-II 341 MW CCPP (Summit)
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 110499
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 470880
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484632
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 458856
63 | Impoprt (Tripura) | 120 | 116 | 112 | 108 | 104 | 94 | 88 | 84 | 82 | 84 | 86 | 92 | 98 | 106 | 90 | 92 | 90 | 86 |  | 118 | 124 | 120 | 126 | 128 | 120 | 118 | 2491200
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 37 | 37 | 30 | 36 | 36 | 42 | 42 | 38 | 38 | 40 | 42 |  | 42 | 42 | 42 | 42 | 40 | 40 | 40 | 1018080
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 21 |  | 21 | 19 | 19 | 19 | 21 | 21 | 21 | 423396
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 |  | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 0 | 196920
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 |  | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 461300
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 13 | 13 | 13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 11 | 18 | 15 | 15 | 15 | 259560
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 646900
72 | Rupganj 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 13 | 14 | 14 | 14 | 12 | 14 | 14 | 14 | 14 | 13 | 13 | 17 | 17 | 17 |  | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 508000
73 | Ghorashal 108MW PP (Regent) | 109 | 109 | 109 | 109 | 106 | 54 | 54 | 54 | 95 | 106 | 104 | 104 | 109 | 109 | 105 | 105 | 30 | 30 |  | 26 | 70 | 104 | 108 | 109 | 109 | 109 | 2070000
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 46 | 46 | 46 | 46 | 26 | [14 empty] | 25 | 36 | 36 | 8 | 8 | 8 | 0 | 353640
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [12 empty] | 10 | 45 | 50 | 16 | 8 | 7 |  | 22 | 40 | 70 | 88 | 92 | 92 | 80 | 613440
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [24 empty] | 5 | 8 | 13440
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 2 | 3 | 2 | 5 | 3 | 1.7 | 0.2 | 1.8 | 0.9 | [9 empty] | 25199
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 30 | 15 | 15 | 15 | 15 | 15 | 22 | 48 | 48 | 60 | 96 | 90 | 48 | 48 | 48 |  | 87 | 96 | 97 | 97 | 97 | 97 | 97 | 1570584
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP(Summit) | 130 | 135 | 135 | 130 | 130 | 135 | 135 | 135 | 140 | 130 | 135 | 135 | 140 | 142 | 130 | 125 | 130 | 133 |  | 144 | 130 | 130 | 125 | 130 | 140 | 130 | 3187549
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 36 | 50 | 50 | 50 | 40 | 16 | 0 | 209280
88 | Ghorashal 78.5 MW PP(MAX) | 73 | 73 | 74 | 74 | 74 | 74 | 74 | 73 | 72 | 70 | 70 | 68 | 68 | 68 | 68 | 40 | 40 | 40 |  | 40 | 40 | 40 | 50 | 72 | 72 | 72 | 1524096
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 50 | 50 | 50 | 50 | 50 | 10 | 10 |  | 17 | 50 | 50 | 50 | 50 | 50 | 50 | 912096
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 10 |  | 20 | 40 | 51 | 51 | 51 | 51 | 51 | 1162624
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 16 | 58 | 58 | 24 | 24 | 24 | 7 | 182592
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV)
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 130 | 163 | 163 | 163 | 163 | 130 | 130 | 110 | 130 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 130 | 130 |  | 130 | 163 | 130 | 163 | 130 | 130 | 130 | 3507709
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.2 | 1.5 | 0.9 | 0.5 | 0.1 | [8 empty] | 13700
103 | Kamalaghat 54 MW PP(Banco Energy) | [21 empty] | 53 | 53 | 35 | 35 | 17 | 201240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [19 empty] | 9 | 80 | 88 | 90 | 57 | 140 | 100 | 508800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 120 | 120 | 64 | 15 | 15 | 15 | 15 | 15 | 15 | 27 | 30 | 30 | 34 | 48 | 45 | 34 | 30 | 30 |  | 73 | 149 | 136 | 149 | 139 | 100 | 87 | 1416960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 10 | 10 | 10 | 10 | [21 empty] | 0 | 54720
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [25 empty] | 0
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 65 | 35 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 78 | 100 | 112 | 35 | 35 | 40 |  | 108 | 115 | 115 | 115 | 115 | 115 | 115 | 1560000
| Anwara 300 MW PP (United) | 216 | 216 | 216 | 162 | 105 | 51 | 51 | 53 | 34 | 34 | 34 | 52 | 105 | 107 | 156 | 81 | 32 | 32 |  | 133 | 200 | 200 | 200 | 196 | 198 | 198 | 2898000
| Juldah unit-2 | 50 | 50 | 50 | 50 | 100 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2104320
120 | Eastern Zone Total | 5334 | 5313 | 5156 | 4947 | 4711 | 4136 | 4156 | 4092 | 4444 | 4334 | 4488 | 4797 | 5265 | 5395.9 | 5504.8 | 5035.7 | 4368.3 | 4077.6 |  | 5147 | 5857 | 5991 | 6146 | 6051 | 5894 | 5648 | 121277924
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | [11 empty] | 5 | 16 | 16 |  |  |  |  | 34 | 99 | 99 | 99 | 99 | 99 | 99 | 563520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 230
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 96 | 48 | 16 | [6 empty] | 16 | 32 | 80 | 110 | 96 | 47 | 32 |  | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 143328
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 97 | 97 | 97 | 97 | 73 | 73 | 73 | 87 | 80 | 93 | 91 | 95 | 95 | 95 | 65 | 65 | 67 |  | 75 | 94 | 95 | 96 | 98 | 98 | 98 | 2111551
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 22 | 22 | 21 | 22 | 21 | 18 | 15 | 14 | 16 | 19 | 19 | 22 | 21 | 24 | 24 | 21 | 21 | 17 |  | 21 | 25 | 23 | 28 | 27 | 26 | 25 | 499800
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 10 | 10 | 6 | 30 | 15 | 0 | 94080
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 40 | 40 | 40 | 40 | 40 | 24 | 192000
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 15 |  | 30 | 35 | 55 | 30 | 10 |  | 0 | 130944
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 15 | [13 empty] | 15 | 15 |  |  |  |  | 32 | 40 | 67 | 105 | 105 | 67 | 443088
146 | Bheramara HVDC | 504 | 456 | 456 | 456 | 456 | 457 | 459 | 459 | 459 | 577 | 604 | 604 | 604 | 604 | 605 | 604 | 604 | 602 |  | 837 | 847 | 847 | 846 | 846 | 847 | 847 | 14603636
147 | Bheramara 410 MW CCPP | 380 | 345 | 335 | 335 | 340 | 340 | 345 | 290 | 320 | 290 | 290 | 355 | 355 | 375 | 330 | 335 | 335 | 335 |  | 390 | 335 | 330 | 335 | 330 | 330 | 335 | 8233344
148 | Payra 1320 MW
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 149 | 150 | 150 | 151 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3662000
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 70 | 70 | 70 | 70 | 70 | 65 | 65 | 65 | 40 | 40 | 40 |  | 70 | 65 | 65 | 70 | 70 | 60 | 60 | 1415000
156 | Baghabari 100 MW GTPP | [11 empty] | 65 | 65 | 65 | 65 | 50 | 50 | 50 |  | 60 | 60 | 60 | 60 | 60 | 55 | 45 | 737000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 192 | 197 | 194 | 187 | 194 | 168 | 160 | 158 | 171 | 190 | 197 | 199 | 204 | 150 | 138 | 172 | 162 | 160 |  | 159 | 197 | 190 | 187 | 186 | 186 | 185 | 4524873
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 205 | 210 | 209 | 210 | 208 | 194 | 183 | 179 | 210 | 210 | 210 | 214 | 212 | 186 | 181 | 176 | 179 | 183 |  | 184 | 207 | 206 | 202 | 199 | 203 | 189 | 5002045
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 225 | 226 | 224 | 223 | 225 | 223 | 294 | 280 | 240 | 240 | 180 | 150 | 150 | 150 | 234 | 296 | 407 | 348 |  | 398 | 420 | 400 | 392 | 424 | 349 | 375 | 6574236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 19 | 19 | 19 | 20 | 20 | 440880
163 | Bogura 20 MW PP (Energyprima) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196560
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 148284
165 | Amnura 50 MW PP(Sinha) | 24 | [18 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 268690
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [13 empty] | 35 | [6 empty] | 70 | 70 | 109 | 109 | 109 | 0 | 547872
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 34 | 35 | 25 | [15 empty] | 16 | 100 | 91 | 104 | 35 | 35 | 0 | 441600
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 5 | 6 | 7 | 7 | 7 | 6.8 | 4.8 | 1.2 | 1.1 | 0.6 | [8 empty] | 50828
178
178