## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-09-01 | Sunday
|  | Date (day): | 2019-09-01 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13567 | MW |  |  | (b) At Evening Peak Hour : |  | 15210 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-31 | 2019-09-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 200 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 380 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 50 | 70 | 75
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 92 | 90 | 90 |  | 18 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 359 | 345 | 360 | 360 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 350 | 350 | 350
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 370 | 370 | 370 |  | 80 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 93 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 285 | 260 | 290 | 290 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 95 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 42 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 70 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 40 | 65 | 100 | 100 | 110 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 70 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 12 | 12 | 12
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 12 | 42 | 46 | 46
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 133 | 133 | 133 |  | 16 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 72 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 46 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 52 | 51 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 82 | 133 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 89 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2648 | 3568 | 3787 | 4592 | 215 | 508
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 32 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 208 | 207 | 210 | 210
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 205 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 130 | 130 | 130
| Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 50 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 30 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 22 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 30 | 75 | 90 | 90 |  | 18 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.4 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 125 | 178 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 0 | 0 | 30 | 31
53 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 17 | 113 | 113
| Chattogram area Total |  |  |  |  | 2172 | 2112 | 1107.2 | 1338 | 1669.4 | 1781 | 140 | 116
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 135 | 135
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 214 | 161 | 225 | 225
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 345 | 360 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 235 | 240 | 240 | 240
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 30 | 30 | 30 |  | 15 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 53 | 55 | 55
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 55 | 55 | 55 | 55 | 140 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 70 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 131 | 132 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 105 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 134 | 192 | 149 | 190
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1516 | 1758 | 1920 | 2211 | 404 | 28
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 169 | 144 | 150 | 150 | 52 |  | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 48 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.9 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 170 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 80 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 326.9 | 546 | 583.6 | 582 | 52 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 59 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 31 | 31 | 30 | 30
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 146 | 240 | 256 | 250 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 46 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 49 | 50 | 50
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 66 | 67 | 67 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 82 | 77 | 77
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 46 | 45 | 46
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 71 | 70 | 100
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 46 | 46 | 46
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 285 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  |  | Under S/D
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1079 | 1247 | 1278 | 1323 | 0 | 0
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 908 | 913 | 924 | 924
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 360 | 380 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 22 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 52 | 101 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1328 | 1809 | 1944 | 2141 | 0 | 0
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 10 | 34 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 173 | 180 | 180
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 53 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 243 | 413 | 370 | 450 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60 | 11 |  | Gas Shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 11 | 40 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 192 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 152 | 189 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 280 | 370 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 7 | 7 | 7 |  | 3 | Engine problem
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 881 | 1324 | 1544 | 1649 | 231 | 111
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 69 | 71 | 70 | 70
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 270 | 280 | 280
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
134 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 76 | 99 | 113 | 113 |  |  | On test
135 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 397.4 | 440 | 471 | 481 | 0 | 105
| Total |  |  |  |  | 19141 | 18618 | 9526.5 | 12443 | 13567 | 15210 | 1042 | 868
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9063.3052 | 11838 | 12907.3492 | 14470.4637
A. |  | 2019-08-31 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 12443 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 9167 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12443 | MW
3 | Day peak Generation : |  |  | 9526.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11838 | MW
4 | Evening peak Generation : |  |  | 12443 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 260.9217 | MKWHr | By Solar | 0.16123 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 158.6106 | MKWHr |  | By Oil: | 62.6749 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 9.0127 | MKWHr |  | By Hydro: | 4.8638 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1042 | MW | Dhaka | 4282 | 4282 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 868 | MW | Chittagong | 1060 | 1060 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 1910 | MW | Khulna | 1490 | 1490 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1368.76 | MMCFD |  |  | Rajshahi | 1269 | 1269 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 152173259.254 | ii) Oil : | Taka | 550553031.33 | Comilla | 1111 | 1111 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 40774993.66 | Total | Taka | 743501284.244 | Mymensingh | 999 | 999 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.2215 | MKWHr. | Sylhet | 534 | 534 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -140 | MW (E to W) at | 20:00 | hrs | Barisal | 359 | 359 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -140 | MW at | 20:00 | hrs | Rangpur | 734 | 734 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.3° C |  |  | Total | 11838 | 11838 |  | 0
B. |  | 2019-09-01 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15210 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
4 | Reserve(Generation end) |  |  |  | 2310 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 270.5046 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9010.93 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8131 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7853 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.37 |  | (b) Today: | 105.4 |  | (c) Rule Curve: |  | 99
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-31
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 0 | 0 | 110 | 380 | 90 | 72 | 350 | 351 |  | 0 | 370 | 285 | 50 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 72 | 133 | 0 | 72 | 0 | 24 | 53 | 35 | 35 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 125 | 90 | 90 | 120 | 25 | 206 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 51 | 50 | 21 | 42 | 0 | 0 | 135 | 345 | 165 | 195 | 55 | 133 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 180 | 151 | 95 | 22 | 0 | 58 | 22 | 50 | 48 | 100 | 145 | 66 | 77 | 46 | 69 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 100 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 200 | 100 | 0 | 115 | 88 | 0 | 0 | 161 | 0 | 17 |  | 897 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 24 | 38 | 40 | 180 | 39 | 110 | 0 | 0 | 55 | 32 | 0 | 93 | 12 | 42 | 38 | 52 | 21 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 189 | 0 | 0 | 0 | 96 | 100 | 209 | 0 | 412 | 35 | 0 | 113 | 104 | 113 | 0 | 0 |  | 7830 | 3889 | 11719 | 4390 | 897 | 2329 | 2958 | 320 | 215 | 430 | 180 | 0 | 0 | 105.37
2:00 | 70 | 0 | 0 | 110 | 380 | 90 | 71 | 348 | 352 |  | 0 | 370 | 280 | 24 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 40 | 120 | 0 | 72 | 0 | 6 | 53 | 17 | 17 | 22 | 25 | 24 | 25 | 33 | 51 | 0 | 122 | 90 | 90 | 120 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 5 | 50 | 21 | 42 | 0 | 0 | 135 | 330 | 235 | 188 | 55 | 132 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 174 | 152 | 95 | 22 | 0 | 58 | 22 | 50 | 48 | 100 | 147 | 66 | 77 | 46 | 75 | 18 | 45 | 9 | 305 | 24 | 11 | 0 | 50 | 0 | 0 | 190 | 0 | 126 | 0 | 100 | 200 | 100 | 0 | 115 | 88 | 0 | 0 | 161 | 0 | 17 |  | 907 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 24 | 35 | 40 | 180 | 38 | 110 | 0 | 0 | 55 | 20 | 0 | 60 | 12 | 42 | 22 | 52 | 21 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 0 | 98 | 70 | 209 | 0 | 416 | 35 | 0 | 113 | 104 | 113 | 0 | 0 |  | 7634 | 3807 | 11441 | 4432 | 907 | 2337 | 2706 | 320 | 212 | 353 | 174 | 0 | 0 | 105.37
3:00 | 70 | 0 | 0 | 110 | 380 | 90 | 71 | 355 | 352 |  | 0 | 370 | 287 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 75 | 0 | 72 | 0 | 12 | 35 | 17 | 17 | 22 | 25 | 17 | 33 | 33 | 51 | 0 | 119 | 90 | 90 | 120 | 25 | 210 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 5 | 41 | 21 | 42 | 0 | 0 | 135 | 350 | 235 | 196 | 55 | 133 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 162 | 152 | 95 | 22 | 0 | 60 | 22 | 50 | 48 | 100 | 147 | 66 | 77 | 46 | 79 | 18 | 45 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 90 | 0 | 100 | 200 | 70 | 0 | 115 | 88 | 0 | 0 | 125 | 0 | 17 |  | 907 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 24 | 35 | 40 | 180 | 38 | 110 | 0 | 0 | 55 | 8 | 0 | 60 | 12 | 42 | 22 | 52 | 21 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 97 | 70 | 209 | 0 | 414 | 35 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7415 | 3799 | 11214 | 4486 | 907 | 2341 | 2493 | 320 | 209 | 296 | 162 | 0 | 0 | 105.37
4:00 | 70 | 0 | 0 | 110 | 380 | 90 | 71 | 351 | 352 |  | 0 | 370 | 288 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 64 | 0 | 72 | 0 | 12 | 35 | 17 | 17 | 22 | 25 | 17 | 25 | 33 | 51 | 0 | 119 | 90 | 90 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 10 | 5 | 37 | 21 | 42 | 0 | 0 | 127 | 335 | 235 | 164 | 55 | 132 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 164 | 153 | 95 | 22 | 0 | 60 | 22 | 50 | 48 | 100 | 147 | 65 | 77 | 46 | 79 | 18 | 45 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 83 | 0 | 100 | 200 | 70 | 0 | 115 | 88 | 0 | 0 | 125 | 0 | 17 |  | 907 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 24 | 35 | 40 | 180 | 30 | 110 | 0 | 0 | 55 | 6 | 0 | 60 | 12 | 42 | 22 | 52 | 21 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 30 | 209 | 0 | 418 | 35 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7326 | 3751 | 11077 | 4410 | 907 | 2341 | 2443 | 320 | 209 | 283 | 164 | 0 | 0 | 105.37
5:00 | 70 | 0 | 0 | 110 | 340 | 90 | 72 | 370 | 322 |  | 0 | 370 | 293 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 16 | 64 | 0 | 72 | 0 | 12 | 35 | 17 | 17 | 22 | 25 | 17 | 25 | 33 | 51 | 0 | 117 | 90 | 90 | 120 | 25 | 216 | 0 | 137 | 0 |  | 0 | 0 | 0 | 10 | 5 | 38 | 21 | 42 | 0 | 0 | 100 | 360 | 230 | 196 | 55 | 133 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 160 | 152 | 95 | 22 | 0 | 60 | 22 | 50 | 48 | 130 | 145 | 65 | 77 | 46 | 79 | 18 | 45 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 84 | 0 | 100 | 200 | 70 | 0 | 115 | 88 | 0 | 0 | 125 | 0 | 17 |  | 907 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 24 | 0 | 40 | 180 | 30 | 110 | 0 | 0 | 55 | 0 | 0 | 60 | 12 | 32 | 22 | 52 | 21 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 0 | 96 | 30 | 207 | 0 | 370 | 35 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7299 | 3659 | 10958 | 4439 | 907 | 2294 | 2440 | 320 | 207 | 191 | 160 | 0 | 0 | 105.37
6:00 | 70 | 0 | 0 | 110 | 340 | 90 | 71 | 351 | 322 |  | 0 | 370 | 258 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 32 | 0 | 72 | 0 | 12 | 35 | 17 | 17 | 22 | 25 | 17 | 25 | 33 | 51 | 0 | 126 | 90 | 90 | 120 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 0 | 21 | 42 | 0 | 0 | 100 | 330 | 240 | 180 | 55 | 125 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 158 | 153 | 95 | 22 | 0 | 58 | 22 | 50 | 48 | 130 | 145 | 67 | 77 | 46 | 68 | 18 | 45 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 61 | 0 | 100 | 160 | 70 | 0 | 115 | 88 | 0 | 0.39 | 125 | 0 | 17 |  | 907 | 0 | 370 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 27 | 32 | 0 | 0 | 55 | 0 | 0 | 60 | 12 | 32 | 0 | 23 | 0 | 22 | 7 | 11 | 70 | 0 | 250 | 0 | 0 | 200 | 0 | 0 | 0 | 97 | 0 | 208 | 0 | 370 | 17 | 0 | 113 | 104 | 114 | 0 | 0 |  | 6977.39 | 3389 | 10366.39 | 4346 | 907 | 2281 | 2046 | 320 | 216 | 92 | 158 | 0.39 | 0 | 105.37
7:00 | 70 | 0 | 0 | 110 | 300 | 90 | 71 | 352 | 322 |  | 0 | 320 | 264 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 13 | 35 | 17 | 0 | 22 | 25 | 17 | 25 | 33 | 52 | 0 | 122 | 90 | 90 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 5 | 0 | 21 | 37 | 0 | 0 | 100 | 315 | 240 | 180 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 146 | 153 | 77 | 22 | 0.2 | 60 | 22 | 49 | 48 | 130 | 145 | 67 | 77 | 46 | 69 | 18 | 44 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 15 | 3 | 50 | 100 | 40 | 0 | 115 | 88 | 0 | 1.3 | 125 | 0 | 17 |  | 908 | 0 | 320 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 40 | 12 | 16 | 0 | 0 | 0 | 22 | 7 | 8 | 70 | 0 | 250 | 0 | 0 | 196 | 0 | 0 | 0 | 96 | 0 | 202 | 0 | 295 | 17 | 0 | 55 | 104 | 72 | 0 | 0.2 |  | 6458.5 | 3010.2 | 9468.7 | 4211 | 908 | 2128 | 1499 | 320 | 212 | 40 | 146 | 4.7 | 0 | 105.37
8:00 | 70 | 0 | 0 | 110 | 300 | 90 | 71 | 344 | 303 |  | 0 | 320 | 260 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 35 | 17 | 0 | 22 | 25 | 17 | 33 | 33 | 52 | 0 | 122 | 90 | 100 | 120 | 25 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 5 | 0 | 21 | 8 | 0 | 0 | 100 | 260 | 240 | 180 | 55 | 131 | 30 | 55 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 148 | 151 | 95 | 22 | 0.3 | 60 | 31 | 50 | 48 | 100 | 146 | 68 | 77 | 46 | 74 | 18 | 21 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 62 | 0 | 15 | 7.4 | 50 | 100 | 12 | 0 | 115 | 88 | 0 | 2.8 | 125 | 0 | 17 |  | 907 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 20 | 16 | 0 | 0 | 55 | 0 | 0 | 40 | 12 | 16 | 0 | 0 | 0 | 22 | 7 | 8 | 69 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 0 | 95 | 0 | 194 | 0 | 280 | 17 | 0 | 55 | 69 | 57 | 0 | 1 |  | 6311.5 | 2887 | 9198.5 | 4119 | 907 | 2001 | 1441 | 319 | 212 | 40 | 148 | 11.5 | 0 | 105.37
9:00 | 70 | 0 | 0 | 110 | 300 | 90 | 71 | 355 | 303 |  | 0 | 320 | 290 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 35 | 17 | 0 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 123 | 90 | 95 | 100 | 25 | 208 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 5 | 1 | 21 | 2 | 0 | 0 | 100 | 280 | 240 | 196 | 55 | 132 | 30 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 33 | 20 | 130 | 149 | 90 | 22 | 0.3 | 58 | 31 | 50 | 48 | 100 | 144 | 67 | 77 | 46 | 73 | 18 | 28 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 25 | 10.7 | 50 | 50 | 12 | 0 | 115 | 88 | 0 | 3.5 | 125 | 0 | 17 |  | 907 | 0 | 280 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 16 | 16 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 16 | 0 | 0 | 0 | 22 | 7 | 8 | 69 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 73 | 0 | 152 | 0 | 280 | 17 | 0 | 55 | 52 | 57 | 0 | 2.5 |  | 6368.5 | 2798.5 | 9167 | 4073 | 907 | 2006 | 1468 | 329 | 213 | 24 | 130 | 17 | 0 | 105.37
10:00 | 70 | 0 | 0 | 110 | 300 | 87 | 71 | 345 | 308 |  | 0 | 320 | 230 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 32 | 32 | 0 | 72 | 0 | 12 | 53 | 35 | 17 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 21 | 21 | 21 | 2 | 0 | 0 | 100 | 260 | 245 | 179 | 55 | 126 | 30 | 56 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 20 | 130 | 152 | 67 | 22 | 0.4 | 60 | 31 | 50 | 48 | 163 | 146 | 69 | 77 | 46 | 70 | 18 | 44 | 9 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 82 | 15.3 | 88 | 80 | 50 | 0 | 115 | 88 | 0 | 4.7 | 125 | 0 | 17 |  | 907 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 168 | 15 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 16 | 0 | 0 | 0 | 22 | 7 | 8 | 70 | 0 | 271 | 0 | 0 | 214 | 0 | 0 | 0 | 73 | 0 | 152 | 0 | 280 | 17 | 0 | 55 | 52 | 35 | 0 | 1.8 |  | 6544.4 | 2744.8 | 9289.2 | 4025 | 907 | 2056 | 1561 | 341 | 215 | 32 | 130 | 22.2 | 0 | 105.37
11:00 | 70 | 0 | 0 | 110 | 300 | 88 | 50 | 355 | 330 |  | 0 | 370 | 295 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 48 | 32 | 0 | 72 | 0 | 12 | 53 | 17 | 17 | 22 | 25 | 24 | 33 | 16 | 52 | 0 | 118 | 90 | 95 | 120 | 25 | 213 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 30 | 32 | 21 | 2 | 0 | 0 | 100 | 325 | 235 | 198 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 20 | 120 | 173 | 50 | 22 | 0.4 | 60 | 31 | 22 | 46 | 130 | 147 | 65 | 50 | 44 | 85 | 18 | 42 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 82 | 12.3 | 100 | 105 | 50 | 0 | 80 | 88 | 0 | 5.3 | 125 | 0 | 17 |  | 907 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 181 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 16 | 0 | 8 | 0 | 22 | 7 | 8 | 69 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 52 | 0 | 152 | 0 | 280 | 30 | 0 | 35 | 52 | 35 | 0 | 2.5 |  | 6697 | 2748.5 | 9445.5 | 4156 | 907 | 2016 | 1657 | 329 | 208 | 32 | 120 | 20.5 | 0 | 105.37
12:00 | 70 | 0 | 0 | 110 | 300 | 87 | 50 | 359 | 346 |  | 0 | 370 | 285 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 48 | 32 | 0 | 72 | 0 | 12 | 53 | 55 | 17 | 22 | 25 | 24 | 33 | 16 | 52 | 0 | 118 | 90 | 90 | 120 | 25 | 209 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 30 | 31 | 21 | 2 | 0 | 0 | 100 | 295 | 235 | 214 | 55 | 131 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 20 | 134 | 169 | 48 | 22 | 0.9 | 60 | 31 | 22 | 46 | 130 | 146 | 65 | 50 | 44 | 80 | 18 | 43 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 82 | 13.8 | 100 | 105 | 50 | 0 | 80 | 88 | 0 | 5.4 | 125 | 0 | 17 |  | 908 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 11 | 8 | 0 | 22 | 7 | 8 | 69 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 0 | 53 | 0 | 152 | 0 | 280 | 22 | 0 | 70 | 52 | 76 | 0 | 2.4 |  | 6677.1 | 2849.4 | 9526.5 | 4122 | 908 | 2032 | 1738 | 319 | 208 | 43 | 134 | 22.5 | 0 | 105.37
13:00 | 70 | 0 | 0 | 110 | 330 | 90 | 72 | 375 | 349 |  | 0 | 370 | 285 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 48 | 32 | 1 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 16 | 52 | 0 | 118 | 90 | 90 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 30 | 32 | 21 | 5 | 0 | 0 | 100 | 270 | 240 | 180 | 55 | 126 | 30 | 49 | 0 | 43 | 0 | 0 | 8 | 16 | 11 | 33 | 20 | 138 | 154 | 48 | 22 | 0.9 | 60 | 31 | 34 | 48 | 130 | 145 | 65 | 76 | 44 | 70 | 18 | 40 | 10 | 320 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 80 | 10.7 | 100 | 105 | 50 | 0 | 80 | 89 | 0 | 4.2 | 115 | 0 | 17 |  | 911 | 0 | 320 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 38 | 8 | 0 | 22 | 7 | 8 | 70 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 0 | 87 | 0 | 185 | 0 | 320 | 17 | 0 | 70 | 62 | 77 | 0 | 3.8 |  | 6804.8 | 3043.8 | 9848.6 | 4234 | 911 | 2189 | 1759 | 320 | 208 | 70 | 138 | 19.6 | 0 | 105.37
14:00 | 70 | 0 | 0 | 110 | 330 | 91 | 40 | 330 | 346 |  | 0 | 370 | 255 | 23 | 0 | 2 | 0 | 0 | 38 | 0 | 19 | 48 | 16 | 10 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 118 | 90 | 90 | 120 | 24 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 30 | 32 | 21 | 2 | 0 | 0 | 100 | 270 | 235 | 180 | 55 | 132 | 30 | 51 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 20 | 144 | 142 | 48 | 22 | 0.2 | 60 | 31 | 47 | 48 | 130 | 212 | 65 | 78 | 44 | 72 | 18 | 42 | 10 | 290 | 16 | 8 | 0 | 9 | 0 | 0 | 7 | 0 | 84 | 13.5 | 100 | 105 | 50 | 0 | 105 | 89 | 0 | 3.7 | 115 | 0 | 17 |  | 911 | 0 | 320 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 170 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 37 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 260 | 0 | 0 | 214 | 0 | 0 | 0 | 94 | 0 | 182 | 0 | 320 | 36 | 0 | 73 | 69 | 77 | 0 | 3.1 |  | 6796.4 | 3121.1 | 9917.5 | 4209 | 911 | 2149 | 1892 | 331 | 208 | 53 | 144 | 20.5 | 0 | 105.37
15:00 | 70 | 0 | 0 | 110 | 330 | 87 | 40 | 364 | 344 |  | 0 | 370 | 288 | 24 | 0 | 15 | 0 | 0 | 93 | 0 | 24 | 48 | 16 | 10 | 72 | 0 | 12 | 53 | 55 | 35 | 0 | 25 | 24 | 33 | 33 | 52 | 0 | 113 | 90 | 90 | 120 | 24 | 215 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 31 | 32 | 21 | 2 | 0 | 0 | 100 | 295 | 235 | 200 | 55 | 132 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 20 | 148 | 141 | 55 | 22 | 0.1 | 60 | 31 | 47 | 49 | 130 | 245 | 63 | 78 | 44 | 81 | 18 | 43 | 10 | 320 | 24 | 8 | 0 | 14 | 0 | 0 | 7 | 0 | 83 | 7.75 | 100 | 118 | 50 | 0 | 111 | 89 | 0 | 4.2 | 115 | 0 | 17 |  | 911 | 0 | 320 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 37 | 8 | 0 | 22 | 7 | 8 | 70 | 0 | 260 | 0 | 0 | 205 | 0 | 0 | 0 | 93 | 0 | 180 | 0 | 404 | 28 | 0 | 73 | 69 | 77 | 0 | 3.4 |  | 7071.05 | 3210.4 | 10281.45 | 4373 | 911 | 2261 | 1987 | 330 | 203 | 53 | 148 | 15.45 | 0 | 105.37
16:00 | 70 | 0 | 0 | 110 | 330 | 92 | 40 | 359 | 343 |  | 0 | 370 | 272 | 24 | 0 | 15 | 0 | 0 | 93 | 0 | 24 | 48 | 16 | 10 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 113 | 90 | 90 | 120 | 24 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 31 | 32 | 21 | 2 | 0 | 0 | 100 | 345 | 235 | 179 | 55 | 125 | 30 | 50 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 20 | 144 | 140 | 95 | 22 | 0.3 | 60 | 31 | 47 | 49 | 163 | 240 | 65 | 78 | 45 | 69 | 18 | 44 | 10 | 305 | 24 | 8 | 0 | 14 | 0 | 0 | 16 | 0 | 84 | 0.8 | 100 | 160 | 50 | 0 | 115 | 89 | 0 | 0.4 | 138 | 0 | 17 |  | 911 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 8 | 40 | 180 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 37 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 260 | 0 | 0 | 192 | 0 | 0 | 0 | 94 | 0 | 176 | 0 | 415 | 22 | 0 | 73 | 69 | 78 | 0 | 1.6 |  | 7191.5 | 3276.6 | 10468.1 | 4407 | 911 | 2294 | 2114 | 331 | 203 | 61 | 144 | 3.1 | 0 | 105.37
17:00 | 70 | 0 | 0 | 110 | 330 | 87 | 70 | 348 | 345 |  | 0 | 370 | 260 | 10 | 0 | 15 | 0 | 0 | 87 | 0 | 7 | 16 | 16 | 10 | 72 | 0 | 19 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 51 | 0 | 113 | 90 | 90 | 120 | 24 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 32 | 32 | 21 | 10 | 0 | 0 | 100 | 345 | 235 | 180 | 55 | 132 | 30 | 51 | 0 | 15 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 136 | 142 | 48 | 22 | 0.3 | 60 | 31 | 47 | 49 | 163 | 241 | 65 | 10 | 44 | 68 | 18 | 47 | 10 | 280 | 24 | 11 | 0 | 14 | 0 | 0 | 16 | 0 | 84 | 0 | 100 | 135 | 20 | 0 | 115 | 89 | 0 | 0.1 | 138 | 0 | 17 |  | 912 | 0 | 360 | 0 | 52 | 0 | 0 | 0 | 0 | 8 | 8 | 180 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 8 | 37 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 260 | 0 | 0 | 188 | 0 | 0 | 0 | 97 | 0 | 160 | 0 | 415 | 17 | 0 | 73 | 69 | 78 | 0 | 0.9 |  | 6906.4 | 3124.9 | 10031.3 | 4364 | 912 | 2213 | 1810 | 331 | 203 | 61 | 136 | 1.3 | 0 | 105.37
18:00 | 70 | 0 | 0 | 110 | 330 | 34 | 50 | 347 | 304 |  | 0 | 370 | 280 | 10 | 0 | 15 | 4 | 0 | 40 | 0 | 7 | 20 | 32 | 10 | 72 | 0 | 19 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 113 | 90 | 90 | 120 | 24 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 37 | 32 | 21 | 12 | 0 | 0 | 100 | 345 | 235 | 185 | 55 | 132 | 30 | 15 | 0 | 15 | 0 | 0 | 30 | 21 | 11 | 33 | 20 | 138 | 145 | 48 | 22 | 0 | 60 | 31 | 11 | 10 | 100 | 239 | 66 | 10 | 10 | 75 | 18 | 12 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 16 | 0 | 84 | 0 | 100 | 109 | 23 | 0 | 115 | 89 | 0 | 0 | 138 | 0 | 17 |  | 912 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 18 | 8 | 180 | 23 | 32 | 0 | 0 | 55 | 0 | 10 | 0 | 12 | 8 | 37 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 270 | 0 | 0 | 170 | 0 | 0 | 0 | 64 | 0 | 166 | 0 | 415 | 18 | 0 | 73 | 69 | 90 | 0 | 0.1 |  | 6587 | 3115.1 | 9702.1 | 4281 | 912 | 1849 | 1881 | 341 | 203 | 97 | 138 | 0.1 | 0 | 105.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 0 | 0 | 110 | 380 | 93 | 50 | 353 | 349 |  | 0 | 370 | 255 | 87 | 30 | 28 | 12 | 0 | 87 | 0 | 63 | 68 | 133 | 63 | 72 | 0 | 18 | 53 | 55 | 35 | 22 | 25 | 21 | 33 | 17 | 51 | 0 | 117 | 90 | 90 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 85 | 40 | 71 | 32 | 22 | 18 | 0 | 0 | 100 | 345 | 240 | 151 | 55 | 128 | 30 | 15 | 0 | 30 | 0 | 50 | 52 | 21 | 11 | 33 | 20 | 188 | 143 | 84 | 22 | 0 | 59 | 31 | 47 | 36 | 163 | 240 | 66 | 81 | 46 | 69 | 18 | 45 | 10 | 290 | 24 | 11 | 0 | 125 | 0 | 0 | 125 | 0 | 110 | 0 | 100 | 168 | 58 | 0 | 115 | 89 | 0 | 0 | 179 | 0 | 17 |  | 912 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 8 | 40 | 40 | 178 | 34 | 110 | 0 | 0 | 55 | 50 | 10 | 92 | 40 | 42 | 38 | 52 | 14 | 22 | 7 | 11 | 70 | 0 | 270 | 0 | 0 | 182 | 0 | 0 | 0 | 96 | 51 | 188 | 0 | 415 | 72 | 0 | 113 | 69 | 99 | 0 | 0 |  | 8086 | 3839 | 11925 | 4431 | 912 | 2272 | 3055 | 340 | 207 | 520 | 188 | 0 | 0 | 105.37
19:30 | 70 | 0 | 0 | 110 | 380 | 92 | 50 | 349 | 348 |  | 0 | 370 | 270 | 90 | 90 | 42 | 12 | 0 | 62 | 0 | 70 | 101 | 133 | 70 | 72 | 0 | 25 | 53 | 55 | 35 | 22 | 25 | 21 | 33 | 17 | 51 | 0 | 117 | 90 | 90 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 85 | 30 | 75 | 32 | 22 | 20 | 0 | 0 | 100 | 345 | 240 | 151 | 55 | 132 | 30 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 186 | 144 | 95 | 22 | 0 | 58 | 31 | 47 | 49 | 163 | 240 | 67 | 81 | 46 | 68 | 18 | 46 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 133 | 0 | 100 | 200 | 70 | 0 | 115 | 89 | 0 | 0 | 178 | 0 | 17 |  | 912 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 25 | 63 | 40 | 171 | 34 | 110 | 0 | 0 | 55 | 50 | 31 | 93 | 50 | 42 | 38 | 52 | 24 | 22 | 7 | 11 | 70 | 0 | 270 | 0 | 0 | 191 | 0 | 0 | 0 | 97 | 100 | 189 | 0 | 370 | 105 | 0 | 113 | 102 | 99 | 0 | 0 |  | 8405 | 4011 | 12416 | 4409 | 912 | 2292 | 3528 | 340 | 207 | 542 | 186 | 0 | 0 | 105.37
20:00 | 70 | 0 | 0 | 110 | 380 | 92 | 50 | 345 | 350 |  | 0 | 370 | 260 | 93 | 95 | 42 | 12 | 0 | 65 | 0 | 70 | 102 | 133 | 70 | 72 | 0 | 42 | 53 | 55 | 35 | 22 | 25 | 21 | 33 | 33 | 51 | 0 | 117 | 90 | 90 | 120 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 85 | 30 | 75 | 32 | 22 | 22 | 0 | 0 | 100 | 345 | 240 | 161 | 55 | 132 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 192 | 144 | 95 | 22 | 0 | 59 | 31 | 46 | 49 | 163 | 240 | 66 | 82 | 46 | 71 | 18 | 46 | 10 | 285 | 24 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 133 | 0 | 100 | 200 | 70 | 0 | 115 | 89 | 0 | 0 | 178 | 0 | 17 |  | 913 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 25 | 50 | 40 | 173 | 34 | 110 | 0 | 0 | 55 | 50 | 10 | 93 | 50 | 42 | 40 | 52 | 28 | 22 | 7 | 11 | 71 | 0 | 270 | 0 | 0 | 192 | 0 | 0 | 0 | 96 | 100 | 189 | 0 | 370 | 105 | 0 | 113 | 101 | 99 | 0 | 0 |  | 8457 | 3986 | 12443 | 4442 | 913 | 2291 | 3543 | 341 | 207 | 514 | 192 | 0 | 0 | 105.37
21:00 | 70 | 0 | 0 | 110 | 380 | 93 | 50 | 345 | 348 |  | 0 | 370 | 285 | 100 | 85 | 42 | 12 | 0 | 0 | 0 | 70 | 102 | 133 | 70 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 119 | 90 | 90 | 120 | 1 | 204 | 0 | 90 | 0 |  | 0 | 0 | 85 | 10 | 12 | 32 | 22 | 35 | 0 | 0 | 100 | 355 | 235 | 179 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 190 | 144 | 95 | 22 | 0 | 60 | 31 | 46 | 49 | 163 | 242 | 65 | 82 | 46 | 80 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 197 | 0 | 0 | 170 | 0 | 135 | 0 | 100 | 200 | 70 | 0 | 115 | 89 | 0 | 0 | 178 | 0 | 17 |  | 912 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 27 | 55 | 40 | 180 | 38 | 110 | 0 | 0 | 55 | 50 | 0 | 93 | 50 | 42 | 37 | 52 | 30 | 22 | 7 | 11 | 71 | 0 | 270 | 0 | 0 | 188 | 0 | 0 | 0 | 97 | 100 | 199 | 0 | 415 | 105 | 0 | 113 | 101 | 99 | 0 | 0 |  | 8345 | 4044 | 12389 | 4392 | 912 | 2369 | 3466 | 341 | 209 | 510 | 190 | 0 | 0 | 105.37
22:00 | 70 | 0 | 0 | 110 | 380 | 94 | 50 | 354 | 348 |  | 0 | 370 | 286 | 97 | 64 | 42 | 12 | 0 | 0 | 0 | 70 | 102 | 133 | 70 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 51 | 0 | 123 | 90 | 90 | 120 | 25 | 211 | 0 | 90 | 0 |  | 0 | 0 | 85 | 10 | 10 | 32 | 22 | 36 | 0 | 0 | 100 | 360 | 235 | 192 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 192 | 144 | 95 | 22 | 0 | 60 | 31 | 47 | 49 | 163 | 242 | 66 | 82 | 46 | 80 | 18 | 46 | 10 | 275 | 24 | 11 | 0 | 194 | 0 | 0 | 170 | 0 | 135 | 0 | 100 | 200 | 70 | 0 | 115 | 89 | 0 | 0 | 178 | 0 | 17 |  | 912 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 31 | 53 | 40 | 180 | 40 | 110 | 0 | 0 | 60 | 50 | 0 | 93 | 50 | 42 | 37 | 52 | 21 | 22 | 7 | 11 | 71 | 0 | 270 | 0 | 0 | 191 | 0 | 0 | 0 | 97 | 100 | 206 | 0 | 415 | 105 | 0 | 113 | 105 | 103 | 0 | 0 |  | 8308 | 4062 | 12370 | 4434 | 912 | 2349 | 3426 | 341 | 213 | 503 | 192 | 0 | 0 | 105.37
23:00 | 70 | 0 | 0 | 110 | 380 | 94 | 50 | 352 | 348 |  | 0 | 370 | 287 | 92 | 64 | 42 | 13 | 0 | 0 | 0 | 70 | 101 | 133 | 70 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 51 | 0 | 125 | 90 | 90 | 120 | 25 | 208 | 0 | 90 | 0 |  | 0 | 0 | 85 | 10 | 10 | 32 | 22 | 38 | 0 | 0 | 100 | 360 | 235 | 198 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 25 | 20 | 190 | 143 | 95 | 22 | 0 | 60 | 31 | 47 | 49 | 163 | 243 | 66 | 82 | 46 | 80 | 18 | 46 | 10 | 320 | 24 | 11 | 0 | 194 | 0 | 0 | 170 | 0 | 120 | 0 | 100 | 196 | 70 | 0 | 115 | 89 | 0 | 0 | 181 | 0 | 17 |  | 912 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 31 | 53 | 40 | 180 | 40 | 110 | 0 | 0 | 60 | 50 | 0 | 93 | 12 | 42 | 38 | 52 | 21 | 22 | 7 | 11 | 72 | 0 | 270 | 0 | 0 | 195 | 0 | 0 | 0 | 94 | 100 | 207 | 0 | 414 | 105 | 0 | 113 | 105 | 105 | 0 | 0 |  | 8328 | 4013 | 12341 | 4433 | 912 | 2392 | 3353 | 342 | 215 | 504 | 190 | 0 | 0 | 105.37
24:00 | 70 | 0 | 0 | 110 | 380 | 94 | 50 | 363 | 348 |  | 0 | 370 | 275 | 100 | 64 | 42 | 12 | 0 | 0 | 0 | 50 | 101 | 133 | 50 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 115 | 90 | 90 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 10 | 32 | 22 | 38 | 0 | 0 | 100 | 345 | 240 | 184 | 55 | 133 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 188 | 159 | 95 | 22 | 0 | 60 | 31 | 47 | 49 | 163 | 241 | 66 | 82 | 46 | 82 | 18 | 46 | 10 | 320 | 24 | 11 | 0 | 194 | 0 | 0 | 170 | 0 | 118 | 0 | 100 | 182 | 70 | 0 | 115 | 89 | 0 | 0 | 180 | 0 | 17 |  | 912 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 31 | 53 | 40 | 180 | 33 | 110 | 0 | 0 | 60 | 50 | 0 | 92 | 12 | 42 | 38 | 52 | 21 | 22 | 7 | 11 | 72 | 0 | 270 | 0 | 0 | 201 | 0 | 0 | 0 | 96 | 99 | 207 | 0 | 414 | 105 | 0 | 113 | 105 | 106 | 0 | 0 |  | 8310 | 4013 | 12323 | 4494 | 912 | 2387 | 3292 | 342 | 205 | 503 | 188 | 0 | 0 | 105.37
KWH | 1555000 | 0 | 0 | 2601900 | 8201500 | 2060590 | 1453536 | 8601600 | 8035000 |  | 0 | 8625625 | 6720349 | 765120 | 474168 | 308741 | 84473 | 0 | 1521000 | 0 | 545280 | 1136304 | 1536480 | 528408 | 1724160 | 0 | 497616 | 1173960 | 927283 | 614264 | 427536 | 600000 | 554760 | 749700 | 730100 | 1238604 | 0 | 2723787 | 2140000 | 2100000 | 2900000 | 567794 | 4891825 | 0 | 2790912 | 0 |  | 0 | 0 | 667062 | 302280 | 631680 | 702240 | 509664 | 543360 | 0 | 0 | 2544572 | 8061100 | 5608500 | 4496000 | 1338181 | 3133430 | 663696 | 1228320 | 0 | 1020864 | 0 | 62464 | 361430 | 371700 | 242820 | 808700 | 516320 | 3785280 | 3504040 | 1946880 | 515844 | 4300 | 1422000 | 744000 | 1032000 | 1131336 | 3366196 | 4152000 | 1557504 | 1705920 | 1017720 | 1854640 | 436000 | 997320 | 246600 | 7515800 | 535032 | 247584 | 0 | 1500436 | 0 | 0 | 2630400 | 0 | 2157120 | 98000 | 2273280 | 3679200 | 1438545 | 0 | 2648400 | 2100168 | 0 | 36480 | 3450000 | 0 | 433234 |  | 21813090 | 0 | 8633664 | 0 | 1837440 | 0 | 0 | 0 | 265920 | 453504 | 728250 | 4445528 | 626705 | 1355520 | 0 | 0 | 1345000 | 376320 | 47369 | 1006920 | 451800 | 770235 | 578333 | 650400 | 200769 | 511200 | 167508 | 226512 | 1716218 | 0 | 7296500 | 0 | 0 | 5027945 | 0 | 0 | 0 | 2110940 | 943680 | 5085873 | 0 | 8875909 | 1052640 | 0 | 2150880 | 1975536 | 2086080 | 0 | 22450 |  | 176085017 | 84836638 | 260921655 | 104999974 | 21813090 | 53610630 | 57479805 | 9012718 | 4863787 | 5195141 | 3785280 | 161230 | 0
Fuel Cost | 1741600 | 0 | 0 | 2914128 | 6069110 | 1998772.3 | 2122162.56 | 6193152 | 6106600 |  | 0 | 6900500 | 6048314.1 | 7804224 | 5135239.44 | 3167682.66 | 104746.52 | 0 | 1901250 | 0 | 6052608 | 11544848.64 | 15226516.8 | 5537715.84 | 15689856 | 0 | 4657685.76 | 11258276.4 | 8846279.82 | 6118069.44 | 320652 | 450000 | 0 | 0 | 0 | 11865826.32 | 0 | 708184.62 | 556400 | 3213000 | 4437000 | 5456500.34 | 5136416.25 | 0 | 3544458.24 | 0 |  | 0 | 0 | 6997480.38 | 3110461.2 | 6007276.8 | 6572966.4 | 468890.88 | 1510540.8 | 0 | 0 | 2671800.6 | 5965214 | 4711140 | 4136320 | 1311417.38 | 4167461.9 | 544230.72 | 1265169.6 | 0 | 1459835.52 | 0 | 732078.08 | 3397442 | 379134 | 182115 | 1528443 | 387240 | 26118432 | 2873312.8 | 18514828.8 | 526160.88 | 70520 | 1933920 | 1011840 | 1403520 | 1414170 | 4174083.04 | 3819840 | 2320680.96 | 3002419.2 | 1129669.2 | 2819052.8 | 693240 | 1166864.4 | 579510 | 5336218 | 401274 | 188163.84 | 0 | 15709564.92 | 0 | 0 | 25304448 | 0 | 21765340.8 | 1130920 | 21186969.6 | 34510896 | 13479166.65 | 0 | 23226468 | 18712496.88 | 0 | 0 | 31809000 | 0 | 0 |  | 58895343 | 0 | 6734257.92 | 0 | 17712921.6 | 0 | 0 | 0 | 3084672 | 5940902.4 | 7202392.5 | 3556422.4 | 971392.75 | 14558284.8 | 0 | 0 | 2528600 | 4192204.8 | 580270.25 | 9968508 | 4685166 | 9019451.85 | 6968912.65 | 6477984 | 1977574.65 | 562320 | 276388.2 | 171469.584 | 10932308.66 | 0 | 29842685 | 0 | 0 | 4424591.6 | 0 | 0 | 0 | 3356394.6 | 15948192 | 4475568.24 | 0 | 6479413.57 | 9957974.4 | 0 | 19745078.4 | 17602025.76 | 19483987.2 | 0 | 0 |  | 522667425.08 | 308313658.784 | 830981083.864 | 99645898.134 | 58895343 | 52527361.12 | 494883911.32 | 40774993.66 | 1264584.62 | 55669120.01 | 26118432 | 1201440 | 0
Yesterday Day Peak | 70 | 0 | 0 | 110 | 300 | 87 | 50 | 359 | 346 |  | 0 | 370 | 285 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 48 | 32 | 0 | 72 | 0 | 12 | 53 | 55 | 17 | 22 | 25 | 24 | 33 | 16 | 52 | 0 | 118 | 90 | 90 | 120 | 25 | 209 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 30 | 31 | 21 | 2 | 0 | 0 | 100 | 295 | 235 | 214 | 55 | 131 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 0 | 11 | 33 | 20 | 134 | 169 | 48 | 22 | 0.9 | 60 | 31 | 22 | 46 | 130 | 146 | 65 | 50 | 44 | 80 | 18 | 43 | 10 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 82 | 13.8 | 100 | 105 | 50 | 0 | 80 | 88 | 0 | 5.4 | 125 | 0 | 17 |  | 908 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 10 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 11 | 8 | 0 | 22 | 7 | 8 | 69 | 0 | 250 | 0 | 0 | 214 | 0 | 0 | 0 | 53 | 0 | 152 | 0 | 280 | 22 | 0 | 70 | 52 | 76 | 0 | 2.4 |  | 9526.5 | DayPeak
Yesterday Evening Peak | 70 | 0 | 0 | 110 | 380 | 92 | 50 | 345 | 350 | 0 | 0 | 370 | 260 | 93 | 95 | 42 | 12 | 0 | 65 | 0 | 70 | 102 | 133 | 70 | 72 | 0 | 42 | 53 | 55 | 35 | 22 | 25 | 21 | 33 | 33 | 51 | 0 | 117 | 90 | 90 | 120 | 25 | 205 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 30 | 75 | 32 | 22 | 22 | 0 | 0 | 100 | 345 | 240 | 161 | 55 | 132 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 192 | 144 | 95 | 22 | 0 | 59 | 31 | 46 | 49 | 163 | 240 | 66 | 82 | 46 | 71 | 18 | 46 | 10 | 285 | 24 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 133 | 0 | 100 | 200 | 70 | 0 | 115 | 89 | 0 | 0 | 178 | 0 | 17 |  | 913 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 25 | 50 | 40 | 173 | 34 | 110 | 0 | 0 | 55 | 50 | 10 | 93 | 50 | 42 | 40 | 52 | 28 | 22 | 7 | 11 | 71 | 0 | 270 | 0 | 0 | 192 | 0 | 0 | 0 | 96 | 100 | 189 | 0 | 370 | 105 | 0 | 113 | 101 | 99 | 0 | 0 |  | 12443 | EvPeak
Forecast for Evening | 70 | 0 | 200 | 110 | 350 | 90 | 75 | 360 | 350 | 0 | 0 | 370 | 290 | 100 | 100 | 55 | 12 | 0 | 100 | 0 | 100 | 100 | 133 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 90 | 100 | 120 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 100 | 90 | 50 | 22 | 30 | 0 | 0 | 135 | 360 | 240 | 225 | 55 | 140 | 30 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 190 | 150 | 95 | 22 | 0 | 60 | 30 | 51 | 50 | 163 | 250 | 67 | 77 | 46 | 100 | 18 | 46 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 31 | 113 |  | 924 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 42 | 47 | 52 | 35 | 22 | 7 | 11 | 70 | 0 | 280 | 0 | 18 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 70 | 0 | 0 | 110 | 350 | 90 | 70 | 360 | 350 | 0 | 0 | 370 | 290 | 100 | 100 | 55 | 12 | 0 | 100 | 0 | 100 | 100 | 133 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 90 | 100 | 120 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 90 | 50 | 22 | 10 | 0 | 0 | 135 | 360 | 240 | 225 | 55 | 140 | 30 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 149 | 150 | 95 | 22 | 1.6 | 60 | 30 | 51 | 50 | 163 | 256 | 67 | 77 | 45 | 70 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 50 | 4.4 | 230 | 30 | 113 |  | 924 | 0 | 380 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 42 | 47 | 52 | 0 | 22 | 7 | 11 | 70 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 70 | 0 | 0 | 110 | 280 | 94 | 50 | 366 | 282 | 0 | 0 | 370 | 301 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 53 | 17 | 0 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 126 | 90 | 95 | 120 | 12 | 192 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 6 | 22 | 12 | 0 | 0 | 100 | 297 | 235 | 180 | 55 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 8 | 16 | 11 | 33 | 20 | 130 | 151 | 91 | 22 | 1 | 60 | 31 | 47 | 49 | 100 | 256 | 63 | 50 | 46 | 77 | 18 | 46 | 10 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 1 | 50 | 17 | 10 | 0 | 115 | 88 | 0 | 0.3 | 107 | 0 | 17 | 0 | 912 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 24 | 0 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 88 | 0 | 192 | 0 | 330 | 17 | 0 | 36 | 52 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9167 | 9:00
| Highest Generation |  | 12443 | 20:00
| Day Peak Generation |  | 9526.5 | 12:00
| Evening Peak Generation |  | 12443 | 20:00
| HVDC Max Flow |  | 913 | 20:00
| HVDC EvPeak Flow |  | 913 | 20:00
| Load factor L.F |  | 87.37%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-09-01
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9526.5 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9010.93 | MW
Evening Peak Generation : |  | 12443 | MW Hour : | 20:00 | Available Max Generation : |  | 15210 | MW
E.P. Demand (at gen end) : |  | 12443 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12443 | MW Hour : | 20:00 | Reserve(Generation end) |  | 2310 | MW
Total Gen. (MKWH) : |  | 260.9217 | System Load Factor : | 87.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -140 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-09-01
Actual : | 105.4 | Ft.(MSL) , | Rule curve : | 99 | Ft.( MSL )
Gas Consumed : | Total = | 1368.76 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152173259.254
|  | Coal : | 40774993.66 | Oil : | 550553031.33 | Total : | 743501284.244
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4561.6352 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1555.6577 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1394.6106 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1260.4298 |  |  | 0 | 0%
) | 0 | 0:00 | 1138.8769 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 919.0446 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 508.159 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 236.4777 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 708.8402 |  |  | 0 | 0%
Total | 0 |  | 12283.7318 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorashal Unit-4
|  |  |  | 2) Khulna ST 110 MW | 8) Sirajganj Unit-2
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ashuganj #3
|  |  |  | 4) Siddhirganj ST | 10) Ghorashal Unit-3
5) Ashuganj #4
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Faridpur-Bheramara 132 kV Ckt-1 was under shut down from 09:10 to 11:36 for D/W.
b) Faridpur 132/33 kV T1 transformer was under shut down from 09:03 to 11:37 for D/W.
c) Patuakhali-Payra 132 kV Ckt was under shut down from 08:37 to 15:25 for D/W.
d) Shariatpur 132/33 kV T2 transformer was under shut down from 08:24 to 11:05 for C/M. |  |  |  |  | About 30 MW power interruption occurred under Shariatpur S/S
e) Naogaon 132/33 kV T1 transformer was under shut down from 09:47 to 11:25 for C/M. |  |  |  |  | area from 08:24 to 11:05.
f) Tongi (Old) T1 & T2 transformers tripped at 09:44 from 33 kV side showing E/F relay at T1 transformer side |  |  |  |  | About 70 MW power interruption occurred under Tongi S/S
& O/C relay at T2 transformer side due to 33 kV Tongi-2 feeder fault and were switched on at 09:57. |  |  |  |  | area from 09:44 to 09:57.
g) Bhulta-Haripur 132 kV Ckt was under shut down from 10:30 to 13:58 for red hot maintenance. |  |  |  |  | About 30 MW power interruption occurred under Bhulta S/S
area from 10:30 to 13:58.
h) Hathazari-Baroaulia 132 kV Ckt-2 tripped at 11:33 from both ends showing E/F relay at Hathazari end &
dist.relay at Baroaulia end and were switched on at 11:58.
i) Tongi 132/33 kV T1 & T2 transformers along with 33 kV bus section were under shut down from 11:25 to |  |  |  |  | About 25 MW power interruption occurred under Tongi S/S
12:20 for maintenance work at 33 kV R-Phase isolator of T2 transformer. |  |  |  |  | area from 11:25 to 12:20.
j) Sonargaon 132/33 kV T1 transformer was under shut down from 08:55 to 12:20 for red hot maintenance.
k) Faridpur-Bheramara 132 kV Ckt-2 was shut down at 11:44 for D/W.
l) Shahjibazar 330 MW GT-2 was synchronized at 13:36.
m) Manikganj 132/33 kV T2 transformer was under shut down from 17:07 to 17:42 for C/M.
n) Feni 132/33 kV T1 transformer tripped at 03:19 (01/09/2019) operating PRD relay and was
switched on at 07:03 (01/09/2019).
o) Purbasadipur 132 kV bus was under shut down from 06:12 to 08:03 (01/09/2019) due to circuit breaker |  |  |  |  | About 155 MW power interruption occurred under Purbasadipur,
maintenance of Purbasadipur-Saidpur 132 kV Ckt-1. |  |  |  |  | Thakurgaon, Panchagar S/S areas from 06:12 to 08:03(01/09/19).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1555000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2601900
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 8201500
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 50 | 1453536 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 92 | 2060590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 8601600 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 350 | 8035000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8625625 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 93 | 765120 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6720349 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 95 | 474168
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 42 | 308741
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 70 | 528408 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 427536
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 65 | 1521000 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 545280 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 12 | 84473 | Gas shortage
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1136304
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 42 | 497616
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1173960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1536480 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 927283
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 614264 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1724160 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1154760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 749700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 730100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 1238604
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1500436 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 2157120
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 89 | 2100168 | Engine problem
| Dhaka area Total |  |  |  | 5693 | 3568 | 69750781
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 567794
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 98000
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 702240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 207 | 4863787
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4891825 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2790912 | FGMO
| Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | Contract Expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 667062
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 30 | 302280 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2273280
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509664
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 543360
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 75 | 631680 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36480
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 178 | 3450000 | Line O/L
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 0 | on test
53 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 433234 | Line O/L
| Chattogram area Total |  |  |  | 2112 | 1338 | 27761598
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2544572
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 161 | 4496000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 8061100 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5608500 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 663696 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1228320
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 1338181 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1020864 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 1438545 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 62464 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 132 | 3133430
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3679200
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 371700
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 192 | 3785280
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 808700
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 361430
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 516320 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1758 | 39361122
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3504040 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 515844
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1946880
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4300
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 2630400
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2648400
| Mymensingh Area Total |  |  |  | 637 | 546 | 11249864
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1422000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 744000
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3366196
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 240 | 4152000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 46 | 1032000
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 49 | 1131336
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 247584
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 66 | 1557504 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1705920
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 46 | 1017720
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 71 | 1854640
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 436000
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 46 | 997320
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 535032
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7515800 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Test
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 246600
| Sylhet Area Total |  |  |  | 1834 | 1247 | 27961652
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 21813090
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1837440
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 265920
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 453504
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8633664 | Frequency control
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 728250
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 943680
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1052640
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 101 | 1975536
| Khulna Area Total |  |  |  | 2314 | 1809 | 37703724
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1355520
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 626705
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4445528
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2110940
| Barisal Area Total |  |  |  | 462 | 413 | 8538693
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1345000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 376320
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 47369 | Low demand
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 451800
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 770235 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 578333
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 192 | 5027945 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 189 | 5085873 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8875909
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 200769
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 511200
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 7 | 167508 | Engine problem
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226512
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 650400
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 1006920
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2150880
| Rajshahi Area Total |  |  |  | 2070 | 1324 | 27472973
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 71 | 1716218
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 7296500
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 2086080
135 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 22450
| Rangpur Area Total |  |  |  | 605 | 440 | 11121248
| Total |  |  |  | 18618 | 12443 | 260921655
| Eastern Grid Total |  |  |  | 13167 | 8457 | 176085017
| Western Grid Total |  |  |  | 5451 | 3986 | 84836638
| National Grid Total |  |  |  | 18618 | 12443 | 260921655
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-08-31
(a) ENTIRE EASTERN GRID : |  | 7986 | MW | (b) ENTIRE WESTERN GRID : |  | 3852 | MW
i) Dhaka area |  | 4282 | MW | i) Khulna area |  | 1490 | MW
ii) Chittagong area |  | 1060 | MW | ii) Rajshahi area |  | 1269 | MW
iii) Comilla area |  | 1111 | MW | iii) Barisal area |  | 359 | MW
iv) Mymensingh area |  | 999 | MW | iv) Rangpur area |  | 734 | MW
v) Sylhet area |  | 534 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11838 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 1500 | Sherpur | 106 | 1930 | Jhenida | 118 | 1930
Munsiganj | 128 | 2100 | Srimongal | 42 | 2200 | Bottail | 132 | 2000
Sonargaon | 96 | 1930 | Shahjibazar | 123 | 2000 | G.K Project | 61 | 2000
Shyampur | 200 | 1100 | Fenchuganj | 47 | 1930 | Faridpur | 180 | 100
Bhulta | 183 | 2100 | Kulawara | 48 | 1830 | Madaripur | 119 | 2200
Madanganj | 58 | 1400 | Sylhet | 148 | 1900 | Sariatpur | 48 | 2200
Shitalakhya | 111 | 1600 | Chatak | 28 | 1900 | Gopalganj | 97 | 2100
Rahim steel | 10 | 1000 | Sunamganj | 47 | 2000 | Bagerhat | 94 | 1900
Matuail | 96 | 1000 | Biani Bazar | 59 | 2000 | Mongla | 36 | 1000
Ghorasal | 81 | 2000 | Comilla (S) | 192 | 2000 | Satkhira | 107 | 2200
Narsingdi | 150 | 2000 | Comilla(N) | 129 | 1830 | Gallamari | 50 | 1300
Haripur (SBU) | 98 | 2000 | Chandpur | 107 | 1930 | Magura | 57 | 1930
Ullon | 95 | 1930 | Feni | 143 | 2200 | Norail | 26 | 1930
Hasnabad | 215 | 2000 | Chowmuhani | 180 | 2000 | Chuadanga | 90 | 2200
Magbazar | 127 | 1100 | Ashuganj | 55 | 2300 | Barisal(N) | 47 | 2200
Maniknagar | 112 | 1600 | Daudkandi | 136 | 1900 | Barisal (S) | 114 | 2200
Bangabhaban | 24 | 1300 | B.Baria | 142 | 1900 | Patuakhali | 115 | 2100
Narinda | 98 | 1600 | Ramganj | 104 | 2200 | Bhandaria | 58 | 2100
Dhanmondi | 151 | 1500 | Madunaghat | 40 | 2100 | Borhan Uddin | 41 | 2100
Lalbag | 89 | 1900 | Hathazari | 109 | 1900 | Ishurdi | 67 | 2000
Madartek | 58 | 2100 | Khulshi | 204 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 113 | 1830 | Halishahar | 139 | 1400 | Natore | 133 | 1930
Kalyanpur | 123 | 1900 | Baraulia | 159 | 1600 | Bogra | 247 | 2000
Gulshan | 148 | 1300 | Sikalbaha | 26 | 1900 | Noagaon | 128 | 1900
Uttara | 86 | 1900 | Dohazari | 78 | 200 | Rajshahi | 159 | 100
Uttara New | 17 | 1200 | Cox'sbazar | 85 | 100 | C.Nawabganj | 72 | 100
Kamrangirchar | 75 | 1830 | Chandraghona | 30 | 1830 | Amnura | 39 | 2000
Savar | 141 | 1200 | Kaptai | 5 | 1900 | Pabna | 115 | 2000
Bhasantec | 170 | 1830 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 107 | 1930
Agargaon | 58 | 1830 | Bakulia | 119 | 2000 | Serajganj | 103 | 1900
Satmosjid | 114 | 2000 | Julda | 21 | 1000 | Niyamatpur | 62 | 2000
Tongi | 155 | 1800 | TK chemical | 15 | 2000 | Joypurhat | 52 | 2000
Kabirpur | 213 | 1500 | Modern Steel | 12 | 1300 | Mohastangor | 17 | 2000
Basundhara | 142 | 2100 | Shahmirpur | 30 | 1500 | Rangpur | 144 | 1930
Manikganj | 90 | 1930 | Khagrachhari | 20 | 1930 | Lalmonirhat | 63 | 1930
Joydevpur | 221 | 2000 | Matarbari | 26 | 100 | Saidpur | 101 | 1930
New Tongi | 116 | 1200 | Baroiar Hat | 30 | 2100 | Purbasadipur | 102 | 100
Korda | 226 | 1600 | Rangamati | 12 | 1800 | Thakurgaon | 72 | 2000
Dhamrai | 74 | 1900 | Abul Khair 230 | 137 | 100 | Palashbari | 123 | 1930
Valuka | 92 | 900 | BSRM | 116 | 600 | Barapukuria | 50 | 100
Tangail | 198 | 1930 | Goalpara | 28 | 1930 | Panchagar | 45 | 1900
Mymensing | 256 | 2000 | Central s/s | 87 | 100 | Joldhaka | 27 | 1900
Kishorganj | 126 | 1900 | Noapara | 80 | 1900 | Kurigram | 40 | 100
Netrokona | 109 | 1930 | Jessore | 116 | 1930
Jamalpur | 138 | 2000 | Benapol | 46 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-31 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 383 | 7:00 | 377 | 16:00 | Kaliakoir | 363 | 6:00 | 353 | 15:00
Bheramara | 399 | 7:00 | 389 | 24:00 | Bhulta | 377 | 4:00 | 365 | 15:00
Ashuganj(N) | 381 | 5:00 | 370 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 15:00
Ghorasal | 228 | 22:00 | 220 | 15:00 | Hathazari | 219 | 19:00 | 215 | 15:00
Ishurdi | 235 | 18:00 | 225 | 19:00 | Megnaghat | 222 | 4:00 | 210 | 16:00
Ashuganj | 235 | 5:00 | 230 | 1:00 | Fenchuganj | 233 | 7:00 | 229 | 18:00
Serajganj | 230 | 17:00 | 223 | 11:00 | Siddhirganj | 219 | 6:00 | 211 | 15:00
Baghabari | 232 | 18:30 | 228 | 1:00 | Maniknagar | 216 | 6:00 | 208 | 16:00
Barapukuria | 233 | 18:00 | 223 | 1:00 | Old Airport | 215 | 6:00 | 207 | 15:00
Bogra | 223 | 18:00 | 210 | 21:00 | Barisal | 233 | 7:00 | 222 | 12:00
Khulna South | 228 | 5:00 | 212 | 19:00 | AKSML | 216 | 7:00 | 211 | 9:00
Rampura | 219 | 3:00 | 210 | 16:00 | BSRM | 217 | 19:00 | 211 | 18:00
Haripur | 216 | 1:00 | 210 | 14:00 | Bibiyana | 230 | 6:00 | 225 | 12:00
Hasnabad | 216 | 2:00 | 209 | 16:00 | Bhulta | 218 | 1:00 | 211 | 15:00
Aminbazar | 217 | 3:00 | 209 | 16:00 | Ashuganj (S) | 232 | 6:00 | 226 | 9:00
Tongi | 222 | 1:00 | 211 | 7:00 | Kaliakoir | 219 | 1:00 | 208 | 16:00
Comilla (N) | 226 | 6:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 2000 | 126 | 1500 | Khulshi | 128 | 100 | 125 | 900
Munsiganj | 134 | 2000 | 125 | 1500 | Halishahar | 132 | 900 | 128 | 1200
Megnaghat | 130 | 2000 | 125 | 1300 | Baraulia | 129 | 500 | 126 | 1200
Shyampur | 132 | 600 | 126 | 1700 | Sikalbaha | 133 | 2000 | 128 | 1400
Bhulta | 124 | 2000 | 115 | 1300 | Dohazari | 132 | 1900 | 125 | 1500
Madanganj | 133 | 2000 | 124 | 900 | Cox'sbazar | 128 | 2000 | 116 | 1200
Shitalakhya | 136 | 2000 | 125 | 1700 | Chandraghona | 132 | 600 | 129 | 1600
Rahim steal | 131 | 100 | 126 | 1700 | Kaptai | 132 | 100 | 130 | 1200
Matuail | 130 | 500 | 124 | 1500 | A. Khaer Stl. | 129 | 100 | 125 | 1400
Ghorasal | 135 | 100 | 130 | 1700 | Bakulia | 131 | 1930 | 126 | 1600
Narsinghdi | 128 | 1600 | 123 | 1000 | Julda | 131 | 600 | 127 | 1500
Haripur (SBU) | 131 | 100 | 127 | 1600 | TK Chemical | 133 | 200 | 127 | 1500
Ullon | 129 | 600 | 122 | 1500 | Modern Steel | 132 | 2000 | 127 | 1500
Hasnabad | 132 | 700 | 127 | 1500 | Shahmirpur | 132 | 1900 | 127 | 1500
Magbazar | 131 | 1300 | 123 | 1200 | Khagrachhari | 131 | 400 | 128 | 1500
Maniknagar | 132 | 600 | 126 | 1600 | Matarbari | 130 | 1900 | 118 | 1500
Bangabhaban | 132 | 600 | 126 | 1600 | Baroiar Hat | 125 | 100 | 124 | 700
Narinda | 132 | 600 | 126 | 1600 | Rangamati | 131 | 500 | 129 | 1300
Dhanmondi | 129 | 600 | 122 | 1500 | Goalpara | 139 | 500 | 129 | 1200
Lalbag | 132 | 2100 | 122 | 1200 | Central s/s | 137 | 500 | 129 | 1200
Madartek | 129 | 2000 | 122 | 1600 | Noapara | 134 | 600 | 125 | 2100
Mirpur | 130 | 400 | 124 | 1600 | Jessore | 130 | 1600 | 116 | 2100
Kalyanpur | 132 | 200 | 127 | 1700 | Benapol | 130 | 1800 | 119 | 2100
Gulshan | 130 | 500 | 121 | 1600 | Jhenida | 126 | 1800 | 111 | 1900
Uttara | 129 | 400 | 122 | 1600 | Bottail | 133 | 1800 | 123 | 2100
Uttara New | 132 | 100 | 125 | 1600 | G.K Project | 140 | 500 | 134 | 1900
Kamrangirchar | 130 | 100 | 122 | 1700 | Faridpur | 130 | 900 | 119 | 1900
Savar | 129 | 600 | 123 | 1600 | Madaripur | 136 | 700 | 125 | 1900
Bhasantec | 129 | 600 | 122 | 1700 | Sariatpur | 133 | 600 | 123 | 2200
Agargaon | 131 | 600 | 124 | 1700 | Gopalganj | 140 | 100 | 131 | 1900
Satmosjid | 130 | 600 | 123 | 1700 | Bagerhat | 136 | 1600 | 128 | 2100
Tongi | 135 | 100 | 128 | 800 | Mongla | 135 | 500 | 124 | 100
Kabirpur | 130 | 1300 | 124 | 1900 | Satkhira | 136 | 500 | 126 | 1900
Basundhara | 130 | 2100 | 125 | 1500 | Gallamari | 138 | 500 | 129 | 1900
Manikganj | 136 | 2100 | 133 | 1500 | Magura | 120 | 400 | 110 | 1900
Joydevpur | 137 | 100 | 127 | 1600 | Norail | 125 | 600 | 107 | 2100
New Tongi | 132 | 2100 | 126 | 1500 | Chuadanga | 121 | 1800 | 102 | 2100
Kodda | 135 | 2100 | 126 | 800 | Barisal(N) | 138 | 200 | 130 | 1200
Dhamrai | 129 | 1000 | 124 | 2100 | Barisal (S) | 138 | 200 | 129 | 1200
Valuka | 126 | 1000 | 113 | 1900 | Patuakhali | 135 | 700 | 125 | 2000
Tangail | 130 | 1000 | 118 | 1930 | Bhandaria | 133 | 1400 | 125 | 300
Mymensing | 129 | 1100 | 115 | 1900 | Ishurdi | 138 | 600 | 132 | 2000
Kishorganj | 129 | 900 | 118 | 1900 | Ruppur Paromanobik | 137 | 500 | 132 | 1900
Netrokona | 128 | 1500 | 112 | 2200 | Natore | 134 | 1830 | 125 | 1100
Jamalpur | 139 | 800 | 128 | 1900 | Bogra | 134 | 1800 | 125 | 100
Sherpur | 139 | 800 | 126 | 1900 | Noagaon | 130 | 1800 | 117 | 1900
Srimongal | 138 | 1000 | 130 | 100 | Rajshahi | 131 | 1800 | 120 | 1100
Shahjibazar | 137 | 800 | 128 | 2100 | C.Nawabganj | 127 | 1930 | 116 | 1100
Fenchuganj | 135 | 700 | 130 | 1800 | Amnura | 130 | 1930 | 116 | 1100
Khulawara | 134 | 800 | 129 | 1900 | Pabna | 136 | 1800 | 129 | 2000
Sylhet | 134 | 800 | 129 | 1900 | Shahjadpur | 140 | 1800 | 134 | 2000
Chatak | 133 | 800 | 127 | 2000 | Serajganj | 135 | 1830 | 128 | 2000
Sunamganj | 134 | 1000 | 124 | 1900 | Niyamatpur | 129 | 1800 | 113 | 2000
Biani Bazar | 132 | 700 | 125 | 1830 | Joypurhat | 130 | 1800 | 115 | 2000
Comilla(s) | 124 | 1700 | 118 | 2100 | Mohastangor | 134 | 1800 | 123 | 1900
Comilla(n) | 133 | 700 | 130 | 1300 | Rangpur | 130 | 1800 | 116 | 100
Chandpur | 130 | 700 | 129 | 2300 | Lalmonirhat | 127 | 1700 | 108 | 100
Feni | 124 | 1000 | 120 | 2300 | Saidpur | 129 | 1800 | 114 | 2000
Chowmuhani | 121 | 800 | 118 | 1700 | Purbasadipur | 129 | 1800 | 111 | 100
Ashuganj | 136 | 1000 | 130 | 2300 | Thakurgaon | 124 | 1800 | 104 | 100
Daudkandi | 127 | 800 | 123 | 1500 | Palashbari | 129 | 1800 | 117 | 2000
B.Baria | 133 | 1000 | 134 | 1900 | Barapukuria | 133 | 1800 | 123 | 100
Ramganj | 122 | 1700 | 118 | 2200 | Panchagar | 120 | 1800 | 97 | 100
Madanhat | 132 | 800 | 128 | 1500 | Joldhaka | 128 | 1700 | 112 | 2000
Hathazari | 130 | 200 | 127 | 1500 | Kurigram | 126 | 1800 | 107 | 100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-08-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 36 | 8310 | 4013 | 12323 |  |  |  | QF-LDC-12
0:30 | 32 | 8070 | 3951 | 12021 | Date: | 2019-08-31
1:00 | 28 | 7830 | 3889 | 11719
1:30 | 39 | 7732 | 3848 | 11580
2:00 | 50 | 7634 | 3807 | 11441
2:30 | 30 | 7524.5 | 3803 | 11327.5 | [5 empty] | Gen. at Eve. Peak | 12443 | 12443 MW (20:00 )
3:00 | 10 | 7415 | 3799 | 11214 | [6 empty] | 20:00
3:30 | 15.5 | 7370.5 | 3775 | 11145.5 | [5 empty] | Gen. at Day Peak | 9526.5 | 9526.5 MW (12:00 )
4:00 | 21 | 7326 | 3751 | 11077 | [6 empty] | 12:00
4:30 | 17.5 | 7312.5 | 3705 | 11017.5 | [5 empty] | Highest Generation | 12443
5:00 | 14 | 7299 | 3659 | 10958 | [6 empty] | 20:00
5:30 | 62 | 7138.195 | 3524 | 10662.195
6:00 | 110 | 6977.39 | 3389 | 10366.39
6:30 | 110 | 6717.945 | 3199.6 | 9917.545
7:00 | 110 | 6458.5 | 3010.2 | 9468.7
7:30 | 115 | 6385 | 2948.6 | 9333.6
8:00 | 120 | 6311.5 | 2887 | 9198.5
8:30 | 175 | 6340 | 2842.75 | 9182.75
9:00 | 230 | 6368.5 | 2798.5 | 9167
9:30 | 205 | 6456.45 | 2771.65 | 9228.1
10:00 | 180 | 6544.4 | 2744.8 | 9289.2
10:30 | 200 | 6620.7 | 2746.65 | 9367.35
11:00 | 220 | 6697 | 2748.5 | 9445.5
11:30 | 245 | 6687.05 | 2798.95 | 9486
12:00 | 270 | 6677.1 | 2849.4 | 9526.5
12:30 | 265 | 6740.95 | 2946.6 | 9687.55
13:00 | 260 | 6804.8 | 3043.8 | 9848.6
13:30 | 300 | 6800.6 | 3082.45 | 9883.05
14:00 | 340 | 6796.4 | 3121.1 | 9917.5
14:30 | 345 | 6933.725 | 3165.75 | 10099.475
15:00 | 350 | 7071.05 | 3210.4 | 10281.45
15:30 | 380 | 7131.275 | 3243.5 | 10374.775
16:00 | 410 | 7191.5 | 3276.6 | 10468.1
16:30 | 410 | 7048.95 | 3200.75 | 10249.7
17:00 | 410 | 6906.4 | 3124.9 | 10031.3
17:30 | 405 | 6746.7 | 3120 | 9866.7
18:00 | 400 | 6587 | 3115.1 | 9702.1
18:30 | 210 | 7336.5 | 3477.05 | 10813.55
19:00 | 20 | 8086 | 3839 | 11925
19:30 | 100 | 8405 | 4011 | 12416
20:00 | 140 | 8457 | 3986 | 12443 |  |  |  | Executive Engineer
20:30 | 110 | 8401 | 4015 | 12416 |  |  |  | Network Operation Division
21:00 | 80 | 8345 | 4044 | 12389
21:30 | 55 | 8326.5 | 4053 | 12379.5
22:00 | 30 | 8308 | 4062 | 12370 |  |  |  |  | Page 6 of 7
22:30 | 19 | 8318 | 4037.5 | 12355.5
23:00 | 8 | 8328 | 4013 | 12341
23:30 | 22 | 8319 | 4013 | 12332
24:00 | 36 | 8310 | 4013 | 12323
12443 MW (20:00 )
9526.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-31 |  | Energy | 260921655
[10 empty] | 2019-08-31 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4494 | 912 | 2387 | 3292 | 342 | 205 | 503 | 0 | 188
0:30 | 4442 | 904.5 | 2358 | 3125 | 331 | 210 | 466.5 | 0 | 184 | Date: | 2019-08-31
1:00 | 4390 | 897 | 2329 | 2958 | 320 | 215 | 430 | 0 | 180
1:30 | 4411 | 902 | 2333 | 2832 | 320 | 213.5 | 391.5 | 0 | 177 | [7 empty] | Total Energy | 260.9217 | Total Energy Gen 260.922 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.922 MKWHr
2:00 | 4432 | 907 | 2337 | 2706 | 320 | 212 | 353 | 0 | 174 | [7 empty] | Energy not Served | 0
2:30 | 4459 | 907 | 2339 | 2599.5 | 320 | 210.5 | 324.5 | 0 | 168 | [7 empty] | Energy Requirement | 260.9217
3:00 | 4486 | 907 | 2341 | 2493 | 320 | 209 | 296 | 0 | 162
3:30 | 4448 | 907 | 2341 | 2468 | 320 | 209 | 289.5 | 0 | 163 | [6 empty] | Shortage
4:00 | 4410 | 907 | 2341 | 2443 | 320 | 209 | 283 | 0 | 164
4:30 | 4424.5 | 907 | 2317.5 | 2441.5 | 320 | 208 | 237 | 0 | 162
5:00 | 4439 | 907 | 2294 | 2440 | 320 | 207 | 191 | 0 | 160
5:30 | 4392.5 | 907 | 2287.5 | 2243 | 320 | 211.5 | 141.5 | 0 | 159
6:00 | 4346 | 907 | 2281 | 2046 | 320 | 216 | 92 | 0 | 158
6:30 | 4278.5 | 907.5 | 2204.5 | 1772.5 | 320 | 214 | 66 | 0 | 152 |  |  |  |  | Coal
7:00 | 4211 | 908 | 2128 | 1499 | 320 | 212 | 40 | 0 | 146
7:30 | 4165 | 907.5 | 2064.5 | 1470 | 319.5 | 212 | 40 | 0 | 147 |  |  |  | Oil |  |  |  | ,
8:00 | 4119 | 907 | 2001 | 1441 | 319 | 212 | 40 | 0 | 148
8:30 | 4096 | 907 | 2003.5 | 1454.5 | 324 | 212.5 | 32 | 0 | 139
9:00 | 4073 | 907 | 2006 | 1468 | 329 | 213 | 24 | 0 | 130
9:30 | 4049 | 907 | 2031 | 1514.5 | 335 | 214 | 28 | 0 | 130
10:00 | 4025 | 907 | 2056 | 1561 | 341 | 215 | 32 | 0 | 130
10:30 | 4090.5 | 907 | 2036 | 1609 | 335 | 211.5 | 32 | 0 | 125
11:00 | 4156 | 907 | 2016 | 1657 | 329 | 208 | 32 | 0 | 120
11:30 | 4139 | 907.5 | 2024 | 1697.5 | 324 | 208 | 37.5 | 0 | 127
12:00 | 4122 | 908 | 2032 | 1738 | 319 | 208 | 43 | 0 | 134
12:30 | 4178 | 909.5 | 2110.5 | 1748.5 | 319.5 | 208 | 56.5 | 0 | 136
13:00 | 4234 | 911 | 2189 | 1759 | 320 | 208 | 70 | 0 | 138
13:30 | 4234 | 911 | 2189 | 1759 | 320 | 208 | 70 | 0 | 138
14:00 | 4234 | 911 | 2189 | 1759 | 320 | 208 | 70 | 0 | 138
14:30 | 4303.5 | 911 | 2225 | 1873 | 325 | 205.5 | 61.5 | 0 | 143
15:00 | 4373 | 911 | 2261 | 1987 | 330 | 203 | 53 | 0 | 148
15:30 | 4390 | 911 | 2277.5 | 2050.5 | 330.5 | 203 | 57 | 0 | 146
16:00 | 4407 | 911 | 2294 | 2114 | 331 | 203 | 61 | 0 | 144
16:30 | 4385.5 | 911.5 | 2253.5 | 1962 | 331 | 203 | 61 | 0 | 140
17:00 | 4364 | 912 | 2213 | 1810 | 331 | 203 | 61 | 0 | 136
17:30 | 4322.5 | 912 | 2031 | 1845.5 | 336 | 203 | 79 | 0 | 137
18:00 | 4281 | 912 | 1849 | 1881 | 341 | 203 | 97 | 0 | 138
18:30 | 4356 | 912 | 2060.5 | 2468 | 340.5 | 205 | 308.5 | 0 | 163
19:00 | 4431 | 912 | 2272 | 3055 | 340 | 207 | 520 | 0 | 188
19:30 | 4409 | 912 | 2292 | 3528 | 340 | 207 | 542 | 0 | 186
20:00 | 4442 | 913 | 2291 | 3543 | 341 | 207 | 514 | 0 | 192
20:30 | 4417 | 912.5 | 2330 | 3504.5 | 341 | 208 | 512 | 0 | 191
21:00 | 4392 | 912 | 2369 | 3466 | 341 | 209 | 510 | 0 | 190
21:30 | 4413 | 912 | 2359 | 3446 | 341 | 211 | 506.5 | 0 | 191
22:00 | 4434 | 912 | 2349 | 3426 | 341 | 213 | 503 | 0 | 192
22:30 | 4433.5 | 912 | 2370.5 | 3389.5 | 341.5 | 214 | 503.5 | 0 | 191
23:00 | 4433 | 912 | 2392 | 3353 | 342 | 215 | 504 | 0 | 190
23:30 | 4463.5 | 912 | 2389.5 | 3322.5 | 342 | 210 | 503.5 | 0 | 189 | Max Temp. in Dhaka |  | 36.3° C
24:00 | 4494 | 912 | 2387 | 3292 | 342 | 205 | 503 | 0 | 188
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 260.922 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.922 MKWHr
Note on W13: Author:

## Generation
2019-08-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 125 | 122 | 119 | 119 | 117 | 126 | 122 | 122 | 123 | 125 | 118 | 118 | 118 | 118 | 113 | 113 | 113 | 113 |  | 117 | 117 | 117 | 119 | 123 | 125 | 115 | 2723787
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2140000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 | 95 | 95 | 95 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 |  | 25 | 25 | 25 | 1 | 25 | 25 | 25 | 567794
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 7.4 | 10.7 | 15.3 | 12.3 | 13.8 | 10.7 | 13.5 | 7.75 | 0.8 | [10 empty] | 98000
6 | Sikalbaha 225MW CCPP (Gas) | 206 | 205 | 210 | 204 | 216 | 205 | 204 | 205 | 208 | 204 | 213 | 209 | 204 | 204 | 215 | 203 | 204 | 204 |  | 203 | 203 | 205 | 204 | 211 | 208 | 204 | 4891825
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 137 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 100 | 100 |  | 130 | 130 | 130 | 90 | 90 | 90 | 130 | 2790912
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 0 | [14 empty] | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 667062
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 0 |  | 50 | 0 | 0 |  |  |  |  | 62464
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 90 | 90 | 90 | 90 | 90 | 87 | 60 | 60 | 60 | 37 | 40 | 40 | 82 | 38 | 93 | 93 | 87 | 40 |  | 87 | 62 | 65 | 0 | 0 |  |  | 1521000
17 | Siddhirganj 335 MW CCPP | [17 empty] | 4 |  | 12 | 12 | 12 | 12 | 12 | 13 | 12 | 84473
18 | Kodda 300 MW PP Unit-2 (Summit) | 100 | 50 | 0 | [10 empty] | 9 | 14 | 14 | 14 | 15 |  | 125 | 195 | 195 | 197 | 194 | 194 | 194 | 1500436
19 | Ashuganj 195MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1338181
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1555000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2601900
24
25 | Ghorasal 365 MW CCPP Unit-7 | 380 | 380 | 380 | 380 | 340 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 330 | 330 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8201500
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 135 | 135 | 135 | 127 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2544572
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 663696
33 | Ashuganj 225 MW CCPP | 195 | 188 | 196 | 164 | 196 | 180 | 180 | 180 | 196 | 179 | 198 | 214 | 180 | 180 | 200 | 179 | 180 | 185 |  | 151 | 151 | 161 | 179 | 192 | 198 | 184 | 4496000
34 | Ashuganj 450 MW CCPP(South) | 165 | 235 | 235 | 235 | 230 | 240 | 240 | 240 | 240 | 245 | 235 | 235 | 240 | 235 | 235 | 235 | 235 | 235 |  | 240 | 240 | 240 | 235 | 235 | 235 | 240 | 5608500
| Ashuganj 450 MW CCPP(North) | 345 | 330 | 350 | 335 | 360 | 330 | 315 | 260 | 280 | 260 | 325 | 295 | 270 | 270 | 295 | 345 | 345 | 345 |  | 345 | 345 | 345 | 355 | 360 | 360 | 345 | 8061100
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 54 | 53 | 54 | 54 | 54 | 55 | 55 | 56 | 54 | 52 | 49 | 51 | 53 | 50 | 51 | 15 |  | 15 | 52 | 53 | 54 | 54 | 54 | 54 | 1228320
36 | Chandpur 150 MW CCPP | 133 | 132 | 133 | 132 | 133 | 125 | 132 | 131 | 132 | 126 | 132 | 131 | 126 | 132 | 132 | 125 | 132 | 132 |  | 128 | 132 | 132 | 132 | 132 | 132 | 133 | 3133430
37 | Tongi 80 MW GTPP | [8 empty] | 0 | 0
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 350 | 348 | 355 | 351 | 370 | 351 | 352 | 344 | 355 | 345 | 355 | 359 | 375 | 330 | 364 | 359 | 348 | 347 |  | 353 | 349 | 345 | 345 | 354 | 352 | 363 | 8601600
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 370 | 370 | 370 | 320 | 320 | 320 | 320 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8625625
41 | Haripur 360MW CCPP(HPL) | 351 | 352 | 352 | 352 | 322 | 322 | 322 | 303 | 303 | 308 | 330 | 346 | 349 | 346 | 344 | 343 | 345 | 304 |  | 349 | 348 | 350 | 348 | 348 | 348 | 348 | 8035000
42 | RPCL 210MW CCPP | 151 | 152 | 152 | 153 | 152 | 153 | 153 | 151 | 149 | 152 | 173 | 169 | 154 | 142 | 141 | 140 | 142 | 145 |  | 143 | 144 | 144 | 144 | 144 | 143 | 159 | 3504040
43
44 | Fenchugonj CCPP Phase-1 | 58 | 58 | 60 | 60 | 60 | 58 | 60 | 60 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 59 | 58 | 59 | 60 | 60 | 60 | 60 | 1422000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 744000
46 | Shajibazar 330 MW CCPP | 145 | 147 | 147 | 147 | 145 | 145 | 145 | 146 | 144 | 146 | 147 | 146 | 145 | 212 | 245 | 240 | 241 | 239 |  | 240 | 240 | 240 | 242 | 242 | 243 | 241 | 4152000
47 | Shahjibazar GTPP Unit- 8 & 9 | 66 | 66 | 66 | 65 | 65 | 67 | 67 | 68 | 67 | 69 | 65 | 65 | 65 | 65 | 63 | 65 | 65 | 66 |  | 66 | 67 | 66 | 65 | 66 | 66 | 66 | 1557504
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 50 | 50 | 76 | 78 | 78 | 78 | 10 | 10 |  | 81 | 81 | 82 | 82 | 82 | 82 | 82 | 1705920
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 45 | 44 | 10 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1017720
50 | Sylhet 150 MW CCPP | 69 | 75 | 79 | 79 | 79 | 68 | 69 | 74 | 73 | 70 | 85 | 80 | 70 | 72 | 81 | 69 | 68 | 75 |  | 69 | 68 | 71 | 80 | 80 | 80 | 82 | 1854640
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 436000
52 | Sylhet 50MW PP (EPL) | 46 | 45 | 45 | 45 | 45 | 45 | 44 | 21 | 28 | 44 | 42 | 43 | 40 | 42 | 43 | 44 | 47 | 12 |  | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 997320
53 | Sylhet 10MW PP (Desh) | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 246600
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247584
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 50 | 50 | 50 | 22 | 22 | 34 | 47 | 47 | 47 | 47 | 11 |  | 47 | 47 | 46 | 46 | 47 | 47 | 47 | 1032000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 535032
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 310 | 315 | 315 | 305 | 290 | 280 | 310 | 280 | 310 | 310 | 320 | 290 | 320 | 305 | 280 | 300 |  | 290 | 290 | 285 | 300 | 275 | 320 | 320 | 7515800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 | 17 | 17 | 17 | 17 | 0 |  |  | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 614264
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509664
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 427536
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 515844
63 | Impoprt (Tripura) | 180 | 174 | 162 | 164 | 160 | 158 | 146 | 148 | 130 | 130 | 120 | 134 | 138 | 144 | 148 | 144 | 136 | 138 |  | 188 | 186 | 192 | 190 | 192 | 190 | 188 | 3785280
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 37 | 8 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 10 | 12 |  | 18 | 20 | 22 | 35 | 36 | 38 | 38 | 543360
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  |  | 16 | 18 | 18 | 18 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 371700
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242820
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 808700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 516320
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 31 | 30 |  | 21 | 21 | 21 | 30 | 30 | 30 | 30 | 554760
71 | Maona 33 MW PP(Summit) | 33 | 25 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 749700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 33 | 33 | 33 | 33 | 33 |  | 17 | 17 | 33 | 33 | 25 | 25 | 33 | 730100
73 | Ghorashal 108MW PP (Regent) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 87 | 88 | 87 | 90 | 91 | 87 | 92 | 87 | 34 |  | 93 | 92 | 92 | 93 | 94 | 94 | 94 | 2060590
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [13 empty] | 19 | 24 | 24 | 7 | 7 |  | 63 | 70 | 70 | 70 | 70 | 70 | 50 | 545280
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1238604
79 | Kodda 150MW PP | 133 | 120 | 75 | 64 | 64 | 32 | 0 |  |  | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 32 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 1536480
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 95 | 95 | 77 | 95 | 90 | 67 | 50 | 48 | 48 | 48 | 55 | 95 | 48 | 48 |  | 84 | 95 | 95 | 95 | 95 | 95 | 95 | 1946880
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 30 |  | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 361430
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 2100168
| Kaptai 7 MW Solar PP | [5 empty] | 0.39 | 1.3 | 2.8 | 3.5 | 4.7 | 5.3 | 5.4 | 4.2 | 3.7 | 4.2 | 0.4 | 0.1 | 0 |  | 0 | [6 empty] | 36480
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433234
82 | Madanganj 102 PP(Summit) | 0 | [16 empty] | 0 |  | 30 | 90 | 95 | 85 | 64 | 64 | 64 | 474168
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 1 | 10 | 10 | 10 | 10 | 10 |  | 63 | 70 | 70 | 70 | 70 | 70 | 50 | 528408
86 | Meghnaghat CCPP(Summit) | 285 | 280 | 287 | 288 | 293 | 258 | 264 | 260 | 290 | 230 | 295 | 285 | 285 | 255 | 288 | 272 | 260 | 280 |  | 255 | 270 | 260 | 285 | 286 | 287 | 275 | 6720349
87 | Meghnaghat 100 MW(IEL) | 50 | 24 | [11 empty] | 23 | 24 | 24 | 10 | 10 |  | 87 | 90 | 93 | 100 | 97 | 92 | 100 | 765120
88 | Ghorashal 78.5 MW PP(MAX) | 72 | 71 | 71 | 71 | 72 | 71 | 71 | 71 | 71 | 71 | 50 | 50 | 72 | 40 | 40 | 40 | 70 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1453536
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 30 | 30 | 10 | 10 | 10 | 10 | 302280
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 48 | 48 | 49 | 49 | 49 | 10 |  | 36 | 49 | 49 | 49 | 49 | 49 | 49 | 1131336
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 15 | 15 |  | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 1020864
94 | Gagnagar 102 MW PP (Digital Power) | 72 | 40 | 16 | 16 | 16 | 0 | 0 |  | 0 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 20 |  | 68 | 101 | 102 | 102 | 102 | 101 | 101 | 1136304
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 41 | 37 | 38 |  |  |  | 1 | 21 | 32 | 31 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 702240
96 | Chattogram 108 MW PP (ECPV) | 51 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 21 | 30 | 30 | 30 | 30 | 31 | 31 | 32 | 37 |  | 71 | 75 | 75 | 12 | 10 | 10 | 10 | 631680
97 | Katpotti 52 MW PP (Sinha) | 24 | 6 | 12 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 19 | 19 |  | 18 | 25 | 42 | 46 | 46 | 46 | 46 | 497616
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1724160
99 | Madanganj-55 MW PP(Summit) | [13 empty] | 2 | 15 | 15 | 15 | 15 |  | 28 | 42 | 42 | 42 | 42 | 42 | 42 | 308741
100 | Manikganj 55 MW PP (Northern) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 927283
101 | Kushiara 163 MW CCPP (KP) | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 100 | 100 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 100 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3366196
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.9 | 0.9 | 0.2 | 0.1 | 0.3 | 0.3 | 0 |  | 0 | [6 empty] | 4300
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1173960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 190 | 190 | 190 | 190 | 190 | 150 | 32 | 62 | 120 | 50 | 50 | 7 | 7 | 7 | 7 | 16 | 16 | 16 |  | 125 | 170 | 170 | 170 | 170 | 170 | 170 | 2630400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 135 | 126 | 90 | 83 | 84 | 61 | 15 | 15 | 25 | 82 | 82 | 82 | 80 | 84 | 83 | 84 | 84 | 84 |  | 110 | 133 | 133 | 135 | 135 | 120 | 118 | 2157120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 88 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2273280
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 160 | 100 | 100 | 50 | 80 | 105 | 105 | 105 | 105 | 118 | 160 | 135 | 109 |  | 168 | 200 | 200 | 200 | 200 | 196 | 182 | 3679200
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 70 | 70 | 70 | 70 | 40 | 12 | 12 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 23 |  | 58 | 70 | 70 | 70 | 70 | 70 | 70 | 1438545
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 80 | 80 | 80 | 105 | 111 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2648400
| Anwara 300 MW PP (United) | 161 | 161 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 115 | 115 | 115 | 138 | 138 | 138 |  | 179 | 178 | 178 | 178 | 178 | 181 | 180 | 3450000
120 | Eastern Zone Total | 7830 | 7634 | 7415 | 7326 | 7299 | 6977.39 | 6458.5 | 6311.5 | 6368.5 | 6544.4 | 6697 | 6677.1 | 6804.8 | 6796.4 | 7071.05 | 7191.5 | 6906.4 | 6587 |  | 8086 | 8405 | 8457 | 8345 | 8308 | 8328 | 8310 | 176085017
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 100 | 39 | 16 | 16 | 16 | 16 | 16 | 22 | 66 | 86 | 115 | 52 | 49 |  | 99 | 115 | 115 | 115 | 115 | 99 | 99 | 1837440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 0 | [13 empty] | 8 | 25 | 25 | 27 | 31 | 31 | 31 | 265920
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 30 | 22 | 17 | 36 | 28 | 22 | 17 | 18 |  | 72 | 105 | 105 | 105 | 105 | 105 | 105 | 1052640
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 32 | 16 | 16 | 16 | 0 | [7 empty] | 32 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1355520
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 98 | 97 | 97 | 96 | 97 | 96 | 95 | 73 | 73 | 52 | 53 | 87 | 94 | 93 | 94 | 97 | 64 |  | 96 | 97 | 96 | 97 | 97 | 94 | 96 | 2110940
| Bhola 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 179 | 180 | 168 | 181 | 180 | 180 | 170 | 180 | 180 | 180 | 180 |  | 178 | 171 | 173 | 180 | 180 | 180 | 180 | 4445528
140 | Bhola 33 MW PP (Venture) | 39 | 38 | 38 | 30 | 30 | 27 | 22 | 20 | 16 | 15 | 10 | 10 | 18 | 19 | 20 | 20 | 19 | 23 |  | 34 | 34 | 34 | 38 | 40 | 40 | 33 | 626705
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 70 | 70 | 30 | 30 | 0 | [13 empty] | 51 | 100 | 100 | 100 | 100 | 100 | 99 | 943680
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 35 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 728250
143 | Gopalganj 100 MW Peaking PP | 38 | 35 | 35 | 35 | 0 | [10 empty] | 8 | 8 | 18 |  | 40 | 63 | 50 | 55 | 53 | 53 | 53 | 453504
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 69 | 52 | 52 | 52 | 52 | 62 | 69 | 69 | 69 | 69 | 69 |  | 69 | 102 | 101 | 101 | 105 | 105 | 105 | 1975536
146 | Bheramara HVDC | 897 | 907 | 907 | 907 | 907 | 907 | 908 | 907 | 907 | 907 | 907 | 908 | 911 | 911 | 911 | 911 | 912 | 912 |  | 912 | 912 | 913 | 912 | 912 | 912 | 912 | 21813090
147 | Bheramara 360 MW CCPP | 370 | 370 | 370 | 370 | 370 | 370 | 320 | 280 | 280 | 290 | 290 | 290 | 320 | 320 | 320 | 360 | 360 | 320 |  | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 8633664
148
149
150 | Barapukuria TPP Unit-1 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 70 | 69 | 69 | 70 | 71 | 70 | 71 | 71 | 71 |  | 70 | 70 | 71 | 71 | 71 | 72 | 72 | 1716218
151 | Barapukuria TPP Unit-2 | [7 empty] | 0
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 271 | 260 | 250 | 250 | 260 | 260 | 260 | 260 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 7296500
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 1345000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 20 | 8 | 6 | 0 | [12 empty] | 0 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 376320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 189 | 186 | 192 | 190 | 200 | 200 | 196 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 205 | 192 | 188 | 170 |  | 182 | 191 | 192 | 188 | 191 | 195 | 201 | 5027945
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 209 | 209 | 209 | 209 | 207 | 208 | 202 | 194 | 152 | 152 | 152 | 152 | 185 | 182 | 180 | 176 | 160 | 166 |  | 188 | 189 | 189 | 199 | 206 | 207 | 207 | 5085873
| Sirajgonj 225MW CCPP Unit-3 (Oil) | 0 | 0 | 0 | 0 | 0 | 0
| Sirajgonj 400 MW CCPP Unit-4 | 412 | 416 | 414 | 418 | 370 | 370 | 295 | 280 | 280 | 280 | 280 | 280 | 320 | 320 | 404 | 415 | 415 | 415 |  | 415 | 370 | 370 | 415 | 415 | 414 | 414 | 8875909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 10 | 31 | 10 | 0 |  |  |  | 47369
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511200
163 | Bogura 20 MW PP (Energyprima) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 167508
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226512
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 40 | 50 | 50 | 50 | 50 | 12 | 12 | 451800
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 42 | 42 | 42 | 42 | 42 | 8 | 8 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 770235
167 | Katakhali 50 MW Peaking PP | 38 | 22 | 22 | 22 | 22 | 0 | [5 empty] | 11 | 38 | 37 | 37 | 37 | 37 | 37 |  | 38 | 38 | 40 | 37 | 37 | 38 | 38 | 578333
168 | Santahar 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 0 | [11 empty] | 0 |  | 14 | 24 | 28 | 30 | 21 | 21 | 21 | 200769
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 23 | 0 | 0 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 650400
170 | Chapainawabganj 100 MW Peaking PP | 93 | 60 | 60 | 60 | 60 | 60 | 40 | 40 | 24 | 0 | 0 | [6 empty] | 0 |  | 92 | 93 | 93 | 93 | 93 | 93 | 92 | 1006920
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 113 | 55 | 55 | 55 | 55 | 35 | 70 | 70 | 73 | 73 | 73 | 73 | 73 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2150880
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [17 empty] | 0 |  | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 114 | 114 | 114 | 114 | 72 | 57 | 57 | 35 | 35 | 76 | 77 | 77 | 77 | 78 | 78 | 90 |  | 99 | 99 | 99 | 99 | 103 | 105 | 106 | 2086080
177 | Sympa Solar Power 8MW | [6 empty] | 0.2 | 1 | 2.5 | 1.8 | 2.5 | 2.4 | 3.8 | 3.1 | 3.4 | 1.6 | 0.9 | 0.1 |  | 0 | [6 empty] | 22450
178
178