## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-09 | Tuesday
|  | Date (day): | 2020-06-09 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13065.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15689 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-08 | 2020-06-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | # 2-Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 220 | 100 | 100 | 200 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 45 | 220 | 360 |  | 5 | Gas shortage
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 66 | 0 | 0 | 0 |  |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 91 | 95 | 100 | 108
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 347 | 340 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 352 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 32 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 230 | 300 | 300
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 80 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 52 | 98 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 70 | 220 | 220 |  | 115 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 93 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 42 | 48 | 48
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 98 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 52 | 55 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 43 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 300 | 100 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 100 | 100
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 2609 | 3199 | 3803 | 4602 | 423 | 695
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 111 | 106 | 106 | 106 | 124 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  |  | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 144 | 140 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 72 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 50 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 80 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 30 | 10 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 97 | 50 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.3 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 307 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 34 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 891.3 | 1242 | 1338 | 1532 | 394 | 98
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 |  | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 90 | 90 | 100 | 100 | 34 |  | Gas shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 188 | 225 | 225 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 305 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 270 | 360 | 360 |  |  | FGMO
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 40 | 40 | 5 |  | Gas Shortage
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 15 | 20 | 35 |  | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 65 | 65 | 130 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 158 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 21 | 20 | 20
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 35 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 35 | 105 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1302 | 1543 | 2067 | 2441 | 468 | 81
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 113 | 104 | 200 | 200
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 72 | 50 | 95
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 40 | 200 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 292.1 | 513 | 558.6 | 632 | 0 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 250 | 249 | 25 | 251 |  | 79 | Engine problem
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 59 | 66 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 75 | 75
| Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contact expired
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 30 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1263 | 1249 | 1068 | 1294 | 0 | 539
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 45
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 944 | 937 | 950 | 950
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 35
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 7 | 0 | 70
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 380 | 245 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 73 | 74 | 50 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 50 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1490 | 1408 | 1715 | 2200 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 50 | 110
| Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 0 | 0 | 0 | 0 | 0 | 0
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 34 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 89 | 83 | 90 | 90 |  | 104 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 74 | 82 | 95 | 95
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 551 | 600 | 660 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 734 | 909 | 925 | 988 | 0 | 104
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 40 | 0 | 0 | 71
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 34
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 70
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 24 | 40 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 46 | 46
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 139 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 153 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 369 | 280 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 34
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 19 | 20 | 20
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 50 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 109 | 50 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 109 | 50 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 884 | 1126 | 1383 | 1697 | 381 | 27
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 12 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 50 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 157.8 | 275 | 208 | 303 | 170 | 0
| Total |  |  |  |  | 20279 | 19788 | 9623.2 | 11464 | 13065.6 | 15689 | 1836 | 1544
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9134.653 | 10882 | 12402.2906 | 14892.5068
A. |  | 2020-06-08 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11495 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8529.6 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11464 | MW
3 | Day peak Generation : |  |  | 9623.2 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10882 | MW
4 | Evening peak Generation : |  |  | 11464 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 236.8464 | MKWHr | By Solar | 0.59494 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.9838 | MKWHr |  | By Oil: | 59.1013 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 17.7999 | MKWHr |  | By Hydro: | 2.4817 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1836 | MW | Dhaka | 3601 | 3601 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1544 | MW | Chittagong | 1033 | 1033 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3380 | MW | Khulna | 1425 | 1425 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1170.25 | MMCFD |  |  | Rajshahi | 1266 | 1266 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 154251355.736 | ii) Oil : | Taka | 457021425.21 | Comilla | 1065 | 1065 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 81916820 | Total | Taka | 693189600.946 | Mymensingh | 926 | 926 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.9325 | MKWHr. | Sylhet | 464 | 464 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -352 | MW (E to W) at | 21:00 | hrs | Barisal | 324 | 324 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -352 | MW at | 21:00 | hrs | Rangpur | 778 | 778 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 10882 | 10882 |  | 0
B. |  | 2020-06-09 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15689 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 3689 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 247.2516 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8770 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7302 | MKWHr. | ii) HVDC Flow at Peak Time |  | 937 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1546 | MKWHr. | iii) Maximum HVDC Flow : |  | 944 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.95 |  | (b) Today: | 81.93 |  | (c) Rule Curve: |  | 77.82
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-06-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 150 | 0 | 0 | 99 | 68 | 328 | 355 |  | 0 | 390 | 240 | 100 | 95 | 55 | 225 | 0 | 0 | 0 | 99 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 39 | 40 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 30 | 0 | 20 | 35 | 0 | 0 | 90 | 260 | 270 | 216 | 8 | 80 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 16 | 5 | 33 | 20 | 158 | 126 | 95 | 22 | 0 | 60 | 30 | 50 | 50 | 130 | 243 | 53 | 75 | 0 | 150 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 220 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 108 | 89 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 941 | 0 | 290 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 34 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 0 | 0 | 0 | 0 | 19 | 11 | 8 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 145 | 0 | 82 | 75 | 166 | 0 | 352 | 105 | 0 | 35 | 0 | 113 | 0 | 0 | 109 | 664 |  | 7184 | 3773 | 10957 | 3593 | 941 | 2101 | 3144 | 814 | 79 | 127 | 158 | 0 | 0 | 81.95
2:00 | 35 | 0 | 150 | 0 | 0 | 100 | 68 | 331 | 355 |  | 0 | 390 | 240 | 100 | 95 | 55 | 222 | 0 | 0 | 0 | 99 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 39 | 75 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 31 | 0 | 20 | 35 | 0 | 0 | 90 | 260 | 270 | 190 | 8 | 87 | 39 | 5 | 0 | 43 | 0 | 0 | 25 | 16 | 5 | 33 | 20 | 148 | 126 | 95 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 250 | 53 | 75 | 0 | 150 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 60 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 10 | 0 | 109 | 52 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 944 | 0 | 295 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 32 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 84 | 20 | 172 | 0 | 362 | 105 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 661 |  | 6885 | 3640 | 10525 | 3597 | 944 | 2146 | 2725 | 811 | 114 | 40 | 148 | 0 | 0 | 81.95
3:00 | 35 | 0 | 150 | 0 | 0 | 101 | 68 | 332 | 355 |  | 0 | 390 | 240 | 100 | 95 | 55 | 220 | 0 | 0 | 0 | 99 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 38 | 73 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 90 | 260 | 270 | 191 | 8 | 91 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 16 | 5 | 33 | 20 | 140 | 134 | 72 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 251 | 53 | 75 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 15 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 10 | 0 | 109 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 944 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 83 | 0 | 174 | 0 | 368 | 70 | 0 | 0 | 0 | 77 | 0 | 0 | 109 | 666 |  | 6713 | 3515 | 10228 | 3623 | 944 | 2177 | 2417 | 816 | 111 | 0 | 140 | 0 | 0 | 81.95
4:00 | 35 | 0 | 150 | 0 | 0 | 102 | 68 | 329 | 355 |  | 0 | 390 | 240 | 75 | 95 | 15 | 224 | 0 | 0 | 0 | 99 | 93 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 35 | 70 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 0 | 90 | 260 | 240 | 182 | 8 | 86 | 39 | 5 | 0 | 43 | 0 | 0 | 0 | 16 | 5 | 33 | 20 | 138 | 142 | 72 | 22 | 0 | 60 | 30 | 48 | 50 | 163 | 243 | 53 | 75 | 0 | 150 | 19 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 |  | 944 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 83 | 0 | 179 | 0 | 337 | 70 | 0 | 0 | 0 | 34 | 0 | 0 | 109 | 663 |  | 6540 | 3491 | 10031 | 3631 | 944 | 2135 | 2265 | 813 | 105 | 0 | 138 | 0 | 0 | 81.95
5:00 | 35 | 0 | 150 | 0 | 0 | 102 | 68 | 330 | 355 |  | 0 | 390 | 240 | 40 | 95 | 15 | 224 | 0 | 0 | 0 | 99 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 35 | 69 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 90 | 260 | 240 | 182 | 8 | 80 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 5 | 33 | 20 | 132 | 142 | 16 | 22 | 0 | 60 | 30 | 48 | 50 | 130 | 244 | 53 | 75 | 0 | 150 | 19 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 |  | 752 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 82 | 0 | 173 | 0 | 336 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 664 |  | 6339 | 3260 | 9599 | 3586 | 752 | 2089 | 2122 | 814 | 104 | 0 | 132 | 0 | 0 | 81.95
6:00 | 35 | 0 | 150 | 0 | 0 | 102 | 69 | 328 | 303 |  | 0 | 350 | 240 | 30 | 95 | 0 | 180 | 0 | 0 | 0 | 65 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 35 | 69 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 42 | 0 | 0 | 90 | 260 | 240 | 181 | 8 | 90 | 3 | 5 | 0 | 43 | 0 | 0 | 0 | 16 | 5 | 6 | 20 | 124 | 142 | 0 | 22 | 0.1 | 60 | 30 | 48 | 50 | 130 | 238 | 53 | 75 | 0 | 150 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 149 | 2 | 70 | 0 | 0 | 0 | 115 | 62 | 0 | 0.2 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 751 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 83 | 11 | 168 | 0 | 342 | 70 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 595 |  | 5845.3 | 2896.4 | 8741.7 | 3496 | 751 | 2000 | 1519 | 745 | 104 | 0 | 124 | 2.7 | 0 | 81.95
7:00 | 35 | 0 | 150 | 0 | 0 | 102 | 68 | 330 | 303 |  | 0 | 320 | 240 | 30 | 48 | 0 | 180 | 0 | 0 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 11 | 0 | 33 | 70 | 90 | 0 | 0 | 0 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 29 | 0 | 0 | 90 | 270 | 250 | 194 | 8 | 91 | 0 | 5 | 0 | 43 | 0 | 0 | 0 | 16 | 5 | 33 | 20 | 124 | 141 | 0 | 22 | 0.5 | 60 | 30 | 48 | 50 | 110 | 246 | 52 | 0 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 5.2 | 50 | 0 | 0 | 0 | 115 | 88 | 0 | 1 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 751 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 84 | 50 | 169 | 0 | 367 | 53 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 553 |  | 5651.7 | 2877.9 | 8529.6 | 3570 | 751 | 1899 | 1371 | 703 | 103 | 0 | 124 | 8.6 | 0 | 81.95
8:00 | 35 | 0 | 150 | 0 | 0 | 95 | 68 | 331 | 303 |  | 0 | 350 | 280 | 30 | 48 | 0 | 180 | 0 | 0 | 0 | 7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 25 | 26 | 33 | 33 | 51 | 0 | 33 | 72 | 90 | 0 | 0 | 0 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 0 | 90 | 270 | 250 | 194 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 104 | 140 | 0 | 22 | 1.1 | 60 | 30 | 47 | 50 | 110 | 247 | 62 | 40 | 0 | 150 | 18 | 0 | 10 | 305 | 22 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 6.1 | 50 | 0 | 0 | 0 | 115 | 88 | 0 | 3.2 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 751 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 83 | 50 | 164 | 0 | 366 | 53 | 0 | 0 | 0 | 0 | 0 | 3.6 | 0 | 552 |  | 5770.4 | 2876.6 | 8647 | 3566 | 751 | 1940 | 1465 | 702 | 105 | 0 | 104 | 14 | 0 | 81.96
9:00 | 35 | 0 | 220 | 0 | 0 | 95 | 68 | 361 | 350 |  | 0 | 380 | 275 | 30 | 48 | 0 | 180 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 25 | 27 | 33 | 33 | 33 | 0 | 34 | 72 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0 | 0 | 90 | 305 | 270 | 201 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 108 | 139 | 0 | 22 | 1.6 | 60 | 30 | 45 | 50 | 140 | 247 | 61 | 72 | 0 | 151 | 18 | 0 | 9 | 315 | 24 | 2 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 12 | 50 | 0 | 0 | 0 | 115 | 88 | 0 | 4.9 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 807 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 72 | 63 | 180 | 0 | 368 | 53 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 549 |  | 6097.5 | 2958.4 | 9055.9 | 3757 | 807 | 2073 | 1483 | 698 | 106 | 0 | 108 | 23.9 | 0 | 81.96
10:00 | 35 | 0 | 220 | 0 | 0 | 92 | 68 | 354 | 353 |  | 0 | 380 | 285 | 32 | 48 | 0 | 180 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 48 | 22 | 25 | 27 | 33 | 33 | 16 | 0 | 34 | 73 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13 | 17 | 2 | 0 | 0 | 90 | 285 | 365 | 195 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 33 | 8 | 108 | 125 | 0 | 22 | 1.9 | 60 | 30 | 45 | 47 | 140 | 246 | 61 | 70 | 0 | 150 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 9.3 | 50 | 0 | 0 | 0 | 115 | 88 | 0 | 3.2 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 944 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 71 | 75 | 203 | 0 | 369 | 53 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 549 |  | 6159.4 | 3139.8 | 9299.2 | 3825 | 944 | 2062 | 1534 | 698 | 107 | 0 | 108 | 21.2 | 0 | 81.96
11:00 | 35 | 0 | 220 | 0 | 0 | 91 | 67 | 348 | 352 |  | 0 | 380 | 270 | 32 | 48 | 0 | 180 | 0 | 0 | 0 | 22 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 27 | 33 | 33 | 16 | 0 | 34 | 75 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 2 | 0 | 0 | 90 | 320 | 285 | 190 | 16 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 5 | 33 | 8 | 102 | 120 | 0 | 22 | 2.1 | 60 | 30 | 45 | 50 | 140 | 246 | 61 | 70 | 0 | 150 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 15.9 | 80 | 0 | 0 | 0 | 115 | 88 | 0 | 5.4 | 307 | 0 | 0 | 0 | 35 | 100 | 0 |  | 944 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 89 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 73 | 74 | 194 | 0 | 368 | 53 | 0 | 0 | 0 | 0 | 0 | 7.8 | 10 | 549 |  | 6183.4 | 3125.8 | 9309.2 | 3752 | 944 | 2069 | 1603 | 699 | 109 | 0 | 102 | 31.2 | 0 | 81.96
12:00 | 35 | 0 | 220 | 0 | 0 | 91 | 66 | 347 | 348 |  | 0 | 380 | 280 | 32 | 64 | 0 | 180 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 27 | 33 | 25 | 16 | 0 | 36 | 75 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 2 | 0 | 0 | 90 | 350 | 315 | 203 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 5 | 33 | 13 | 102 | 113 | 0 | 22 | 2.1 | 60 | 30 | 48 | 50 | 140 | 250 | 61 | 72 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 17 | 80 | 0 | 0 | 0 | 115 | 88 | 0 | 5.3 | 307 | 0 | 0 | 0 | 35 | 100 | 30 |  | 944 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 74 | 73 | 192 | 0 | 369 | 53 | 0 | 0 | 0 | 0 | 0 | 7.8 | 35 | 551 |  | 6357.4 | 3265.8 | 9623.2 | 3932 | 944 | 2071 | 1730 | 701 | 111 | 0 | 102 | 32.2 | 0 | 81.96
13:00 | 35 | 0 | 220 | 0 | 0 | 94 | 20 | 355 | 347 |  | 0 | 380 | 230 | 45 | 78 | 0 | 120 | 0 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 55 | 22 | 25 | 27 | 33 | 33 | 16 | 0 | 36 | 75 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 7 | 0 | 0 | 90 | 315 | 290 | 162 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 33 | 13 | 110 | 106 | 0 | 22 | 1 | 60 | 30 | 48 | 50 | 163 | 245 | 61 | 70 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 53 | 0 | 149 | 15.9 | 90 | 0 | 0 | 0 | 115 | 88 | 0 | 4.2 | 307 | 0 | 0 | 0 | 35 | 100 | 40 |  | 944 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 73 | 74 | 192 | 0 | 367 | 53 | 0 | 0 | 0 | 4 | 0 | 7.6 | 50 | 601 |  | 6247.1 | 3268.6 | 9515.7 | 3729 | 944 | 2048 | 1794 | 751 | 111 | 0 | 110 | 28.7 | 0 | 81.96
14:00 | 35 | 0 | 220 | 0 | 0 | 96 | 20 | 342 | 352 |  | 0 | 420 | 230 | 70 | 78 | 0 | 70 | 0 | 0 | 0 | 98 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 55 | 0 | 25 | 28 | 33 | 33 | 16 | 0 | 36 | 75 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 21 | 20 | 3 | 0 | 0 | 90 | 315 | 270 | 150 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 13 | 114 | 93 | 0 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 248 | 59 | 72 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 149 | 18 | 100 | 0 | 0 | 0 | 115 | 88 | 0 | 4.7 | 307 | 0 | 0 | 0 | 49 | 100 | 40 |  | 936 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 89 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 72 | 74 | 189 | 0 | 397 | 53 | 0 | 0 | 0 | 42 | 0 | 6.7 | 100 | 601 |  | 6295.7 | 3388.7 | 9684.4 | 3626 | 936 | 2109 | 2008 | 751 | 111 | 0 | 114 | 29.4 | 0 | 81.96
15:00 | 35 | 0 | 220 | 0 | 20 | 96 | 20 | 370 | 353 |  | 0 | 420 | 230 | 85 | 78 | 3 | 70 | 0 | 0 | 0 | 98 | 64 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 55 | 0 | 25 | 28 | 33 | 33 | 17 | 0 | 35 | 72 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 36 | 21 | 2 | 0 | 0 | 90 | 305 | 270 | 151 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 124 | 96 | 0 | 22 | 1.5 | 60 | 30 | 47 | 50 | 163 | 247 | 60 | 71 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 2 | 0 | 0 | 94 | 0 | 149 | 11.1 | 100 | 0 | 0 | 0 | 115 | 88 | 0 | 3.8 | 307 | 0 | 0 | 0 | 72 | 100 | 40 |  | 935 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 20 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 73 | 74 | 199 | 0 | 387 | 53 | 0 | 0 | 0 | 54 | 0 | 6 | 109 | 600 |  | 6447.4 | 3433 | 9880.4 | 3704 | 935 | 2087 | 2151 | 750 | 107 | 0 | 124 | 22.4 | 0 | 81.96
16:00 | 35 | 0 | 180 | 0 | 20 | 96 | 0 | 334 | 235 |  | 0 | 350 | 230 | 100 | 79 | 50 | 70 | 0 | 0 | 0 | 98 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 35 | 68 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 25 | 38 | 21 | 4 | 0 | 0 | 90 | 300 | 270 | 177 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 122 | 100 | 0 | 22 | 0.8 | 60 | 30 | 47 | 50 | 100 | 240 | 59 | 72 | 0 | 120 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 30 | 0 | 0 | 100 | 0 | 149 | 12.4 | 100 | 0 | 10 | 0 | 115 | 88 | 0 | 2.8 | 307 | 0 | 0 | 0 | 105 | 100 | 40 |  | 935 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 89 | 18 | 13 | 0 | 0 | 40 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 18 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 73 | 74 | 192 | 0 | 405 | 17 | 0 | 0 | 0 | 69 | 0 | 4.3 | 109 | 601 |  | 6360 | 3403.3 | 9763.3 | 3597 | 935 | 1825 | 2392 | 750 | 103 | 19 | 122 | 20.3 | 0 | 81.96
17:00 | 35 | 0 | 100 | 0 | 30 | 96 | 0 | 330 | 235 |  | 0 | 320 | 230 | 65 | 79 | 55 | 70 | 0 | 0 | 0 | 80 | 48 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 0 | 33 | 51 | 0 | 33 | 68 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 25 | 38 | 21 | 16 | 0 | 0 | 90 | 300 | 270 | 185 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 18 | 114 | 103 | 0 | 22 | 0.5 | 60 | 30 | 45 | 50 | 100 | 240 | 61 | 74 | 0 | 71 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 30 | 0 | 0 | 100 | 0 | 149 | 2.3 | 20 | 0 | 10 | 0 | 115 | 88 | 0 | 0.4 | 210 | 0 | 0 | 0 | 55 | 100 | 40 |  | 937 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 89 | 19 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 145 | 0 | 44 | 60 | 170 | 0 | 380 | 17 | 0 | 0 | 0 | 45 | 0 | 1.6 | 35 | 600 |  | 5853.2 | 3188.6 | 9041.8 | 3419 | 937 | 1755 | 1942 | 749 | 101 | 20 | 114 | 4.8 | 0 | 81.96
18:00 | 35 | 0 | 100 | 0 | 30 | 99 | 0 | 330 | 263 |  | 0 | 320 | 230 | 32 | 90 | 55 | 70 | 0 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 19 | 25 | 28 | 0 | 33 | 25 | 0 | 33 | 68 | 90 | 0 | 0 | 0 | 0 | 100 | 0 |  | 0 | 0 | 17 | 0 | 24 | 38 | 20 | 13 | 0 | 0 | 90 | 300 | 270 | 190 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 116 | 103 | 0 | 22 | 0.2 | 60 | 30 | 50 | 50 | 100 | 240 | 59 | 40 | 0 | 71 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 30 | 0 | 0 | 55 | 0 | 149 | 0.7 | 20 | 0 | 10 | 0 | 115 | 88 | 0 | 0.2 | 160 | 0 | 0 | 0 | 55 | 50 | 40 |  | 936 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 83 | 20 | 110 | 0 | 0 | 65 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 143 | 0 | 12 | 30 | 165 | 0 | 403 | 17 | 0 | 0 | 0 | 35 | 0 | 0.5 | 35 | 522 |  | 5517.1 | 3131.5 | 8648.6 | 3357 | 936 | 1756 | 1690 | 671 | 101 | 20 | 116 | 1.6 | 0 | 81.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 100 | 0 | 30 | 99 | 0 | 363 | 336 |  | 0 | 350 | 230 | 44 | 95 | 55 | 70 | 0 | 0 | 0 | 75 | 64 | 0 | 2 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 22 | 33 | 33 | 25 | 0 | 35 | 68 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 83 | 0 | 28 | 38 | 21 | 25 | 0 | 0 | 90 | 300 | 270 | 188 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 156 | 103 | 5 | 22 | 0 | 58 | 30 | 50 | 50 | 130 | 261 | 57 | 72 | 0 | 130 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 42 | 0 | 0 | 70 | 0 | 149 | 0 | 70 | 0 | 23 | 0 | 115 | 88 | 15 | 0 | 307 | 1 | 0 | 0 | 66 | 100 | 0 |  | 936 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 83 | 31 | 110 | 0 | 0 | 65 | 0 | 0 | 76 | 40 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 142 | 0 | 12 | 30 | 158 | 0 | 328 | 17 | 0 | 0 | 0 | 46 | 0 | 0 | 90 | 541 |  | 6383 | 3222 | 9605 | 3449 | 936 | 1889 | 2205 | 690 | 103 | 177 | 156 | 0 | 0 | 81.96
19:30 | 35 | 0 | 100 | 0 | 30 | 99 | 0 | 389 | 352 |  | 0 | 380 | 230 | 100 | 95 | 55 | 70 | 0 | 0 | 0 | 100 | 93 | 32 | 50 | 0 | 0 | 12 | 53 | 55 | 17 | 19 | 25 | 25 | 33 | 33 | 40 | 0 | 35 | 70 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 85 | 0 | 90 | 40 | 21 | 27 | 0 | 0 | 90 | 300 | 270 | 188 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 154 | 103 | 24 | 22 | 0 | 59 | 30 | 50 | 50 | 163 | 261 | 59 | 74 | 0 | 151 | 18 | 0 | 10 | 340 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 50 | 0 | 115 | 88 | 50 | 0 | 307 | 34 | 0 | 0 | 106 | 100 | 0 |  | 936 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 83 | 24 | 110 | 0 | 0 | 40 | 0 | 0 | 100 | 40 | 0 | 0 | 3 | 0 | 19 | 11 | 11 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 143 | 0 | 42 | 74 | 161 | 0 | 285 | 73 | 0 | 70 | 0 | 55 | 0 | 0 | 109 | 552 |  | 7310 | 3400 | 10710 | 3473 | 936 | 1982 | 3127 | 701 | 105 | 232 | 154 | 0 | 0 | 0
20:00 | 35 | 0 | 100 | 0 | 30 | 99 | 0 | 376 | 352 |  | 0 | 380 | 230 | 100 | 80 | 55 | 70 | 0 | 0 | 0 | 99 | 93 | 98 | 70 | 0 | 0 | 14 | 53 | 55 | 45 | 22 | 25 | 30 | 33 | 33 | 40 | 0 | 35 | 70 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 85 | 10 | 91 | 42 | 21 | 35 | 0 | 0 | 90 | 305 | 270 | 183 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 16 | 21 | 8 | 33 | 21 | 156 | 104 | 46 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 250 | 59 | 75 | 0 | 150 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 275 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 51 | 0 | 115 | 88 | 72 | 0 | 307 | 34 | 0 | 1 | 103 | 100 | 0 |  | 936 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 83 | 23 | 110 | 0 | 0 | 40 | 0 | 0 | 100 | 40 | 0 | 17 | 43 | 0 | 19 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 142 | 0 | 76 | 71 | 154 | 0 | 278 | 105 | 0 | 68 | 0 | 111 | 0 | 0 | 109 | 600 |  | 7532 | 3605 | 11137 | 3444 | 936 | 1997 | 3431 | 750 | 105 | 318 | 156 | 0 | 0 | 81.96
21:00 | 35 | 0 | 100 | 0 | 45 | 95 | 0 | 340 | 352 |  | 0 | 380 | 230 | 100 | 80 | 55 | 70 | 0 | 0 | 0 | 98 | 93 | 98 | 100 | 0 | 0 | 42 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 35 | 71 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 85 | 10 | 97 | 50 | 21 | 30 | 0 | 0 | 90 | 305 | 270 | 188 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 158 | 104 | 72 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 249 | 59 | 75 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 88 | 72 | 0 | 307 | 34 | 0 | 35 | 105 | 100 | 0 |  | 937 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | 83 | 34 | 110 | 0 | 0 | 40 | 0 | 0 | 100 | 40 | 0 | 45 | 43 | 27 | 19 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 139 | 0 | 82 | 74 | 153 | 0 | 280 | 105 | 0 | 109 | 0 | 113 | 0 | 0 | 109 | 600 |  | 7746 | 3718 | 11464 | 3419 | 937 | 1987 | 3733 | 750 | 106 | 374 | 158 | 0 | 0 | 81.96
22:00 | 35 | 0 | 100 | 0 | 80 | 96 | 0 | 351 | 322 |  | 0 | 380 | 230 | 100 | 85 | 55 | 70 | 0 | 0 | 0 | 99 | 93 | 82 | 100 | 0 | 0 | 42 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 36 | 73 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 10 | 96 | 50 | 21 | 30 | 0 | 0 | 90 | 305 | 270 | 193 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 158 | 104 | 72 | 22 | 0 | 60 | 30 | 50 | 50 | 130 | 241 | 61 | 75 | 0 | 151 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 88 | 72 | 0 | 307 | 34 | 0 | 0 | 93 | 100 | 0 |  | 936 | 0 | 230 | 0 | 26 | 0 | 0 | 0 | 0 | 7 | 40 | 88 | 36 | 110 | 0 | 0 | 40 | 0 | 0 | 100 | 40 | 0 | 38 | 43 | 33 | 19 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 140 | 0 | 85 | 74 | 151 | 0 | 279 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 600 |  | 7646 | 3739 | 11385 | 3454 | 936 | 1934 | 3721 | 750 | 109 | 323 | 158 | 0 | 0 | 76.35
23:00 | 35 | 0 | 100 | 0 | 177 | 99 | 0 | 333 | 303 |  | 0 | 380 | 200 | 100 | 95 | 55 | 140 | 0 | 0 | 0 | 99 | 93 | 82 | 80 | 0 | 0 | 42 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 49 | 0 | 36 | 73 | 90 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 51 | 10 | 97 | 50 | 21 | 32 | 0 | 0 | 90 | 300 | 270 | 200 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 158 | 84 | 72 | 22 | 0 | 59 | 30 | 50 | 50 | 163 | 236 | 40 | 75 | 0 | 151 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 88 | 70 | 0 | 307 | 34 | 0 | 0 | 97 | 100 | 0 |  | 934 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 2 | 40 | 88 | 36 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 0 | 38 | 43 | 33 | 20 | 11 | 11 | 0 | 0 | 151 | 0 | 10 | 0 | 0 | 139 | 0 | 86 | 74 | 149 | 0 | 282 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 602 |  | 7711 | 3784 | 11495 | 3518 | 934 | 1943 | 3764 | 753 | 109 | 316 | 158 | 0 | 0 | 81.96
24:00 | 35 | 0 | 100 | 0 | 175 | 95 | 0 | 332 | 303 |  | 0 | 380 | 130 | 100 | 95 | 55 | 218 | 0 | 0 | 0 | 99 | 93 | 62 | 0 | 0 | 0 | 41 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 52 | 0 | 37 | 75 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 97 | 50 | 21 | 32 | 0 | 0 | 90 | 305 | 270 | 208 | 8 | 85 | 10 | 5 | 0 | 43 | 0 | 0 | 34 | 21 | 8 | 33 | 20 | 152 | 84 | 95 | 22 | 0 | 58 | 30 | 50 | 50 | 163 | 241 | 63 | 75 | 0 | 151 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 300 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 0 | 103 | 0 | 115 | 88 | 70 | 0 | 307 | 34 | 0 | 0 | 104 | 100 | 0 |  | 934 | 0 | 230 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 88 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 0 | 0 | 43 | 33 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 142 | 0 | 84 | 74 | 149 | 0 | 281 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 109 | 601 |  | 7548 | 3706 | 11254 | 3622 | 934 | 1930 | 3548 | 751 | 112 | 205 | 152 | 0 | 0 | 76.33
KWH | 782000 | 0 | 3752000 | 0 | 578918 | 2293727 | 887488 | 8348800 | 7795000 |  | 0 | 8913000 | 5797673 | 1636800 | 1948800 | 724039 | 3724 | 0 | 0 | 0 | 1798080 | 1474848 | 382560 | 396301 | 0 | 0 | 184464 | 897120 | 585696 | 768864 | 442116 | 600000 | 639720 | 735700 | 811800 | 623784 | 0 | 817745 | 1664000 | 2100000 | 0 | 1944 | 0 | 0 | 3304276 | 0 |  | 0 | 0 | 428094 | 39120 | 669120 | 532320 | 465888 | 530400 | 0 | 0 | 2163888 | 7333500 | 6626000 | 4558000 | 234181 | 2103370 | 368640 | 136320 | 0 | 1038228 | 0 | 0 | 324624 | 364896 | 140760 | 760400 | 461980 | 3154560 | 2704760 | 765120 | 441540 | 12550 | 1424000 | 722520 | 1165600 | 1186056 | 3455018 | 5560000 | 1380960 | 1631040 | 0 | 3373430 | 429000 | 0 | 238680 | 7471700 | 568632 | 189264 | 0 | 2014799 | 0 | 0 | 3024000 | 0 | 3615840 | 127170 | 1989120 | 0 | 685818 | 0 | 2724000 | 1777980 | 398107 | 402400 | 7125818 | 173838 | 0 | 64980 | 1823640 | 2374080 | 270000 |  | 21730181 | 0 | 7810272 | 0 | 802560 | 0 | 0 | 0 | 0 | 30464 | 941250 | 2161977 | 587770 | 1242048 | 0 | 0 | 400000 | 0 | 0 | 676728 | 679960 | 0 | 130151 | 189120 | 111087 | 447360 | 268704 | 242028 | 0 | 0 | 3665300 | 0 | 67000 | 0 | 0 | 3953073 | 0 | 1745282 | 1347840 | 4395509 | 0 | 8484909 | 1572960 | 0 | 580992 | 0 | 1223040 | 0 | 52824 | 1734720 | 14134600 |  | 155436736 | 81409709 | 236846445 | 83473341 | 21730181 | 48510463 | 57275227 | 17799900 | 2481745 | 1826084 | 3154560 | 594944 | 0
Fuel Cost | 1282480 | 0 | 5477920 | 0 | 642598.98 | 3027719.64 | 1508729.6 | 8432288 | 8028850 |  | 0 | 9715170 | 6435417.03 | 12423312 | 13427232 | 6125369.94 | 3872.96 | 0 | 0 | 0 | 13539542.4 | 13450613.76 | 3764390.4 | 3653895.22 | 0 | 0 | 1676777.76 | 6548976 | 4527430.08 | 7580999.04 | 331587 | 450000 | 0 | 0 | 0 | 6031991.28 | 0 | 220791.15 | 449280 | 3801000 | 0 | 18059.76 | 0 | 0 | 5617269.2 | 0 |  | 0 | 0 | 4152511.8 | 373596 | 5821344 | 4215974.4 | 587018.88 | 1575288 | 0 | 0 | 3180915.36 | 5426790 | 6626000 | 4193360 | 302093.49 | 2418875.5 | 416563.2 | 190848 | 0 | 1775369.88 | 0 | 0 | 3100159.2 | 463417.92 | 105570 | 1330700 | 346485 | 23659200 | 2867045.6 | 6947289.6 | 560755.8 | 200047 | 2335360 | 1156032 | 2074768 | 1850247.36 | 3938720.52 | 5782400 | 2720491.2 | 3115286.4 | 0 | 5836033.9 | 939510 | 0 | 486907.2 | 7546417 | 426474 | 143840.64 | 0 | 15231880.44 | 0 | 0 | 15724800 | 0 | 35579865.6 | 1486617.3 | 16211328 | 0 | 4835016.9 | 0 | 24842880 | 16801911 | 3467511.97 | 0 | 53871184.08 | 1514128.98 | 0 | 648500.4 | 15628594.8 | 15811372.8 | 0 |  | 125165842.56 | 0 | 8200785.6 | 0 | 6308121.6 | 0 | 0 | 0 | 0 | 319262.72 | 9807825 | 2443034.01 | 911043.5 | 12122388.48 | 0 | 0 | 820000 | 0 | 0 | 5989042.8 | 5235692 | 0 | 1261163.19 | 1832572.8 | 1077543.9 | 858931.2 | 416491.2 | 183215.196 | 0 | 0 | 19865926 | 0 | 1911510 | 0 | 0 | 5218056.36 | 0 | 2617923 | 22926758.4 | 5142745.53 | 0 | 8400059.91 | 16421702.4 | 0 | 5513614.08 | 0 | 9490790.4 | 0 | 583705.2 | 12819580.8 | 62050894 |  | 489038862.32 | 355916221.836 | 844955084.156 | 95910491.836 | 125165842.56 | 58340863.9 | 438546000.4 | 81916820 | 670071.15 | 18475424.81 | 23659200 | 2270369.5 | 0
Yesterday Day Peak | 35 | 0 | 220 | 0 | 0 | 91 | 66 | 347 | 348 |  | 0 | 380 | 280 | 32 | 64 | 0 | 180 | 0 | 0 | 0 | 52 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 27 | 33 | 25 | 16 | 0 | 36 | 75 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 17 | 2 | 0 | 0 | 90 | 350 | 315 | 203 | 8 | 90 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 5 | 33 | 13 | 102 | 113 | 0 | 22 | 2.1 | 60 | 30 | 48 | 50 | 140 | 250 | 61 | 72 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 17 | 80 | 0 | 0 | 0 | 115 | 88 | 0 | 5.3 | 307 | 0 | 0 | 0 | 35 | 100 | 30 |  | 944 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 89 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 19 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 74 | 73 | 192 | 0 | 369 | 53 | 0 | 0 | 0 | 0 | 0 | 7.8 | 35 | 551 |  | 9623.2 | DayPeak
Yesterday Evening Peak | 35 | 0 | 100 | 0 | 45 | 95 | 0 | 340 | 352 | 0 | 0 | 380 | 230 | 100 | 80 | 55 | 70 | 0 | 0 | 0 | 98 | 93 | 98 | 100 | 0 | 0 | 42 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 35 | 71 | 90 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 85 | 10 | 97 | 50 | 21 | 30 | 0 | 0 | 90 | 305 | 270 | 188 | 8 | 91 | 10 | 5 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 33 | 21 | 158 | 104 | 72 | 22 | 0 | 60 | 30 | 50 | 50 | 163 | 249 | 59 | 75 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 0 | 100 | 0 | 115 | 88 | 72 | 0 | 307 | 34 | 0 | 35 | 105 | 100 | 0 |  | 937 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | 83 | 34 | 110 | 0 | 0 | 40 | 0 | 0 | 100 | 40 | 0 | 45 | 43 | 27 | 19 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 139 | 0 | 82 | 74 | 153 | 0 | 280 | 105 | 0 | 109 | 0 | 113 | 0 | 0 | 109 | 600 |  | 11464 | EvPeak
Forecast for Evening | 35 | 0 | 200 | 0 | 360 | 108 | 0 | 412 | 360 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 220 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 35 | 71 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 50 | 22 | 25 | 0 | 0 | 100 | 360 | 360 | 225 | 65 | 90 | 40 | 20 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 173 | 200 | 95 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 251 | 66 | 75 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  |  | 950 | 45 | 410 | 0 | 115 | 225 | 0 | 0 | 35 | 70 | 40 | 90 | 33 | 110 | 0 | 0 | 0 | 34 | 70 | 100 | 40 | 42 | 46 | 43 | 34 | 20 | 11 | 11 | 0 | 0 | 150 | 20 | 20 | 0 | 0 | 200 | 0 | 95 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 100 | 0 | 220 | 100 |  | 412 | 360 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 220 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 35 | 71 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 100 | 50 | 50 | 50 | 22 | 10 | 0 |  | 100 | 360 | 360 | 225 | 65 | 90 | 40 | 15 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 200 | 50 | 22 | 1.6 | 60 | 30 | 51 | 44 | 163 | 25 | 66 | 75 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 100 | 100 | 50 | 170 | 50 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  |  | 950 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 90 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 42 | 46 | 43 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 95 | 50 | 210 | 0 | 410 | 50 | 0 | 50 | 100 | 50 | 0 | 8 | 50 | 660
Generation at 08:00(Today) | 35 | 0 | 100 | 0 | 220 | 99 | 0 | 348 | 351 | 0 | 0 | 360 | 130 | 7 | 95 | 15 | 180 | 0 | 0 | 0 | 60 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 0 | 25 | 30 | 33 | 33 | 8 | 0 | 36 | 71 | 90 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 0 | 0 | 90 | 325 | 270 | 213 | 8 | 90 | 36 | 15 | 0 | 43 | 0 | 0 | 0 | 19 | 8 | 33 | 15 | 122 | 139 | 0 | 22 | 1.1 | 60 | 30 | 50 | 50 | 163 | 251 | 59 | 75 | 0 | 110 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 16 | 0 | 0 | 45 | 0 | 149 | 10 | 30 | 0 | 135 | 0 | 115 | 70 | 0 | 1.8 | 180 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 746 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 73 | 0 | 168 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 35 | 600 | 0
199
| Minimum Generation |  | 8529.6 | 7:00
| Highest Generation |  | 11495 | 23:00
| Day Peak Generation |  | 9623.2 | 12:00
| Evening Peak Generation |  | 11464 | 21:00
| HVDC Max Flow |  | 944 | 2:00
| HVDC EvPeak Flow |  | 937 | 21:00
| Load factor L.F |  | 85.85%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-09
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9623.2 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8770 | MW
Evening Peak Generation : |  | 11464 | MW Hour : | 21:00 | Available Max Generation : |  | 15689 | MW
E.P. Demand (at gen end) : |  | 11464 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11495 | MW Hour : | 23:00 | Reserve(Generation end) |  | 3689 | MW
Total Gen. (MKWH) : |  | 236.8464 | System Load Factor : | 85.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -352 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-09
Actual : | 81.93 | Ft.(MSL) , | Rule curve : | 77.82 | Ft.( MSL )
Gas Consumed : | Total = | 1170.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 154251355.736
: |  | Coal : | 81916820 | Oil : | 457021425.21 | Total : | 693189600.946
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4237.7887 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1443.1841 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1293.4196 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1168.8466 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1056.1965 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 852.3185 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 473.8704 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.3775 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 657.3633 |  |  | 0 | 0%
Total | 0 |  | 11402.3651 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,5.
4) Ashuganj unit-4,5
5) Bhola-225 MW GT-2
6) Kaptai-1,2,4
7) Raozan # 2
8) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) After maintenance Khulna(S)-HVDC Bheramara 230 kV Ckt-1 was switched on at 09:39.
b) Uttara 132/33 kV T3 transformer was under shut down since 09:52 for fire protection work.
c) Cumilla(S)-Tripura 132 kV Ckt-2 tripped at 11:38 from Cumilla(S) end showing pole discrepancy and was
switched on at 11:56.
d) Baghabari 71 MW was synchronized at 11:53 and tripped at 12:06 for GBC problem.
e) Jamalpur 132/33 kV T1 transformer was under shut down from 10:30 to 11:48 for D/W.
f) Jamalpur 132/33 kV T3 transformer was under shut down from 11:54 to 12:42 for D/W.
g) Jamalpur S/S-Jamalpur United 132 kV Ckt-2 was under shut down from 10:35 to 12:24 for D/W.
h) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 12:39 to 15:17 for D/W.
i) Jamalpur S/S-Jamalpur 95 MW 132 kV Ckt was under shut down from 14:43 to 16:16 for C/M.
j) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 15:20 to 16:26 for C/M.
k) Madunaghat 132/33 kV T1 & T2 transformer tripped at 15:34 from 33 kV side showing O/C relay and was |  |  |  |  | About 47 MW power interruption occurred under Madunaghat S/S area
switched on at 15:47. |  |  |  |  | from 15:34 to 15:47.
l) After maintenance Ghorasal # 07 GT & ST were synchronized at 14:49,20:21 respectively.
m) Cumilla(N)-Daudkandi 132 kV Ckt-2 tripped at 14:05 from Daudkandi end showing dist ABC,Z1 and was
switched on at 14:13.
n) Jessore-Jhenaidah 132 kV both Ckt were under shut down from 14:14 to 15:51 for remove kite one
after another .
o) Cumilla(N) 132/33 kV T3 transformer tripped at 14:12 from both side showing REF and was switched on |  |  |  |  | About 24 MW power interruption occurred under Cumilla(N) S/S area
at 18:08. |  |  |  |  | from 14:12 to 18:08.
p) Benapole 132/33 kV T1 & T2 transformer tripped at 19:10 from 33 kV side showing O/C,E/F relay and were |  |  |  |  | About 30 MW power interruption occurred under Benapole S/S area
switched on at 19:20. |  |  |  |  | from 19:10 to 19:20.
q) Khulna© main bus was switched on at 18:44.
r) After maintenance Tangail-Mymensing RPCL Ckt-2 switched on at 18:42.
s) Summit Meghna GT-1 was under shut down since 23:25 for low gas pressure.
t) Ghorasal # 07 tripped at 01:01 and were synchronized GT & ST at 02:15,04:12 respectively.
u) Tongi-Bashundhara 132 kV Ckt-2 is under shut down since 07:15 for D/W.
v) Kaliakoir 400/132 kV T2 transformer is under shut down from 05:41 to 06:48 for C/M.
w) Kabirpur 132 kV bus-2 is under shut down since 06:27 for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 782000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 100 | 3752000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 45 | 578918
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 887488 | Gas shortage.
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2293727
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8348800 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 352 | 7795000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8913000 | Frequency control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1636800
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 230 | 5797673 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 80 | 1948800 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 724039
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 396301
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 442116
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1798080
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 70 | 3724 | Machine problem.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 1474848 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 42 | 184464
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 897120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 382560 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 585696
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 768864
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1239720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 735700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 623784
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 2014799
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3615840
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1777980 | Engine problem
| Dhaka area Total |  |  |  | 5791 | 3199 | 61211641
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 1944 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127170
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 532320
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 106 | 2481745 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3304276 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 72 | 398107 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 428094 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 39120 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1989120
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 465888
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 530400
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 669120
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 402400
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 7125818
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 34 | 173838 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2374080
| Chattogram area Total |  |  |  | 2266 | 1242 | 23143440
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 2163888 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4558000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7333500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6626000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 368640 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 136320 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 234181 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1038228 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 685818 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2103370
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 364896
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 140760 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3154560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 760400
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 324624
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 461980
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 35 | 64980 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1823640
| Cumilla Area Total |  |  |  | 2980 | 1543 | 32343785
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 2704760 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 441540
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 765120 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12550
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3024000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2724000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 513 | 9671970
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1424000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 722520
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3455018
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 249 | 5560000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1165600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 1186056
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 189264
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1380960 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1631040 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 0 | 0 | Contact expired
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3373430
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 429000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 568632
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7471700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238680
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 270000 | On test
| Sylhet Area Total |  |  |  | 2038 | 1249 | 29065900
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 937 | 21730181
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 802560 | Reserve
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 7 | 30464 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 7810272 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 941250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 74 | 1347840 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1572960
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1408 | 34235527
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1242048
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 587770
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 83 | 2161977
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 82 | 1745282 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 600 | 14134600
| Barisal Area Total |  |  |  | 1084 | 909 | 19871677
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 40 | 400000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 679960 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 130151 | Reserve
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 139 | 3953073 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 153 | 4395509 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 280 | 8484909 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 111087 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 447360
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 268704
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242028
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 189120
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 676728
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 109 | 580992
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1734720
| Rajshahi Area Total |  |  |  | 2183 | 1126 | 22294341
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3665300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 67000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1223040
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 52824
| Rangpur Area Total |  |  |  | 605 | 275 | 5008164
| Total |  |  |  | 19868 | 11464 | 236846445
| Eastern Grid Total |  |  |  | 13712 | 7746 | 155436736
| Western Grid Total |  |  |  | 6156 | 3718 | 81409709
| National Grid Total |  |  |  | 19868 | 11464 | 236846445
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-08
(a) ENTIRE EASTERN GRID : |  | 7089 | MW | (b) ENTIRE WESTERN GRID : |  | 3793 | MW
i) Dhaka area |  | 3601 | MW | i) Khulna area |  | 1425 | MW
ii) Chittagong area |  | 1033 | MW | ii) Rajshahi area |  | 1266 | MW
iii) Comilla area |  | 1065 | MW | iii) Barisal area |  | 324 | MW
iv) Mymensingh area |  | 926 | MW | iv) Rangpur area |  | 778 | MW
v) Sylhet area |  | 464 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10882 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 15:00 | Sherpur | 120 | 20:00 | Benapol | 36 | 23:00
Munsiganj | 120 | 21:00 | Srimongal | 49 | 19:30 | Jhenida | 108 | 20:00
Sonargaon | 75 | 19:30 | Shahjibazar | 106 | 22:00 | Bottail | 128 | 23:00
Shyampur | 178 | 1:00 | Fenchuganj | 36 | 1:00 | G.K Project | 55 | 21:00
Bhulta | 169 | 11:00 | Kulawara | 42 | 19:00 | Faridpur | 172 | 21:00
Madanganj | 47 | 10:00 | Sylhet | 113 | 19:00 | Madaripur | 95 | 23:00
Shitalakhya | 94 | 10:00 | Chatak | 28 | 21:00 | Sariatpur | 60 | 21:00
Rahim steel | 22 | 17:00 | Sunamganj | 45 | 21:00 | Gopalganj | 92 | 21:00
Matuail | 90 | 10:00 | Biani Bazar | 56 | 21:00 | Bagerhat | 94 | 21:00
Ghorasal | 72 | 22:00 | Comilla (S) | 158 | 21:00 | Mongla | 48 | 12:00
Narsingdi | 148 | 21:00 | Comilla(N) | 91 | 19:30 | Satkhira | 112 | 23:00
Haripur (SBU) | 96 | 11:00 | Chandpur | 98 | 22:00 | Gallamari | 46 | 23:00
Ullon | 51 | 14:00 | Feni | 111 | 21:00 | Magura | 52 | 19:30
Hasnabad | 181 | 22:00 | Chowmuhani | 160 | 22:00 | Norail | 39 | 19:30
Magbazar | 103 | 12:00 | Ashuganj | 54 | 22:00 | Chuadanga | 87 | 23:00
Maniknagar | 104 | 13:00 | Daudkandi | 132 | 21:00 | Barisal(N) | 45 | 21:00
Bangabhaban | 32 | 10:00 | B.Baria | 144 | 21:00 | Barisal (S) | 98 | 21:00
Narinda | 100 | 13:00 | Ramganj | 104 | 21:00 | Patuakhali | 122 | 22:00
Dhanmondi | 148 | 12:00 | Chaddagram | 34 | 20:00 | Bhandaria | 54 | 21:00
Lalbag | 72 | 13:00 | PHP | 5 | 18:00 | Borhan Uddin | 42 | 1:00
Madartek | 66 | 22:00 | Madunaghat | 58 | 11:00 | Ishurdi | 66 | 23:00
Dhaka University |  |  | Hathazari | 98 | 20:00 | Ruppur Paromanobik | 2 | 22:00
Mirpur | 97 | 15:00 | Khulshi | 189 | 12:00 | Natore | 126 | 21:00
Kalyanpur | 84 | 19:30 | Halishahar | 133 | 15:00 | Bogra | 168 | 22:00
Gulshan | 112 | 12:00 | Baraulia | 138 | 0:00 | Noagaon | 132 | 21:00
Uttara | 79 | 12:00 | Sikalbaha | 28 | 10:00 | Rajshahi | 146 | 23:00
Uttara New | 21 | 12:00 | Dohazari | 92 | 22:00 | Rajshahi New | 10 | 19:30
Kamrangirchar | 77 | 12:00 | Cox'sbazar | 94 | 19:00 | C.Nawabganj | 79 | 23:00
Savar | 128 | 12:00 | Chandraghona | 30 | 22:00 | Amnura | 48 | 22:00
Bhasantec | 136 | 13:00 | Kaptai | 4 | 19:00 | Pabna | 113 | 21:00
Agargaon | 52 | 11:00 | A. Khaer Stl. | 0 | 1:00 | Shahjadpur | 97 | 21:00
Satmosjid | 89 | 12:00 | Bakulia | 99 | 12:00 | Serajganj | 94 | 20:00
Tongi | 144 | 12:00 | Julda | 20 | 1:00 | Niyamatpur | 60 | 21:00
Kabirpur | 201 | 15:00 | TK chemical | 17 | 19:00 | Joypurhat | 48 | 21:00
Basundhara | 109 | 11:00 | Modern Steel | 17 | 11:00 | Sherpur(Bogura) | 50 | 22:00
Manikganj | 60 | 21:00 | Shahmirpur | 28 | 21:00 | Mohastangor | 58 | 21:00
Joydevpur | 149 | 15:00 | Khagrachhari | 24 | 19:00 | Rangpur | 144 | 22:00
New Tongi | 99 | 12:00 | Matarbari | 35 | 21:00 | Lalmonirhat | 50 | 24:00
Kodda | 226 | 16:00 | Baroiar Hat | 34 | 19:30 | Saidpur | 106 | 20:00
Dhamrai | 94 | 21:00 | Rangamati | 10 | 12:00 | Purbasadipur | 110 | 23:00
Rajendrapur | 84 | 21:00 | Abul Khair 230 | 120 | 6:00 | Thakurgaon | 82 | 23:00
Valuka | 90 | 21:00 | BSRM | 106 | 11:00 | Palashbari | 125 | 21:00
Tangail | 186 | 22:00 | GPH Ispat | 51 | 13:00 | Barapukuria | 49 | 21:00
Mymensing | 205 | 21:00 | Goalpara | 25 | 19:00 | Panchagar | 49 | 21:00
Kishorganj | 134 | 22:00 | Central s/s | 90 | 22:00 | Joldhaka | 28 | 19:30
Netrokona | 138 | 22:00 | Noapara | 56 | 22:00 | Kurigram | 55 | 21:00
Jamalpur | 114 | 20:00 | Jessore | 116 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 23:00 | 391 | 10:00 | Kaliakoir | 383 | 0.83333 | 368 | 0.41667
| Bheramara | 403 | 7:00 | 391 | 20:00 | Bhulta | 397 | 0.95833 | 381 | 0.41667
| Ashuganj(N) | 400 | 23:00 | 387 | 10:00 | Gopalganj | 405 | 0.25 | 378 | 0.91667
| Payra | 415 | 6:00 | 402 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 240 | 1:00 | 232 | 13:00 | Comilla (N) | 236 | 20:00 | 230 | 14:00
| Ishurdi | 234 | 5:00 | 223 | 9:00 | Hathazari | 226 | 21:00 | 219 | 7:00
| Ashuganj | 240 | 22:00 | 232 | 10:00 | Megnaghat | 236 | 21:00 | 228 | 9:00
| Serajganj | 232 | 18:00 | 226 | 21:00 | Fenchuganj | 241 | 23:00 | 236 | 12:00
| Baghabari | 240 | 18:00 | 232 | 19:30 | Siddhirganj | 234 | 4:00 | 226 | 12:00
| Barapukuria | 234 | 5:00 | 225 | 20:00 | Maniknagar | 232 | 23:00 | 223 | 10:00
| Bogra | 229 | 19:00 | 219 | 20:00 | Agargaon | 231 | 22:00 | 219 | 12:00
| Rajshahi | 230 | 18:00 | 221 | 10:00 | Barisal | 248 | 18:30 | 236 | 1:00
| Khulna South | 231 | 18:00 | 207 | 9:00 | AKSML | 223 | 20:00 | 217 | 10:00
| Rampura | 230 | 3:00 | 224 | 12:00 | BSRM | 226 | 20:00 | 219 | 9:00
| Haripur | 231 | 19:30 | 222 | 12:00 | Bibiyana | 240 | 23:00 | 233 | 11:00
| Hasnabad | 232 | 20:00 | 222 | 10:00 | Bhulta | 234 | 1:00 | 225 | 12:00
| Shyampur | 230 | 21:00 | 219 | 12:00 | Ashuganj (S) | 238 | 22:00 | 230 | 10:00
| Aminbazar | 232 | 22:00 | 221 | 12:00 | Kaliakoir | 232 | 1:00 | 223 | 10:00
| Tongi | 232 | 22:00 | 217 | 10:00 | GPH | 224 | 1:00 | 215 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 22:00 | 128 | 10:00 | Hathazari | 134 | 0.875 | 130 | 0.29167
| Munsiganj | 137 | 22:00 | 126 | 9:00 | Khulshi | 132 | 0.8125 | 127 | 0.375
| Sonargaon | 133 | 22:00 | 126 | 11:00 | Halishahar | 135 | 0.8125 | 129 | 0.41667
| Shyampur | 135 | 21:00 | 128 | 10:00 | Baraulia | 135 | 0.875 | 128 | 0.375
| Bhulta | 127 | 20:00 | 121 | 10:00 | Sikalbaha | 136 | 20:00 | 130 | 0.45833
| Madanganj | 132 | 7:00 | 129 | 16:00 | Dohazari | 134 | 21:00 | 127 | 0.375
| Shitalakhya | 141 | 20:00 | 125 | 10:00 | Cox'sbazar | 126 | 0.8125 | 117 | 0.083333
| Rahim steal | 134 | 19:30 | 128 | 11:00 | Chandraghona | 134 | 0.83333 | 130 | 0.375
| Matuail | 134 | 22:00 | 128 | 10:00 | Kaptai | 132 | 1:00 | 130 | 0.375
| Ghorasal | 138 | 18:00 | 134 | 1:00 | A. Khaer Stl. | 132 | 0.83333 | 128 | 11:00
| Narsinghdi | 129 | 5:00 | 123 | 10:00 | Bakulia | 135 | 0.875 | 128 | 0.375
| Haripur (SBU) | 135 | 1:00 | 127 | 10:00 | Julda | 135 | 0.79167 | 130 | 0.375
| Ullon | 131 | 22:00 | 124 | 12:00 | TK Chemical | 136 | 0.875 | 130 | 9:00
| Hasnabad | 136 | 24:00 | 126 | 10:00 | Modern Steel | 134 | 0.79167 | 128 | 0.41667
| Magbazar | 130 | 1:00 | 124 | 12:00 | Shahmirpur | 135 | 0.83333 | 130 | 0.375
| Maniknagar | 135 | 4:00 | 129 | 12:00 | Khagrachhari | 133 | 0.875 | 129 | 0.41667
| Bangabhaban | 135 | 4:00 | 129 | 12:00 | Matarbari | 129 | 0.875 | 120 | 0.041667
| Narinda | 135 | 4:00 | 129 | 12:00 | Baroiar Hat | 131 | 0.75 | 127 | 0.041667
| Dhanmondi | 131 | 22:00 | 124 | 12:00 | Rangamati | 133 | 0.875 | 129 | 12:00
| Lalbag | 138 | 21:00 | 124 | 10:00 | Goalpara S/S | 140 | 0.75 | 126 | 9:00
| Madartek | 131 | 5:00 | 125 | 10:00 | Khulna Central S/S | 136 | 0.625 | 125 | 21:00
| Dhaka University |  |  |  |  | Noapara | 132 | 5:00 | 116 | 13:00
| Mirpur | 132 | 6:00 | 126 | 12:00 | Jessore | 126 | 23:00 | 112 | 13:00
| Kalyanpur | 133 | 5:00 | 126 | 12:00 | Benapol | 127 | 1:00 | 113 | 13:00
| Gulshan | 132 | 20:00 | 124 | 12:00 | Jhenida | 121 | 0.75 | 109 | 21:00
| Uttara | 133 | 20:00 | 126 | 12:00 | Bottail | 129 | 6:00 | 121 | 20:00
| Uttara New | 132 | 20:00 | 124 | 12:00 | G.K Project | 137 | 0.75 | 132 | 20:00
| Kamrangirchar | 135 | 20:00 | 124 | 12:00 | Faridpur | 132 | 6:00 | 122 | 21:00
| Savar | 132 | 20:00 | 124 | 11:00 | Madaripur | 138 | 0.25 | 128 | 21:00
| Bhasantec | 130 | 6:00 | 123 | 12:00 | Shariyatpur S/S | 140 | 0.25 | 123 | 22:00
| Agargaon | 132 | 5:00 | 125 | 12:00 | Gopalganj | 137 | 5:00 | 120 | 21:00
| Satmosjid | 131 | 6:00 | 124 | 12:00 | Bagerhat | 135 | 0.16667 | 123 | 9:00
| Tongi | 138 | 0.95833 | 130 | 10:00 | Mongla | 134 | 0.75 | 121 | 19:00
| Kabirpur | 136 | 7:00 | 127 | 10:00 | Satkhira | 139 | 0.77083 | 121 | 21:00
| Basundhara | 131 | 24:00 | 124 | 10:00 | Gallamari | 140 | 18:00 | 126 | 9:00
| Manikganj | 136 | 24:00 | 128 | 10:00 | Magura | 124 | 0.77083 | 110 | 13:00
| Joydevpur | 141 | 24:00 | 132 | 10:00 | Norail | 120 | 0.75 | 104 | 21:00
| New Tongi | 136 | 0.91667 | 128 | 12:00 | Chuadanga | 115 | 5:00 | 98 | 21:00
| Kodda | 140 | 6:00 | 129 | 0.5 | Barisal(N) | 141 | 7:00 | 128 | 22:00
| Dhamrai | 133 | 7:00 | 123 | 12:00 | Barisal (S) | 139 | 0.20833 | 128 | 22:00
| Rajendrapur | 138 | 5:00 | 127 | 12:00 | Patuakhali | 133 | 0.29167 | 118 | 22:00
| Valuka | 131 | 6:00 | 116 | 15:00 | Bhandaria | 136 | 6:00 | 120 | 22:00
| Tangail | 134 | 7:00 | 126 | 12:00 | Ishurdi | 136 | 6:00 | 130 | 9:00
| Mymensing | 133 | 6:00 | 118 | 23:00 | Ruppur Paromanobik | 135 | 5:00 | 130 | 14:00
| Kishorganj | 134 | 6:00 | 123 | 1:00 | Natore | 133 | 18:30 | 126 | 9:00
| Netrokona | 140 | 4:00 | 125 | 11:00 | Bogra | 133 | 19:00 | 126 | 20:00
| Jamalpur | 131 | 6:00 | 115 | 0.95833 | Noagaon | 128 | 18:00 | 119 | 20:00
| Sherpur | 138 | 4:00 | 126 | 0.41667 | Rajshahi | 132 | 18:00 | 124 | 9:00
| Srimongal | 138 | 6:00 | 134 | 0.041667 | Rajshahi New | 133 | 19:00 | 123 | 9:00
| Shahjibazar | 139 | 6:00 | 133 | 0.041667 | C.Nawabganj | 132 | 19:00 | 120 | 9:00
| Fenchuganj | 137 | 8:00 | 134 | 0.66667 | Amnura | 134 | 19:00 | 121 | 8:00
| Khulawara | 136 | 9:00 | 133 | 1:00 | Pabna | 133 | 18:00 | 128 | 21:00
| Sylhet | 136 | 6:00 | 132 | 0.79167 | Shahjadpur | 138 | 18:00 | 133 | 20:00
| Chatak | 135 | 6:00 | 130 | 21:00 | Serajganj | 133 | 19:00 | 126 | 21:00
| Sunamganj | 135 | 6:00 | 128 | 0.875 | Niyamatpur | 127 | 5:00 | 117 | 20:00
| Biani Bazar | 135 | 6:00 | 129 | 0.875 | Joypurhat | 130 | 19:00 | 118 | 20:00
| Comilla(s) | 126 | 12:00 | 119 | 19:00 | Sherpur(Bogura) | 133 | 19:00 | 126 | 20:00
| Comilla(n) | 136 | 0.70833 | 133 | 9:00 | Mohastangor | 132 | 19:00 | 123 | 20:00
| Chandpur | 130 | 8:00 | 125 | 22:00 | Rangpur | 132 | 19:00 | 118 | 20:00
| Feni | 130 | 16:00 | 127 | 22:00 | Lalmonirhat | 127 | 19:00 | 112 | 20:00
| Chowmuhani | 130 | 11:00 | 122 | 19:30 | Saidpur | 131 | 6:00 | 116 | 20:00
| Ashuganj | 137 | 6:00 | 133 | 16:00 | Purbasadipur | 128 | 5:00 | 109 | 20:00
| Daudkandi | 131 | 17:00 | 127 | 10:00 | Thakurgaon | 126 | 6:00 | 108 | 20:00
| B.Baria | 135 | 7:00 | 129 | 14:00 | Palashbari | 126 | 5:00 | 115 | 20:00
| Ramganj | 126 | 11:00 | 120 | 19:00 | Barapukuria | 134 | 5:00 | 125 | 20:00
| Chaddagram | 132 | 16:00 | 129 | 10:00 | Panchagar | 125 | 6:00 | 104 | 20:00
| PHP | 132 | 12:00 | 126 | 9:00 | Joldhaka | 127 | 6:00 | 111 | 20:00
| Madanhat | 136 | 19:30 | 131 | 9:00 | Kurigram | 127 | 19:00 | 112 | 20:00

## L-Curve
Date | 2020-06-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 253 | 7548 | 3706 | 11254 |  |  |  | QF-LDC-12
0:30 | 142.5 | 7366 | 3739.5 | 11105.5 | Date: | 2020-06-08
1:00 | 32 | 7184 | 3773 | 10957
1:30 | 16 | 7034.5 | 3706.5 | 10741
2:00 | 0 | 6885 | 3640 | 10525
2:30 | 4 | 6799 | 3577.5 | 10376.5 | [5 empty] | Gen. at Eve. Peak | 11464 | 11464 MW (21:00 )
3:00 | 8 | 6713 | 3515 | 10228 | [6 empty] | 21:00
3:30 | 30 | 6626.5 | 3503 | 10129.5 | [5 empty] | Gen. at Day Peak | 9623.2 | 9623.2 MW (12:00 )
4:00 | 52 | 6540 | 3491 | 10031 | [6 empty] | 12:00
4:30 | 38 | 6439.5 | 3375.5 | 9815 | [5 empty] | Highest Generation | 11495
5:00 | 24 | 6339 | 3260 | 9599 | [6 empty] | 23:00
5:30 | 48 | 6092.15 | 3078.2 | 9170.35
6:00 | 72 | 5845.3 | 2896.4 | 8741.7
6:30 | 68.5 | 5748.5 | 2887.15 | 8635.65
7:00 | 65 | 5651.7 | 2877.9 | 8529.6
7:30 | 104 | 5711.05 | 2877.25 | 8588.3
8:00 | 143 | 5770.4 | 2876.6 | 8647
8:30 | 216 | 5933.95 | 2917.5 | 8851.45
9:00 | 289 | 6097.5 | 2958.4 | 9055.9
9:30 | 305.5 | 6128.45 | 3049.1 | 9177.55
10:00 | 322 | 6159.4 | 3139.8 | 9299.2
10:30 | 293.5 | 6171.4 | 3132.8 | 9304.2
11:00 | 265 | 6183.4 | 3125.8 | 9309.2
11:30 | 282.5 | 6270.4 | 3195.8 | 9466.2
12:00 | 300 | 6357.4 | 3265.8 | 9623.2
12:30 | 293.5 | 6302.25 | 3267.2 | 9569.45
13:00 | 287 | 6247.1 | 3268.6 | 9515.7
13:30 | 330.5 | 6271.4 | 3328.65 | 9600.05
14:00 | 374 | 6295.7 | 3388.7 | 9684.4
14:30 | 355.5 | 6371.55 | 3410.85 | 9782.4
15:00 | 337 | 6447.4 | 3433 | 9880.4
15:30 | 363.5 | 6403.7 | 3418.15 | 9821.85
16:00 | 390 | 6360 | 3403.3 | 9763.3
16:30 | 370.5 | 6106.6 | 3295.95 | 9402.55
17:00 | 351 | 5853.2 | 3188.6 | 9041.8
17:30 | 376.5 | 5685.15 | 3160.05 | 8845.2
18:00 | 402 | 5517.1 | 3131.5 | 8648.6
18:30 | 250.5 | 5950.05 | 3176.75 | 9126.8
19:00 | 99 | 6383 | 3222 | 9605
19:30 | 198 | 7310 | 3400 | 10710
20:00 | 300 | 7532 | 3605 | 11137 |  |  |  | Executive Engineer
20:30 | 326 | 7639 | 3661.5 | 11300.5 |  |  |  | Network Operation Division
21:00 | 352 | 7746 | 3718 | 11464
21:30 | 331 | 7696 | 3728.5 | 11424.5
22:00 | 310 | 7646 | 3739 | 11385 |  |  |  |  | Page 6 of 7
22:30 | 286 | 7678.5 | 3761.5 | 11440
23:00 | 262 | 7711 | 3784 | 11495
23:30 | 257.5 | 7629.5 | 3745 | 11374.5
24:00 | 253 | 7548 | 3706 | 11254
11464 MW (21:00 )
9623.2 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-08 |  | Energy | 236846445
[10 empty] | 2020-06-08 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3622 | 934 | 1930 | 3764 | 751 | 112 | 205 | 0 | 152
0:30 | 3607.5 | 937.5 | 2015.5 | 3454 | 782.5 | 95.5 | 166 | 0 | 155 | Date: | 2020-06-08
1:00 | 3593 | 941 | 2101 | 3144 | 814 | 79 | 127 | 0 | 158
1:30 | 3595 | 942.5 | 2123.5 | 2934.5 | 812.5 | 96.5 | 83.5 | 0 | 153 | [7 empty] | Total Energy | 236.8464 | Total Energy Gen 236.846 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.846 MKWHr
2:00 | 3597 | 944 | 2146 | 2725 | 811 | 114 | 40 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 3610 | 944 | 2161.5 | 2571 | 813.5 | 112.5 | 20 | 0 | 144 | [7 empty] | Energy Requirement | 236.8464
3:00 | 3623 | 944 | 2177 | 2417 | 816 | 111 | 0 | 0 | 140
3:30 | 3627 | 944 | 2156 | 2341 | 814.5 | 108 | 0 | 0 | 139 | [6 empty] | Shortage
4:00 | 3631 | 944 | 2135 | 2265 | 813 | 105 | 0 | 0 | 138
4:30 | 3608.5 | 848 | 2112 | 2193.5 | 813.5 | 104.5 | 0 | 0 | 135
5:00 | 3586 | 752 | 2089 | 2122 | 814 | 104 | 0 | 0 | 132
5:30 | 3541 | 751.5 | 2044.5 | 1820.5 | 779.5 | 104 | 0 | 0 | 128
6:00 | 3496 | 751 | 2000 | 1519 | 745 | 104 | 0 | 0 | 124
6:30 | 3533 | 751 | 1949.5 | 1445 | 724 | 103.5 | 0 | 0 | 124 |  |  |  |  | Coal
7:00 | 3570 | 751 | 1899 | 1371 | 703 | 103 | 0 | 0 | 124
7:30 | 3568 | 751 | 1919.5 | 1418 | 702.5 | 104 | 0 | 0 | 114 |  |  |  | Oil |  |  |  | ,
8:00 | 3566 | 751 | 1940 | 1465 | 702 | 105 | 0 | 0 | 104
8:30 | 3661.5 | 779 | 2006.5 | 1474 | 700 | 105.5 | 0 | 0 | 106
9:00 | 3757 | 807 | 2073 | 1483 | 698 | 106 | 0 | 0 | 108
9:30 | 3791 | 875.5 | 2067.5 | 1508.5 | 698 | 106.5 | 0 | 0 | 108
10:00 | 3825 | 944 | 2062 | 1534 | 698 | 107 | 0 | 0 | 108
10:30 | 3788.5 | 944 | 2065.5 | 1568.5 | 698.5 | 108 | 0 | 0 | 105
11:00 | 3752 | 944 | 2069 | 1603 | 699 | 109 | 0 | 0 | 102
11:30 | 3842 | 944 | 2070 | 1666.5 | 700 | 110 | 0 | 0 | 102
12:00 | 3932 | 944 | 2071 | 1730 | 701 | 111 | 0 | 0 | 102
12:30 | 3830.5 | 944 | 2059.5 | 1762 | 726 | 111 | 0 | 0 | 106
13:00 | 3729 | 944 | 2048 | 1794 | 751 | 111 | 0 | 0 | 110
13:30 | 3729 | 944 | 2048 | 1794 | 751 | 111 | 0 | 0 | 110
14:00 | 3729 | 944 | 2048 | 1794 | 751 | 111 | 0 | 0 | 110
14:30 | 3716.5 | 939.5 | 2067.5 | 1972.5 | 750.5 | 109 | 0 | 0 | 117
15:00 | 3704 | 935 | 2087 | 2151 | 750 | 107 | 0 | 0 | 124
15:30 | 3650.5 | 935 | 1956 | 2271.5 | 750 | 105 | 9.5 | 0 | 123
16:00 | 3597 | 935 | 1825 | 2392 | 750 | 103 | 19 | 0 | 122
16:30 | 3508 | 936 | 1790 | 2167 | 749.5 | 102 | 19.5 | 0 | 118
17:00 | 3419 | 937 | 1755 | 1942 | 749 | 101 | 20 | 0 | 114
17:30 | 3388 | 936.5 | 1755.5 | 1816 | 710 | 101 | 20 | 0 | 115
18:00 | 3357 | 936 | 1756 | 1690 | 671 | 101 | 20 | 0 | 116
18:30 | 3403 | 936 | 1822.5 | 1947.5 | 680.5 | 102 | 98.5 | 0 | 136
19:00 | 3449 | 936 | 1889 | 2205 | 690 | 103 | 177 | 0 | 156
19:30 | 3473 | 936 | 1982 | 3127 | 701 | 105 | 232 | 0 | 154
20:00 | 3444 | 936 | 1997 | 3431 | 750 | 105 | 318 | 0 | 156
20:30 | 3431.5 | 936.5 | 1992 | 3582 | 750 | 105.5 | 346 | 0 | 157
21:00 | 3419 | 937 | 1987 | 3733 | 750 | 106 | 374 | 0 | 158
21:30 | 3436.5 | 936.5 | 1960.5 | 3727 | 750 | 107.5 | 348.5 | 0 | 158
22:00 | 3454 | 936 | 1934 | 3721 | 750 | 109 | 323 | 0 | 158
22:30 | 3486 | 935 | 1938.5 | 3742.5 | 751.5 | 109 | 319.5 | 0 | 158
23:00 | 3518 | 934 | 1943 | 3764 | 753 | 109 | 316 | 0 | 158
23:30 | 3570 | 934 | 1936.5 | 3764 | 752 | 110.5 | 260.5 | 0 | 155 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 3622 | 934 | 1930 | 3764 | 751 | 112 | 205 | 0 | 152
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 236.846 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 236.846 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 39 | 39 | 38 | 35 | 35 | 35 | 33 | 33 | 34 | 34 | 34 | 36 | 36 | 36 | 35 | 35 | 33 | 33 |  | 35 | 35 | 35 | 35 | 36 | 36 | 37 | 817745
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 75 | 73 | 70 | 69 | 69 | 70 | 72 | 72 | 73 | 75 | 75 | 75 | 75 | 72 | 68 | 68 | 68 |  | 68 | 70 | 70 | 71 | 73 | 73 | 75 | 1664000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 1944
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 5.2 | 6.1 | 12 | 9.3 | 15.9 | 17 | 15.9 | 18 | 11.1 | 12.4 | 2.3 | 0.7 | [8 empty] | 127170
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 139 | 139 | 138 | 138 | 139 | 139 | 139 | 144 | 139 | 139 | 139 | 139 | 139 | 100 |  | 140 | 140 | 140 | 140 | 140 | 145 | 139 | 3304276
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [14 empty] | 17 | 17 | 17 |  | 83 | 85 | 85 | 85 | 51 | 51 | 0 | 428094
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 15 | 50 | 72 | 72 | 72 | 70 | 70 | 398107
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 225 | 222 | 220 | 224 | 224 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 120 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 140 | 218 | 3724
18 | Kodda 300 MW PP Unit-2 (Summit) | 220 | 60 | 15 | [11 empty] | 2 | 30 | 30 | 30 |  | 42 | 200 | 275 | 300 | 300 | 300 | 300 | 2014799
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 234181
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 782000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 3752000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | [14 empty] | 20 | 20 | 30 | 30 |  | 30 | 30 | 30 | 45 | 80 | 177 | 175 | 578918
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2163888
32 | Ashuganj 50 MW PP | 39 | 39 | 39 | 39 | 0 | 3 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 368640
33 | Ashuganj 225 MW CCPP | 216 | 190 | 191 | 182 | 182 | 181 | 194 | 194 | 201 | 195 | 190 | 203 | 162 | 150 | 151 | 177 | 185 | 190 |  | 188 | 188 | 183 | 188 | 193 | 200 | 208 | 4558000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 240 | 240 | 240 | 250 | 250 | 270 | 365 | 285 | 315 | 290 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6626000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 270 | 270 | 305 | 285 | 320 | 350 | 315 | 315 | 305 | 300 | 300 | 300 |  | 300 | 300 | 305 | 305 | 305 | 300 | 305 | 7333500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 136320
36 | Chandpur 150 MW CCPP | 80 | 87 | 91 | 86 | 80 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 90 | 91 |  | 91 | 91 | 90 | 91 | 91 | 90 | 85 | 2103370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 328 | 331 | 332 | 329 | 330 | 328 | 330 | 331 | 361 | 354 | 348 | 347 | 355 | 342 | 370 | 334 | 330 | 330 |  | 363 | 389 | 376 | 340 | 351 | 333 | 332 | 8348800
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 390 | 390 | 350 | 320 | 350 | 380 | 380 | 380 | 380 | 380 | 420 | 420 | 350 | 320 | 320 |  | 350 | 380 | 380 | 380 | 380 | 380 | 380 | 8913000
41 | Haripur 360MW CCPP(HPL) | 355 | 355 | 355 | 355 | 355 | 303 | 303 | 303 | 350 | 353 | 352 | 348 | 347 | 352 | 353 | 235 | 235 | 263 |  | 336 | 352 | 352 | 352 | 322 | 303 | 303 | 7795000
42 | RPCL 210MW CCPP | 126 | 126 | 134 | 142 | 142 | 142 | 141 | 140 | 139 | 125 | 120 | 113 | 106 | 93 | 96 | 100 | 103 | 103 |  | 103 | 103 | 104 | 104 | 104 | 84 | 84 | 2704760
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 58 | 59 | 60 | 60 | 60 | 59 | 58 | 1424000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 722520
46 | Shajibazar 330 MW CCPP | 243 | 250 | 251 | 243 | 244 | 238 | 246 | 247 | 247 | 246 | 246 | 250 | 245 | 248 | 247 | 240 | 240 | 240 |  | 261 | 261 | 250 | 249 | 241 | 236 | 241 | 5560000
47 | Shahjibazar GTPP Unit- 8 & 9 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 62 | 61 | 61 | 61 | 61 | 61 | 59 | 60 | 59 | 61 | 59 |  | 57 | 59 | 59 | 59 | 61 | 40 | 63 | 1380960
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 |  | 40 | 72 | 70 | 70 | 72 | 70 | 72 | 71 | 72 | 74 | 40 |  | 72 | 74 | 75 | 75 | 75 | 75 | 75 | 1631040
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 71 | 71 |  | 130 | 151 | 150 | 150 | 151 | 151 | 151 | 3373430
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 429000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238680
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 |  |  |  | 2 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 189264
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 48 | 48 | 48 | 48 | 47 | 45 | 45 | 45 | 48 | 48 | 50 | 47 | 47 | 45 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1165600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 568632
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 305 | 295 | 290 | 285 | 300 | 305 | 315 | 310 | 310 | 315 | 315 | 300 | 290 | 280 | 280 | 290 |  | 310 | 340 | 320 | 300 | 305 | 290 | 285 | 7471700
| Bibiyana South 400 MW | [11 empty] | 30 | 40 | 40 | 40 | 40 | 40 | 40 | [8 empty] | 270000
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | [5 empty] | 12 | 17 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 |  | 17 | 17 | 45 | 55 | 55 | 55 | 17 | 768864
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 21 | 21 | 21 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 465888
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 | 22 | 19 | 442116
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 441540
63 | Impoprt (Tripura) | 158 | 148 | 140 | 138 | 132 | 124 | 124 | 104 | 108 | 108 | 102 | 102 | 110 | 114 | 124 | 122 | 114 | 116 |  | 156 | 154 | 156 | 158 | 158 | 158 | 152 | 3154560
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 41 | 41 | 42 | 42 | 29 | 6 | 2 | 2 | 2 | 2 | 7 | 3 | 2 | 4 | 16 | 13 |  | 25 | 27 | 35 | 30 | 30 | 32 | 32 | 530400
65 | Feni 22MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [5 empty] | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 364896
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 140760
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 6 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 760400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 8 | 8 | 13 | 13 | 13 | 21 | 18 | 18 | 15 |  | 15 | 21 | 21 | 21 | 21 | 20 | 20 | 461980
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 |  | 22 | 25 | 30 | 30 | 30 | 30 | 30 | 639720
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 735700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811800
73 | Ghorashal 108MW PP (Regent) | 99 | 100 | 101 | 102 | 102 | 102 | 102 | 95 | 95 | 92 | 91 | 91 | 94 | 96 | 96 | 96 | 96 | 99 |  | 99 | 99 | 99 | 95 | 96 | 99 | 95 | 2293727
| Feni Lanka Power | [21 empty] | 1 | 35 |  |  | 0 | 64980
| Chowmuhani 113 MW | 113 | 113 | 105 | 104 | 104 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 49 | 72 | 105 | 55 | 55 |  | 66 | 106 | 103 | 105 | 93 | 97 | 104 | 1823640
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 99 | 99 | 99 | 99 | 99 | 65 | 7 | 7 | 7 | 7 | 22 | 52 | 75 | 98 | 98 | 98 | 80 | 50 |  | 75 | 100 | 99 | 98 | 99 | 99 | 99 | 1798080
78 | Gazipur 52 MW PP | [6 empty] | 11 | 51 | 33 | 16 | 16 | 16 | 16 | 16 | 17 | 50 | 51 | 25 |  | 25 | 40 | 40 | 43 | 43 | 49 | 52 | 623784
79 | Kodda 150MW PP | [20 empty] | 32 | 98 | 98 | 82 | 82 | 62 | 382560
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 72 | 72 | 16 | [14 empty] | 5 | 24 | 46 | 72 | 72 | 72 | 95 | 765120
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 25 | [19 empty] | 16 | 52 | 52 | 52 | 34 | 324624
| Gazipur 100 MW PP | 89 | 52 |  |  |  | 62 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1777980
| Kaptai 7 MW Solar PP | [5 empty] | 0.2 | 1 | 3.2 | 4.9 | 3.2 | 5.4 | 5.3 | 4.2 | 4.7 | 3.8 | 2.8 | 0.4 | 0.2 | [8 empty] | 402400
| Jodiac Power | [19 empty] | 1 | 34 | 34 | 34 | 34 | 34 | 34 | 173838
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 48 | 48 | 48 | 48 | 48 | 64 | 78 | 78 | 78 | 79 | 79 | 90 |  | 95 | 95 | 80 | 80 | 85 | 95 | 95 | 1948800
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 2 | 50 | 70 | 100 | 100 | 80 | 0 | 396301
86 | Meghnaghat CCPP(Summit) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 275 | 285 | 270 | 280 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 200 | 130 | 5797673
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 75 | 40 | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 45 | 70 | 85 | 100 | 65 | 32 |  | 44 | 100 | 100 | 100 | 100 | 100 | 100 | 1636800
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 69 | 68 | 68 | 68 | 68 | 67 | 66 | 20 | 20 | 20 | [10 empty] | 0 | 887488
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [21 empty] | 10 | 10 | 10 | 10 | 0 | 39120
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1186056
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1038228
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 8 | 8 | 10 | 16 | 16 | 24 | 40 | 40 | 40 | 64 | 93 | 48 | 24 |  | 64 | 93 | 93 | 93 | 93 | 93 | 93 | 1474848
95 | Patenga 50MW PP (Baraka) | [9 empty] | 13 | 18 | 18 | 18 | 21 | 36 | 38 | 38 | 38 |  | 38 | 40 | 42 | 50 | 50 | 50 | 50 | 532320
96 | Chattogram 108 MW PP (ECPV) | 30 | 31 | [13 empty] | 25 | 25 | 24 |  | 28 | 90 | 91 | 97 | 96 | 97 | 97 | 669120
97 | Katpotti 52 MW PP (Sinha) | [20 empty] | 12 | 14 | 42 | 42 | 42 | 41 | 184464
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 15 | 15 | [9 empty] | 3 | 50 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 724039
100 | Manikganj 55 MW PP (Northern) | 17 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 | 55 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 585696
101 | Kushiara 163 MW CCPP (KP) | 130 | 163 | 163 | 163 | 130 | 130 | 110 | 110 | 140 | 140 | 140 | 140 | 163 | 163 | 163 | 100 | 100 | 100 |  | 130 | 163 | 163 | 163 | 130 | 163 | 163 | 3455018
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.5 | 1.1 | 1.6 | 1.9 | 2.1 | 2.1 | 1 |  | 1.5 | 0.8 | 0.5 | 0.2 | [8 empty] | 12550
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 35 | 17 | [5 empty] | 17 | 17 | 22 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 897120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 200 | 200 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 80 | 94 | 100 | 100 | 55 |  | 70 | 200 | 200 | 200 | 200 | 185 | 185 | 3024000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3615840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 70 | 50 | 50 | 50 | 50 | 80 | 80 | 90 | 100 | 100 | 100 | 20 | 20 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 1989120
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | 100 | 10 | 10 | [12 empty] | 10 | 10 | 10 |  | 23 | 50 | 51 | 100 | 100 | 100 | 103 | 685818
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 108 | 109 | 109 | 109 | 109 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2724000
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 210 | 160 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 7125818
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2374080
120 | Eastern Zone Total | 7184 | 6885 | 6713 | 6540 | 6339 | 5845.3 | 5651.7 | 5770.4 | 6097.5 | 6159.4 | 6183.4 | 6357.4 | 6247.1 | 6295.7 | 6447.4 | 6360 | 5853.2 | 5517.1 |  | 6383 | 7310 | 7532 | 7746 | 7646 | 7711 | 7548 | 155436736
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | [18 empty] | 26 | 115 | 115 | 802560
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 70 | 70 | 70 | 70 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 |  | 17 | 73 | 105 | 105 | 105 | 105 | 70 | 1572960
130
131
132
133
| Barisal 110 MW PP (Summit ) | 80 | 80 | 64 | 64 | 64 | 32 | [9 empty] | 13 | 16 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1242048
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 82 | 84 | 83 | 83 | 82 | 83 | 84 | 83 | 72 | 71 | 73 | 74 | 73 | 72 | 73 | 73 | 44 | 12 |  | 12 | 42 | 76 | 82 | 85 | 86 | 84 | 1745282
| Bhola 225 MW CCPP | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 83 |  | 83 | 83 | 83 | 83 | 88 | 88 | 88 | 2161977
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 31 | 31 | 29 | 24 | 21 | 20 | 20 | 19 | 18 | 20 | 19 | 19 | 20 | 18 | 19 | 20 |  | 31 | 24 | 23 | 34 | 36 | 36 | 35 | 587770
141 | Noapara 100 MW PP (Bangla Trac) | 75 | 20 |  |  |  | 11 | 50 | 50 | 63 | 75 | 74 | 73 | 74 | 74 | 74 | 74 | 60 | 30 |  | 30 | 74 | 71 | 74 | 74 | 74 | 74 | 1347840
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 40 | 33 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 941250
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 2 | 3 | 3 |  | 6 | 3 | 6 | 7 | 7 | 2 | 0 | 30464
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 941 | 944 | 944 | 944 | 752 | 751 | 751 | 751 | 807 | 944 | 944 | 944 | 944 | 936 | 935 | 935 | 937 | 936 |  | 936 | 936 | 936 | 937 | 936 | 934 | 934 | 21730181
147 | Bheramara 410 MW CCPP | 290 | 295 | 300 | 345 | 345 | 340 | 345 | 355 | 375 | 360 | 345 | 380 | 350 | 370 | 355 | 345 | 330 | 305 |  | 270 | 255 | 250 | 245 | 230 | 230 | 230 | 7810272
148 | Payra 1320 MW | 664 | 661 | 666 | 663 | 664 | 595 | 553 | 552 | 549 | 549 | 549 | 551 | 601 | 601 | 600 | 601 | 600 | 522 |  | 541 | 552 | 600 | 600 | 600 | 602 | 601 | 14134600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 |  | 149 | 149 | 150 | 150 | 150 | 151 | 150 | 3665300
153 | Baghabari 71 MW GTPP | [11 empty] | 60 |  |  | 40 | 40 | 50 | 65 |  | 65 | 40 | 40 | 40 | 40 |  |  | 400000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 145 | 150 | 156 | 159 | 163 | 162 | 165 | 161 | 147 | 171 | 178 | 164 | 176 | 178 | 170 | 149 | 145 | 143 |  | 142 | 143 | 142 | 139 | 140 | 139 | 142 | 3953073
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 172 | 174 | 179 | 173 | 168 | 169 | 164 | 180 | 203 | 194 | 192 | 192 | 189 | 199 | 192 | 170 | 165 |  | 158 | 161 | 154 | 153 | 151 | 149 | 149 | 4395509
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 352 | 362 | 368 | 337 | 336 | 342 | 367 | 366 | 368 | 369 | 368 | 369 | 367 | 397 | 387 | 405 | 380 | 403 |  | 328 | 285 | 278 | 280 | 279 | 282 | 281 | 8484909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 18 | 18 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 447360
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 268704
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 242028
165 | Amnura 50 MW PP(Sinha) | 40 | 40 | 40 | 40 | 40 | [6 empty] | 24 | 40 | 40 | 40 | 40 | 18 | 18 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 679960
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | [21 empty] | 17 | 45 | 38 | 38 | 0 | 130151
168 | Santahar 50 MW Peaking PP | [22 empty] | 27 | 33 | 33 | 33 | 111087
169 | Natore 52 MW PP (Rajlanka) | [20 empty] | 3 | 43 | 43 | 43 | 43 | 43 | 189120
170 | Chapainawabganj 100 MW Peaking PP | 100 | 40 | [17 empty] | 76 | 100 | 100 | 100 | 100 | 100 | 100 | 676728
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [19 empty] | 70 | 68 | 109 | 113 | 113 | 113 | 580992
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | [5 empty] | 10 | 35 | 50 | 100 | 109 | 109 | 35 | 35 |  | 90 | 109 | 109 | 109 | 109 | 109 | 109 | 1734720
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 10 | [18 empty] | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 67000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 77 | 34 | [8 empty] | 4 | 42 | 54 | 69 | 45 | 35 |  | 46 | 55 | 111 | 113 | 113 | 113 | 113 | 1223040
177 | Sympa Solar Power 8MW | [5 empty] | 0.4 | 1.9 | 3.6 | 5.4 | 6.8 | 7.8 | 7.8 | 7.6 | 6.7 | 6 | 4.3 | 1.6 | 0.5 | [8 empty] | 52824
178
178