## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-19 | Friday
|  | Date (day): | 2020-06-19 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13635.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15071 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-18 | 2020-06-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 67 | 30 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 93 | 96 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 26/06/2020
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 333 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 55 | 83 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 275 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 60 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 83 | 91 | 91 | 91 |  | 9 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 170 | 200 | 220 | 220 |  | 115 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 102 | 93 | 93 |  | 9 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 48 | 51
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 34 | 34 |  | 18 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 194 | 286 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 96 | 114 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 35 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 2300 | 2763 | 3643 | 3965 | 423 | 1330
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 100 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2.5 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 12 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 98 | 99 | 100 | 100 | 130 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 6 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 50 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 38 | 35 | 35
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3.7 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 159 | 307 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 677.2 | 912 | 1427 | 1546 | 390 | 225
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 75 | 90 | 80 | 100 | 35 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 |  | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 198 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 325 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 295 | 360 | 360 |  |  | FGMO
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 38 | 38 | 38 |  | 7 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 30 | 30 | 50 |  | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 195 | 195
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 91 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 96 | 140 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 32 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 105 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1204 | 1525 | 2377 | 2567 | 348 | 88
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 140 | 134 | 150 | 150 | 52 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 60 | 95
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.5 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 187 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 285.5 | 466 | 518.6 | 582 | 52 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 59 | 58 | 90 | 90
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 248 | 251 | 275 | 275 |  | 55 | Engine problem
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 46 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 61 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 77 | 80 | 80
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 16 | 16
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1115 | 1259 | 1340 | 1345 | 0 | 515
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 933 | 933 | 958 | 958
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 360 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 24 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 60 | 85 |  | 15 | Engine problem
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1278 | 1482 | 1788 | 2144 | 0 | 15
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 50 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 28 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 63 | 69 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 76 | 78 | 78 |  | 17 | Engine problem
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 418 | 599 | 660 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 573 | 852 | 886 | 949 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 43 | 43
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 193 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 193 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 408 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 20 | 20 | 21
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 25 | 50 | 50 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 109 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 810 | 995 | 1428 | 1690 | 381 | 19
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 3 | 107 | 70 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3.8 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 155.8 | 256 | 228 | 283 | 170 | 0
| Total |  |  |  |  | 20279 | 19788 | 8398.5 | 10510 | 13635.6 | 15071 | 1764 | 2335
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8024.523 | 10042 | 13028.4201 | 14399.9031
A. |  | 2020-06-18 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10510 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7402.4 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10510 | MW
3 | Day peak Generation : |  |  | 8398.5 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10042 | MW
4 | Evening peak Generation : |  |  | 10510 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 214.5516 | MKWHr | By Solar | 0.056249 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.1986 | MKWHr |  | By Oil: | 40.683 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.2789 | MKWHr |  | By Hydro: | 2.2792 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1764 | MW | Dhaka | 3439 | 3439 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2335 | MW | Chittagong | 891 | 891 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4099 | MW | Khulna | 1324 | 1324 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1138.21 | MMCFD |  |  | Rajshahi | 1138 | 1138 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 153437181.02 | ii) Oil : | Taka | 279357449.72 | Comilla | 943 | 943 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 66449536 | Total | Taka | 499244166.74 | Mymensingh | 885 | 885 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.255 | MKWHr. | Sylhet | 415 | 415 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -151 | MW (E to W) at | 21:00 | hrs | Barisal | 292 | 292 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -152 | MW at | 19:30 | hrs | Rangpur | 715 | 715 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0° C |  |  | Total | 10042 | 10042 |  | 0
B. |  | 2020-06-19 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15071 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
4 | Reserve(Generation end) |  |  |  | 5071 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 204.1404 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7176.3 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.4233 | MKWHr. | ii) HVDC Flow at Peak Time |  | 933 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6323 | MKWHr. | iii) Maximum HVDC Flow : |  | 945 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83 |  | (b) Today: | 83.38 |  | (c) Rule Curve: |  | 80.76
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-06-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 |  | 0 | 380 | 270 | 100 | 95 | 15 | 217 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 19 | 25 | 25 | 28 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 260 | 250 | 189 | 8 | 90 | 37 | 30 | 0 | 30 | 0 | 0 | 0 | 21 | 8 | 32 | 15 | 122 | 140 | 0 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 246 | 61 | 79 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 225 | 0 | 0 | 170 | 0 | 112 | 0 | 30 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 37 | 100 | 0 |  | 936 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 79 | 0 | 192 | 0 | 413 | 0 | 0 | 0 | 105 | 105 | 0 | 0 | 109 | 350 |  | 6395 | 3123 | 9518 | 3473 | 936 | 2218 | 2164 | 499 | 98 | 8 | 122 | 0 | 0 | 82.95
2:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 |  | 0 | 380 | 270 | 70 | 95 | 15 | 215 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 19 | 25 | 28 | 28 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 265 | 255 | 191 | 8 | 91 | 37 | 30 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 32 | 10 | 116 | 139 | 0 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 242 | 61 | 79 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 110 | 0 | 0 | 170 | 0 | 112 | 0 | 10 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 8 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 159 | 0 | 79 | 0 | 164 | 0 | 391 | 0 | 0 | 0 | 105 | 70 | 0 | 0 | 109 | 351 |  | 6189 | 2992 | 9181 | 3419 | 936 | 2186 | 1919 | 499 | 98 | 8 | 116 | 0 | 0 | 82.96
3:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 |  | 0 | 380 | 275 | 50 | 95 | 15 | 215 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 30 | 28 | 33 | 0 | 0 | 62 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 265 | 250 | 192 | 8 | 90 | 37 | 30 | 0 | 30 | 0 | 0 | 0 | 21 | 8 | 32 | 10 | 102 | 140 | 0 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 243 | 62 | 79 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 65 | 0 | 0 | 170 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 79 | 0 | 161 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 387 |  | 6024 | 2842 | 8866 | 3407 | 936 | 2185 | 1595 | 536 | 97 | 8 | 102 | 0 | 0 | 82.97
4:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 353 |  | 0 | 380 | 260 | 15 | 95 | 0 | 217 | 0 | 0 | 0 | 91 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 19 | 25 | 10 | 28 | 33 | 0 | 0 | 62 | 35 | 90 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 265 | 250 | 190 | 8 | 91 | 37 | 30 | 0 | 30 | 0 | 0 | 0 | 21 | 8 | 32 | 10 | 114 | 140 | 0 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 242 | 62 | 76 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 79 | 0 | 159 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 450 |  | 5796 | 2860 | 8656 | 3391 | 936 | 2179 | 1332 | 599 | 97 | 8 | 114 | 0 | 0 | 82.98
5:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 358 |  | 0 | 380 | 250 | 7 | 95 | 0 | 218 | 0 | 0 | 0 | 84 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 25 | 27 | 28 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 260 | 250 | 183 | 8 | 80 | 35 | 30 | 0 | 30 | 0 | 0 | 0 | 21 | 8 | 32 | 10 | 112 | 142 | 0 | 22 | 0 | 60 | 30 | 47 | 46 | 130 | 241 | 62 | 76 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 79 | 0 | 159 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 451 |  | 5586 | 2792 | 8378 | 3373 | 936 | 2120 | 1130 | 601 | 98 | 8 | 112 | 0 | 0 | 82.99
6:00 | 35 | 0 | 0 | 0 | 300 | 53 | 40 | 0 | 309 |  | 0 | 350 | 260 | 7 | 91 | 0 | 170 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 27 | 28 | 33 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 42 | 75 | 0 | 0 | 260 | 250 | 182 | 8 | 85 | 35 | 30 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 32 | 10 | 88 | 141 | 0 | 22 | 0.1 | 60 | 30 | 48 | 46 | 130 | 240 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 0.9 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0.2 | 88 | 0 | 0 | 0 | 26 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 144 | 0 | 79 | 0 | 154 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 |  | 4931.2 | 2756 | 7687.2 | 3236 | 936 | 1941 | 778 | 600 | 99 | 8 | 88 | 1.2 | 0 | 83
7:00 | 35 | 0 | 0 | 0 | 300 | 14 | 40 | 0 | 309 |  | 0 | 320 | 240 | 0 | 15 | 0 | 170 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 28 | 33 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 29 | 75 | 0 | 0 | 270 | 260 | 195 | 8 | 90 | 34 | 30 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 32 | 13 | 78 | 138 | 0 | 22 | 0.3 | 60 | 30 | 47 | 46 | 130 | 241 | 40 | 77 | 0 | 101 | 18 | 0 | 10 | 295 | 24 | 0 | 0 | 2 | 0 | 0 | 8 | 0 | 45 | 1.3 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0.4 | 53 | 0 | 0 | 0 | 26 | 100 | 0 |  | 936 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 146 | 0 | 78 | 0 | 157 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 452 |  | 4672 | 2730.4 | 7402.4 | 3280 | 936 | 1837 | 558 | 602 | 101 | 8 | 78 | 2.4 | 0 | 83.01
8:00 | 35 | 0 | 0 | 0 | 300 | 14 | 40 | 0 | 309 |  | 0 | 320 | 260 | 0 | 15 | 0 | 170 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 28 | 33 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 10 | 75 | 0 | 0 | 285 | 275 | 200 | 8 | 90 | 36 | 30 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 32 | 13 | 90 | 139 | 0 | 22 | 0.6 | 60 | 30 | 48 | 46 | 130 | 248 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 3 | 0 | 45 | 0 | 0 | 8 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0.8 | 105 | 0 | 0 | 0 | 26 | 100 | 0 |  | 936 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 78 | 0 | 170 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 423 |  | 4856.4 | 2744.5 | 7600.9 | 3381 | 936 | 1823 | 687 | 573 | 101 | 8 | 90 | 1.9 | 0 | 83.02
9:00 | 35 | 0 | 0 | 0 | 300 | 70 | 40 | 0 | 356 |  | 0 | 370 | 260 | 0 | 15 | 0 | 170 | 0 | 0 | 0 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 5 | 75 | 0 | 0 | 325 | 265 | 197 | 8 | 90 | 33 | 30 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 52 | 140 | 0 | 22 | 0.1 | 58 | 30 | 48 | 46 | 130 | 252 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 51 | 0 | 0 | 8 | 0 | 72 | 3.6 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 2.1 | 107 | 0 | 0 | 0 | 8 | 100 | 0 |  | 933 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 161 | 0 | 77 | 0 | 172 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 25 | 421 |  | 4990.8 | 2794.6 | 7785.4 | 3357 | 933 | 2008 | 750 | 570 | 101 | 8 | 52 | 6.4 | 0 | 83.05
10:00 | 35 | 0 | 0 | 0 | 300 | 88 | 40 | 0 | 353 |  | 0 | 370 | 250 | 0 | 37 | 0 | 170 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 21 | 5 | 75 | 0 | 0 | 345 | 290 | 205 | 8 | 91 | 30 | 30 | 0 | 27 | 0 | 0 | 0 | 21 | 0 | 25 | 0 | 64 | 140 | 0 | 22 | 0 | 58 | 30 | 45 | 46 | 163 | 253 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 315 | 24 | 5 | 0 | 75 | 0 | 0 | 8 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 4.7 | 108 | 0 | 0 | 0 | 8 | 100 | 0 |  | 933 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 77 | 0 | 169 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 35 | 420 |  | 5328.7 | 2854.2 | 8182.9 | 3457 | 933 | 2081 | 938 | 569 | 101 | 33 | 64 | 6.9 | 0 | 83.04
11:00 | 35 | 0 | 0 | 0 | 300 | 86 | 50 | 0 | 353 |  | 0 | 370 | 270 | 7 | 48 | 0 | 170 | 0 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 21 | 25 | 29 | 33 | 33 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 7 | 0 | 0 | 0 | 0 | 21 | 4 | 75 | 0 | 0 | 325 | 265 | 194 | 8 | 90 | 35 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 20 | 76 | 140 | 0 | 22 | 0 | 58 | 30 | 45 | 46 | 163 | 245 | 40 | 77 | 0 | 100 | 18 | 0 | 9 | 310 | 24 | 5 | 0 | 94 | 0 | 0 | 8 | 0 | 96 | 0.52 | 36 | 0 | 0 | 0 | 115 | 20 | 0 | 3.6 | 156 | 0 | 0 | 0 | 8 | 100 | 0 |  | 932 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 78 | 0 | 173 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 50 | 420 |  | 5480.12 | 2856.8 | 8336.92 | 3393 | 932 | 2110 | 1120 | 569 | 99 | 32 | 76 | 5.92 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 93 | 67 | 0 | 302 |  | 0 | 370 | 230 | 55 | 60 | 0 | 170 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 21 | 25 | 26 | 33 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 6 | 0 | 0 | 0 | 11 | 21 | 7 | 75 | 0 | 0 | 310 | 250 | 185 | 8 | 85 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 20 | 96 | 140 | 0 | 22 | 0.5 | 59 | 30 | 47 | 46 | 130 | 248 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 194 | 0 | 0 | 8 | 0 | 96 | 2.5 | 40 | 0 | 0 | 0 | 115 | 52 | 0 | 3.7 | 159 | 0 | 0 | 0 | 18 | 100 | 0 |  | 933 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 78 | 0 | 162 | 0 | 340 | 0 | 0 | 0 | 0 | 3 | 0 | 3.8 | 70 | 418 |  | 5581.7 | 2816.8 | 8398.5 | 3332 | 933 | 1982 | 1349 | 567 | 98 | 31 | 96 | 10.5 | 0 | 83.06
13:00 | 35 | 0 | 0 | 0 | 300 | 92 | 67 | 0 | 300 |  | 0 | 400 | 270 | 55 | 97 | 0 | 170 | 0 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 9 | 0 | 0 | 0 | 12 | 21 | 13 | 75 | 0 | 0 | 330 | 310 | 193 | 8 | 90 | 37 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 25 | 15 | 110 | 127 | 0 | 22 | 0.6 | 58 | 30 | 47 | 46 | 130 | 245 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 98 | 2.55 | 40 | 0 | 0 | 0 | 115 | 52 | 0 | 1.3 | 161 | 0 | 0 | 0 | 36 | 100 | 0 |  | 932 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 77 | 0 | 198 | 0 | 392 | 0 | 0 | 0 | 0 | 40 | 0 | 3.6 | 85 | 427 |  | 5886.45 | 3019.6 | 8906.05 | 3495 | 932 | 2079 | 1574 | 576 | 98 | 34 | 110 | 8.05 | 0 | 83.07
14:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 275 |  | 0 | 400 | 270 | 55 | 86 | 15 | 170 | 0 | 0 | 0 | 83 | 70 | 0 | 15 | 0 | 0 | 0 | 35 | 55 | 45 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 60 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 6 | 0 | 0 | 0 | 12 | 21 | 14 | 75 | 0 | 0 | 310 | 285 | 188 | 8 | 90 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 25 | 21 | 116 | 115 | 0 | 22 | 1.1 | 58 | 30 | 50 | 46 | 130 | 252 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 295 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 110 | 0 | 40 | 0 | 0 | 0 | 115 | 52 | 0 | 1.3 | 212 | 0 | 0 | 0 | 36 | 100 | 0 |  | 932 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 78 | 0 | 194 | 0 | 385 | 0 | 0 | 0 | 0 | 36 | 0 | 4.2 | 109 | 420 |  | 5980.4 | 2993.2 | 8973.6 | 3421 | 932 | 2049 | 1754 | 569 | 95 | 31 | 116 | 6.6 | 0 | 83.08
15:00 | 35 | 0 | 0 | 0 | 300 | 93 | 64 | 0 | 300 |  | 0 | 400 | 270 | 55 | 86 | 15 | 170 | 0 | 0 | 0 | 83 | 70 | 0 | 30 | 0 | 0 | 0 | 35 | 35 | 55 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 59 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 7 | 0 | 0 | 0 | 12 | 21 | 6 | 90 | 0 | 0 | 320 | 290 | 195 | 8 | 90 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 25 | 21 | 118 | 123 | 0 | 22 | 0.8 | 58 | 30 | 50 | 46 | 130 | 243 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 195 | 0 | 0 | 8 | 0 | 113 | 2.1 | 40 | 0 | 0 | 0 | 115 | 52 | 0 | 1 | 216 | 0 | 0 | 0 | 36 | 100 | 0 |  | 932 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 78 | 0 | 200 | 0 | 389 | 0 | 0 | 0 | 0 | 35 | 0 | 3.2 | 109 | 421 |  | 6049.9 | 3014.2 | 9064.1 | 3470 | 932 | 2073 | 1765 | 570 | 94 | 35 | 118 | 7.1 | 0 | 83.09
16:00 | 35 | 0 | 0 | 0 | 300 | 93 | 66 | 0 | 320 |  | 0 | 400 | 230 | 55 | 96 | 15 | 170 | 0 | 0 | 0 | 80 | 70 | 0 | 30 | 0 | 0 | 0 | 35 | 35 | 55 | 21 | 25 | 30 | 0 | 33 | 0 | 0 | 59 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 8 | 0 | 0 | 0 | 12 | 21 | 2 | 90 | 0 | 0 | 310 | 280 | 183 | 8 | 80 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 20 | 8 | 30 | 21 | 104 | 124 | 0 | 22 | 0.6 | 58 | 30 | 50 | 46 | 130 | 243 | 40 | 77 | 0 | 100 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 195 | 0 | 0 | 22 | 0 | 111 | 1.3 | 10 | 0 | 0 | 0 | 115 | 40 | 0 | 0.6 | 216 | 0 | 0 | 0 | 36 | 100 | 0 |  | 934 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 78 | 0 | 188 | 0 | 338 | 0 | 0 | 0 | 0 | 35 | 0 | 1.2 | 50 | 420 |  | 5906.5 | 2876.2 | 8782.7 | 3368 | 934 | 2024 | 1643 | 569 | 94 | 43 | 104 | 3.7 | 0 | 83.1
17:00 | 35 | 0 | 0 | 0 | 250 | 53 | 35 | 0 | 302 |  | 0 | 350 | 250 | 19 | 96 | 15 | 170 | 0 | 0 | 0 | 50 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 21 | 6 | 90 | 0 | 0 | 270 | 270 | 183 | 8 | 80 | 35 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 21 | 112 | 125 | 0 | 22 | 0.4 | 58 | 30 | 22 | 20 | 130 | 247 | 40 | 30 | 0 | 100 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 195 | 0 | 0 | 32 | 0 | 93 | 0 | 10 | 0 | 0 | 0 | 115 | 35 | 0 | 0.7 | 125 | 0 | 0 | 0 | 8 | 100 | 0 |  | 934 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 64 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 48 | 0 | 181 | 0 | 352 | 0 | 0 | 0 | 0 | 35 | 0 | 1.1 | 35 | 423 |  | 5338.1 | 2834.1 | 8172.2 | 3277 | 934 | 1767 | 1377 | 572 | 96 | 35 | 112 | 2.2 | 0 | 83.12
18:00 | 35 | 0 | 0 | 0 | 250 | 29 | 30 | 0 | 273 |  | 0 | 350 | 270 | 16 | 87 | 15 | 140 | 0 | 0 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 21 | 25 | 30 | 25 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 15 | 90 | 0 | 0 | 270 | 270 | 182 | 8 | 85 | 38 | 30 | 0 | 34 | 0 | 0 | 0 | 21 | 8 | 20 | 18 | 110 | 141 | 0 | 22 | 0 | 58 | 30 | 11 | 10 | 100 | 247 | 40 | 20 | 0 | 100 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 195 | 0 | 0 | 16 | 0 | 79 | 0.2 | 10 | 0 | 0 | 0 | 75 | 35 | 0 | 0.2 | 124 | 0 | 0 | 0 | 8 | 100 | 0 |  | 934 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 66 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 23 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 0 | 35 | 0 | 0.6 | 35 | 423 |  | 5065.4 | 2763.6 | 7829 | 3151 | 934 | 1666 | 1257 | 572 | 96 | 42 | 110 | 1 | 0 | 83.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 250 | 29 | 30 | 0 | 270 |  | 0 | 350 | 270 | 33 | 81 | 16 | 170 | 0 | 0 | 0 | 45 | 40 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 21 | 25 | 20 | 25 | 33 | 0 | 0 | 62 | 35 | 100 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 51 | 0 | 2 | 12 | 21 | 29 | 90 | 0 | 0 | 310 | 290 | 202 | 8 | 90 | 35 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 138 | 134 | 0 | 22 | 0 | 58 | 30 | 41 | 20 | 100 | 260 | 52 | 77 | 0 | 100 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 217 | 0 | 0 | 38 | 0 | 86 | 0 | 50 | 0 | 6 | 0 | 95 | 35 | 0 | 0 | 230 | 0 | 0 | 0 | 33 | 100 | 0 |  | 934 | 0 | 385 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 26 | 40 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 65 | 0 | 173 | 0 | 391 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 80 | 468 |  | 5795 | 3155 | 8950 | 3458 | 934 | 1855 | 1750 | 617 | 97 | 101 | 138 | 0 | 0 | 83.16
19:30 | 35 | 0 | 0 | 0 | 300 | 88 | 30 | 0 | 330 |  | 0 | 400 | 270 | 94 | 97 | 40 | 170 | 0 | 0 | 0 | 92 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 22 | 30 | 33 | 0 | 0 | 62 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 12 | 12 | 21 | 32 | 90 | 0 | 0 | 325 | 280 | 201 | 8 | 90 | 35 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 140 | 135 | 0 | 22 | 0 | 58 | 30 | 50 | 46 | 130 | 252 | 61 | 77 | 0 | 151 | 18 | 0 | 10 | 325 | 24 | 11 | 0 | 280 | 0 | 0 | 100 | 0 | 86 | 0 | 50 | 0 | 50 | 0 | 115 | 35 | 0 | 0 | 301 | 0 | 0 | 0 | 105 | 100 | 0 |  | 934 | 0 | 370 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 68 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 75 | 25 | 197 | 0 | 410 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 500 |  | 6676 | 3445 | 10121 | 3572 | 934 | 2143 | 2502 | 649 | 97 | 84 | 140 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 300 | 92 | 30 | 0 | 330 |  | 0 | 400 | 265 | 91 | 96 | 40 | 170 | 0 | 0 | 0 | 91 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 12 | 12 | 21 | 37 | 90 | 0 | 0 | 300 | 275 | 185 | 8 | 89 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 138 | 133 | 7 | 22 | 0 | 58 | 30 | 50 | 46 | 130 | 248 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 285 | 0 | 0 | 168 | 0 | 104 | 0 | 50 | 0 | 80 | 0 | 115 | 35 | 0 | 0 | 301 | 0 | 0 | 0 | 105 | 100 | 0 |  | 934 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 32 | 68 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 194 | 0 | 77 | 33 | 198 | 0 | 409 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 604 |  | 6752 | 3572 | 10324 | 3516 | 934 | 2143 | 2658 | 753 | 98 | 84 | 138 | 0 | 0 | 83.22
21:00 | 35 | 0 | 0 | 0 | 300 | 96 | 30 | 0 | 333 |  | 0 | 400 | 275 | 83 | 97 | 40 | 200 | 0 | 0 | 0 | 91 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 64 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 12 | 12 | 21 | 38 | 90 | 0 | 0 | 325 | 295 | 198 | 8 | 91 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 140 | 134 | 8 | 22 | 0 | 58 | 30 | 50 | 46 | 163 | 251 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 187 | 0 | 114 | 0 | 50 | 0 | 80 | 0 | 115 | 35 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 933 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 69 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 76 | 50 | 193 | 0 | 408 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 599 |  | 6925 | 3585 | 10510 | 3620 | 933 | 2177 | 2709 | 748 | 99 | 84 | 140 | 0 | 0 | 83.2
22:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 333 |  | 0 | 400 | 275 | 90 | 97 | 40 | 200 | 0 | 0 | 0 | 86 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 64 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 12 | 0 | 21 | 41 | 90 | 0 | 0 | 320 | 290 | 196 | 8 | 90 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 142 | 134 | 29 | 22 | 0 | 58 | 30 | 47 | 46 | 163 | 250 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 250 | 0 | 0 | 170 | 0 | 113 | 0 | 50 | 0 | 80 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 103 | 100 | 0 |  | 934 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 68 | 30 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 198 | 0 | 77 | 70 | 197 | 0 | 408 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 109 | 600 |  | 6871 | 3612 | 10483 | 3599 | 934 | 2219 | 2674 | 749 | 99 | 67 | 142 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 300 | 97 | 67 | 0 | 333 |  | 0 | 400 | 265 | 92 | 97 | 40 | 200 | 0 | 0 | 0 | 86 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 64 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 12 | 0 | 21 | 41 | 90 | 0 | 0 | 310 | 275 | 187 | 8 | 90 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 140 | 141 | 40 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 249 | 62 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 16 | 11 | 0 | 250 | 0 | 0 | 170 | 0 | 113 | 0 | 50 | 0 | 80 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 934 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 33 | 69 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 78 | 70 | 195 | 0 | 395 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 602 |  | 6841 | 3588 | 10429 | 3555 | 934 | 2203 | 2680 | 751 | 99 | 67 | 140 | 0 | 0 | 83.26
24:00 | 35 | 0 | 0 | 0 | 300 | 98 | 67 | 0 | 334 |  | 0 | 400 | 250 | 93 | 97 | 40 | 200 | 0 | 0 | 0 | 91 | 102 | 0 | 15 | 0 | 0 | 0 | 53 | 55 | 35 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 62 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 41 | 90 | 0 | 0 | 310 | 275 | 182 | 8 | 81 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 136 | 142 | 40 | 22 | 0 | 60 | 30 | 47 | 46 | 163 | 247 | 62 | 77 | 0 | 151 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 250 | 0 | 0 | 170 | 0 | 113 | 0 | 50 | 0 | 80 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 945 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 69 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 79 | 30 | 188 | 0 | 365 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 109 | 600 |  | 6825 | 3521 | 10346 | 3531 | 945 | 2168 | 2670 | 749 | 97 | 50 | 136 | 0 | 0 | 76.33
KWH | 769000 | 0 | 0 | 0 | 7002927 | 1873454 | 1303008 | 0 | 7748000 |  | 0 | 8980500 | 6359709 | 1099200 | 1904784 | 392233 | 4525147 | 0 | 0 | 0 | 1663680 | 1467216 | 0 | 120850 | 0 | 0 | 0 | 801000 | 663639 | 324083 | 351720 | 600000 | 647460 | 725200 | 832300 | 0 | 0 | 1435167 | 844000 | 2200000 | 0 | 0 | 0 | 0 | 3359720 | 0 |  | 0 | 122768 | 143397 | 0 | 67200 | 126720 | 477264 | 597120 | 2006858 | 0 | 0 | 7469000 | 6601000 | 4648000 | 200727 | 2082710 | 824328 | 736320 | 0 | 827816 | 0 | 0 | 0 | 494712 | 146700 | 687300 | 420630 | 2632320 | 3188240 | 133440 | 456300 | 5200 | 1398000 | 716040 | 1082400 | 1064304 | 3488890 | 5587000 | 1200672 | 1730880 | 0 | 2926330 | 423000 | 0 | 237960 | 7460500 | 474528 | 170352 | 0 | 3715962 | 0 | 0 | 2023200 | 0 | 2332800 | 12690 | 578880 | 0 | 441600 | 0 | 2608800 | 506676 | 0 | 20880 | 4764764 | 0 | 0 | 0 | 930720 | 2443200 | 0 |  | 22423272 | 0 | 8511840 | 0 | 582720 | 0 | 0 | 0 | 0 | 30208 | 144750 | 1638000 | 473809 | 385920 | 0 | 0 | 0 | 0 | 0 | 545260 | 0 | 0 | 0 | 0 | 0 | 473280 | 267624 | 179910 | 0 | 0 | 3655500 | 0 | 0 | 0 | 0 | 4368591 | 0 | 1788656 | 280320 | 4494055 | 0 | 9258545 | 0 | 0 | 0 | 270432 | 994560 | 0 | 17479 | 1712352 | 10623400 |  | 141431095 | 73120483 | 214551578 | 82604834 | 22423272 | 49593793 | 39841410 | 14278900 | 2279167 | 841633 | 2632320 | 56249 | 0
Fuel Cost | 1261160 | 0 | 0 | 0 | 7773248.97 | 2472959.28 | 2215113.6 | 0 | 7980440 |  | 0 | 9788745 | 7059276.99 | 8342928 | 13123961.76 | 3318291.18 | 4706152.88 | 0 | 0 | 0 | 12527510.4 | 13381009.92 | 0 | 1114237 | 0 | 0 | 0 | 5847300 | 5129929.47 | 3195458.38 | 263790 | 450000 | 0 | 0 | 0 | 0 | 0 | 387495.09 | 227880 | 3982000 | 0 | 0 | 0 | 0 | 5711524 | 0 |  | 0 | 1187166.56 | 1390950.9 | 0 | 584640 | 1003622.4 | 601352.64 | 1773446.4 | 2970149.84 | 0 | 0 | 5527060 | 6601000 | 4276160 | 258937.83 | 2395116.5 | 931490.64 | 1030848 | 0 | 1415565.36 | 0 | 0 | 0 | 628284.24 | 110025 | 1202775 | 315472.5 | 19742400 | 3379534.4 | 1211635.2 | 579501 | 82888 | 2292720 | 1145664 | 1926672 | 1660314.24 | 3977334.6 | 5810480 | 2365323.84 | 3305980.8 | 0 | 5062550.9 | 926370 | 0 | 485438.4 | 7535105 | 355896 | 129467.52 | 0 | 28092672.72 | 0 | 0 | 10520640 | 0 | 22954752 | 148346.1 | 4717872 | 0 | 3113280 | 0 | 23792256 | 4788088.2 | 0 | 0 | 36021615.84 | 0 | 0 | 0 | 7976270.4 | 16271712 | 0 |  | 129158046.72 | 0 | 8937432 | 0 | 4580179.2 | 0 | 0 | 0 | 0 | 316579.84 | 1508295 | 1850940 | 734403.95 | 3766579.2 | 0 | 0 | 0 | 0 | 0 | 4825551 | 0 | 0 | 0 | 0 | 0 | 908697.6 | 414817.2 | 136191.87 | 0 | 0 | 19812810 | 0 | 0 | 0 | 0 | 5766540.12 | 0 | 2682984 | 4768243.2 | 5258044.35 | 0 | 9165959.55 | 0 | 0 | 0 | 2552878.08 | 7717785.6 | 0 | 193142.95 | 12654281.28 | 46636726 |  | 374837256.89 | 274347108.71 | 649184365.6 | 93703418.21 | 129158046.72 | 59733762.81 | 271637201.42 | 66449536 | 615375.09 | 7720248.3 | 19742400 | 424377.05 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 93 | 67 | 0 | 302 |  | 0 | 370 | 230 | 55 | 60 | 0 | 170 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 21 | 25 | 26 | 33 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 6 | 0 | 0 | 0 | 11 | 21 | 7 | 75 | 0 | 0 | 310 | 250 | 185 | 8 | 85 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 20 | 96 | 140 | 0 | 22 | 0.5 | 59 | 30 | 47 | 46 | 130 | 248 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 194 | 0 | 0 | 8 | 0 | 96 | 2.5 | 40 | 0 | 0 | 0 | 115 | 52 | 0 | 3.7 | 159 | 0 | 0 | 0 | 18 | 100 | 0 |  | 933 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 78 | 0 | 162 | 0 | 340 | 0 | 0 | 0 | 0 | 3 | 0 | 3.8 | 70 | 418 |  | 8398.5 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 96 | 30 | 0 | 333 | 0 | 0 | 400 | 275 | 83 | 97 | 40 | 200 | 0 | 0 | 0 | 91 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 64 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 34 | 0 | 12 | 12 | 21 | 38 | 90 | 0 | 0 | 325 | 295 | 198 | 8 | 91 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 21 | 140 | 134 | 8 | 22 | 0 | 58 | 30 | 50 | 46 | 163 | 251 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 187 | 0 | 114 | 0 | 50 | 0 | 80 | 0 | 115 | 35 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 933 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 24 | 69 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 76 | 50 | 193 | 0 | 408 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 109 | 599 |  | 10510 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 0 | 0 | 91 | 93 | 149 | 100 | 0 | 0 | 51 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 22 | 35 | 100 | 0 | 0 | 360 | 360 | 215 | 195 | 90 | 38 | 30 | 0 | 43 | 0 | 50 | 52 | 22 | 8 | 33 | 21 | 173 | 150 | 95 | 22 | 0 | 90 | 30 | 51 | 44 | 163 | 275 | 66 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  |  | 958 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 25 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 50 | 43 | 43 | 35 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 20 | 0 | 0 | 200 | 0 | 78 | 85 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 0 | 0 | 91 | 93 | 100 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 22 | 35 | 80 |  | 0 | 360 | 360 | 215 | 195 | 90 | 38 | 30 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 154 | 150 | 60 | 22 | 1.6 | 90 | 30 | 51 | 44 | 163 | 275 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 88 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  |  | 958 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 43 | 43 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 70 | 0 | 8 | 70 | 660
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 46 | 40 | 0 | 323 | 0 | 0 | 350 | 265 | 0 | 48 | 15 | 180 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 66 | 35 | 100 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 90 | 0 | 0 | 310 | 270 | 182 | 8 | 86 | 38 | 30 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 23 | 15 | 90 | 141 | 0 | 22 | 0.7 | 59 | 30 | 11 | 10 | 100 | 246 | 40 | 10 | 0 | 150 | 18 | 0 | 8 | 280 | 24 | 5 | 0 | 15 | 0 | 0 | 32 | 0 | 64 | 0.6 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0.3 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 507 | 0 | 270 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 144 | 0 | 40 | 30 | 154 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 35 | 529 | 0
199
| Minimum Generation |  | 7402.4 | 7:00
| Highest Generation |  | 10510 | 21:00
| Day Peak Generation |  | 8398.5 | 12:00
| Evening Peak Generation |  | 10510 | 21:00
| HVDC Max Flow |  | 945 | 24:00
| HVDC EvPeak Flow |  | 933 | 21:00
| Load factor L.F |  | 85.06%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-19
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8398.5 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7176.3 | MW
Evening Peak Generation : |  | 10510 | MW Hour : | 21:00 | Available Max Generation : |  | 15071 | MW
E.P. Demand (at gen end) : |  | 10510 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10510 | MW Hour : | 21:00 | Reserve(Generation end) |  | 5071 | MW
Total Gen. (MKWH) : |  | 214.5516 | System Load Factor : | 85.06% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -152 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-19
Actual : | 83.38 | Ft.(MSL) , | Rule curve : | 80.76 | Ft.( MSL )
Gas Consumed : | Total = | 1138.21 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 153437181.02
: |  | Coal : | 66449536 | Oil : | 279357449.72 | Total : | 499244166.74
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3562.6404 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1208.7014 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1082.4587 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 977.916 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 883.826 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 713.2092 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 402.3863 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 183.7273 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 550.0452 |  |  | 0 | 0%
Total | 0 |  | 9564.9105 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-4,5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Baghabari 71 & 100 MW
9) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Barishal 132/33 kV T-1 transformer was under shut down from 10:18 to 11:49 for C/M.
b) Hasnabad 230/132 kV T-1,T-2 & T-3 transformers tripped at 11:40 due to flashing at DS, Y-phase of HT side |  |  |  |  | About 375 MW power interruption occurred under Hasnabad,
and were switched on at 13:33, 16:02 & 12:27 respectively. |  |  |  |  | Shitalakhya,Lalbgh,Kamrangichor S/S areas from 11:40 to 11:58.
c) Madaripur 132/33 kV T-3 transformer was under shut down from 13:10 to 15:14 for 33 kV feeder maintenance.
d) Daudkandi-Comilla(N) 132 kV Ckt-1 transformer was under shut down from 10:06 to 13:15 for D/W.
e) Savar-Manikganj(160 MW) P/S 132 kV Ckt-2 was under shut down from 12:15 to 13:07 for C/M.
f) Comilla(N)-Choddagram 132 kV Ckt-2 tripped at 16:34 showing Dist. B,C-Phase, Dir. O/C, ARC at Comilla(N)
end and Dist. Z1,L2,L3 at Choddagram end and was switched on at 16:53.
g) Ashuganj-Sirajganj 230 kV Ckt-2 was switched on at 18:01.
h) Hasnabad 132/33 kV T-1 transformer was switched on at 18:24.
i) Shympur-Meghnaghat 230 kV Ckt-2 was under shut down from 23:56 to 00:39(19/06/2020) for C/M.
j) Bheramara HVDC Block-1 was under shut down from 06:16(19/6/2020) to 11:20 for C/M.
k) Natore 33 kV Bus of T-1 & T-2 132/33 kV transformer was under shut down from 06:08(19/6/2020) to 09:14 |  |  |  |  | About 45 MW power interruption occurred under Natore S/S area
for D/W. |  |  |  |  | from 06:08(19/6/2020) to 09:14.
l) Rajshahi 132 kV main Bus was under shut down from 05:04(19/06/2020) to 08:41 for C/M. |  |  |  |  | About 90 MW power interruption occurred under Rajshahi S/S area
from 05:04(19/06/2020) to 08:41.
m) Kustia 132 kV Bus-A & B was shut down at 06:35(19/6/2020) for D/W. |  |  |  |  | About 120 MW power interruption occurred under Jashore,Benapul,Jhenaidah,
Chuadanga,Magura,Norail,Bottail S/S areas from 06:35(19/06/2020) to till now.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 769000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7002927
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 30 | 1303008 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 1873454 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 333 | 7748000 | Frequency Control.
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8980500 | Frequency Control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 83 | 1099200
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6359709 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1904784
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 392233 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 120850 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 351720
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 1663680 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 200 | 4525147 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1467216
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 801000
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 663639
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 324083 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1247460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 725200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 832300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 3715962
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 114 | 2332800 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 35 | 506676 | Low demand
| Dhaka area Total |  |  |  | 5791 | 2763 | 56710548
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2200000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 12690
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 126720 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 99 | 2279167 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3359720 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 122768
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 143397 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 578880 | Low demand
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 477264
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 597120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 67200 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20880
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 4764764
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2443200
| Chattogram area Total |  |  |  | 2266 | 912 | 17193770
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 90 | 2006858 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4648000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7469000 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 6601000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 824328 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 736320 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 827816 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 441600 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2082710
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 494712
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 146700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2632320
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 687300
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 420630 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 930720 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1525 | 31150741
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 134 | 3188240 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 456300
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 133440 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5200
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 187 | 2023200
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2608800 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 466 | 8415180
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1398000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 716040
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3488890
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 251 | 5587000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1082400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 1064304
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 170352
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1200672 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1730880 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 2926330
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 474528
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7460500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237960
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1259 | 27960856
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 933 | 22423272
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 582720
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 30208 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8511840 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 24 | 144750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 280320 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 270432
| Khulna Area Total |  |  |  | 2284 | 1482 | 32243542
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 385920 | Low demand
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 473809
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 69 | 1638000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1788656 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 599 | 10623400
| Barisal Area Total |  |  |  | 1054 | 852 | 14909785
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4368591 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 193 | 4494055 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 9258545 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 473280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 267624
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 179910
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 545260 | Low demand
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 0 | Reserve
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 109 | 1712352
| Rajshahi Area Total |  |  |  | 2183 | 995 | 21299617
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3655500 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 994560
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 17479
| Rangpur Area Total |  |  |  | 605 | 256 | 4667539
| Total |  |  |  | 19788 | 10510 | 214551578
| Eastern Grid Total |  |  |  | 13662 | 6925 | 141431095
| Western Grid Total |  |  |  | 6126 | 3585 | 73120483
| National Grid Total |  |  |  | 19788 | 10510 | 214551578
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-18
(a) ENTIRE EASTERN GRID : |  | 6573 | MW | (b) ENTIRE WESTERN GRID : |  | 3469 | MW
i) Dhaka area |  | 3439 | MW | i) Khulna area |  | 1324 | MW
ii) Chittagong area |  | 891 | MW | ii) Rajshahi area |  | 1138 | MW
iii) Comilla area |  | 943 | MW | iii) Barisal area |  | 292 | MW
iv) Mymensingh area |  | 885 | MW | iv) Rangpur area |  | 715 | MW
v) Sylhet area |  | 415 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10042 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 15:00 | Sherpur | 100 | 22:00 | Benapol | 44 | 19:30
Munsiganj | 102 | 19:30 | Srimongal | 47 | 21:00 | Jhenida | 102 | 19:30
Sonargaon | 63 | 1:00 | Shahjibazar | 92 | 21:00 | Bottail | 120 | 20:00
Shyampur | 172 | 1:00 | Fenchuganj | 33 | 19:30 | G.K Project | 51 | 21:00
Bhulta | 170 | 0:00 | Kulawara | 42 | 19:30 | Faridpur | 165 | 0.875
Madanganj | 38 | 8:00 | Sylhet | 105 | 20:00 | Madaripur | 85 | 0.91667
Shitalakhya | 90 | 16:00 | Chatak | 25 | 20:00 | Sariatpur | 54 | 21:00
Rahim steel | 13 | 15:00 | Sunamganj | 36 | 19:30 | Gopalganj | 82 | 19:30
Matuail | 83 | 14:00 | Biani Bazar | 50 | 20:00 | Bagerhat | 78 | 0.83333
Ghorasal | 72 | 21:00 | Comilla (S) | 142 | 22:00 | Mongla | 42 | 11:00
Narsingdi | 142 | 21:00 | Comilla(N) | 75 | 22:00 | Satkhira | 97 | 0.91667
Haripur (SBU) | 94 | 12:00 | Chandpur | 88 | 22:00 | Gallamari | 36 | 12:00
Ullon | 50 | 14:00 | Feni | 101 | 20:00 | Magura | 46 | 0.8125
Hasnabad | 200 | 10:00 | Chowmuhani | 146 | 21:00 | Norail | 35 | 19:30
Magbazar | 94 | 14:00 | Ashuganj | 52 | 22:00 | Chuadanga | 83 | 20:00
Maniknagar | 96 | 12:00 | Daudkandi | 126 | 22:00 | Barisal(N) | 37 | 0.91667
Bangabhaban | 28 | 12:00 | B.Baria | 130 | 21:00 | Barisal (S) | 84 | 0.83333
Narinda | 100 | 13:00 | Ramganj | 99 | 19:00 | Patuakhali | 97 | 0.91667
Dhanmondi | 141 | 14:00 | Chaddagram | 24 | 19:30 | Bhandaria | 46 | 20:00
Lalbag | 79 | 11:00 | PHP | 8 | 18:30 | Borhan Uddin | 37 | 21:00
Madartek | 62 | 21:00 | Madunaghat | 49 | 13:00 | Ishurdi | 55 | 20:00
Dhaka University |  |  | Hathazari | 82 | 0.79167 | Ruppur Paromanobik | 2 | 10:00
Mirpur | 89 | 14:00 | Khulshi | 162 | 0.45833 | Natore | 118 | 21:00
Kalyanpur | 75 | 22:00 | Halishahar | 109 | 0.45833 | Bogra | 150 | 22:00
Gulshan | 118 | 14:00 | Baraulia | 133 | 0.25 | Noagaon | 119 | 24:00
Uttara | 76 | 16:00 | Sikalbaha | 27 | 0.8125 | Rajshahi | 126 | 21:00
Uttara New | 20 | 14:00 | Dohazari | 68 | 0.79167 | Rajshahi New | 10 | 21:00
Kamrangirchar | 75 | 11:00 | Cox'sbazar | 73 | 0.875 | C.Nawabganj | 68 | 21:00
Savar | 118 | 12:00 | Chandraghona | 26 | 0.8125 | Amnura | 38 | 21:00
Bhasantec | 136 | 14:00 | Kaptai | 4 | 0.79167 | Pabna | 114 | 19:30
Agargaon | 55 | 14:00 | A. Khaer Stl. | 22 | 0.20833 | Shahjadpur | 94 | 20:00
Satmosjid | 92 | 15:00 | Bakulia | 86 | 0.5 | Serajganj | 89 | 21:00
Tongi | 130 | 0.66667 | Julda | 13 | 0.041667 | Niyamatpur | 51 | 19:30
Kabirpur | 202 | 12:00 | TK chemical | 22.6 | 0.79167 | Joypurhat | 40 | 21:00
Basundhara | 95 | 14:00 | Modern Steel | 14 | 0.95833 | Sherpur(Bogura) | 44 | 22:00
Manikganj | 60 | 21:00 | Shahmirpur | 22 | 0.875 | Mohastangor | 53 | 21:00
Joydevpur | 145 | 19:30 | Khagrachhari | 20 | 0.875 | Rangpur | 136 | 20:00
New Tongi | 94 | 12:00 | Matarbari | 23 | 0.875 | Lalmonirhat | 48 | 21:00
Kodda | 202 | 15:00 | Baroiar Hat | 28 | 0.79167 | Saidpur | 97 | 20:00
Dhamrai | 86 | 19:30 | Rangamati | 10 | 0.79167 | Purbasadipur | 103 | 20:00
Rajendrapur | 82 | 15:00 | Abul Khair 230 | 134 | 0 | Thakurgaon | 70 | 19:30
Valuka | 84 | 15:00 | BSRM | 156 | 0.375 | Palashbari | 113 | 21:00
Tangail | 181 | 21:00 | GPH Ispat | 15 | 0.58333 | Barapukuria | 47 | 20:00
Mymensing | 197 | 21:00 | Goalpara | 23 | 19:30 | Panchagar | 42 | 19:30
Kishorganj | 128 | 22:00 | Central s/s | 78 | 19:30 | Joldhaka | 22 | 20:00
Netrokona | 102 | 21:00 | Noapara | 52 | 19:30 | Kurigram | 51 | 20:00
Jamalpur | 117 | 21:00 | Jessore | 104 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 396 | 12:00 | 389 | 9:00 | Kaliakoir | 377 | 0.20833 | 366 | 0.58333
| Bheramara | 403 | 7:00 | 396 | 22:00 | Bhulta | 390 | 24:00 | 377 | 0.41667
| Ashuganj(N) | 395 | 24:00 | 383 | 10:00 | Gopalganj | 411 | 0.66667 | 390 | 0.875
| Payra | 417 | 9:00 | 403 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 23:00 | 230 | 1:00 | Comilla (N) | 234 | 19:30 | 227 | 7:00
| Ishurdi | 235 | 5:00 | 223 | 21:00 | Hathazari | 226 | 20:00 | 217 | 10:00
| Ashuganj | 235 | 1:00 | 230 | 7:00 | Megnaghat | 232 | 21:00 | 225 | 9:00
| Serajganj | 233 | 8:00 | 225 | 21:00 | Fenchuganj | 237 | 6:00 | 235 | 7:00
| Baghabari | 239 | 18:00 | 232 | 1:00 | Siddhirganj | 231 | 4:00 | 222 | 10:00
| Barapukuria | 232 | 6:00 | 221 | 8:00 | Maniknagar | 229 | 4:00 | 221 | 10:00
| Bogra | 228 | 12:00 | 214 | 21:00 | Agargaon | 227 | 3:00 | 218 | 10:00
| Rajshahi | 233 | 17:00 | 217 | 21:00 | Barisal | 246 | 7:00 | 232 | 21:00
| Khulna South | 227 | 6:00 | 210 | 1:00 | AKSML | 224 | 20:00 | 214 | 10:00
| Rampura | 225 | 1:00 | 220 | 11:00 | BSRM | 227 | 20:00 | 215 | 9:00
| Haripur | 229 | 24:00 | 221 | 10:00 | Bibiyana | 236 | 23:00 | 232 | 10:00
| Hasnabad | 229 | 23:00 | 220 | 10:00 | Bhulta | 232 | 5:00 | 223 | 10:00
| Shyampur | 225 | 1:00 | 217 | 10:00 | Ashuganj (S) | 235 | 19:30 | 229 | 13:00
| Aminbazar | 229 | 24:00 | 219 | 13:00 | Kaliakoir | 231 | 24:00 | 221 | 10:00
| Tongi | 226 | 4:00 | 216 | 9:00 | GPH | 224 | 24:00 | 214 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 132 | 4:00 | 124 | 10:00 | Hathazari | 135 | 0.83333 | 129 | 0.41667
| Munsiganj | 134 | 3:00 | 125 | 10:00 | Khulshi | 133 | 0.79167 | 127 | 0.375
| Sonargaon | 131 | 20:00 | 122 | 13:00 | Halishahar | 136 | 0.83333 | 128 | 0.375
| Shyampur | 136 | 3:00 | 130 | 10:00 | Baraulia | 135 | 0.83333 | 130 | 0.29167
| Bhulta | 125 | 19:30 | 120 | 11:00 | Sikalbaha | 135 | 19:00 | 130 | 0.29167
| Madanganj | 133 | 1:00 | 130 | 10:00 | Dohazari | 135 | 18:30 | 126 | 0.29167
| Shitalakhya | 141 | 0:00 | 127 | 13:00 | Cox'sbazar | 128 | 0.70833 | 118 | 0.083333
| Rahim steal | 132 | 19:00 | 126 | 10:00 | Chandraghona | 136 | 0.8125 | 130 | 0.41667
| Matuail | 132 | 4:00 | 124 | 10:00 | Kaptai | 134 | 1:00 | 128 | 0.20833
| Ghorasal | 138 | 0:00 | 136 | 1:00 | A. Khaer Stl. | 134 | 0.8125 | 128 | 10:00
| Narsinghdi | 127 | 18:30 | 121 | 10:00 | Bakulia | 134 | 0.79167 | 127 | 0.41667
| Haripur (SBU) | 132 | 5:00 | 125 | 11:00 | Julda | 135 | 0.79167 | 129 | 0.375
| Ullon | 136 | 3:00 | 130 | 10:00 | TK Chemical | 135 | 0.83333 | 130 | 6:00
| Hasnabad | 138 | 24:00 | 128 | 11:00 | Modern Steel | 134 | 0.83333 | 128 | 0.41667
| Magbazar | 135 | 1:00 | 130 | 10:00 | Shahmirpur | 134 | 0.8125 | 130 | 0.29167
| Maniknagar | 134 | 3:00 | 128 | 11:00 | Khagrachhari | 134 | 0.8125 | 130 | 0.375
| Bangabhaban | 134 | 3:00 | 128 | 11:00 | Matarbari | 130 | 0.625 | 122 | 0.041667
| Narinda | 134 | 3:00 | 128 | 11:00 | Baroiar Hat | 131 | 0.29167 | 126 | 0.041667
| Dhanmondi | 136 | 3:00 | 130 | 10:00 | Rangamati | 134 | 0.79167 | 129 | 10:00
| Lalbag | 135 | 3:00 | 121 | 13:00:00 PM | Goalpara S/S | 137 | 6:00 | 126 | 1:00
| Madartek | 136 | 3:00 | 130 | 10:00 | Khulna Central S/S | 137 | 0.25 | 126 | 1:00
| Dhaka University |  |  |  |  | Noapara | 134 | 6:00 | 123 | 1:00
| Mirpur | 131 | 5:00 | 124 | 14:00 | Jessore | 131 | 6:00 | 118 | 21:00
| Kalyanpur | 132 | 5:00 | 125 | 14:00 | Benapol | 131 | 2:00 | 118 | 21:00
| Gulshan | 136 | 6:00 | 130 | 13:00 | Jhenida | 127 | 0.20833 | 110 | 21:00
| Uttara | 131 | 5:00 | 123 | 10:00 | Bottail | 132 | 6:00 | 121 | 21:00
| Uttara New | 131 | 5:00 | 121 | 14:00 | G.K Project | 139 | 0.70833 | 131 | 21:00
| Kamrangirchar | 134 | 1:00 | 121 | 14:00 | Faridpur | 133 | 12:00 | 123 | 21:00
| Savar | 130 | 5:00 | 123 | 14:00 | Madaripur | 138 | 0.25 | 130 | 19:30
| Bhasantec | 129 | 5:00 | 122 | 13:00 | Shariyatpur S/S | 138 | 0.29167 | 125 | 21:00
| Agargaon | 130 | 5:00 | 124 | 13:00 | Gopalganj | 138 | 6:00 | 125 | 21:00
| Satmosjid | 130 | 5:00 | 123 | 13:00 | Bagerhat | 135 | 0.25 | 124 | 19:00
| Tongi | 134 | 0.8125 | 127 | 9:00 | Mongla | 131 | 0.70833 | 117 | 18:30
| Kabirpur | 132 | 23:00 | 124 | 14:00 | Satkhira | 137 | 0.25 | 123 | 21:00
| Basundhara | 135 | 21:00 | 130 | 9:00 | Gallamari | 138 | 6:00 | 128 | 1:00
| Manikganj | 135 | 24:00 | 128 | 9:00 | Magura | 126 | 0.25 | 108 | 21:00
| Joydevpur | 140 | 6:00 | 135 | 13:00 | Norail | 125 | 0.25 | 105 | 21:00
| New Tongi | 133 | 1904-01-02 | 124 | 10:00 | Chuadanga | 123 | 18:00 | 100 | 21:00
| Kodda | 129 | 4:00 | 117 | 0.33333 | Barisal(N) | 140 | 7:00 | 130 | 19:00
| Dhamrai | 130 | 24:00 | 125 | 15:00 | Barisal (S) | 138 | 0.29167 | 129 | 21:00
| Rajendrapur | 128 | 4:00 | 116 | 11:00 | Patuakhali | 137 | 0.29167 | 123 | 19:30
| Valuka | 127 | 17:00 | 117 | 21:00 | Bhandaria | 138 | 7:00 | 122 | 23:00
| Tangail | 132 | 18:00 | 126 | 21:00 | Ishurdi | 138 | 17:00 | 129 | 21:00
| Mymensing | 129 | 5:00 | 119 | 21:00 | Ruppur Paromanobik | 135 | 6:00 | 131 | 19:00
| Kishorganj | 129 | 10:00 | 121 | 21:00 | Natore | 134 | 17:00 | 123 | 21:00
| Netrokona | 127 | 5:00 | 116 | 21:00 | Bogra | 132 | 14:00 | 124 | 21:00
| Jamalpur | 134 | 19:30 | 123 | 7:00 | Noagaon | 129 | 17:00 | 117 | 21:00
| Sherpur | 133 | 4:00 | 124 | 0.625 | Rajshahi | 133 | 17:00 | 123 | 21:00
| Srimongal | 138 | 4:00 | 134 | 0.875 | Rajshahi New | 133 | 17:00 | 123 | 21:00
| Shahjibazar | 137 | 6:00 | 131 | 0.875 | C.Nawabganj | 132 | 17:00 | 119 | 21:00
| Fenchuganj | 135 | 5:00 | 133 | 0.041667 | Amnura | 133 | 17:00 | 120 | 21:00
| Khulawara | 135 | 6:00 | 133 | 0.041667 | Pabna | 134 | 17:00 | 126 | 21:00
| Sylhet | 134 | 6:00 | 132 | 0.083333 | Shahjadpur | 139 | 17:00 | 132 | 21:00
| Chatak | 133 | 5:00 | 131 | 1:00 | Serajganj | 135 | 17:00 | 126 | 21:00
| Sunamganj | 131 | 6:00 | 129 | 0.041667 | Niyamatpur | 128 | 12:00 | 115 | 21:00
| Biani Bazar | 133 | 6:00 | 129 | 0.041667 | Joypurhat | 130 | 18:00 | 116 | 21:00
| Comilla(s) | 128 | 6:00 | 120 | 19:30 | Sherpur(Bogura) | 133 | 17:00 | 124 | 21:00
| Comilla(n) | 135 | 12:00 | 133 | 14:00 | Mohastangor | 131 | 17:00 | 121 | 21:00
| Chandpur | 132 | 8:00 | 127 | 18:00 | Rangpur | 128 | 17:00 | 118 | 21:00
| Feni | 130 | 19:00 | 124 | 22:00 | Lalmonirhat | 123 | 17:00 | 111 | 21:00
| Chowmuhani | 130 | 9:00 | 124 | 22:00 | Saidpur | 128 | 17:00 | 117 | 21:00
| Ashuganj | 137 | 6:00 | 132 | 21:00 | Purbasadipur | 126 | 17:00 | 110 | 21:00
| Daudkandi | 131 | 19:00 | 125 | 11:00 | Thakurgaon | 124 | 17:00 | 112 | 20:00
| B.Baria | 133 | 8:00 | 127 | 22:00 | Palashbari | 125 | 15:00 | 115 | 21:00
| Ramganj | 128 | 7:00 | 119 | 19:30 | Barapukuria | 132 | 16:00 | 123 | 21:00
| Chaddagram | 132 | 7:00 | 129 | 14:00 | Panchagar | 124 | 17:00 | 108 | 1:00
| PHP | 130 | 8:00 | 126 | 1:00 | Joldhaka | 127 | 17:00 | 112 | 21:00
| Madanhat | 136 | 19:00 | 131 | 10:00 | Kurigram | 126 | 17:00 | 110 | 21:00

## L-Curve
Date | 2020-06-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 14 | 6825 | 3521 | 10346 |  |  |  | QF-LDC-12
0:30 | 8.5 | 6610 | 3322 | 9932 | Date: | 2020-06-18
1:00 | 3 | 6395 | 3123 | 9518
1:30 | 18.5 | 6292 | 3057.5 | 9349.5
2:00 | 34 | 6189 | 2992 | 9181
2:30 | 31 | 6106.5 | 2917 | 9023.5 | [5 empty] | Gen. at Eve. Peak | 10510 | 9500 MW (19:30 )
3:00 | 28 | 6024 | 2842 | 8866 | [6 empty] | 21:00
3:30 | 56.5 | 5910 | 2851 | 8761 | [5 empty] | Gen. at Day Peak | 8398.5 | 7952.5 MW (12:00 )
4:00 | 85 | 5796 | 2860 | 8656 | [6 empty] | 12:00
4:30 | 112.5 | 5691 | 2826 | 8517 | [5 empty] | Highest Generation | 10510
5:00 | 140 | 5586 | 2792 | 8378 | [6 empty] | 21:00
5:30 | 233.5 | 5258.6 | 2774 | 8032.6
6:00 | 327 | 4931.2 | 2756 | 7687.2
6:30 | 363.5 | 4801.6 | 2743.2 | 7544.8
7:00 | 400 | 4672 | 2730.4 | 7402.4
7:30 | 365.5 | 4764.2 | 2737.45 | 7501.65
8:00 | 331 | 4856.4 | 2744.5 | 7600.9
8:30 | 342.5 | 4923.6 | 2769.55 | 7693.15
9:00 | 354 | 4990.8 | 2794.6 | 7785.4
9:30 | 398 | 5159.75 | 2824.4 | 7984.15
10:00 | 442 | 5328.7 | 2854.2 | 8182.9
10:30 | 388.5 | 5404.41 | 2855.5 | 8259.91
11:00 | 335 | 5480.12 | 2856.8 | 8336.92
11:30 | 297.5 | 5530.91 | 2836.8 | 8367.71
12:00 | 260 | 5581.7 | 2816.8 | 8398.5
12:30 | 270 | 5734.075 | 2918.2 | 8652.275
13:00 | 280 | 5886.45 | 3019.6 | 8906.05
13:30 | 296 | 5933.425 | 3006.4 | 8939.825
14:00 | 312 | 5980.4 | 2993.2 | 8973.6
14:30 | 333.5 | 6015.15 | 3003.7 | 9018.85
15:00 | 355 | 6049.9 | 3014.2 | 9064.1
15:30 | 313.5 | 5978.2 | 2945.2 | 8923.4
16:00 | 272 | 5906.5 | 2876.2 | 8782.7
16:30 | 334 | 5622.3 | 2855.15 | 8477.45
17:00 | 396 | 5338.1 | 2834.1 | 8172.2
17:30 | 362 | 5201.75 | 2798.85 | 8000.6
18:00 | 328 | 5065.4 | 2763.6 | 7829
18:30 | 235 | 5430.2 | 2959.3 | 8389.5
19:00 | 142 | 5795 | 3155 | 8950
19:30 | 152 | 6676 | 3445 | 10121
20:00 | 138 | 6752 | 3572 | 10324 |  |  |  | Executive Engineer
20:30 | 144.5 | 6838.5 | 3578.5 | 10417 |  |  |  | Network Operation Division
21:00 | 151 | 6925 | 3585 | 10510
21:30 | 120.5 | 6898 | 3598.5 | 10496.5
22:00 | 90 | 6871 | 3612 | 10483 |  |  |  |  | Page 6 of 7
22:30 | 53 | 6856 | 3600 | 10456
23:00 | 16 | 6841 | 3588 | 10429
23:30 | 15 | 6833 | 3554.5 | 10387.5
24:00 | 14 | 6825 | 3521 | 10346
9500 MW (19:30 )
7952.5 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-18 |  | Energy | 214551578
[10 empty] | 2020-06-18 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3531 | 945 | 2168 | 2680 | 749 | 97 | 50 | 0 | 136
0:30 | 3502 | 940.5 | 2193 | 2422 | 624 | 97.5 | 29 | 0 | 129 | Date: | 2020-06-18
1:00 | 3473 | 936 | 2218 | 2164 | 499 | 98 | 8 | 0 | 122
1:30 | 3446 | 936 | 2202 | 2041.5 | 499 | 98 | 8 | 0 | 119 | [7 empty] | Total Energy | 214.5516 | Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
2:00 | 3419 | 936 | 2186 | 1919 | 499 | 98 | 8 | 0 | 116 | [7 empty] | Energy not Served | 0
2:30 | 3413 | 936 | 2185.5 | 1757 | 517.5 | 97.5 | 8 | 0 | 109 | [7 empty] | Energy Requirement | 214.5516
3:00 | 3407 | 936 | 2185 | 1595 | 536 | 97 | 8 | 0 | 102
3:30 | 3399 | 936 | 2182 | 1463.5 | 567.5 | 97 | 8 | 0 | 108 | [6 empty] | Shortage
4:00 | 3391 | 936 | 2179 | 1332 | 599 | 97 | 8 | 0 | 114
4:30 | 3382 | 936 | 2149.5 | 1231 | 600 | 97.5 | 8 | 0 | 113
5:00 | 3373 | 936 | 2120 | 1130 | 601 | 98 | 8 | 0 | 112
5:30 | 3304.5 | 936 | 2030.5 | 954 | 600.5 | 98.5 | 8 | 0 | 100
6:00 | 3236 | 936 | 1941 | 778 | 600 | 99 | 8 | 0 | 88
6:30 | 3258 | 936 | 1889 | 668 | 601 | 100 | 8 | 0 | 83 |  |  |  |  | Coal
7:00 | 3280 | 936 | 1837 | 558 | 602 | 101 | 8 | 0 | 78
7:30 | 3330.5 | 936 | 1830 | 622.5 | 587.5 | 101 | 8 | 0 | 84 |  |  |  | Oil |  |  |  | ,
8:00 | 3381 | 936 | 1823 | 687 | 573 | 101 | 8 | 0 | 90
8:30 | 3369 | 934.5 | 1915.5 | 718.5 | 571.5 | 101 | 8 | 0 | 71
9:00 | 3357 | 933 | 2008 | 750 | 570 | 101 | 8 | 0 | 52
9:30 | 3407 | 933 | 2044.5 | 844 | 569.5 | 101 | 20.5 | 0 | 58
10:00 | 3457 | 933 | 2081 | 938 | 569 | 101 | 33 | 0 | 64
10:30 | 3425 | 932.5 | 2095.5 | 1029 | 569 | 100 | 32.5 | 0 | 70
11:00 | 3393 | 932 | 2110 | 1120 | 569 | 99 | 32 | 0 | 76
11:30 | 3362.5 | 932.5 | 2046 | 1234.5 | 568 | 98.5 | 31.5 | 0 | 86
12:00 | 3332 | 933 | 1982 | 1349 | 567 | 98 | 31 | 0 | 96
12:30 | 3413.5 | 932.5 | 2030.5 | 1461.5 | 571.5 | 98 | 32.5 | 0 | 103
13:00 | 3495 | 932 | 2079 | 1574 | 576 | 98 | 34 | 0 | 110
13:30 | 3495 | 932 | 2079 | 1574 | 576 | 98 | 34 | 0 | 110
14:00 | 3495 | 932 | 2079 | 1574 | 576 | 98 | 34 | 0 | 110
14:30 | 3482.5 | 932 | 2076 | 1669.5 | 573 | 96 | 34.5 | 0 | 114
15:00 | 3470 | 932 | 2073 | 1765 | 570 | 94 | 35 | 0 | 118
15:30 | 3419 | 933 | 2048.5 | 1704 | 569.5 | 94 | 39 | 0 | 111
16:00 | 3368 | 934 | 2024 | 1643 | 569 | 94 | 43 | 0 | 104
16:30 | 3322.5 | 934 | 1895.5 | 1510 | 570.5 | 95 | 39 | 0 | 108
17:00 | 3277 | 934 | 1767 | 1377 | 572 | 96 | 35 | 0 | 112
17:30 | 3214 | 934 | 1716.5 | 1317 | 572 | 96 | 38.5 | 0 | 111
18:00 | 3151 | 934 | 1666 | 1257 | 572 | 96 | 42 | 0 | 110
18:30 | 3304.5 | 934 | 1760.5 | 1503.5 | 594.5 | 96.5 | 71.5 | 0 | 124
19:00 | 3458 | 934 | 1855 | 1750 | 617 | 97 | 101 | 0 | 138
19:30 | 3572 | 934 | 2143 | 2502 | 649 | 97 | 84 | 0 | 140
20:00 | 3516 | 934 | 2143 | 2658 | 753 | 98 | 84 | 0 | 138
20:30 | 3568 | 933.5 | 2160 | 2683.5 | 750.5 | 98.5 | 84 | 0 | 139
21:00 | 3620 | 933 | 2177 | 2709 | 748 | 99 | 84 | 0 | 140
21:30 | 3609.5 | 933.5 | 2198 | 2691.5 | 748.5 | 99 | 75.5 | 0 | 141
22:00 | 3599 | 934 | 2219 | 2674 | 749 | 99 | 67 | 0 | 142
22:30 | 3577 | 934 | 2211 | 2677 | 750 | 99 | 67 | 0 | 141
23:00 | 3555 | 934 | 2203 | 2680 | 751 | 99 | 67 | 0 | 140
23:30 | 3543 | 939.5 | 2185.5 | 2680 | 750 | 98 | 58.5 | 0 | 138 | Max Temp. in Dhaka |  | 32.0° C
24:00 | 3531 | 945 | 2168 | 2680 | 749 | 97 | 50 | 0 | 136
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 182.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 182.074 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 63 | 63 | 62 | 62 | 63 | 64 | 66 | 66 | 66 | 66 | 64 | 63 | 63 | 60 | 59 | 59 | 61 | 61 |  | 62 | 62 | 63 | 64 | 64 | 64 | 62 | 1435167
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.9 | 1.3 |  | 3.6 |  | 0.52 | 2.5 | 2.55 |  | 2.1 | 1.3 |  | 0.2 | [8 empty] | 12690
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 139 | 139 | 147 | 139 | 139 | 139 | 139 | 139 | 145 | 141 | 139 | 139 | 139 | 139 | 139 | 139 | 139 |  | 145 | 139 | 139 | 139 | 139 | 139 | 139 | 3359720
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 34 | 34 | 34 | 17 | 17 |  | 143397
12 | Hathazari 100 MW peaking PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 6 | 9 | 6 | 7 | 8 | [10 empty] | 122768
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 217 | 215 | 215 | 217 | 218 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 140 |  | 170 | 170 | 170 | 200 | 200 | 200 | 200 | 4525147
18 | Kodda 300 MW PP Unit-2 (Summit) | 225 | 110 | 65 |  |  |  | 2 | 45 | 51 | 75 | 94 | 194 | 195 | 195 | 195 | 195 | 195 | 195 |  | 217 | 280 | 285 | 286 | 250 | 250 | 250 | 3715962
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 769000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 250 |  | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 7002927
26
28 | Ashuganj TPP Unit- 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2006858
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 35 | 35 | 34 | 36 | 33 | 30 | 35 | 38 | 37 | 38 | 38 | 38 | 35 | 38 |  | 35 | 35 | 38 | 38 | 38 | 38 | 38 | 824328
33 | Ashuganj 225 MW CCPP | 189 | 191 | 192 | 190 | 183 | 182 | 195 | 200 | 197 | 205 | 194 | 185 | 193 | 188 | 195 | 183 | 183 | 182 |  | 202 | 201 | 185 | 198 | 196 | 187 | 182 | 4648000
34 | Ashuganj 450 MW CCPP(South) | 250 | 255 | 250 | 250 | 250 | 250 | 260 | 275 | 265 | 290 | 265 | 250 | 310 | 285 | 290 | 280 | 270 | 270 |  | 290 | 280 | 275 | 295 | 290 | 275 | 275 | 6601000
| Ashuganj 450 MW CCPP(North) | 260 | 265 | 265 | 265 | 260 | 260 | 270 | 285 | 325 | 345 | 325 | 310 | 330 | 310 | 320 | 310 | 270 | 270 |  | 310 | 325 | 300 | 325 | 320 | 310 | 310 | 7469000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 736320
36 | Chandpur 150 MW CCPP | 90 | 91 | 90 | 91 | 80 | 85 | 90 | 90 | 90 | 91 | 90 | 85 | 90 | 90 | 90 | 80 | 80 | 85 |  | 90 | 90 | 89 | 91 | 90 | 90 | 81 | 2082710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 350 | 320 | 320 | 370 | 370 | 370 | 370 | 400 | 400 | 400 | 400 | 350 | 350 |  | 350 | 400 | 400 | 400 | 400 | 400 | 400 | 8980500
41 | Haripur 360MW CCPP(HPL) | 354 | 354 | 354 | 353 | 358 | 309 | 309 | 309 | 356 | 353 | 353 | 302 | 300 | 275 | 300 | 320 | 302 | 273 |  | 270 | 330 | 330 | 333 | 333 | 333 | 334 | 7748000
42 | RPCL 210MW CCPP | 140 | 139 | 140 | 140 | 142 | 141 | 138 | 139 | 140 | 140 | 140 | 140 | 127 | 115 | 123 | 124 | 125 | 141 |  | 134 | 135 | 133 | 134 | 134 | 141 | 142 | 3188240
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 58 | 59 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 1398000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716040
46 | Shajibazar 330 MW CCPP | 246 | 242 | 243 | 242 | 241 | 240 | 241 | 248 | 252 | 253 | 245 | 248 | 245 | 252 | 243 | 243 | 247 | 247 |  | 260 | 252 | 248 | 251 | 250 | 249 | 247 | 5587000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 62 | 62 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 52 | 61 | 61 | 61 | 61 | 62 | 62 | 1200672
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 76 | 76 | 76 | 77 | 77 | 77 | 77 | 77 | 76 | 77 | 77 | 77 | 77 | 30 | 20 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1730880
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 150 | 150 | 150 | 150 | 100 | 101 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 151 | 150 | 150 | 150 | 150 | 151 | 2926330
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237960
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 |  |  | 3 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 170352
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 48 | 47 | 48 | 48 | 45 | 45 | 47 | 47 | 50 | 50 | 50 | 22 | 11 |  | 41 | 50 | 50 | 50 | 47 | 47 | 47 | 1082400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 474528
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 305 | 300 | 300 | 300 | 285 | 295 | 310 | 305 | 315 | 310 | 290 | 300 | 295 | 300 | 285 | 280 | 285 |  | 305 | 325 | 315 | 310 | 310 | 310 | 300 | 7460500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | [11 empty] | 45 | 55 | 55 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 324083
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 477264
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | [6 empty] | 351720
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 456300
63 | Impoprt (Tripura) | 122 | 116 | 102 | 114 | 112 | 88 | 78 | 90 | 52 | 64 | 76 | 96 | 110 | 116 | 118 | 104 | 112 | 110 |  | 138 | 140 | 138 | 140 | 142 | 140 | 136 | 2632320
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 29 | 10 | 5 | 5 | 4 | 7 | 13 | 14 | 6 | 2 | 6 | 15 |  | 29 | 32 | 37 | 38 | 41 | 41 | 41 | 597120
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 20 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494712
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 8 |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 146700
67 | Jangalia 33MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 25 | 20 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 687300
68 | Cumilla 25 MW PP (Summit) | 15 | 10 | 10 | 10 | 10 | 10 | 13 | 13 |  |  | 20 | 20 | 15 | 21 | 21 | 21 | 21 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 420630
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 28 | 30 | 10 | 27 | 27 | 28 | 28 | 28 | 28 | 29 | 26 | 28 | 30 | 30 | 30 | 30 | 30 |  | 20 | 22 | 30 | 30 | 30 | 30 | 27 | 647460
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 |  | 25 | 30 | 33 | 33 | 33 | 33 | 33 | 725200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 832300
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 53 | 14 | 14 | 70 | 88 | 86 | 93 | 92 | 95 | 93 | 93 | 53 | 29 |  | 29 | 88 | 92 | 96 | 96 | 97 | 98 | 1873454
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 37 | 8 |  |  |  | 26 | 26 | 26 | 8 | 8 | 8 | 18 | 36 | 36 | 36 | 36 | 8 | 8 |  | 33 | 105 | 105 | 105 | 103 | 105 | 105 | 930720
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 91 | 91 | 91 | 91 | 84 | 24 | 7 | 7 | 10 | 50 | 55 | 83 | 88 | 83 | 83 | 80 | 50 | 35 |  | 45 | 92 | 91 | 91 | 86 | 86 | 91 | 1663680
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP
80 | Jamalpur 95 MW PP(Powerpac) | [21 empty] | 7 | 8 | 29 | 40 | 40 | 133440
81 | Jangalia 52 MW PP (Lakdanavi)
| Gazipur 100 MW PP | [10 empty] | 20 | 52 | 52 | 52 | 52 | 40 | 35 | 35 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 506676
| Kaptai 7 MW Solar PP | [5 empty] | 0.2 | 0.4 | 0.8 | 2.1 | 4.7 | 3.6 | 3.7 | 1.3 | 1.3 | 1 | 0.6 | 0.7 | 0.2 | [8 empty] | 20880
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 95 | 95 | 95 | 95 | 95 | 91 | 15 | 15 | 15 | 37 | 48 | 60 | 97 | 86 | 86 | 96 | 96 | 87 |  | 81 | 97 | 96 | 97 | 97 | 97 | 97 | 1904784
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [13 empty] | 15 | 30 | 30 | [9 empty] | 15 | 120850
86 | Meghnaghat CCPP(Summit) | 270 | 270 | 275 | 260 | 250 | 260 | 240 | 260 | 260 | 250 | 270 | 230 | 270 | 270 | 270 | 230 | 250 | 270 |  | 270 | 270 | 265 | 275 | 275 | 265 | 250 | 6359709
87 | Meghnaghat 100 MW(IEL) | 100 | 70 | 50 | 15 | 7 | 7 |  |  |  |  | 7 | 55 | 55 | 55 | 55 | 55 | 19 | 16 |  | 33 | 94 | 91 | 83 | 90 | 92 | 93 | 1099200
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 40 | 40 | 40 | 40 | 40 | 50 | 67 | 67 | 66 | 64 | 66 | 35 | 30 |  | 30 | 30 | 30 | 30 | 68 | 67 | 67 | 1303008
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 20 | 10 |  | 20 | 46 | 46 | 46 | 46 | 46 | 46 | 1064304
93 | Ashuganj 51 MW PP (Midland) | 30 | 26 | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 827816
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 64 | 7 | 7 | 7 | 16 | 40 | 40 |  | 32 | 70 | 70 | 70 | 68 | 24 |  | 40 | 102 | 102 | 102 | 102 | 102 | 102 | 1467216
95 | Patenga 50MW PP (Baraka) | [11 empty] | 11 | 12 | 12 | 12 | 12 | 9 | 11 |  | 12 | 12 | 12 | 12 |  |  |  | 126720
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 2 | 12 | 12 | 12 | 12 | 12 | 12 | 67200
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | [10 empty] | 15 | 15 | 15 | 15 | 15 |  | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 392233
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 663639
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 100 |  | 100 | 130 | 130 | 163 | 163 | 163 | 163 | 3488890
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.3 | 0.6 | 0.1 |  |  | 0.5 | 0.6 | 1.1 | 0.8 | 0.6 | 0.4 | [9 empty] | 5200
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 35 | [7 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 801000
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 170 | 170 | 170 | 170 | 150 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 22 | 32 | 16 |  | 38 | 100 | 168 | 187 | 170 | 170 | 170 | 2023200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 112 | 112 | 112 | 111 | 88 | 52 | 45 | 59 | 72 | 95 | 96 | 96 | 98 | 110 | 113 | 111 | 93 | 79 |  | 86 | 86 | 104 | 114 | 113 | 113 | 113 | 2332800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 10 | [8 empty] | 36 | 40 | 40 | 40 | 40 | 10 | 10 | 10 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 578880
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | [19 empty] | 6 | 50 | 80 | 80 | 80 | 80 | 80 | 441600
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 55 | 55 | 78 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 75 |  | 95 | 115 | 115 | 115 | 115 | 115 | 115 | 2608800
| Anwara 300 MW PP (United) | 306 | 306 | 252 | 159 | 107 | 88 | 53 | 105 | 107 | 108 | 156 | 159 | 161 | 212 | 216 | 216 | 125 | 124 |  | 230 | 301 | 301 | 307 | 307 | 307 | 307 | 4764764
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2443200
120 | Eastern Zone Total | 6395 | 6189 | 6024 | 5796 | 5586 | 4931.2 | 4672 | 4856.4 | 4990.8 | 5328.7 | 5480.12 | 5581.7 | 5886.45 | 5980.4 | 6049.9 | 5906.5 | 5338.1 | 5065.4 |  | 5795 | 6676 | 6752 | 6925 | 6871 | 6841 | 6825 | 141431095
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 16 | [18 empty] | 68 | 115 | 115 | 115 | 115 | 115 | 115 | 582720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha)
130
131
132
133
| Barisal 110 MW PP (Summit ) | [19 empty] | 40 | 48 | 80 | 80 | 80 | 80 | 80 | 385920
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 79 | 79 | 79 | 79 | 79 | 79 | 78 | 78 | 77 | 77 | 78 | 78 | 77 | 78 | 78 | 78 | 48 | 23 |  | 65 | 75 | 77 | 76 | 77 | 78 | 79 | 1788656
| Bhola 225 MW CCPP | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 70 | 70 | 69 | 70 | 63 | 69 | 70 | 66 | 65 | 64 | 66 |  | 68 | 68 | 68 | 69 | 68 | 69 | 69 | 1638000
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 26 | 26 | 25 | 21 | 14 | 6 | 12 | 11 | 15 | 14 | 16 | 16 | 18 | 17 | 17 | 17 |  | 26 | 28 | 28 | 28 | 30 | 26 | 28 | 473809
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 25 | 33 | 50 | 70 | 70 | 30 | 280320
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 32 | 32 | 24 | 33 | 33 | 40 | 144750
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 3 | 10 | 10 | 10 | [8 empty] | 30208
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | [24 empty] | 270432
146 | Bheramara HVDC | 936 | 936 | 936 | 936 | 936 | 936 | 936 | 936 | 933 | 933 | 932 | 933 | 932 | 932 | 932 | 934 | 934 | 934 |  | 934 | 934 | 934 | 933 | 934 | 934 | 945 | 22423272
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 370 | 355 | 385 | 350 | 345 | 370 | 345 | 350 | 345 | 345 | 290 |  | 385 | 370 | 345 | 360 | 345 | 340 | 340 | 8511840
148 | Payra 1320 MW | 350 | 351 | 387 | 450 | 451 | 450 | 452 | 423 | 421 | 420 | 420 | 418 | 427 | 420 | 421 | 420 | 423 | 423 |  | 468 | 500 | 604 | 599 | 600 | 602 | 600 | 10623400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 148 | 149 | 149 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3655500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 159 | 150 | 148 | 147 | 144 | 146 | 159 | 161 | 158 | 162 | 174 | 197 | 191 | 197 | 185 | 179 | 163 |  | 171 | 189 | 194 | 193 | 198 | 193 | 185 | 4368591
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 164 | 161 | 159 | 159 | 154 | 157 | 170 | 172 | 169 | 173 | 162 | 198 | 194 | 200 | 188 | 181 | 160 |  | 173 | 197 | 198 | 193 | 197 | 195 | 188 | 4494055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 413 | 391 | 392 | 390 | 363 | 372 | 348 | 345 | 382 | 385 | 392 | 340 | 392 | 385 | 389 | 338 | 352 | 390 |  | 391 | 410 | 409 | 408 | 408 | 395 | 365 | 9258545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 473280
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 267624
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 179910
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 545260
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 70 | 35 |  |  |  | 25 | 35 | 50 | 70 | 85 | 109 | 109 | 50 | 35 | 35 |  | 80 | 109 | 109 | 109 | 109 | 109 | 109 | 1712352
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 105 | 70 | [9 empty] | 3 | 40 | 36 | 35 | 35 | 35 | 35 |  | 48 | 107 | 105 | 107 | 106 | 107 | 106 | 994560
177 | Sympa Solar Power 8MW | [6 empty] | 0.4 | 0.5 | 0.6 | 2.2 | 1.8 | 3.8 | 3.6 | 4.2 | 3.2 | 1.2 | 1.1 | 0.6 | [8 empty] | 17479
178
178