## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-22 | Monday
|  | Date (day): | 2020-06-22 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13406.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14865 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-22 | 2020-06-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 67 | 68 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 99 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 26/06/2020
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 304 | 354 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 255 | 260 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 41 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 21 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 87 | 94 | 100 | 100 | 110 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 98 | 99 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 212 | 218 | 220 | 220 |  | 115 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 3 | 48 | 48 | 51
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 82 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 200 | 267 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 130 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 88 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 2852 | 3204 | 3762 | 4099 | 323 | 1294
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 15 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 98 | 100 | 100 | 130 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 139 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 86 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 27 | 35 | 35
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 24 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0.9 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 306 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 875.9 | 1087 | 1427 | 1546 | 390 | 225
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 130 | 100 | 100 | 35 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 110 | 100 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 216 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 38 | 38 | 38 |  | 7 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 42 | 30 | 50 | 50
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 55 | 55 | 140 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 25 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 80 | 148 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 81 | 80 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 99 | 124 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 32 | 32
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 1 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 20 | 21
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 6 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1315 | 1445 | 1996 | 2169 | 358 | 88
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 139 | 141 | 150 | 150 | 52 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 95 | 95 | 60 | 95
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.6 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 60 | 154 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 409.6 | 527 | 518.6 | 582 | 52 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 60 | 60
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 244 | 246 | 275 | 275 |  | 55 | Engine problem
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 43 | 43 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 76 | 76 | 76
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 149 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1234 | 1232 | 1314 | 1320 | 0 | 515
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 948 | 949 | 952 | 956
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 0 | 30
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 345 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 21 | 105 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1025 | 1744 | 1782 | 2162 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 50 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 30 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 65 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 78 | 78 | 78 |  | 17 | Engine problem
| Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 15 | 0 | 0
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 0 | 660 | 660
| Barisal Area Total |  |  |  |  | 1094 | 1084 | 15 | 298 | 886 | 949 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 60 | 65 | 65
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 65 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 43 | 43
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 188 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 186 | 187 | 210 | 210
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 392 | 393 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 20 | 21
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 50 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 8 | 113 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 880 | 1280 | 1493 | 1755 | 310 | 19
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 106 | 113 | 70 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.2 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 262.2 | 273 | 228 | 283 | 170 | 0
| Total |  |  |  |  | 20319 | 19818 | 8868.7 | 11090 | 13406.6 | 14865 | 1603 | 2284
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8292.1145 | 10369 | 12534.9897 | 13898.5739
A. |  | 2020-06-22 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11090 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8276.1 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11090 | MW
3 | Day peak Generation : |  |  | 8868.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10369 | MW
4 | Evening peak Generation : |  |  | 11090 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 230.2485 | MKWHr | By Solar | 0.13376 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 128.5318 | MKWHr |  | By Oil: | 63.6555 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 10.1275 | MKWHr |  | By Hydro: | 2.2624 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1603 | MW | Dhaka | 3464 | 3464 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2284 | MW | Chittagong | 967 | 967 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3887 | MW | Khulna | 1389 | 1389 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1151.66 | MMCFD |  |  | Rajshahi | 1161 | 1161 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 153533767.214 | ii) Oil : | Taka | 478620151.2 | Comilla | 989 | 989 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 48224787 | Total | Taka | 680378705.414 | Mymensingh | 936 | 936 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.467 | MKWHr. | Sylhet | 432 | 432 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -248 | MW (E to W) at | 21:00 | hrs | Barisal | 293 | 293 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -324 | MW at | 12:00 | hrs | Rangpur | 738 | 738 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.2° C |  |  | Total | 10369 | 10369 |  | 0
B. |  | 2020-06-22 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14865 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 3365 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 238.7608 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7985.1 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.7469 | MKWHr. | ii) HVDC Flow at Peak Time |  | 949 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7907 | MKWHr. | iii) Maximum HVDC Flow : |  | 949 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.88 |  | (b) Today: | 83.99 |  | (c) Rule Curve: |  | 81.57
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-06-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 338 |  | 0 | 360 | 250 | 100 | 97 | 15 | 150 | 0 | 88 | 0 | 98 | 102 | 64 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 64 | 35 | 95 | 0 | 0 | 0 | 0 | 138 | 0 |  | 0 | 0 | 0 | 0 | 98 | 0 | 20 | 33 | 70 | 80 | 0 | 260 | 125 | 182 | 8 | 85 | 20 | 5 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 20 | 150 | 141 | 95 | 22 | 0 | 58 | 30 | 50 | 43 | 130 | 243 | 61 | 76 | 0 | 120 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 267 | 0 | 0 | 190 | 0 | 130 | 0 | 100 | 0 | 142 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 |  | 948 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 157 | 0 | 80 | 100 | 187 | 0 | 400 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 630 |  | 6885 | 3711 | 10596 | 3345 | 948 | 2094 | 3007 | 779 | 99 | 174 | 150 | 0 | 0 | 83.83
2:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 339 |  | 0 | 360 | 260 | 100 | 97 | 15 | 180 | 0 | 88 | 0 | 98 | 102 | 20 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 98 | 0 | 20 | 33 | 70 | 80 | 0 | 280 | 0 | 190 | 8 | 91 | 38 | 5 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 20 | 146 | 141 | 95 | 22 | 0 | 58 | 30 | 50 | 43 | 130 | 249 | 61 | 76 | 0 | 120 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 267 | 0 | 0 | 190 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 79 | 100 | 0 |  | 948 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 78 | 20 | 187 | 0 | 416 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 109 | 630 |  | 6771 | 3531 | 10302 | 3311 | 948 | 2104 | 2822 | 779 | 97 | 95 | 146 | 0 | 0 | 83.84
3:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 338 |  | 0 | 380 | 255 | 100 | 97 | 15 | 180 | 0 | 88 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 98 | 0 | 20 | 27 | 70 | 80 | 0 | 280 | 0 | 181 | 8 | 90 | 38 | 15 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 20 | 140 | 141 | 95 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 243 | 60 | 76 | 0 | 121 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 269 | 0 | 0 | 190 | 0 | 129 | 0 | 100 | 0 | 148 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 36 | 100 | 0 |  | 948 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 78 | 0 | 187 | 0 | 396 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 109 | 630 |  | 6707 | 3381 | 10088 | 3299 | 948 | 2107 | 2668 | 779 | 97 | 50 | 140 | 0 | 0 | 83.85
4:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 357 |  | 0 | 420 | 270 | 100 | 97 | 15 | 210 | 0 | 95 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 82 | 0 | 20 | 33 | 70 | 80 | 0 | 310 | 0 | 182 | 8 | 80 | 38 | 25 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 20 | 136 | 141 | 48 | 22 | 0 | 59 | 30 | 50 | 43 | 163 | 244 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 264 | 0 | 0 | 190 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 0 |  | 949 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 78 | 0 | 187 | 0 | 344 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 631 |  | 6775 | 2925 | 9700 | 3048 | 949 | 2160 | 2480 | 780 | 97 | 50 | 136 | 0 | 0 | 83.86
5:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 355 |  | 0 | 420 | 260 | 100 | 97 | 15 | 214 | 0 | 94 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 41 | 70 | 80 | 0 | 310 | 0 | 181 | 55 | 90 | 38 | 40 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 10 | 128 | 141 | 0 | 22 | 0 | 59 | 30 | 50 | 43 | 163 | 245 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 130 | 0 | 70 | 0 | 148 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 100 | 0 |  | 948 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 78 | 0 | 187 | 0 | 337 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 109 | 631 |  | 6607 | 2892 | 9499 | 3029 | 948 | 2209 | 2257 | 780 | 98 | 50 | 128 | 0 | 0 | 83.87
6:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 355 |  | 0 | 420 | 265 | 35 | 97 | 0 | 214 | 0 | 96 | 0 | 99 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 39 | 70 | 80 | 0 | 310 | 0 | 182 | 55 | 88 | 38 | 42 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 10 | 114 | 141 | 0 | 22 | 0.1 | 59 | 30 | 47 | 43 | 100 | 244 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 75 | 0 | 104 | 2.6 | 30 | 0 | 50 | 0 | 115 | 0 | 0 | 0.3 | 160 | 0 | 0 | 0 | 0 | 100 | 0 |  | 949 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 78 | 0 | 187 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 109 | 630 |  | 5758 | 2810.2 | 8568.2 | 3041 | 949 | 2184 | 1400 | 779 | 98 | 0 | 114 | 3.2 | 0 | 83.88
7:00 | 35 | 0 | 0 | 0 | 300 | 93 | 68 | 0 | 357 |  | 0 | 420 | 255 | 7 | 97 | 0 | 215 | 0 | 96 | 0 | 62 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 26 | 70 | 80 | 0 | 310 | 0 | 182 | 55 | 88 | 38 | 46 | 0 | 26 | 0 | 0 | 0 | 21 | 8 | 25 | 6 | 106 | 140 | 0 | 22 | 0.2 | 59 | 30 | 47 | 43 | 100 | 243 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 45 | 0 | 0 | 75 | 0 | 100 | 2.9 | 30 | 0 | 50 | 0 | 115 | 0 | 0 | 2.2 | 160 | 0 | 0 | 0 | 0 | 100 | 0 |  | 948 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 78 | 0 | 187 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 35 | 577 |  | 5662.3 | 2670.2 | 8332.5 | 3034 | 948 | 2167 | 1247 | 726 | 98 | 0 | 106 | 6.5 | 0 | 83.89
8:00 | 35 | 0 | 0 | 0 | 300 | 93 | 68 | 0 | 356 |  | 0 | 420 | 255 | 7 | 97 | 0 | 214 | 0 | 96 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 100 | 80 | 0 | 310 | 0 | 184 | 55 | 91 | 38 | 48 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 6 | 102 | 139 | 0 | 22 | 0.7 | 58 | 30 | 47 | 43 | 100 | 251 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 45 | 0 | 0 | 75 | 0 | 100 | 6.6 | 30 | 0 | 50 | 0 | 115 | 0 | 0 | 2.9 | 160 | 0 | 0 | 0 | 0 | 100 | 0 |  | 948 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 76 | 0 | 186 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 35 | 500 |  | 5671.2 | 2604.9 | 8276.1 | 3084 | 948 | 2149 | 1235 | 649 | 98 | 0 | 102 | 11.1 | 0 | 83.9
9:00 | 35 | 0 | 0 | 0 | 300 | 93 | 69 | 0 | 352 |  | 0 | 420 | 265 | 7 | 97 | 0 | 213 | 0 | 87 | 0 | 55 | 64 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 3 | 100 | 100 | 0 | 330 | 0 | 195 | 45 | 91 | 38 | 47 | 0 | 25 | 0 | 0 | 0 | 18 | 8 | 25 | 6 | 91 | 138 | 0 | 0 | 1 | 58 | 30 | 47 | 43 | 163 | 249 | 59 | 74 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 45 | 0 | 0 | 88 | 0 | 110 | 3.4 | 30 | 0 | 50 | 0 | 115 | 0 | 0 | 4.4 | 160 | 0 | 0 | 0 | 0 | 100 | 0 |  | 948 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 17 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 79 | 0 | 187 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 70 | 500 |  | 5782.8 | 2769.3 | 8552.1 | 3179 | 948 | 2246 | 1326 | 649 | 100 | 0 | 91 | 13.1 | 0 | 83.93
10:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 354 |  | 0 | 380 | 240 | 51 | 97 | 25 | 214 | 0 | 87 | 0 | 90 | 84 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 30 | 25 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 135 | 100 | 0 | 315 | 0 | 181 | 45 | 81 | 38 | 43 | 0 | 25 | 0 | 0 | 0 | 18 | 8 | 25 | 14 | 98 | 139 | 0 | 0 | 0.6 | 58 | 30 | 45 | 43 | 163 | 248 | 60 | 74 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 66 | 0 | 0 | 120 | 0 | 126 | 4.2 | 70 | 0 | 50 | 0 | 115 | 0 | 0 | 2.8 | 215 | 0 | 0 | 0 | 31 | 100 | 0 |  | 948 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 68 | 18 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 78 | 0 | 187 | 0 | 380 | 0 | 0 | 0 | 0 | 28 | 0 | 4.8 | 20 | 502 |  | 6097.6 | 2752.8 | 8850.4 | 3187 | 948 | 2156 | 1698 | 651 | 100 | 0 | 98 | 12.4 | 0 | 83.92
11:00 | 35 | 0 | 0 | 0 | 300 | 96 | 67 | 0 | 352 |  | 0 | 420 | 280 | 100 | 97 | 42 | 209 | 0 | 87 | 0 | 98 | 93 | 0 | 5 | 0 | 0 | 0 | 53 | 55 | 50 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 2 | 135 | 110 | 0 | 340 | 0 | 202 | 45 | 90 | 35 | 41 | 0 | 25 | 0 | 0 | 0 | 18 | 5 | 25 | 14 | 101 | 140 | 25 | 0 | 1 | 58 | 30 | 45 | 43 | 130 | 245 | 59 | 74 | 0 | 149 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 130 | 0 | 0 | 80 | 0 | 129 | 12.9 | 100 | 0 | 50 | 0 | 115 | 15 | 0 | 5 | 215 | 0 | 0 | 0 | 86 | 100 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 186 | 0 | 408 | 0 | 0 | 0 | 0 | 77 | 0 | 3.4 | 0 | 0 |  | 6526.9 | 2134.4 | 8661.3 | 3175 | 948 | 2106 | 2059 | 150 | 100 | 0 | 101 | 22.3 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 96 | 67 | 0 | 304 |  | 0 | 420 | 255 | 100 | 97 | 41 | 212 | 0 | 87 | 0 | 98 | 93 | 0 | 21 | 0 | 0 | 3 | 53 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 2 | 135 | 110 | 0 | 310 | 0 | 182 | 45 | 81 | 35 | 42 | 0 | 25 | 0 | 0 | 1 | 21 | 5 | 25 | 14 | 99 | 139 | 95 | 0 | 0.6 | 58 | 30 | 47 | 43 | 163 | 244 | 61 | 76 | 0 | 149 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 60 | 0 | 133 | 0 | 100 | 0 | 80 | 0 | 115 | 17 | 0 | 0.9 | 305 | 0 | 0 | 0 | 105 | 100 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 186 | 0 | 392 | 0 | 0 | 8 | 21 | 106 | 0 | 6.2 | 0 | 0 |  | 6686.5 | 2182.2 | 8868.7 | 3098 | 948 | 2078 | 2388 | 150 | 100 | 0 | 99 | 7.7 | 0 | 83.93
13:00 | 35 | 0 | 0 | 0 | 300 | 99 | 67 | 0 | 304 |  | 0 | 420 | 250 | 100 | 97 | 41 | 190 | 0 | 87 | 0 | 98 | 93 | 0 | 50 | 0 | 0 | 43 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 48 | 19 | 2 | 135 | 110 | 0 | 305 | 0 | 182 | 45 | 80 | 38 | 45 | 0 | 25 | 0 | 0 | 8 | 21 | 5 | 25 | 14 | 98 | 140 | 95 | 0 | 0.5 | 59 | 30 | 50 | 43 | 100 | 247 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 254 | 0 | 0 | 40 | 0 | 133 | 1.7 | 100 | 0 | 142 | 0 | 115 | 17 | 0 | 1.6 | 307 | 25 | 0 | 0 | 105 | 100 | 0 |  | 949 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 187 | 0 | 328 | 0 | 0 | 35 | 0 | 106 | 0 | 1.8 | 0 | 0 |  | 6844.8 | 2201.8 | 9046.6 | 3113 | 949 | 1936 | 2654 | 150 | 100 | 41 | 98 | 5.6 | 0 | 83.94
14:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 303 |  | 0 | 400 | 276 | 100 | 97 | 41 | 180 | 0 | 37 | 0 | 98 | 93 | 0 | 20 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 28 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 4 | 135 | 110 | 0 | 275 | 0 | 183 | 45 | 90 | 36 | 45 | 0 | 25 | 0 | 0 | 8 | 21 | 5 | 25 | 14 | 108 | 125 | 70 | 17 | 0.6 | 59 | 30 | 50 | 43 | 163 | 248 | 40 | 76 | 0 | 149 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 250 | 0 | 0 | 8 | 0 | 132 | 4 | 100 | 0 | 145 | 0 | 115 | 17 | 0 | 3.4 | 271 | 17 | 0 | 0 | 107 | 100 | 0 |  | 948 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 48 | 0 | 65 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 186 | 0 | 378 | 0 | 0 | 35 | 32 | 67 | 0 | 4.9 | 0 | 0 |  | 6640 | 2267.9 | 8907.9 | 2985 | 948 | 1990 | 2576 | 150 | 97 | 41 | 108 | 12.9 | 0 | 83.94
15:00 | 35 | 0 | 0 | 0 | 300 | 93 | 66 | 0 | 349 |  | 0 | 420 | 270 | 100 | 97 | 41 | 212 | 0 | 35 | 0 | 98 | 93 | 0 | 53 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 60 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 26 | 20 | 4 | 120 | 110 | 0 | 260 | 0 | 190 | 45 | 90 | 36 | 10 | 0 | 25 | 0 | 0 | 8 | 21 | 5 | 25 | 14 | 120 | 125 | 78 | 20 | 0.2 | 58 | 30 | 47 | 43 | 163 | 248 | 40 | 76 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 253 | 0 | 0 | 24 | 0 | 133 | 4.6 | 100 | 0 | 145 | 0 | 115 | 17 | 0 | 0.7 | 306 | 17 | 0 | 0 | 113 | 100 | 0 |  | 949 | 0 | 140 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 110 | 0 | 65 | 50 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 11 | 0 | 184 | 0 | 384 | 0 | 0 | 35 | 85 | 67 | 0 | 1.8 | 0 | 0 |  | 6859.5 | 2610.8 | 9470.3 | 3210 | 949 | 2110 | 2784 | 150 | 95 | 45 | 120 | 7.3 | 0 | 83.95
16:00 | 35 | 0 | 0 | 0 | 300 | 96 | 66 | 0 | 304 |  | 0 | 380 | 265 | 100 | 97 | 41 | 214 | 0 | 37 | 0 | 98 | 93 | 0 | 76 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 60 | 35 | 95 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 80 | 100 | 0 | 260 | 0 | 183 | 8 | 85 | 36 | 10 | 0 | 25 | 0 | 0 | 0 | 21 | 5 | 25 | 20 | 120 | 124 | 90 | 22 | 0.8 | 58 | 30 | 47 | 43 | 130 | 246 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 253 | 0 | 0 | 16 | 0 | 132 | 4.2 | 100 | 0 | 100 | 0 | 115 | 52 | 0 | 0.5 | 306 | 0 | 0 | 0 | 113 | 100 | 0 |  | 948 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 96 | 0 | 65 | 60 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 75 | 0 | 186 | 0 | 363 | 0 | 0 | 0 | 67 | 101 | 0 | 3 | 0 | 0 |  | 6453.5 | 2830 | 9283.5 | 3276 | 948 | 1971 | 2630 | 150 | 95 | 85 | 120 | 8.5 | 0 | 83.95
17:00 | 35 | 0 | 0 | 0 | 300 | 23 | 40 | 0 | 304 |  | 0 | 380 | 250 | 100 | 97 | 41 | 218 | 0 | 35 | 0 | 98 | 93 | 0 | 10 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 95 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 80 | 100 | 0 | 260 | 0 | 182 | 8 | 90 | 36 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 20 | 112 | 124 | 48 | 22 | 0.2 | 58 | 30 | 50 | 43 | 130 | 243 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 253 | 0 | 0 | 8 | 0 | 132 | 2.7 | 100 | 0 | 70 | 0 | 115 | 17 | 0 | 0.9 | 160 | 0 | 0 | 0 | 113 | 100 | 0 |  | 949 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 8 | 0 | 18 | 98 | 0 | 60 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 78 | 0 | 186 | 0 | 324 | 0 | 0 | 0 | 15 | 62 | 0 | 1.3 | 0 | 0 |  | 6001.8 | 2688.3 | 8690.1 | 3267 | 949 | 1834 | 2167 | 150 | 96 | 110 | 112 | 5.1 | 0 | 83.96
18:00 | 35 | 0 | 0 | 0 | 250 | 23 | 40 | 0 | 296 |  | 0 | 320 | 275 | 100 | 96 | 41 | 144 | 0 | 37 | 0 | 98 | 102 | 0 | 10 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 6 | 80 | 100 | 0 | 260 | 0 | 182 | 8 | 83 | 37 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 104 | 126 | 48 | 22 | 0.1 | 60 | 30 | 14 | 10 | 110 | 246 | 40 | 20 | 0 | 70 | 18 | 0 | 10 | 300 | 21 | 11 | 0 | 253 | 0 | 0 | 8 | 0 | 132 | 0.6 | 100 | 0 | 70 | 0 | 115 | 17 | 0 | 0 | 160 | 0 | 0 | 0 | 113 | 100 | 0 |  | 949 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 23 | 8 | 60 | 18 | 110 | 0 | 60 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 54 | 0 | 186 | 0 | 307 | 0 | 0 | 0 | 15 | 35 | 0 | 0.5 | 0 | 0 |  | 5679.7 | 2614.5 | 8294.2 | 3081 | 949 | 1587 | 2185 | 150 | 97 | 140 | 104 | 1.2 | 0 | 83.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 250 | 50 | 40 | 0 | 304 |  | 0 | 350 | 280 | 100 | 96 | 41 | 144 | 0 | 37 | 0 | 98 | 102 | 48 | 19 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 16 | 2 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 70 | 10 | 19 | 3 | 20 | 18 | 80 | 100 | 0 | 295 | 0 | 203 | 8 | 90 | 34 | 10 | 0 | 10 | 0 | 0 | 3 | 21 | 8 | 25 | 21 | 134 | 123 | 54 | 22 | 0 | 60 | 30 | 23 | 15 | 110 | 253 | 61 | 20 | 0 | 130 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 268 | 0 | 0 | 8 | 0 | 132 | 0 | 100 | 0 | 92 | 0 | 115 | 65 | 0 | 0 | 225 | 2 | 0 | 18 | 113 | 100 | 0 |  | 949 | 0 | 370 | 0 | 78 | 0 | 0 | 0 | 18 | 40 | 40 | 68 | 26 | 110 | 0 | 60 | 40 | 25 | 10 | 100 | 0 | 8 | 12 | 25 | 28 | 20 | 11 | 8 | 0 | 0 | 151 | 0 | 12 | 0 | 0 | 150 | 0 | 50 | 2 | 186 | 0 | 341 | 0 | 0 | 65 | 15 | 59 | 0 | 0 | 5 | 0 |  | 6201 | 3082 | 9283 | 3258 | 949 | 1696 | 2635 | 151 | 97 | 363 | 134 | 0 | 0 | 83.97
19:30 | 35 | 0 | 0 | 0 | 285 | 99 | 68 | 0 | 355 |  | 0 | 400 | 250 | 100 | 96 | 41 | 219 | 0 | 37 | 0 | 99 | 102 | 82 | 30 | 0 | 0 | 14 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 16 | 25 | 0 | 62 | 35 | 95 | 0 | 18 | 0 | 0 | 140 | 0 |  | 0 | 0 | 79 | 10 | 93 | 50 | 20 | 15 | 80 | 100 | 0 | 260 | 0 | 216 | 8 | 80 | 34 | 10 | 0 | 10 | 0 | 26 | 16 | 21 | 8 | 25 | 21 | 124 | 127 | 80 | 22 | 0 | 60 | 30 | 45 | 43 | 130 | 242 | 63 | 76 | 0 | 150 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 268 | 0 | 0 | 60 | 0 | 131 | 0 | 100 | 0 | 145 | 0 | 115 | 88 | 10 | 0 | 286 | 18 | 0 | 51 | 113 | 100 | 0 |  | 948 | 0 | 340 | 0 | 83 | 0 | 0 | 0 | 19 | 62 | 40 | 65 | 28 | 110 | 0 | 0 | 60 | 50 | 10 | 100 | 0 | 42 | 30 | 43 | 33 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 11 | 0 | 0 | 173 | 0 | 75 | 70 | 187 | 0 | 322 | 0 | 0 | 108 | 87 | 113 | 0 | 0 | 35 | 0 |  | 7158 | 3433 | 10591 | 3372 | 948 | 1995 | 3403 | 150 | 97 | 502 | 124 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 285 | 99 | 68 | 0 | 354 |  | 0 | 420 | 260 | 100 | 96 | 41 | 219 | 0 | 34 | 0 | 99 | 102 | 82 | 10 | 0 | 0 | 38 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 39 | 0 | 63 | 35 | 95 | 0 | 18 | 0 | 0 | 140 | 0 |  | 0 | 0 | 85 | 0 | 93 | 45 | 20 | 17 | 80 | 100 | 0 | 260 | 0 | 217 | 8 | 85 | 36 | 10 | 0 | 20 | 0 | 50 | 48 | 21 | 8 | 25 | 21 | 122 | 127 | 95 | 22 | 0 | 60 | 30 | 50 | 43 | 130 | 244 | 62 | 76 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 267 | 0 | 0 | 60 | 0 | 131 | 0 | 100 | 25 | 147 | 0 | 115 | 88 | 0 | 0 | 305 | 45 | 0 | 51 | 113 | 100 | 0 |  | 949 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 21 | 62 | 40 | 65 | 30 | 110 | 7 | 0 | 60 | 50 | 15 | 100 | 0 | 50 | 39 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 175 | 0 | 76 | 68 | 187 | 0 | 322 | 17 | 0 | 110 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7388 | 3496 | 10884 | 3415 | 949 | 2045 | 3549 | 150 | 98 | 556 | 122 | 0 | 0 | 83.98
21:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 |  | 0 | 420 | 260 | 100 | 96 | 41 | 218 | 0 | 94 | 0 | 99 | 102 | 82 | 0 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 0 | 86 | 0 | 24 | 50 | 20 | 27 | 130 | 100 | 0 | 300 | 0 | 216 | 8 | 80 | 38 | 30 | 0 | 25 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 124 | 141 | 95 | 22 | 0 | 60 | 30 | 50 | 43 | 163 | 246 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 267 | 0 | 0 | 154 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 88 | 0 | 0 | 306 | 17 | 0 | 6 | 113 | 100 | 0 |  | 949 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 21 | 52 | 40 | 65 | 30 | 110 | 15 | 0 | 60 | 50 | 41 | 92 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 188 | 0 | 78 | 100 | 187 | 0 | 393 | 17 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7495 | 3595 | 11090 | 3599 | 949 | 2196 | 3455 | 150 | 98 | 519 | 124 | 0 | 0 | 83.97
22:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 352 |  | 0 | 420 | 260 | 100 | 97 | 41 | 215 | 0 | 94 | 0 | 99 | 102 | 64 | 0 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 95 | 0 | 19 | 50 | 20 | 28 | 135 | 100 | 0 | 335 | 0 | 214 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 124 | 134 | 48 | 22 | 0 | 59 | 30 | 50 | 43 | 163 | 254 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 268 | 0 | 0 | 200 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 948 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 21 | 51 | 40 | 65 | 31 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 186 | 0 | 80 | 100 | 187 | 0 | 414 | 17 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7359 | 3517 | 10876 | 3643 | 948 | 2219 | 3281 | 150 | 100 | 411 | 124 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 |  | 0 | 420 | 260 | 100 | 97 | 41 | 217 | 0 | 94 | 0 | 99 | 102 | 64 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 0 | 50 | 20 | 32 | 135 | 120 | 0 | 325 | 0 | 213 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 138 | 139 | 48 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 252 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 258 | 0 | 0 | 200 | 0 | 131 | 0 | 100 | 0 | 148 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 946 | 0 | 315 | 0 | 115 | 0 | 0 | 0 | 21 | 51 | 40 | 65 | 31 | 110 | 0 | 0 | 60 | 0 | 0 | 91 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 197 | 0 | 80 | 100 | 187 | 0 | 414 | 17 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7314 | 3488 | 10802 | 3640 | 946 | 2213 | 3205 | 149 | 100 | 411 | 138 | 0 | 0 | 83.99
24:00 | 35 | 0 | 0 | 0 | 300 | 99 | 69 | 0 | 354 |  | 0 | 420 | 260 | 100 | 97 | 41 | 217 | 0 | 94 | 0 | 99 | 102 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 91 | 0 | 0 | 50 | 20 | 32 | 135 | 120 | 0 | 310 | 0 | 214 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 20 | 136 | 139 | 48 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 250 | 61 | 77 | 0 | 150 | 18 | 0 | 10 | 315 | 24 | 11 | 0 | 249 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 149 | 0 | 107 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 946 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 5 | 0 | 40 | 65 | 28 | 110 | 0 | 0 | 50 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 194 | 0 | 78 | 100 | 187 | 0 | 415 | 17 | 0 | 113 | 50 | 113 | 0 | 0 | 0 | 151 |  | 7244 | 3447 | 10691 | 3641 | 946 | 2215 | 3076 | 300 | 100 | 277 | 136 | 0 | 0 | 76.33
KWH | 720000 | 0 | 0 | 0 | 7138891 | 2042818 | 1516256 | 0 | 8014000 |  | 0 | 9446250 | 6328931 | 2066880 | 2335344 | 689326 | 4957966 | 0 | 1958000 | 0 | 2252160 | 2178864 | 484320 | 370763 | 0 | 0 | 366624 | 1183680 | 968205 | 763286 | 454824 | 600000 | 677700 | 659600 | 801100 | 49284 | 0 | 1426353 | 836000 | 2200000 | 0 | 56129 | 0 | 0 | 3209236 | 0 |  | 0 | 0 | 496993 | 9360 | 635520 | 416160 | 444912 | 481440 | 2402298 | 2275850 | 0 | 7412600 | 249000 | 4682000 | 652363 | 2060720 | 813960 | 738240 | 0 | 588176 | 0 | 39416 | 165293 | 488268 | 174780 | 615800 | 396340 | 2790720 | 3162720 | 1338240 | 366840 | 7250 | 1397000 | 714000 | 1096800 | 982656 | 3332700 | 5628000 | 1341408 | 1716480 | 0 | 3280380 | 425000 | 0 | 232560 | 7369500 | 561792 | 264000 | 4992 | 5025707 | 0 | 0 | 2596800 | 4610 | 3067200 | 63720 | 2093760 | 28320 | 2748290 | 0 | 2766000 | 487500 | 46836 | 24601 | 6240109 | 168096 | 0 | 80940 | 1817760 | 2415360 | 0 |  | 22746909 | 0 | 4233888 | 0 | 1519680 | 0 | 0 | 0 | 103680 | 286080 | 590250 | 1135000 | 536741 | 1325472 | 15965 | 687000 | 540000 | 131384 | 59442 | 1285344 | 0 | 53463 | 159178 | 219360 | 174400 | 480720 | 255096 | 170172 | 0 | 0 | 3655400 | 0 | 81000 | 0 | 0 | 4412109 | 0 | 1459145 | 658560 | 4720600 | 0 | 9156090 | 79680 | 0 | 782976 | 765360 | 1687680 | 0 | 38192 | 889440 | 6472100 |  | 158680926 | 71567556 | 230248482 | 78433754 | 22746909 | 50098031 | 60338250 | 10127500 | 2262353 | 3317202 | 2790720 | 133763 | 0
Fuel Cost | 1180800 | 0 | 0 | 0 | 7924169.01 | 2696519.76 | 2577635.2 | 0 | 8254420 |  | 0 | 10296412.5 | 7025113.41 | 15687619.2 | 16090520.16 | 5831697.96 | 5156284.64 | 0 | 3387340 | 0 | 16958764.8 | 19871239.68 | 4765708.8 | 3418434.86 | 0 | 0 | 3332612.16 | 8640864 | 7484224.65 | 7525999.96 | 341118 | 450000 | 0 | 0 | 0 | 476576.28 | 0 | 385115.31 | 225720 | 3982000 | 0 | 521438.41 | 0 | 0 | 5455701.2 | 0 |  | 0 | 0 | 4820832.1 | 89388 | 5529024 | 3295987.2 | 560589.12 | 1429876.8 | 3555401.04 | 3368258 | 0 | 5485324 | 249000 | 4307440 | 841548.27 | 2369828 | 919774.8 | 1033536 | 0 | 1005780.96 | 0 | 398101.6 | 1578548.15 | 620100.36 | 131085 | 1077650 | 297255 | 20930400 | 3352483.2 | 12151219.2 | 465886.8 | 115565 | 2291080 | 1142400 | 1952304 | 1532943.36 | 3799278 | 5853120 | 2642573.76 | 3278476.8 | 0 | 5675057.4 | 930750 | 0 | 474422.4 | 7443195 | 421344 | 200640 | 84913.92 | 37994344.92 | 0 | 0 | 13503360 | 77079.2 | 30181248 | 744886.8 | 17064144 | 307272 | 19375444.5 | 0 | 25225920 | 4606875 | 407941.56 | 0 | 47175224.04 | 1464116.16 | 0 | 807781.2 | 15578203.2 | 16086297.6 | 0 |  | 131022195.84 | 0 | 4445582.4 | 0 | 11944684.8 | 0 | 0 | 0 | 1087603.2 | 2998118.4 | 6150405 | 1282550 | 831948.55 | 12936606.72 | 44382.7 | 1408350 | 1107000 | 1292818.56 | 603930.72 | 11375294.4 | 0 | 722819.76 | 1542434.82 | 2125598.4 | 1691680 | 922982.4 | 395398.8 | 128820.204 | 0 | 0 | 19812268 | 0 | 2310930 | 0 | 0 | 5823983.88 | 0 | 2188717.5 | 11202105.6 | 5523102 | 0 | 9064529.1 | 831859.2 | 0 | 7430442.24 | 7224998.4 | 13096396.8 | 0 | 422021.6 | 6572961.6 | 28412519 |  | 518246569.37 | 315978040.594 | 834224609.964 | 93513841.814 | 131022195.84 | 60019925.4 | 445688315.9 | 48224787 | 610835.31 | 32931835.3 | 20930400 | 1282473.4 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 96 | 67 | 0 | 304 |  | 0 | 420 | 255 | 100 | 97 | 41 | 212 | 0 | 87 | 0 | 98 | 93 | 0 | 21 | 0 | 0 | 3 | 53 | 55 | 55 | 22 | 25 | 30 | 0 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 2 | 135 | 110 | 0 | 310 | 0 | 182 | 45 | 81 | 35 | 42 | 0 | 25 | 0 | 0 | 1 | 21 | 5 | 25 | 14 | 99 | 139 | 95 | 0 | 0.6 | 58 | 30 | 47 | 43 | 163 | 244 | 61 | 76 | 0 | 149 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 60 | 0 | 133 | 0 | 100 | 0 | 80 | 0 | 115 | 17 | 0 | 0.9 | 305 | 0 | 0 | 0 | 105 | 100 | 0 |  | 948 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 186 | 0 | 392 | 0 | 0 | 8 | 21 | 106 | 0 | 6.2 | 0 | 0 |  | 8868.7 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 354 | 0 | 0 | 420 | 260 | 100 | 96 | 41 | 218 | 0 | 94 | 0 | 99 | 102 | 82 | 0 | 0 | 0 | 48 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 25 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 86 | 0 | 24 | 50 | 20 | 27 | 130 | 100 | 0 | 300 | 0 | 216 | 8 | 80 | 38 | 30 | 0 | 25 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 124 | 141 | 95 | 22 | 0 | 60 | 30 | 50 | 43 | 163 | 246 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 267 | 0 | 0 | 154 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 88 | 0 | 0 | 306 | 17 | 0 | 6 | 113 | 100 | 0 |  | 949 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 21 | 52 | 40 | 65 | 30 | 110 | 15 | 0 | 60 | 50 | 41 | 92 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 188 | 0 | 78 | 100 | 187 | 0 | 393 | 17 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 11090 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 51 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 22 | 35 | 100 | 80 | 0 | 360 | 0 | 215 | 55 | 90 | 38 | 50 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 32 | 21 | 173 | 150 | 95 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 275 | 66 | 76 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  |  | 956 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 40 | 50 | 43 | 43 | 35 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 20 | 0 | 0 | 200 | 0 | 78 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 100 | 0 | 100 | 102 | 100 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 22 | 35 | 100 | 80 | 0 | 360 | 0 | 215 | 55 | 90 | 38 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 32 | 20 | 154 | 150 | 60 | 22 | 1.6 | 60 | 30 | 51 | 44 | 163 | 275 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 88 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  |  | 952 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 50 | 0 | 0 | 65 | 0 | 0 | 50 | 40 | 50 | 43 | 43 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 70 | 0 | 8 | 70 | 660
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 95 | 68 | 0 | 309 | 0 | 0 | 390 | 275 | 7 | 30 | 0 | 217 | 0 | 95 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 35 | 95 | 0 | 16 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 80 | 120 | 0 | 335 | 0 | 155 | 8 | 92 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 14 | 102 | 139 | 40 | 22 | 0.7 | 59 | 30 | 47 | 43 | 100 | 255 | 61 | 74 | 0 | 150 | 0 | 0 | 10 | 320 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5.7 | 50 | 0 | 0 | 0 | 115 | 0 | 0 | 2 | 142 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 941 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 203 | 0 | 77 | 0 | 187 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 495 | 0
199
| Minimum Generation |  | 8276.1 | 8:00
| Highest Generation |  | 11090 | 21:00
| Day Peak Generation |  | 8868.7 | 12:00
| Evening Peak Generation |  | 11090 | 21:00
| HVDC Max Flow |  | 949 | 4:00
| HVDC EvPeak Flow |  | 949 | 21:00
| Load factor L.F |  | 86.51%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-22
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8868.7 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7985.1 | MW
Evening Peak Generation : |  | 11090 | MW Hour : | 21:00 | Available Max Generation : |  | 14865 | MW
E.P. Demand (at gen end) : |  | 11090 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11090 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3365 | MW
Total Gen. (MKWH) : |  | 230.2485 | System Load Factor : | 86.51% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -324 | MW at | 12:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-22
Actual : | 83.99 | Ft.(MSL) , | Rule curve : | 81.57 | Ft.( MSL )
Gas Consumed : | Total = | 1151.66 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 153533767.214
: |  | Coal : | 48224787 | Oil : | 478620151.2 | Total : | 680378705.414
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4004.5328 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1362.1731 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1220.535 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1102.8823 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 996.6445 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 804.2579 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 449.1735 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 207.0608 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 620.2861 |  |  | 0 | 0%
Total | 0 |  | 10767.546 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj(S) 360 MW
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-4,5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Baghabari-100 MW
9) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sonargaon-Haripur 132 kV Ckt-1 was under shut down from 10:05 to 11:11 for C/M.
b) Sonargaon-Haripur 132 kV Ckt-2 was under shut down from 11:12 to 12:10 for C/M.
c) Sonargaon-Daudkandi 132 kV Ckt-1 was under shut down from 12:13 to 12:50 for C/M.
d) Tripura-Cumilla(S) 132 kV Ckt-2 was under shut down from 08:58 to 16:31 for C/M.
e) Tripura-Cumilla(S) 132 kV Ckt-1 tripped at 12:05 from Tripura end showing Dist. Z3(144 km) R,Y,B phases |  |  |  |  | About 100 MW power interruption occurred under Cumilla(S) S/S area
and was switched on at 12:35. |  |  |  |  | from 12:05 to 12:35.
f) Payra-Gopalganj 400 kV Ckt tripped at 10:35 from both ends showing Dist. Z1(93.5 km), R, B phases at Payra
end & Dist. Z1(73.5 km) R, Y phases at Gopalganj end and was switched on at 10:53.
g) Payra Unit-1 tripped at 10:45 showing MFT and was synchronized at 23:32. |  |  |  |  | About 100 MW power interruption occurred under Faridpur S/S area and
h) Bhola CCPP tripped at 10:35 due to low voltage and was synchronized at 17:10. |  |  |  |  | 54 MW was at Barishal(S) S/S area since 10:35 to 14:00.
i) Bhola Aggreko tripped at 10:35 due to low voltage and was synchronized at 14:50.
j) Ashuganj-Ghorashal 230 kV Ckt-1 tripped at 12:21 from both ends showing Dist. B,C at Ashuganj end &
Remote A,B at Ghorashal end and was switched on at 13:00.
k) Payra-Gopalganj 400 kV Ckt was opened at 12:51 due to voltage unbalanced and was closed
at 14:41.
l) Rampura-Bashundhara 132 kV CKt-1 was switched on at 09:50.
m) Bheramara 410 MW GT was synchronized at 13:21 and ST was at 14:22..
n) Haripur-EGCB 132 kV Ckt & Haripur 132 kV main Bus was under shut down from 10:37 to 18:37 for C/M.
o) Haripur-Bhulta 230 kV Ckt-1 was under shut down from 08:37 to 21:43 for D/W.
p) Madanganj 132/33 kV T1 transformer was under shut down from 11:27 to 14:51 for Y-phase LA replacement.
q) Cumilla(N)-Chaddogram 132 kV Ckt-1 tripped at 16:32 from both ends showing Dist. A at Cumilla(N) end
& Dist. R-phase, Z1 at Chaddogram end and was switched on at 16:44.
r) Cumilla(N)-Chaddogram 132 kV Ckt-1 again tripped at 16:49 from both ends showing Dist. A at Cumilla(N) end
& Dist. R-phase, Z1 at Chaddogram end and was switched on at 21:11.
s) Bhola GT-1 was synchronized at 17:00.
t) Sreemangal 132/33 kV T2 & T3 transformers tripped at 18:22 showing PRD and T2 was switched on at 19:32.
u) Baghabari 100 MW tripped at 19:17 due to low gas pressure.
v) Halishahar 132/33 kV T1 transformer was under shut down from 20:45 to 21:59 due to R/H at 33 kV CT.
w) Cumilla(N)-Daudkandi 132 kV Ckt-1 tripped at 04:20(22/06/2020) from both ends showing Dist. A,B phases
Cumilla(N) end & Dist. Z2 B-phase at Daudkandi end and was switched on at 05:18(22/06/2020).
x) Madunaghat 132/33 kV T1 transformer was under shut down from 05:37(22/06/2020) to 07:56(22/06/2020)
due to R/H maintenance at different points.
y) Haripur-Bhulta 230 kV Ckt-2 was shut down at 07:34(22/06/2020).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 720000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7138891
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 68 | 1516256 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2042818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 354 | 8014000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9446250 | Frequency Control.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2066880
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6328931 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2335344
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 41 | 689326 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 370763 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 454824
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 94 | 1958000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 99 | 2252160
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 218 | 4957966 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2178864
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 366624
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1183680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 484320 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 968205
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 763286
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1277700 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 659600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 801100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 49284 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 267 | 5025707
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 4610 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 3067200 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 487500 | Engine problem
| Dhaka area Total |  |  |  | 5791 | 3204 | 67610089
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 56129 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 63720
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 416160
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 98 | 2262353 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3209236 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 46836 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 86 | 496993 | Low demand
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 9360 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2093760
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 444912
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 481440
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 635520 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24601
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 6240109
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 168096 | Low demand
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2415360
| Chattogram area Total |  |  |  | 2266 | 1087 | 21264585
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 130 | 2402298
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2275850 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4682000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7412600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 249000 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 813960 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 738240 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 652363 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 588176 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 148 | 2748290
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 39416 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2060720
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 28320 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 488268
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 174780 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2790720
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 615800 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 165293 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 396340 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 4992 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 6 | 80940 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1817760
| Cumilla Area Total |  |  |  | 2980 | 1445 | 31226126
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 141 | 3162720 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 366840
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1338240
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7250
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 154 | 2596800
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2766000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 527 | 10237850
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1397000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714000
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3332700
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 246 | 5628000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1096800
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 43 | 982656
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1341408 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1716480 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3280380
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 561792
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7369500 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232560
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1232 | 28342276
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 949 | 22746909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1519680
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 103680 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 286080 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 4233888 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 590250
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 658560
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 79680 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 105 | 765360
| Khulna Area Total |  |  |  | 2284 | 1744 | 30984087
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1325472
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 536741
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1135000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1459145 | Engine problem
| Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 15 | 15965
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 0 | 6472100 | Tripped at 10:24.
| Barisal Area Total |  |  |  | 1084 | 298 | 10944423
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 540000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 687000 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 131384
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 59442
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 53463 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 159178
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4412109 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4720600 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 393 | 9156090 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 174400
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 480720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 255096
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 170172
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 219360 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 1285344
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 782976
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 889440 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1280 | 24176774
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3655400 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 81000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1687680
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38192
| Rangpur Area Total |  |  |  | 605 | 273 | 5462272
| Total |  |  |  | 19818 | 11090 | 230248482
| Eastern Grid Total |  |  |  | 13662 | 7495 | 158680926
| Western Grid Total |  |  |  | 6156 | 3595 | 71567556
| National Grid Total |  |  |  | 19818 | 11090 | 230248482
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-22
(a) ENTIRE EASTERN GRID : |  | 6788 | MW | (b) ENTIRE WESTERN GRID : |  | 3581 | MW
i) Dhaka area |  | 3464 | MW | i) Khulna area |  | 1389 | MW
ii) Chittagong area |  | 967 | MW | ii) Rajshahi area |  | 1161 | MW
iii) Comilla area |  | 989 | MW | iii) Barisal area |  | 293 | MW
iv) Mymensingh area |  | 936 | MW | iv) Rangpur area |  | 738 | MW
v) Sylhet area |  | 432 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10369 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 12:00 | Sherpur | 114 | 21:00 | Benapol | 48 | 21:00
Munsiganj | 114 | 1:00 | Srimongal | 45 | 15:00 | Jhenida | 99 | 22:00
Sonargaon | 68 | 24:00 | Shahjibazar | 100 | 21:00 | Bottail | 118 | 20:00
Shyampur | 182 | 24:00 | Fenchuganj | 46 | 19:00 | G.K Project | 50 | 20:00
Bhulta | 183 | 24:00 | Kulawara | 46 | 19:30 | Faridpur | 174 | 0.83333
Madanganj | 52 | 24:00 | Sylhet | 115 | 19:30 | Madaripur | 97 | 0.83333
Shitalakhya | 98 | 13:00 | Chatak | 26 | 23:00 | Sariatpur | 60 | 21:00
Rahim steel | 12 | 12:00 | Sunamganj | 40 | 20:00 | Gopalganj | 82 | 19:30
Matuail | 84 | 10:00 | Biani Bazar | 54 | 23:00 | Bagerhat | 93 | 21:0
Ghorasal | 69 | 21:00 | Comilla (S) | 140 | 22:00 | Mongla | 36 | 1:00
Narsingdi | 154 | 21:00 | Comilla(N) | 113 | 21:00 | Satkhira | 100 | 0.875
Haripur (SBU) | 106 | 12:00 | Chandpur | 90 | 22:00 | Gallamari | 47 | 19:00
Ullon | 52 | 23:00 | Feni | 97 | 21:00 | Magura | 50 | 0.83333
Hasnabad | 184 | 21:00 | Chowmuhani | 150 | 19:30 | Norail | 37 | 20:00
Magbazar | 95 | 15:00 | Ashuganj | 58 | 23:00 | Chuadanga | 83 | 20:00
Maniknagar | 98 | 12:00 | Daudkandi | 126 | 23:00 | Barisal(N) | 41 | 0.91667
Bangabhaban | 32 | 10:00 | B.Baria | 140 | 20:00 | Barisal (S) | 92 | 0.8125
Narinda | 92 | 13:00 | Ramganj | 96 | 19:30 | Patuakhali | 103 | 0.91667
Dhanmondi | 139 | 12:00 | Chaddagram | 32 | 21:00 | Bhandaria | 52 | 20:00
Lalbag | 90 | 13:00 | PHP | 11 | 18:30 | Borhan Uddin | 41 | 22:00
Madartek | 64 | 19:30 | Madunaghat | 55 | 19:30 | Ishurdi | 54 | 21:00
Dhaka University |  |  | Hathazari | 89 | 0.83333 | Ruppur Paromanobik | 1 | 21:00
Mirpur | 94 | 12:00 | Khulshi | 154 | 0.041667 | Natore | 114 | 20:00
Kalyanpur | 78 | 12:00 | Halishahar | 115 | 0.8125 | Bogra | 152 | 21:00
Gulshan | 110 | 12:00 | Baraulia | 132 | 0.083333 | Noagaon | 127 | 22:0
Uttara | 75 | 12:00 | Sikalbaha | 21 | 0.8125 | Rajshahi | 134 | 21:00
Uttara New | 21 | 18:00 | Dohazari | 88 | 0.91667 | Rajshahi New | 10 | 21:00
Kamrangirchar | 85 | 12:00 | Cox'sbazar | 78 | 0.83333 | C.Nawabganj | 69 | 21:00
Savar | 128 | 15:00 | Chandraghona | 30 | 0.83333 | Amnura | 40 | 21:00
Bhasantec | 137 | 15:00 | Kaptai | 4 | 0.77083 | Pabna | 113 | 21:00
Agargaon | 58 | 15:00 | A. Khaer Stl. | 8 | 0.20833 | Shahjadpur | 91 | 21:00
Satmosjid | 92 | 15:00 | Bakulia | 93 | 0.41667 | Serajganj | 97 | 21:00
Tongi | 127 | 0.5 | Julda | 22 | 0.375 | Niyamatpur | 50 | 21:00
Kabirpur | 220 | 15:00 | TK chemical | 22 | 0.041667 | Joypurhat | 39 | 20:00
Basundhara | 107 | 14:00 | Modern Steel | 14 | 0.45833 | Sherpur(Bogura) | 45 | 21:00
Manikganj | 64 | 22:00 | Shahmirpur | 25 | 0.083333 | Mohastangor | 52 | 21:00
Joydevpur | 175 | 15:00 | Khagrachhari | 22 | 0.8125 | Rangpur | 134 | 23:00
New Tongi | 95 | 15:00 | Matarbari | 27 | 0.875 | Lalmonirhat | 58 | 20:00
Kodda | 189 | 10:00 | Baroiar Hat | 32 | 0.79167 | Saidpur | 101 | 20:00
Dhamrai | 88 | 19:30 | Rangamati | 10 | 0.79167 | Purbasadipur | 106 | 20:00
Rajendrapur | 90 | 19:30 | Abul Khair 230 | 34 | 0.66667 | Thakurgaon | 76 | 21:00
Valuka | 80 | 21:00 | BSRM | 151 | 0.45833 | Palashbari | 118 | 22:00
Tangail | 176 | 21:00 | GPH Ispat | 64 | 0.45833 | Barapukuria | 49 | 21:00
Mymensing | 215 | 20:00 | Goalpara | 20 | 13:00 | Panchagar | 47 | 21:00
Kishorganj | 133 | 23:00 | Central s/s | 84 | 20:00 | Joldhaka | 27 | 22:00
Netrokona | 110 | 20:00 | Noapara | 68 | 20:00 | Kurigram | 57 | 20:00
Jamalpur | 125 | 21:00 | Jessore | 92 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 400 | 18:30 | 392 | 9:00 | Kaliakoir | 384 | 0.75 | 371 | 0.375
| Bheramara | 397 | 18:30 | 391 | 1:00 | Bhulta | 394 | 0.79167 | 384 | 0.375
| Ashuganj(N) | 398 | 5:00 | 391 | 9:00 | Gopalganj | 418 | 0.75 | 323 | 0.54167
| Payra | 424 | 12:00 | 0 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 18:00 | 235 | 1:00 | Comilla (N) | 236 | 14:00 | 229 | 9:00
| Ishurdi | 235 | 15:00 | 223 | 4:00 | Hathazari | 229 | 19:30 | 222 | 10:00
| Ashuganj | 237 | 14:00 | 234 | 9:00 | Megnaghat | 238 | 19:30 | 231 | 2:00
| Serajganj | 232 | 18:30 | 225 | 4:00 | Fenchuganj | 240 | 4:00 | 236 | 1:00
| Baghabari | 238 | 7:00 | 230 | 1:00 | Siddhirganj | 234 | 4:00 | 226 | 9:00
| Barapukuria | 233 | 18:00 | 222 | 21:00 | Maniknagar | 231 | 18:30 | 225 | 9:00
| Bogra | 230 | 19:00 | 216 | 21:00 | Agargaon | 230 | 20:00 | 222 | 9:00
| Rajshahi | 234 | 17:00 | 220 | 22:00 | Barisal | 250 | 17:00 | 180 | 13:00
| Khulna South | 226 | 19:00 | 208 | 19:30 | AKSML | 227 | 21:00 | 217 | 9:00
| Rampura | 229 | 18:30 | 224 | 8:00 | BSRM | 229 | 19:30 | 217 | 9:00
| Haripur | 231 | 19:30 | 225 | 10:00 | Bibiyana | 238 | 12:00 | 234 | 9:00
| Hasnabad | 231 | 20:00 | 226 | 9:00 | Bhulta | 234 | 17:00 | 228 | 9:00
| Shyampur | 229 | 20:00 | 220 | 9:00 | Ashuganj (S) | 237 | 13:00 | 232 | 9:00
| Aminbazar | 231 | 18:30 | 223 | 9:00 | Kaliakoir | 234 | 18:00 | 225 | 9:00
| Tongi | 228 | 5:00 | 225 | 9:00 | GPH | 226 | 18:00 | 215 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:00 | 129 | 9:00 | Hathazari | 136 | 0.83333 | 132 | 0.125
| Munsiganj | 138 | 20:00 | 132 | 9:00 | Khulshi | 135 | 0.8125 | 129 | 0.375
| Sonargaon | 134 | 19:30 | 130 | 1:00 | Halishahar | 138 | 0.79167 | 129 | 0.375
| Shyampur | 138 | 19:30 | 133 | 9:00 | Baraulia | 134 | 0.8125 | 129 | 0.33333
| Bhulta | 128 | 18:30 | 122 | 11:00 | Sikalbaha | 138 | 19:30 | 131 | 0.375
| Madanganj | 131 | 4:00 | 129 | 7:00 | Dohazari | 136 | 20:00 | 127 | 0.33333
| Shitalakhya | 142 | 19:30 | 132 | 9:00 | Cox'sbazar | 127 | 0.083333 | 117 | 0.79167
| Rahim steal | 134 | 18:00 | 129 | 10:00 | Chandraghona | 137 | 0.8125 | 131 | 0.375
| Matuail | 134 | 19:00 | 129 | 9:00 | Kaptai | 135 | 18:00 | 132 | 0.29167
| Ghorasal | 138 | 1:00 | 136 | 8:00 | A. Khaer Stl. | 135 | 0.8125 | 130 | 6:00
| Narsinghdi | 128 | 4:00 | 125 | 10:00 | Bakulia | 136 | 0.8125 | 129 | 0.375
| Haripur (SBU) | 135 | 19:30 | 129 | 9:00 | Julda | 136 | 0.041667 | 132 | 0.45833
| Ullon | 137 | 19:00 | 133 | 8:00 | TK Chemical | 138 | 0.83333 | 130 | 9:00
| Hasnabad | 137 | 19:00 | 131 | 8:00 | Modern Steel | 136 | 0.8125 | 130 | 0.375
| Magbazar | 137 | 20:00 | 133 | 10:00 | Shahmirpur | 137 | 0.8125 | 130 | 0.29167
| Maniknagar | 135 | 3:00 | 131 | 10:00 | Khagrachhari | 134 | 0.083333 | 132 | 0.29167
| Bangabhaban | 135 | 3:00 | 131 | 10:00 | Matarbari | 130 | 0.5 | 122 | 0.79167
| Narinda | 135 | 3:00 | 131 | 10:00 | Baroiar Hat | 133 | 0.54167 | 128 | 0.95833
| Dhanmondi | 137 | 19:00 | 133 | 8:00 | Rangamati | 136 | 0.8125 | 131 | 8:00
| Lalbag | 138 | 19:30 | 129 | 9:00 | Goalpara S/S | 137 | 18:30 | 127 | 4:00
| Madartek | 137 | 5:00 | 133 | 9:00 | Khulna Central S/S | 137 | 0.79167 | 125 | 4:00
| Dhaka University |  |  |  |  | Noapara | 136 | 19:00 | 125 | 12:00
| Mirpur | 133 | 5:00 | 128 | 11:00 | Jessore | 132 | 19:00 | 116 | 3:00
| Kalyanpur | 132 | 5:00 | 127 | 11:00 | Benapol | 131 | 18:00 | 116 | 3:00
| Gulshan | 136 | 5:00 | 132 | 11:00 | Jhenida | 127 | 0.70833 | 113 | 4:00
| Uttara | 132 | 5:00 | 127 | 11:00 | Bottail | 132 | 17:00 | 116 | 3:00
| Uttara New | 134 | 5:00 | 127 | 11:00 | G.K Project | 138 | 0.70833 | 125 | 4:00
| Kamrangirchar | 135 | 5:00 | 130 | 11:00 | Faridpur | 135 | 18:00 | 115 | 13:00
| Savar | 131 | 5:00 | 127 | 13;00 | Madaripur | 139 | 0.75 | 105 | 13:00
| Bhasantec | 132 | 6:00 | 126 | 10:00 | Shariyatpur S/S | 138 | 0.33333 | 109 | 13:00
| Agargaon | 131 | 6:00 | 126 | 10:00 | Gopalganj | 144 | 18:00 | 110 | 13:00
| Satmosjid | 132 | 6:00 | 125 | 10:00 | Bagerhat | 135 | 0.77083 | 122 | 19:30
| Tongi | 137 | 0.8125 | 133 | 11:00 | Mongla | 132 | 0.75 | 119 | 19:30
| Kabirpur | 134 | 18:30 | 130 | 22:00 | Satkhira | 135 | 0.75 | 123 | 19:30
| Basundhara | 136 | 21:00 | 131 | 9:00 | Gallamari | 138 | 19:00 | 126 | 4:00
| Manikganj | 140 | 20:00 | 130 | 9:00 | Magura | 126 | 0.70833 | 110 | 19:30
| Joydevpur | 141 | 21:00 | 136 | 9:00 | Norail | 124 | 0.70833 | 107 | 20:00
| New Tongi | 137 | 0.83333 | 129 | 9:00 | Chuadanga | 123 | 18:30 | 103 | 4:00
| Kodda | 146 | 1:00 | 124 | 0.41667 | Barisal(N) | 140 | 18:00 | 107 | 13:00
| Dhamrai | 133 | 18:00 | 129 | 22:00 | Barisal (S) | 139 | 0.75 | 104 | 13:00
| Rajendrapur | 133 | 19:30 | 122 | 10:00 | Patuakhali | 136 | 0.75 | 102 | 13:00
| Valuka | 129 | 11:00 | 118 | 19:00 | Bhandaria | 135 | 18:00 | 100 | 13:00
| Tangail | 135 | 12:00 | 130 | 19:30 | Ishurdi | 138 | 18:00 | 127 | 4:00
| Mymensing | 132 | 13:00 | 120 | 22:00 | Ruppur Paromanobik | 137 | 17:00 | 128 | 2:00
| Kishorganj | 131 | 18:00 | 122 | 1:00 | Natore | 136 | 19:00 | 126 | 1:00
| Netrokona | 129 | 11:00 | 117 | 22:00 | Bogra | 134 | 19:00 | 124 | 21:00
| Jamalpur | 140 | 11:00 | 134 | 20:00 | Noagaon | 130 | 19:00 | 119 | 21:00
| Sherpur | 140 | 11:00 | 125 | 0.77083 | Rajshahi | 134 | 18:00 | 122 | 3:00
| Srimongal | 137 | 8:00 | 133 | 0.91667 | Rajshahi New | 134 | 18:00 | 125 | 2:00
| Shahjibazar | 135 | 12:00 | 130 | 0.041667 | C.Nawabganj | 134 | 19:00 | 122 | 4:00
| Fenchuganj | 136 | 7:00 | 133 | 0.041667 | Amnura | 134 | 18:00 | 122 | 4:00
| Khulawara | 134 | 5:00 | 131 | 0.95833 | Pabna | 134 | 17:00 | 124 | 19:00
| Sylhet | 133 | 9:00 | 130 | 0.95833 | Shahjadpur | 139 | 18:00 | 133 | 22:00
| Chatak | 132 | 8:00 | 129 | 1:00 | Serajganj | 135 | 19:00 | 126 | 21:00
| Sunamganj | 130 | 6:00 | 128 | 0.041667 | Niyamatpur | 128 | 18:30 | 115 | 21:00
| Biani Bazar | 132 | 7:00 | 127 | 0.95833 | Joypurhat | 130 | 18:00 | 119 | 21:00
| Comilla(s) | 127 | 7:00 | 117 | 15:00 | Sherpur(Bogura) | 135 | 19:00 | 125 | 21:00
| Comilla(n) | 138 | 19:30 | 132 | 9:00 | Mohastangor | 134 | 19:00 | 122 | 21:00
| Chandpur | 132 | 11:00 | 129 | 7:00 | Rangpur | 130 | 19:00 | 116 | 22:00
| Feni | 134 | 19:30 | 130 | 7:00 | Lalmonirhat | 125 | 17:00 | 110 | 21:00
| Chowmuhani | 132 | 18:30 | 126 | 23:00 | Saidpur | 128 | 17:00 | 114 | 21:00
| Ashuganj | 137 | 18:00 | 132 | 1:00 | Purbasadipur | 126 | 18:30 | 106 | 22:00
| Daudkandi | 135 | 19:30 | 128 | 9:00 | Thakurgaon | 124 | 6:00 | 105 | 21:00
| B.Baria | 133 | 7:00 | 128 | 21:00 | Palashbari | 130 | 19:00 | 116 | 1:00
| Ramganj | 128 | 19:30 | 123 | 9:00 | Barapukuria | 133 | 18:00 | 122 | 21:00
| Chaddagram | 135 | 19:30 | 129 | 23:00 | Panchagar | 124 | 17:00 | 103 | 22:00
| PHP | 134 | 19:30 | 127 | 9:00 | Joldhaka | 128 | 19:00 | 109 | 21:00
| Madanhat | 139 | 19:30 | 133 | 9:00 | Kurigram | 127 | 18:30 | 106 | 21:00

## L-Curve
Date | 2020-06-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 155 | 7244 | 3447 | 10691 |  |  |  | QF-LDC-12
0:30 | 113.5 | 7064.5 | 3579 | 10643.5 | Date: | 2020-06-22
1:00 | 72 | 6885 | 3711 | 10596
1:30 | 59.5 | 6828 | 3621 | 10449
2:00 | 47 | 6771 | 3531 | 10302
2:30 | 26.5 | 6739 | 3456 | 10195 | [5 empty] | Gen. at Eve. Peak | 11090 | 11090 MW (21:00 )
3:00 | 6 | 6707 | 3381 | 10088 | [6 empty] | 21:00
3:30 | 40.5 | 6741 | 3153 | 9894 | [5 empty] | Gen. at Day Peak | 8868.7 | 8868.7 MW (12:00 )
4:00 | 75 | 6775 | 2925 | 9700 | [6 empty] | 12:00
4:30 | 37.5 | 6691 | 2908.5 | 9599.5 | [5 empty] | Highest Generation | 11090
5:00 | 0 | 6607 | 2892 | 9499 | [6 empty] | 21:00
5:30 | 25 | 6182.5 | 2851.1 | 9033.6
6:00 | 50 | 5758 | 2810.2 | 8568.2
6:30 | 48.5 | 5710.15 | 2740.2 | 8450.35
7:00 | 47 | 5662.3 | 2670.2 | 8332.5
7:30 | 40.5 | 5666.75 | 2637.55 | 8304.3
8:00 | 34 | 5671.2 | 2604.9 | 8276.1
8:30 | 112 | 5727 | 2687.1 | 8414.1
9:00 | 190 | 5782.8 | 2769.3 | 8552.1
9:30 | 160 | 5940.2 | 2761.05 | 8701.25
10:00 | 130 | 6097.6 | 2752.8 | 8850.4
10:30 | 176.5 | 6312.25 | 2443.6 | 8755.85
11:00 | 223 | 6526.9 | 2134.4 | 8661.3
11:30 | 273.5 | 6606.7 | 2158.3 | 8765
12:00 | 324 | 6686.5 | 2182.2 | 8868.7
12:30 | 307 | 6765.65 | 2192 | 8957.65
13:00 | 290 | 6844.8 | 2201.8 | 9046.6
13:30 | 225 | 6742.4 | 2234.85 | 8977.25
14:00 | 160 | 6640 | 2267.9 | 8907.9
14:30 | 99.5 | 6749.75 | 2439.35 | 9189.1
15:00 | 39 | 6859.5 | 2610.8 | 9470.3
15:30 | 106 | 6656.5 | 2720.4 | 9376.9
16:00 | 173 | 6453.5 | 2830 | 9283.5
16:30 | 188.5 | 6227.65 | 2759.15 | 8986.8
17:00 | 204 | 6001.8 | 2688.3 | 8690.1
17:30 | 180.5 | 5840.75 | 2651.4 | 8492.15
18:00 | 157 | 5679.7 | 2614.5 | 8294.2
18:30 | 212.5 | 5940.35 | 2848.25 | 8788.6
19:00 | 268 | 6201 | 3082 | 9283
19:30 | 250 | 7158 | 3433 | 10591
20:00 | 300 | 7388 | 3496 | 10884 |  |  |  | Executive Engineer
20:30 | 274 | 7441.5 | 3545.5 | 10987 |  |  |  | Network Operation Division
21:00 | 248 | 7495 | 3595 | 11090
21:30 | 240 | 7427 | 3556 | 10983
22:00 | 232 | 7359 | 3517 | 10876 |  |  |  |  | Page 6 of 7
22:30 | 211.5 | 7336.5 | 3502.5 | 10839
23:00 | 191 | 7314 | 3488 | 10802
23:30 | 173 | 7279 | 3467.5 | 10746.5
24:00 | 155 | 7244 | 3447 | 10691
11090 MW (21:00 )
8868.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-22 |  | Energy | 230248482
[10 empty] | 2020-06-22 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3641 | 946 | 2215 | 3205 | 300 | 100 | 277 | 0 | 136
0:30 | 3493 | 947 | 2154.5 | 3106 | 539.5 | 99.5 | 225.5 | 0 | 143 | Date: | 2020-06-22
1:00 | 3345 | 948 | 2094 | 3007 | 779 | 99 | 174 | 0 | 150
1:30 | 3328 | 948 | 2099 | 2914.5 | 779 | 98 | 134.5 | 0 | 148 | [7 empty] | Total Energy | 230.2485 | Total Energy Gen 230.248 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.248 MKWHr
2:00 | 3311 | 948 | 2104 | 2822 | 779 | 97 | 95 | 0 | 146 | [7 empty] | Energy not Served | 0
2:30 | 3305 | 948 | 2105.5 | 2745 | 779 | 97 | 72.5 | 0 | 143 | [7 empty] | Energy Requirement | 230.2485
3:00 | 3299 | 948 | 2107 | 2668 | 779 | 97 | 50 | 0 | 140
3:30 | 3173.5 | 948.5 | 2133.5 | 2574 | 779.5 | 97 | 50 | 0 | 138 | [6 empty] | Shortage
4:00 | 3048 | 949 | 2160 | 2480 | 780 | 97 | 50 | 0 | 136
4:30 | 3038.5 | 948.5 | 2184.5 | 2368.5 | 780 | 97.5 | 50 | 0 | 132
5:00 | 3029 | 948 | 2209 | 2257 | 780 | 98 | 50 | 0 | 128
5:30 | 3035 | 948.5 | 2196.5 | 1828.5 | 779.5 | 98 | 25 | 0 | 121
6:00 | 3041 | 949 | 2184 | 1400 | 779 | 98 | 0 | 0 | 114
6:30 | 3037.5 | 948.5 | 2175.5 | 1323.5 | 752.5 | 98 | 0 | 0 | 110 |  |  |  |  | Coal
7:00 | 3034 | 948 | 2167 | 1247 | 726 | 98 | 0 | 0 | 106
7:30 | 3059 | 948 | 2158 | 1241 | 687.5 | 98 | 0 | 0 | 104 |  |  |  | Oil |  |  |  | ,
8:00 | 3084 | 948 | 2149 | 1235 | 649 | 98 | 0 | 0 | 102
8:30 | 3131.5 | 948 | 2197.5 | 1280.5 | 649 | 99 | 0 | 0 | 96.5
9:00 | 3179 | 948 | 2246 | 1326 | 649 | 100 | 0 | 0 | 91
9:30 | 3183 | 948 | 2201 | 1512 | 650 | 100 | 0 | 0 | 94.5
10:00 | 3187 | 948 | 2156 | 1698 | 651 | 100 | 0 | 0 | 98
10:30 | 3181 | 948 | 2131 | 1878.5 | 400.5 | 100 | 0 | 0 | 99.5
11:00 | 3175 | 948 | 2106 | 2059 | 150 | 100 | 0 | 0 | 101
11:30 | 3136.5 | 948 | 2092 | 2223.5 | 150 | 100 | 0 | 0 | 100
12:00 | 3098 | 948 | 2078 | 2388 | 150 | 100 | 0 | 0 | 99
12:30 | 3105.5 | 948.5 | 2007 | 2521 | 150 | 100 | 20.5 | 0 | 98.5
13:00 | 3113 | 949 | 1936 | 2654 | 150 | 100 | 41 | 0 | 98
13:30 | 3113 | 949 | 1936 | 2654 | 150 | 100 | 41 | 0 | 98
14:00 | 3113 | 949 | 1936 | 2654 | 150 | 100 | 41 | 0 | 98
14:30 | 3161.5 | 949 | 2023 | 2719 | 150 | 97.5 | 43 | 0 | 109
15:00 | 3210 | 949 | 2110 | 2784 | 150 | 95 | 45 | 0 | 120
15:30 | 3243 | 948.5 | 2040.5 | 2707 | 150 | 95 | 65 | 0 | 120
16:00 | 3276 | 948 | 1971 | 2630 | 150 | 95 | 85 | 0 | 120
16:30 | 3271.5 | 948.5 | 1902.5 | 2398.5 | 150 | 95.5 | 97.5 | 0 | 116
17:00 | 3267 | 949 | 1834 | 2167 | 150 | 96 | 110 | 0 | 112
17:30 | 3174 | 949 | 1710.5 | 2176 | 150 | 96.5 | 125 | 0 | 108
18:00 | 3081 | 949 | 1587 | 2185 | 150 | 97 | 140 | 0 | 104
18:30 | 3169.5 | 949 | 1641.5 | 2410 | 150.5 | 97 | 251.5 | 0 | 119
19:00 | 3258 | 949 | 1696 | 2635 | 151 | 97 | 363 | 0 | 134
19:30 | 3372 | 948 | 1995 | 3403 | 150 | 97 | 502 | 0 | 124
20:00 | 3415 | 949 | 2045 | 3549 | 150 | 98 | 556 | 0 | 122
20:30 | 3507 | 949 | 2120.5 | 3502 | 150 | 98 | 537.5 | 0 | 123
21:00 | 3599 | 949 | 2196 | 3455 | 150 | 98 | 519 | 0 | 124
21:30 | 3621 | 948.5 | 2207.5 | 3368 | 150 | 99 | 465 | 0 | 124
22:00 | 3643 | 948 | 2219 | 3281 | 150 | 100 | 411 | 0 | 124
22:30 | 3641.5 | 947 | 2216 | 3243 | 149.5 | 100 | 411 | 0 | 131
23:00 | 3640 | 946 | 2213 | 3205 | 149 | 100 | 411 | 0 | 138
23:30 | 3640.5 | 946 | 2214 | 3205 | 224.5 | 100 | 344 | 0 | 137 | Max Temp. in Dhaka |  | 31.2° C
24:00 | 3641 | 946 | 2215 | 3205 | 300 | 100 | 277 | 0 | 136
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 230.248 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 230.248 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 64 | 62 | 62 | 62 | 63 | 63 | 63 | 63 | 65 | 65 | 65 | 65 | 65 | 62 | 60 | 60 | 61 | 62 |  | 62 | 62 | 63 | 63 | 65 | 65 | 65 | 1426353
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 0 | 18 | 18 | 25 |  |  |  | 56129
| Teknaf 20MW PP (Solartech) | [5 empty] | 2.6 | 2.9 | 6.6 | 3.4 | 4.2 | 12.9 |  | 1.7 | 4 | 4.6 | 4.2 | 2.7 | 0.6 | [8 empty] | 63720
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 138 | 140 | 140 | 140 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 139 | 140 | 140 | 104 | 104 | 104 |  | 70 | 140 | 140 | 139 | 139 | 139 | 140 | 3209236
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 70 | 79 | 85 | 86 | 95 | 102 | 91 | 496993
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [20 empty] | 10 | [5 empty] | 46836
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 4992
14 | Titas 50 MW Peaking PP | [20 empty] | 26 | 50 |  |  |  |  | 39416
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 88 | 88 | 88 | 95 | 94 | 96 | 96 | 96 | 87 | 87 | 87 | 87 | 87 | 37 | 35 | 37 | 35 | 37 |  | 37 | 37 | 34 | 94 | 94 | 94 | 94 | 1958000
17 | Siddhirganj 335 MW CCPP | 150 | 180 | 180 | 210 | 214 | 214 | 215 | 214 | 213 | 214 | 209 | 212 | 190 | 180 | 212 | 214 | 218 | 144 |  | 144 | 219 | 219 | 218 | 215 | 217 | 217 | 4957966
18 | Kodda 300 MW PP Unit-2 (Summit) | 267 | 267 | 269 | 264 | 195 | 45 | 45 | 45 | 45 | 66 | 130 | 200 | 254 | 250 | 253 | 253 | 253 | 253 |  | 268 | 268 | 267 | 267 | 268 | 258 | 249 | 5025707
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 55 | 55 | 55 | 55 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 652363
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 720000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 |  | 250 | 285 | 285 | 300 | 300 | 300 | 300 | 7138891
26
28 | Ashuganj TPP Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 120 | 80 | 80 | 80 |  | 80 | 80 | 80 | 130 | 135 | 135 | 135 | 2402298
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 2275850
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 38 | 36 | 36 | 36 | 36 | 37 |  | 34 | 34 | 36 | 38 | 38 | 38 | 38 | 813960
33 | Ashuganj 225 MW CCPP | 182 | 190 | 181 | 182 | 181 | 182 | 182 | 184 | 195 | 181 | 202 | 182 | 182 | 183 | 190 | 183 | 182 | 182 |  | 203 | 216 | 217 | 216 | 214 | 213 | 214 | 4682000
34 | Ashuganj 450 MW CCPP(South) | 125 | [25 empty] | 249000
| Ashuganj 450 MW CCPP(North) | 260 | 280 | 280 | 310 | 310 | 310 | 310 | 310 | 330 | 315 | 340 | 310 | 305 | 275 | 260 | 260 | 260 | 260 |  | 295 | 260 | 260 | 300 | 335 | 325 | 310 | 7412600
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 15 | 25 | 40 | 42 | 46 | 48 | 47 | 43 | 41 | 42 | 45 | 45 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 738240
36 | Chandpur 150 MW CCPP | 85 | 91 | 90 | 80 | 90 | 88 | 88 | 91 | 91 | 81 | 90 | 81 | 80 | 90 | 90 | 85 | 90 | 83 |  | 90 | 80 | 85 | 80 | 91 | 91 | 91 | 2060720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 380 | 420 | 420 | 420 | 420 | 420 | 420 | 380 | 420 | 420 | 420 | 400 | 420 | 380 | 380 | 320 |  | 350 | 400 | 420 | 420 | 420 | 420 | 420 | 9446250
41 | Haripur 360MW CCPP(HPL) | 338 | 339 | 338 | 357 | 355 | 355 | 357 | 356 | 352 | 354 | 352 | 304 | 304 | 303 | 349 | 304 | 304 | 296 |  | 304 | 355 | 354 | 354 | 352 | 354 | 354 | 8014000
42 | RPCL 210MW CCPP | 141 | 141 | 141 | 141 | 141 | 141 | 140 | 139 | 138 | 139 | 140 | 139 | 140 | 125 | 125 | 124 | 124 | 126 |  | 123 | 127 | 127 | 141 | 134 | 139 | 139 | 3162720
43
44 | Fenchugonj CCPP Phase-1 | 58 | 58 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 59 | 59 | 58 | 58 | 58 | 60 |  | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 1397000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714000
46 | Shajibazar 330 MW CCPP | 243 | 249 | 243 | 244 | 245 | 244 | 243 | 251 | 249 | 248 | 245 | 244 | 247 | 248 | 248 | 246 | 243 | 246 |  | 253 | 242 | 244 | 246 | 254 | 252 | 250 | 5628000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 60 | 61 | 61 | 61 | 61 | 61 | 59 | 60 | 59 | 61 | 61 | 40 | 40 | 40 | 40 | 40 |  | 61 | 63 | 62 | 61 | 61 | 61 | 61 | 1341408
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 77 | 77 | 77 | 76 | 76 | 74 | 74 | 74 | 76 | 76 | 76 | 76 | 76 | 76 | 20 |  | 20 | 76 | 76 | 76 | 76 | 77 | 77 | 1716480
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 121 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 149 | 150 | 100 | 100 | 70 |  | 130 | 150 | 150 | 150 | 150 | 150 | 150 | 3280380
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232560
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 45 | 45 | 47 | 50 | 50 | 47 | 47 | 50 | 14 |  | 23 | 45 | 50 | 50 | 50 | 50 | 50 | 1096800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 561792
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 305 | 305 | 305 | 295 | 300 | 305 | 305 | 315 | 300 | 300 | 300 | 275 | 295 | 315 | 285 | 285 | 300 |  | 280 | 270 | 280 | 290 | 290 | 310 | 315 | 7369500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | [9 empty] | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 763286
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 |  | 17 | 17 | 17 | 18 | 18 | 17 | 18 | 19 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 444912
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 19 | 19 | 21 | 21 | 454824
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [5 empty] | 17 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 366840
63 | Impoprt (Tripura) | 150 | 146 | 140 | 136 | 128 | 114 | 106 | 102 | 91 | 98 | 101 | 99 | 98 | 108 | 120 | 120 | 112 | 104 |  | 134 | 124 | 122 | 124 | 124 | 138 | 136 | 2790720
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 27 | 33 | 41 | 39 | 26 | 6 | 3 | 2 | 2 | 2 | 2 | 4 | 4 | 7 | 14 | 6 |  | 18 | 15 | 17 | 27 | 28 | 32 | 32 | 481440
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 488268
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174780
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 10 | 10 | 6 | 6 | 6 | 14 | 14 | 14 | 14 | 14 | 14 | 20 | 20 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 396340
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 677700
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 28 | 28 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 659600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 801100
73 | Ghorashal 108MW PP (Regent) | 99 | 96 | 96 | 96 | 96 | 96 | 93 | 93 | 93 | 96 | 96 | 96 | 99 | 53 | 93 | 96 | 23 | 23 |  | 50 | 99 | 99 | 99 | 99 | 99 | 99 | 2042818
| Feni Lanka Power | [19 empty] | 18 | 51 | 51 | 6 |  |  |  | 80940
| Chowmuhani 113 MW | 105 | 79 | 36 | [6 empty] | 31 | 86 | 105 | 105 | 107 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1817760
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 98 | 98 | 99 | 99 | 99 | 99 | 62 | 50 | 55 | 90 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 |  | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 2252160
78 | Gazipur 52 MW PP | [19 empty] | 2 | 25 | 39 |  |  |  |  | 49284
79 | Kodda 150MW PP | 64 | 20 | [17 empty] | 48 | 82 | 82 | 82 | 64 | 64 | 48 | 484320
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 48 | [6 empty] | 25 | 95 | 95 | 70 | 78 | 90 | 48 | 48 |  | 54 | 80 | 95 | 95 | 48 | 48 | 48 | 1338240
81 | Jangalia 52 MW PP (Lakdanavi) | [11 empty] | 1 | 8 | 8 | 8 |  |  |  |  | 3 | 16 | 48 | 52 |  |  |  | 165293
| Gazipur 100 MW PP | [10 empty] | 15 | 17 | 17 | 17 | 17 | 52 | 17 | 17 |  | 65 | 88 | 88 | 88 | 17 | 17 |  | 487500
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 2.2 | 2.9 | 4.4 | 2.8 | 5 | 0.9 | 1.6 | 3.4 | 0.7 | 0.5 | 0.9 | [9 empty] | 24601
| Jodiac Power | [12 empty] | 25 | 17 | 17 |  |  |  |  | 2 | 18 | 45 | 17 |  |  |  | 168096
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 |  | 96 | 96 | 96 | 96 | 97 | 97 | 97 | 2335344
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 5 | 21 | 50 | 20 | 53 | 76 | 10 | 10 |  | 19 | 30 | 10 |  |  |  |  | 370763
86 | Meghnaghat CCPP(Summit) | 250 | 260 | 255 | 270 | 260 | 265 | 255 | 255 | 265 | 240 | 280 | 255 | 250 | 276 | 270 | 265 | 250 | 275 |  | 280 | 250 | 260 | 260 | 260 | 260 | 260 | 6328931
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 35 | 7 | 7 | 7 | 51 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2066880
88 | Ghorashal 78.5 MW PP(MAX) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 68 | 67 | 67 | 67 | 50 | 66 | 66 | 40 | 40 |  | 40 | 68 | 68 | 68 | 68 | 68 | 69 | 1516256
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 10 | 10 | [5 empty] | 9360
92 | Fenchuganj 44MW (Energyprima) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 |  | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 982656
93 | Ashuganj 51 MW PP (Midland) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 10 | 10 |  | 10 | 10 | 20 | 25 | 25 | 25 | 25 | 588176
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 50 | 50 | 50 | 64 | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2178864
95 | Patenga 50MW PP (Baraka) | [10 empty] | 8 | 15 | 48 | 29 | 26 |  |  |  |  | 3 | 50 | 45 | 50 | 50 | 50 | 50 | 416160
96 | Chattogram 108 MW PP (ECPV) | 98 | 98 | 98 | 82 | 75 | [14 empty] | 19 | 93 | 93 | 24 | 19 |  |  | 635520
97 | Katpotti 52 MW PP (Sinha) | [11 empty] | 3 | 43 | 48 | 48 | [5 empty] | 14 | 38 | 48 | 48 |  |  | 366624
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 25 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 689326
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | [5 empty] | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 968205
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 163 | 163 | 130 | 163 | 100 | 163 | 163 | 130 | 130 | 110 |  | 110 | 130 | 130 | 163 | 163 | 130 | 130 | 3332700
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.2 | 0.7 | 1 | 0.6 | 1 | 0.6 | 0.5 | 0.6 | 0.2 | 0.8 | 0.2 | 0.1 | [8 empty] | 7250
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 21 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1183680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 190 | 190 | 190 | 190 | 170 | 75 | 75 | 75 | 88 | 120 | 80 | 60 | 40 | 8 | 24 | 16 | 8 | 8 |  | 8 | 60 | 60 | 154 | 200 | 200 | 200 | 2596800
112 | Aurahati 100MW PP (Aggreko) | [26 empty] | 4610
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 130 | 129 | 130 | 130 | 104 | 100 | 100 | 110 | 126 | 129 | 133 | 133 | 132 | 133 | 132 | 132 | 132 |  | 132 | 131 | 131 | 130 | 130 | 131 | 133 | 3067200
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 70 | 30 | 30 | 30 | 30 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2093760
116 | Chandpur 200MW (Desh energy) | [21 empty] | 25 |  |  |  |  | 28320
117 | Ashuganj 150MW PP (Midland) | 142 | 148 | 148 | 148 | 148 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 142 | 145 | 145 | 100 | 70 | 70 |  | 92 | 145 | 147 | 148 | 148 | 148 | 149 | 2748290
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 107 | 2766000
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 160 | 160 | 160 | 160 | 215 | 215 | 305 | 307 | 271 | 306 | 306 | 160 | 160 |  | 225 | 286 | 305 | 306 | 307 | 307 | 307 | 6240109
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2415360
120 | Eastern Zone Total | 6885 | 6771 | 6707 | 6775 | 6607 | 5758 | 5662.3 | 5671.2 | 5782.8 | 6097.6 | 6526.9 | 6686.5 | 6844.8 | 6640 | 6859.5 | 6453.5 | 6001.8 | 5679.7 |  | 6201 | 7158 | 7388 | 7495 | 7359 | 7314 | 7244 | 158680926
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 83 | 83 | 77 | 49 | 49 | 49 | 49 | 49 | 16 | 16 | 49 | 49 | 49 | 16 | 16 | 16 |  | 78 | 83 | 99 | 115 | 115 | 115 | 115 | 1519680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 18 | 19 | 21 | 21 | 21 | 21 | 5 | 103680
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [21 empty] | 17 | 17 | 17 | 17 | 17 | 79680
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 32 | 16 | 16 | [9 empty] | 48 | 110 | 96 | 98 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1325472
136 | Barisal GT PP Unit-1& 2 | [21 empty] | 7 | 15 |  |  |  | 15965
137 | Bhola 95 MW PP (Aggreko) | 80 | 78 | 78 | 78 | 78 | 78 | 78 | 76 | 79 | 78 |  |  |  |  | 11 | 75 | 78 | 54 |  | 50 | 75 | 76 | 78 | 80 | 80 | 78 | 1459145
| Bhola 225 MW CCPP | 68 | 68 | 69 | 69 | 68 | 69 | 69 | 68 | 67 | 68 | [7 empty] | 60 |  | 68 | 65 | 65 | 65 | 65 | 65 | 65 | 1135000
140 | Bhola 33 MW PP (Venture) | 31 | 29 | 29 | 25 | 23 | 21 | 18 | 14 | 17 | 18 | 16 | 15 | 16 | 19 | 18 | 15 | 18 | 18 |  | 26 | 28 | 30 | 30 | 31 | 31 | 28 | 536741
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 20 | [17 empty] | 2 | 70 | 68 | 100 | 100 | 100 | 100 | 658560
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | [7 empty] | 33 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 590250
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 23 |  | 40 | 62 | 62 | 52 | 51 | 51 |  | 286080
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [11 empty] | 21 |  | 32 | 85 | 67 | 15 | 15 |  | 15 | 87 | 105 | 105 | 105 | 105 | 50 | 765360
146 | Bheramara HVDC | 948 | 948 | 948 | 949 | 948 | 949 | 948 | 948 | 948 | 948 | 948 | 948 | 949 | 948 | 949 | 948 | 949 | 949 |  | 949 | 948 | 949 | 949 | 948 | 946 | 946 | 22746909
147 | Bheramara 410 MW CCPP | 340 | 340 | 345 |  | 0 | 0 | [8 empty] | 140 | 340 | 345 | 270 |  | 370 | 340 | 345 | 345 | 345 | 315 | 345 | 4233888
148 | Payra 1320 MW | 630 | 630 | 630 | 631 | 631 | 630 | 577 | 500 | 500 | 502 | [15 empty] | 151 | 6472100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 151 | 150 | 150 | 150 | 150 | 149 | 149 | 3655400
153 | Baghabari 71 MW GTPP | [14 empty] | 50 | 60 | 60 | 60 |  | 40 | 60 | 60 | 60 | 60 | 60 | 50 | 540000
156 | Baghabari 100 MW GTPP | [8 empty] | 60 | 60 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 60 |  | 60 | [6 empty] | 687000
| Baghabari 50 MW Peaking PP | [19 empty] | 25 | 50 | 50 | 50 |  |  |  | 131384
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 157 | 158 | 155 | 160 | 163 | 157 | 155 | 167 | 190 | 191 | 188 | 193 | 198 | 169 | 191 | 184 | 172 | 157 |  | 150 | 173 | 175 | 188 | 186 | 197 | 194 | 4412109
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 186 | 187 | 187 | 186 | 186 | 187 | 186 | 184 | 186 | 186 | 186 |  | 186 | 187 | 187 | 187 | 187 | 187 | 187 | 4720600
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 400 | 416 | 396 | 344 | 337 | 375 | 367 | 375 | 412 | 380 | 408 | 392 | 328 | 378 | 384 | 363 | 324 | 307 |  | 341 | 322 | 322 | 393 | 414 | 414 | 415 | 9156090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 10 | 10 | 15 | 41 |  |  |  | 59442
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 480720
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255096
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 170172
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 42 | 50 |  |  |  |  | 53463
167 | Katakhali 50 MW Peaking PP | [19 empty] | 12 | 30 | 39 | 37 | 37 | 37 |  | 159178
168 | Santahar 50 MW Peaking PP | [19 empty] | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 174400
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 25 | 43 | 43 | 43 | 43 | 43 | 0 | 219360
170 | Chapainawabganj 100 MW Peaking PP | 100 | 75 | 50 | 50 | 50 | [7 empty] | 41 | 41 | 45 | 85 | 100 | 100 |  | 100 | 100 | 100 | 92 | 100 | 91 | 88 | 1285344
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [11 empty] | 8 | 35 | 35 | 35 |  |  |  |  | 65 | 108 | 110 | 113 | 113 | 113 | 113 | 782976
172 | Confidence Power Bogura Unit-1 113 MW | 109 | 109 | 109 | 109 | 109 | 109 | 35 | 35 | 70 | 20 | [9 empty] | 5 | 35 | [5 empty] | 889440
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 10 | [18 empty] | 12 | 11 | 12 | 10 | 10 | 12 | 12 | 81000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 97 | 35 | 35 |  |  |  |  | 28 | 77 | 106 | 106 | 67 | 67 | 101 | 62 | 35 |  | 59 | 113 | 113 | 113 | 113 | 113 | 113 | 1687680
177 | Sympa Solar Power 8MW | [5 empty] | 0.2 | 1.2 | 0.9 | 4.3 | 4.8 | 3.4 | 6.2 | 1.8 | 4.9 | 1.8 | 3 | 1.3 | 0.5 | [8 empty] | 38192
178
178