## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April' 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | April 2020 |  | March 2020 |  | April 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10344 | 14/04/20 | 10790 | 18/03/20 | 12200 | 29/04/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 4292.2 | 25/04/20 | 5676.1 | 03/03/20 | 4404 | 07/04/19 | - | -
|  |  | 6:00 |  | 5:00 |  | 1:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10344 | 14/04/20 | 10790 | 18/03/20 | 12200 | 29/04/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 8389.7 | 05/04/20 | 9428.9 | 18/03/20 | 10057 | 24/04/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10344 | 14/04/20 | 10790 | 18/03/20 | 12200 | 29/04/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:30 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8896.9333 |  | 9878.5806 |  | 10379.3333 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 7031.8517 |  | 8156.329 |  | 8450.5167 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 949 | 09/04/2020 | 943 | 23/03/2020 | 954 | 16/04/19 | 956 | 27/3/2019
|  |  | 22:00 |  | 20:00 |  | 20:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 142 | 14/04/2020 | 152 | 15/03/2020 | 188 | 28'/04/19 | 194 | 12/06/19
|  |  | 20:00 |  | 18:30 |  | 22:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3300.8626 |  | 3442.7368 |  | 3100.9672 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 99.2395 |  | 103.8241 |  | 126.2914
22 | Net Generation of BPDB (MKWH) | 3201.6231 |  | 3338.9126 |  | 2974.6758
23 | Net Generation of IPP & RPCL (MKWH) | 134.1374 |  | 1608.1902 |  | 1935.4012
24 | Net Generation of REB (MKWH) | 101.3435 |  | 135.7736 |  | 128.616
24 | Net Generation of Rental Power Plant (MKWH) | 202.4975 |  | 297.8023 |  | 427.5001
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3639.6015 |  | 5380.6788 |  | 5466.1931 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 3983.5017 |  | 4372.4084 |  | 4100.9893 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 102.8552 |  | 137.8528 |  | 237.3993 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 295.0235 |  | 556.2721 |  | 1029.0544 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 24.8805 |  | 49.3088 |  | 51.4805 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 5.7632 |  | 6.9723 |  | 4.0002 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 416.1569 |  | 361.6886 |  | 169.5608 |  | 416.1569 | 2020-04-17
32 | Enegry Import from India (HVDC & AC) (MKWH) | 403.908 |  | 453.512 |  | 626.1175 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 70.2513 |  | 73.9685 |  | 70.7946 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10344 | 14/04/20 | 21:00
Generation Period
| Dhaka | MW | 2777
| Chattogram | MW | 881
| Cumilla | MW | 1064
| Mymensingh | MW | 926
| Sylhet | MW | 414
a) | Total supply in East zone | MW | 6062
| Khulna | MW | 1360
| Barisal | MW | 305
| Rajshahi | MW | 1269
| Rangpur | MW | 758
b) | Total supply in West zone | MW | 3692
c) | Total supply in both zone ( a+b) | MW | 9754
Ref: | 27.21.0000.603.16.087.20.270 | Date: 20/05/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 400 | 26/04/20 | 19:00
| b) Ishurdi end | MW | 204 | 20/04/20 | 20:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 475 | 20/04/20 | 20:00
| b) Ishurdi end | MW | 151 | 26/04/20 | 19:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 1.6005 | 11/04/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.5757 | 11/04/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 24.4309
| b) Ishurdi end | MKWH | 16.2505
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 10.606
| b) Ishurdi end | MKWH | 23.7193
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 410 | 11/04/20 | 22:00
| b)Serajganj end | MW | 580 | 15/04/20 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 550 | 15/04/20 | 23:00
| b)Sirajganj end | MW | 340 | 11/04/20 | 22:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 3.724 | 11/04/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 3.708 | 11/04/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 89.948
| b)Sirajganj end | MKWH | 10.606
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.32
| b)Sirajganj end | MKWH | 89.654
30 | Transmission loss of EWI /NO-2 | % | 0.955
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformers-T1 | 2020-04-07 20:19 | 2020-04-07 20:25 | 0:06 | T | Tripped showing O/C (C-phase) relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-04-07 20:19 | 2020-04-07 22:19 | 2:00 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-04-08 01:20 | 2020-04-08 01:28 | 2:00 | T |  | 55 | 110 | Power interruption
Kishoreganj | 132/33 kV Transformers-T1 | 2020-04-09 06:58 | 2020-04-09 08:40 | 1:42 | E/O | Due to red-hot maintenance | 50 | 85 | Power interruption
| 132/33 kV Transformers-T2 | 2020-04-09 06:58 | 2020-04-09 08:30 | 1:42 | E/O
Mymensingh | 132/33 kV Transformers-T1 & T2 | 2020-04-10 07:53 | 2020-04-10 08:01 | 0:08 | T | Tripped showing 33 kV feeder fault | 110 | 14.6667 | Power interruption
Jamalpur | 132/33 kV Transformers-T1 | 2020-04-10 07:53 | 2020-04-10 08:22 | 0:29 | T |  | 50 | 24.1667 | Power interruption
| 132/33 kV Transformers-T2 | 2020-04-10 07:53 | 2020-04-10 09:12 | 1:19 | T
| 132/33 kV Transformers-T4 | 2020-04-16 21:34 | 2020-04-16 23:49 | 2:15 | E/O | Due to red-hot maintenance | 12 | 27 | Power interruption
Netrakona | 132/33 kV Transformers-T2 | 2020-04-17 20:00 | 2020-04-17 20:40 | 0:40 | E/O | Due to red-hot maintenance at PBS feeder | 10 | 6.6667 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 & T2 | 2020-04-19 16:58 | 2020-04-19 17:15 | 0:17 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1 & T2 | 2020-04-20 03:18 | 2020-04-20 05:20 | 2:02 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers-T1 & T2 | 2020-04-20 21:50 | 2020-04-20 22:08 | 0:18 | T | Tripped showing 33 kV feeder fault | 60 | 18 | Power interruption
Kabirpur | 132/33 kV Transformers-T1 & T2 | 2020-04-20 22:59 | 2020-04-20 23:11 | 0:12 | T | Tripped showing 33 kV feeder fault | 44 | 8.8 | Power interruption
Manikganj | 132/33 kV Transformer-T3 | 2020-04-20 07:44 | 2020-04-20 08:52 | 1:08 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2020-04-22 09:25 | 2020-04-22 11:07 | 1:42 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T2 | 2020-04-22 11:05 | 2020-04-22 12:43 | 1:38 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2020-04-29 09:02 | 2020-04-29 09:02 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 19:38 |  | Unserved Energy: |  | 294.3
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV Transformer-T01 | 2020-04-01 07:04 | 2020-04-01 07:04 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformers-T1 & T2 | 2020-04-02 21:52 | 2020-04-02 22:13 | 0:21 | T | Tripped showing E/F relay at 33 kV side | 80 | 28 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2020-04-08 07:56 | 2020-04-08 08:07 | 0:11 | T |  | 70 | 12.8333 | Power interruption
Tongi | 230 kV Bus-2 | 2020-04-13 15:10 | 2020-04-13 16:40 | 1:30 | T | Tripped showing master protection relay | 0 | 0 | No interruption
Ghorashal | 230 kV Bus | 2020-04-13 15:33 | 2020-04-13 16:20 | 0:47 | T | Tripped showing dist (A-phase)relay | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2020-04-20 15:44 | 2020-04-20 17:37 | 1:53 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 4:42 |  | Unserved Energy: |  | 40.8333
Chattogram Grid Circle :
Bakulia | 132/33 kV Transformer-T3 | 2020-04-04 06:10 | 2020-04-04 06:10 | 0:00 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1,& T2 & T3 | 2020-04-16 04:15 | 2020-04-16 04:35 | 0:20 | T | Tripped showing E/F relay | 29 | 9.6667 | Power interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-04-18 06:28 | 2020-04-18 09:35 | 3:07 | E/O | Due to red-hot maintenance at 33 kV side | 24 | 74.8 | Power interruption
Khulshi | 132/33 kV Transformers-T1,& T3 | 2020-04-19 00:52 | 2020-04-19 01:21 | 0:29 | T | Tripped showing E/F relay at 33 kV side | 30 | 14.5 | Power interruption
Rangamati | 132/33 kV Transformer-T1 | 2020-04-19 11:26 | 2020-04-19 19:45 | 8:19 | T | Tripped showing winding temperature high | 26 | 216.2333 | Power interruption
Halishahar | 132/33 kV Transformers-T1, | 2020-04-21 11:58 | 2020-04-21 12:10 | 0:12 | T | Tripped showing 33 kV feeder fault | 26 | 5.2 | Power interruption
| 132/33 kV Transformers-T3 | 2020-04-21 11:58 | 2020-04-21 12:15 | 0:17 | T
|  |  | Total : | 12:44 |  | Unserved Energy: |  | 320.4
Cumilla Grid Circle :
Chattak | 132/33 kV Transformer-T1 | 2020-04-02 19:41 | 2020-04-02 19:54 | 0:13 | T | Tripped showing E/F relay at 33 kV side | 2 | 0.43333 | Power interruption
Cumilla (N) | 132/33 kV Transformers-T3 & T4 | 2020-04-04 17:38 | 2020-04-04 18:05 | 0:27 | T | Tripped showing O/C relay | 32 | 14.4 | Power interruption
Sumamganj | 132/33 kV Transformers-T1 | 2020-04-05 12:20 | 2020-04-05 12:36 | 0:16 | T |  | 18 | 4.8 | Power interruption
| 132/33 kV Transformers-T2 | 2020-04-05 12:20 | 2020-04-05 12:54 | 0:34 | T
Chandpur | 132/33 kV Transformer-T2 | 2020-04-06 00:39 | 2020-04-06 08:42 | 8:03 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-04-06 08:23 | 2020-04-06 09:32 | 1:09 | E/O | Due to red-hot maintenance at 33 kV side | 24 | 27.6 | Power interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-04-06 12:30 | 2020-04-06 17:43 | 5:13 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV Transformers-T3 | 2020-04-06 16:14 | 2020-04-06 18:27 | 2:13 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformers-T4 | 2020-04-06 16:14 | 2020-04-06 16:50 | 0:36 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 & T4 | 2020-04-07 15:27 | 2020-04-07 15:47 | 0:20 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2020-04-08 03:55 | 2020-04-08 04:13 | 0:18 | T | Tripped showing buchholz relay at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-04-09 13:39 | 2020-04-09 13:50 | 0:11 | T | Tripped showing Lockout 132 kV side & Under Voltage 33 kV side | 25 | 4.5833 | Power interruption
| 132/33 kV Transformer-T2 | 2020-04-11 08:24 | 2020-04-11 13:55 | 5:31 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-04-11 17:22 | 2020-04-11 17:22 | 0:00 | E/O | Due to O/C & E/F relay at 33 kV incoming Breaker burst
| 132/33 kV Transformer-T4 | 2020-04-11 17:22 | 2020-04-11 18:11 | 0:49 | E/O |  | 90 | 73.5 | Power interruption 17:52 to 18:11
Page: 2/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T3 | 2020-04-12 10:44 | 2020-04-12 12:40 | 1:56 | E/O | Due to Oil leakage | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2020-04-16 20:48 | 2020-04-16 21:34 | 0:46 | E/O | Due to red-hot maintenance at 33 kV side | 50 | 38.3333 | Power interruption 17:52 to 18:11
Kulaura | 132/33 kV Transformer-T1 | 2020-04-17 01:40 | 2020-04-17 03:33 | 1:53 | T | Tripped showing dist & E/F relay | 16 | 30.1333 | Power interruption 17:52 to 18:11
Sylhet | 132/33 kV Transformer-T2 | 2020-04-18 06:43 | 2020-04-18 11:30 | 4:47 | T | Tripped showing Buchhloz relay | 0 | 0 | No interruption
Srimongal | 132/33 kV Transformer-T3 | 2020-04-30 09:08 | 2020-04-30 12:40 | 3:32 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 38:47 |  | Unserved Energy: |  | 193.7833
Khulna Grid Circle :
Bagerhat | 132/33 kV Transformer-T1 | 2020-04-03 07:05 | 2020-04-03 07:05 | 0:00 | E/O | Due to Oil leakage at 33 kV Y-phase CT | 0 | 0 | No interruption
Barishal(N) | 230/132 kV Transformer-T2 | 2020-04-03 12:36 | 2020-04-03 14:15 | 1:39 | E/O | Due to Oil leakage at 132 kV side | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformer-T1 | 2020-04-04 10:42 | 2020-04-04 10:52 | 0:10 | T | Tripped showing O/C & E/F relay | 10 | 1.6667 | Power interruption
| 132/33 kV Transformer-T3 | 2020-04-10 07:16 | 2020-04-10 08:34 | 1:18 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T6 | 2020-04-11 06:50 | 2020-04-11 08:26 | 1:36 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T6 | 2020-04-11 20:44 | 2020-04-12 11:04 | 14:20 | T | Tripped showing differential relay | 0 | 0 | No interruption
Bagerhat | 132/33 kV Transformers-T1 | 2020-04-21 08:47 | 2020-04-21 10:52 | 2:05 | T | Tripped showing O/V relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T2 | 2020-04-21 08:47 | 2020-04-21 09:26 | 0:39 | T |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-04-23 09:42 | 2020-04-23 09:48 | 0:06 | T | Tripped showing 33 kV feeder fault | 13 | 1.3 | Power interruption
Bhandaria | 132/33 kV Transformer-T1 | 2020-04-24 18:25 | 2020-04-24 21:24 | 2:59 | T | Tripped showing PRD relay | 80 | 238.6667 | Power interruption
Shariatpur | 132/33 kV Transformer-T2 | 2020-04-26 21:36 | 2020-04-26 22:52 | 1:16 | E/O | Due to red-hot maintenance at 33 kV side | 25 | 31.6667 | Power interruption
Barishal(N) | 230/132 kV Transformer-T01 | 2020-04-28 12:10 | 2020-04-28 13:07 | 0:57 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-04-29 07:10 | 2020-04-29 12:43 | 5:33 | E/O | Due to red-hot maintenance at 33 kV side | 8 | 44.4 | Power interruption
| 132/33 kV Transformers-T1 | 2020-04-30 09:27 | 2020-04-30 09:44 | 0:17 | T | Tripped showing E/F relay at 33 kV feeder fault | 0 | 0
| 132/33 kV Transformers-T2 | 2020-04-30 09:27 | 2020-04-30 09:38 | 0:11 | T |  | 40 | 7.3333 | Power interruption
|  |  | Total : | 33:06 |  | Unserved Energy: |  | 325.0333
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformer-T2 | 2020-04-01 10:17 | 2020-04-01 10:44 | 0:27 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T4 | 2020-04-06 10:33 | 2020-04-06 12:23 | 1:50 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-04-13 14:50 | 2020-04-13 16:24 | 1:34 | T | Tripped showing differential relay at 33 kV | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-04-15 12:28 | 2020-04-15 13:32 | 1:04 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-04-15 22:40 | 2020-04-16 00:03 | 1:23 | E/O | Due to red-hot maintenance | 40 | 55.3333 | Power interruption
|  |  | Total : | 6:18 |  |  |  | 55.3333
Bogura Grid Circle:
Barapukuria | 132/33 kV Transformer-T4 | 2020-04-04 17:15 | 2020-04-04 18:55 | 1:40 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 33.3333 | Power interruption
Bogura | 132/33 kV Transformer-T2 | 2020-04-08 09:20 | 2020-04-08 13:15 | 3:55 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformers-T2 & T3 | 2020-04-08 12:30 | 2020-04-08 12:38 | 0:08 | T | Tripped showing O/C relay | 80 | 10.6667 | Power interruption
| 132/33 kV Transformer-T1 | 2020-04-08 11:05 | 2020-04-09 05:51 | 18:46 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T4 | 2020-04-11 10:43 | 2020-04-11 14:07 | 0:23 | E/O | Due to 33 kV cable burst | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T2 | 2020-04-11 10:43 | 2020-04-11 14:32 | 0:23 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-04-12 10:15 | 2020-04-12 11:30 | 1:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T2 | 2020-04-12 08:10 | 2020-04-12 14:23 | 0:07 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformers-T2 & T6 | 2020-04-14 02:36 | 2020-04-14 03:10 | 0:07 | T | Tripped showing master protection relay | 0 | 0 | No interruption
Panchagar | 132/33 kV Transformers-T1, T2 & T3 | 2020-04-15 09:43 | 2020-04-15 10:31 | 0:48 | E/O | Due to Oil leakage | 20 | 16 | Power interruption
Naogaon | 132/33 kV Transformer-T2 | 2020-04-16 09:35 | 2020-04-16 12:10 | 2:35 | E/O | Due to red-hot maintenance at 33 kV side | 18 | 46.5 | Power interruption
Bogura (O) | 132/33 kV Transformer-T3 | 2020-04-16 09:32 | 2020-04-16 13:14 | 3:42 | E/O | Due to red-hot maintenance at 132 kV CT | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2020-04-21 12:35 | 2020-04-21 13:10 | 0:35 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 11.6667 | Power interruption
Saidpur | 132/33 kV Transformer-T2 | 2020-04-22 09:40 | 2020-04-22 11:25 | 1:45 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-04-22 19:45 | 2020-04-22 19:45 | 0:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2020-04-23 08:32 | 2020-04-23 10:35 | 2:03 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Bogura (O) | 132/33 kV Transformer-T3 | 2020-04-23 11:25 | 2020-04-23 13:35 | 2:10 | E/O | Due to red-hot maintenance at 33 kV side | 15 | 32.5 | Power interruption
Page: 3/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Narail | 132/33 kV Transformer-T2 | 2020-04-24 09:22 | 2020-04-24 10:26 | 1:04 | E/O | Due to red-hot maintenance | 3 | 3.2 | Power interruption
| 132/33 kV Transformer-T4 | 2020-04-24 10:25 | 2020-04-24 11:26 | 1:01 | E/O | Due to red-hot maintenance at 33 kV side | 3 | 3.05 | Power interruption
Bogura (O) | 132/33 kV Transformer-T4 | 2020-04-25 07:30 | 2020-04-25 07:30 | 0:07 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Mohasthangarh | 132/33 kV Transformer-T1 | 2020-04-26 10:52 | 2020-04-26 12:36 | 1:44 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2020-04-26 12:46 | 2020-04-26 12:54 | 0:07 | T | Tripped showing O/C relay at 33 kV feeder fault | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-04-26 17:03 | 2020-04-26 17:12 | 0:07 | T | Tripped showing differential relay | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T2 | 2020-04-28 09:50 | 2020-04-28 10:50 | 1:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-04-28 09:50 | 2020-04-28 10:50 | 1:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T3 | 2020-04-30 09:14 | 2020-04-30 10:20 | 1:06 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 47:38 |  | Unserved Energy: |  | 156.9167
Others :
Ullon | 132/33 kV Transformer-T1, T2 & T3 | 2020-04-11 15:55 | 2020-04-11 16:51 | 0:56 | E/O | Due to as fire orginated from T3 | 50 | 46.6667 | Power interruption
|  |  | Total : | 0:56 |  | Unserved Energy: |  | 46.6667
Total outage period of Sub-station Equipment : |  |  |  | 163:49 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-04-02 17:24 | 2020-04-02 18:05 | 0:41 | T | Tripped showing dist.(C-Phase) relay | 100 | 68.3333 | Power interruption 17: 40 18:05
| Tongi-Kabirpur 132 kV line-2 | 2020-04-02 17:40 | 2020-04-02 18:05 | 0:25 | T
Kadda 300 MW | Kadda 300 MW-Kaliakoir 230 kV line | 2020-04-02 17:45 | 2020-04-02 18:46 | 1:01 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Kadda 300 MW-Tongi 230 kV line | 2020-04-02 17:45 | 2020-04-02 18:45 | 1:00 | T |  | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-04-03 09:52 | 2020-04-03 10:10 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV line |  | 2020-04-05 17:52 |  | T | Tripped showing dist. relay | 0 | 0 | No interruption
MymensinghRPCL | MymensinghRPCL-Mymensingh 132 kV line-1 | 2020-04-07 20:18 | 2020-04-07 20:44 | 0:26 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| MymensinghRPCL-Mymensingh 132 kV line-2 | 2020-04-07 20:18 | 2020-04-07 20:45 | 0:27 | T |  | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-04-07 20:18 | 2020-04-07 20:35 | 0:17 | T | Tripped showing O/C. (B-phase) relay | 635 | 179.9167 | Power interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-04-07 20:19 | 2020-04-07 20:49 | 0:30 | T | Tripped showing O/C. (C-phase) relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-1 | 2020-04-15 12:28 | 2020-04-15 16:05 | 3:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2020-04-16 00:06 | 2020-04-16 01:25 | 1:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV line-1 | 2020-04-16 00:31 | 2020-04-16 01:04 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2020-04-18 00:12 | 2020-04-18 00:23 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-04-20 04:05 | 2020-04-20 06:46 | 2:41 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-04-20 14:02 | 2020-04-20 14:17 | 0:15 | T | Tripped showing Cas,CAT ,CD & CE signal | 50 | 12.5 | Power interruption
Mirpur | Mirpur-Uttara 132 kV line | 2020-04-21 07:08 | 2020-04-21 07:19 | 0:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-1 | 2020-04-21 07:44 | 2020-04-21 08:52 | 1:08 | E/O | Due to red-hot maintenance at 33 kV CB | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-04-23 15:11 | 2020-04-23 15:50 | 0:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
UMPL | UMPL-Sherpur 132 kV line-2 | 2020-04-24 07:46 | 2020-04-24 07:52 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 15:45 |  | Unserved Energy: |  | 260.75
Dhaka (South) Grid Circle :
Rampura | Rampura-Bashundhara 132 kV line-2 | 2020-04-01 20:33 | 2020-04-02 11:44 | 15:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-B.Baria 132 kV line-1 | 2020-04-02 14:01 | 2020-04-02 14:10 | 0:09 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2020-04-02 17:57 | 2020-04-02 18:47 | 0:50 | T |  | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line-1 | 2020-04-02 18:11 | 2020-04-02 18:47 | 0:36 | T | Tripped showing dist.(R-phase) relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Haripur 230 kV line-1 | 2020-04-05 07:24 | 2020-04-05 07:24 |  | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2020-04-07 04:10 | 2020-04-07 04:29 | 0:19 | T | Tripped showing dist. relay | 18 | 5.7 | Power interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2020-04-09 06:18 | 2020-04-09 06:18 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
APR | APR-Shyampur 230 kV line | 2020-04-09 06:39 | 2020-04-09 09:30 | 2:51 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2020-04-09 12:59 | 2020-04-09 13:50 | 0:51 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2020-04-11 21:58 | 2020-04-11 22:30 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Siddhirganj-Siddhirganj GT 132 kV line-1 & 2 | 2020-04-11 21:58 | 2020-04-11 22:32 | 0:34 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2020-04-13 14:20 | 2020-04-13 20:55 | 6:35 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-1 | 2020-04-13 15:33 | 2020-04-13 16:20 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2020-04-20 04:35 | 2020-04-20 05:04 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV line | 2020-04-20 04:50 | 2020-04-20 08:30 | 3:40 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Harirpur-Ullon 132 kV line-2 | 2020-04-23 16:11 | 2020-04-23 16:51 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV line | 2020-04-23 16:03 | 2020-04-23 16:36 | 0:33 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2020-04-23 16:05 | 2020-04-23 16:57 | 0:52 | T | Tripped showing dist.& master trip. relay | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Rampura | Rampura-Moghbazar 132 kV line-2 | 2020-04-23 16:15 | 2020-04-23 16:48 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line | 2020-04-23 16:22 | 2020-04-23 17:29 | 1:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV line | 2020-04-26 14:02 | 2020-04-26 15:18 | 1:16 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Harirpur-Ullon 132 kV line | 2020-04-28 13:48 | 2020-04-28 14:17 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 | 2020-04-29 17:01 | 2020-04-29 17:15 | 0:14 | T | Tripped showing differential. relay | 0 | 0 | No interruption
Haripur | Harirpur-Ullon 132 kV line-1 | 2020-04-30 13:49 | 2020-04-30 14:02 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 39:21 |  | Unserved Energy: |  | 5.7
Chittagong Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2020-04-02 09:59 | 2020-04-02 11:47 | 1:48 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV line-1 | 2020-04-02 15:49 | 2020-04-02 15:56 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line | 2020-04-07 02:48 | 2020-04-07 03:15 | 0:27 | T | Tripped showing dist. relay | 439 | 197.55 | Power interruption
Modern | Modern-Bakulia 132 kV line | 2020-04-07 02:48 | 2020-04-07 03:40 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sikalbaha(New) | Sikalbaha(New)-T.K chemical 132 kV line | 2020-04-07 02:48 | 2020-04-08 04:09 | 25:21 | T | Tripped showing main protection. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV line | 2020-04-07 02:48 | 2020-04-07 04:12 | 1:24 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sikalbaha 132 kV line | 2020-04-07 02:48 | 2020-04-07 04:05 | 1:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV line-2 | 2020-04-16 04:01 | 2020-04-16 04:19 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-04-16 04:15 | 2020-04-16 04:37 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV line-1 | 2020-04-19 00:38 | 2020-04-19 02:04 | 1:26 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Halishahar | Halishahar -Khulshi132 kV line | 2020-04-19 00:52 | 2020-04-19 01:28 | 0:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV line | 2020-04-19 03:12 | 2020-04-19 03:28 | 0:16 | T | Tripped showing dist.(B-phase) & E/F relay | 0 | 0 | No interruption
Juldah | Jiuldah-Shahmirpur 132 kV line-1 | 2020-04-21 11:15 | 2020-04-21 12:13 | 0:58 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Baraulia | Baraulia-Modern Steel 132 kVline | 2020-04-21 11:27 | 2020-04-21 11:55 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2020-04-26 06:53 | 2020-04-26 07:27 | 0:34 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
|  |  | Total : | 36:14 |  | Unserved Energy: |  | 197.55
Cumilla Grid Circle :
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 & 2 | 2020-04-03 16:09 | 2020-04-03 16:16 | 0:07 | T | Tripped showing dist.(A-phase) relay | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur P/S 132 kV line-1& 2 | 2020-04-10 08:05 | 2020-04-10 15:12 | 7:07 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-04-11 16:59 | 2020-04-11 17:52 | 0:53 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chattak 132 kV lne | 2020-04-11 18:54 | 2020-04-11 19:23 | 0:29 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-04-11 20:59 | 2020-04-11 23:56 | 2:57 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV line | 2020-04-13 17:10 | 2020-04-13 18:05 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-04-14 08:30 | 2020-04-14 09:59 | 1:29 | E/O | Due to air pressure low | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line | 2020-04-15 13:20 | 2020-04-15 16:34 | 3:14 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-1 | 2020-04-15 12:55 | 2020-04-15 13:04 | 0:09 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-04-15 13:43 | 2020-04-15 15:15 | 1:32 | T | Tripped showing dist.(Z1) relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-04-16 01:01 | 2020-04-16 01:45 | 0:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Chandpur 132 kV line-2 | 2020-04-16 17:39 | 2020-04-16 21:06 | 3:27 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-04-17 01:04 | 2020-04-17 01:04 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV lin-2 | 2020-04-17 02:41 | 2020-04-17 02:57 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-04-18 12:22 | 2020-04-18 13:25 | 1:03 | T | Tripped showing dist. relay | 9 | 9.45 | Power interruption
Cumilla(N) | Cumilla(N)-Chandpur 132 kV line-1 | 2020-04-18 19:38 | 2020-04-18 19:53 | 0:15 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV line-2 | 2020-04-18 19:46 | 2020-04-18 20:41 | 0:55 | T |  | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura(India) 132 kV line-2 | 2020-04-18 20:15 | 2020-04-18 20:44 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2020-04-19 03:00 | 2020-04-19 03:31 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2020-04-20 01:23 | 2020-04-20 05:09 | 3:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur | Chandpur-Cumilla(N) 132 kV line-1 | 2020-04-22 16:34 | 2020-04-22 16:44 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 230 kV line-3 | 2020-04-23 13:41 | 2020-04-23 14:31 | 0:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2020-04-24 15:50 | 2020-04-24 17:29 | 1:39 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2020-04-24 16:13 | 2020-04-24 16:41 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line | 2020-04-28 15:17 | 2020-04-28 15:47 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 33:55 |  | Unserved Energy: |  | 9.45
Khulna Grid Circle :
Bagerhat | Bagerhat-Mongla 132 kV line | 2020-04-02 05:16 | 2020-04-02 05:36 | 0:20 | T | Tripped showing dist. Relay at 33 kV feeder fault | 32 | 10.6667 | Power interruption
Barisal(S) | Barisal(S)-Barisal(N) 132 kV line-1 & 2 | 2020-04-11 06:37 | 2020-04-11 07:07 | 0:30 | T | Tripped showing dist. relay | 112 | 56 | Power interruption
Barisal | Barisal-Bhola 230 kV line-1 &2 | 2020-04-12 12:36 | 2020-04-12 13:40 | 1:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2020-04-12 12:19 | 2020-04-12 13:33 | 1:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 400 kV line-3 | 2020-04-13 13:48 | 2020-04-13 14:18 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(New) | Gopalganj(New)-Gopalganj(Old) 132 kV line-3 | 2020-04-15 13:48 | 2020-04-15 14:16 | 0:28 | T | Tripped showing dist. relay | 55 | 25.6667 | Power interruption
Jessore | Jessore-Noapara 132 kV line-2 | 2020-04-16 08:26 | 2020-04-16 10:03 | 1:37 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2020-04-16 13:06 | 2020-04-16 13:26 | 0:20 | T | Tripped showing dist. relay | 26 | 8.6667 | Power interruption
Barisal | Barisal-Bhandaria 132 kV line | 2020-04-17 17:00 | 2020-04-17 17:14 | 0:14 | T | Tripped showing O/C relay at33 kV feeder fault | 35 | 8.1667 | Power interruption
Jessore | Jessore-Jhenidah 132 kV line-1 | 2020-04-17 22:04 | 2020-04-17 22:23 | 0:19 | T | Tripped showing U/V relay relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-04-18 01:38 | 2020-04-18 02:08 | 0:30 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Noapara | Noapara-Jessore 132 kV line e-1 | 2020-04-21 08:42 | 2020-04-21 09:05 | 0:23 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
| Noapara-Jessore 132 kV line e-2 | 2020-04-21 08:42 | 2020-04-21 09:06 | 0:24 | T |  | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line | 2020-04-21 08:43 | 2020-04-21 09:01 | 0:18 | T | Tripped showing dist.(Z3) relay | 6 | 1.8 | Power interruption
Gopalganj(New) | Gopalganj(New)-Gopalganj(Old) 132 kV line | 2020-04-21 09:54 | 2020-04-21 10:16 | 0:20 | T | Tripped showing dist. relay at 33 kV feeder fault | 28 | 9.3333 | Power interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-04-21 09:42 | 2020-04-21 09:55 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV line | 2020-04-23 12:10 | 2020-04-23 12:15 | 0:05 | T | Tripped showing E/F fault at 33 kV side | 24 | 2 | Power interruption
Goalpara | Goalpara-Khulna Central 132 kV line-2 | 2020-04-23 18:15 | 2020-04-23 18:55 | 0:40 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Goalpara-Orion 132 kV line | 2020-04-23 18:15 | 2020-04-23 20:41 | 2:26 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Gopalganj(New) | Gopalganj(New)-Madaripur 132 kV line-3 | 2020-04-24 16:55 | 2020-04-24 18:22 | 1:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-04-30 16:13 | 2020-04-30 16:27 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 13:36 |  | Unserved Energy: |  | 122.3
HVDC Grid Circle :
Baghabari | Baghabari-Shahjadpur 132 kV line-2 | 2020-04-07 06:05 | 2020-04-07 06:14 | 0:09 | T | Tripped showing dist. relay | 64 | 9.6 | Power interruption
Bottail | Bottail-Bheramara 132 kV line-1 | 2020-04-12 10:12 | 2020-04-12 10:35 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Jhenidah | Jhenidah-Jessore 132 kV line | 2020-04-21 08:43 | 2020-04-21 08:59 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Jhenidah-Bottail 132 kV line-1 | 2020-04-27 09:56 | 2020-04-27 10:14 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:06 |  | Unserved Energy: |  | 9.6
Page: 4/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Bogura(Sherpur) | Bogura(Sherpur)-Bogura 132 kV line-1 | 2020-04-01 12:31 | 2020-04-01 21:11 | 8:40 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura(Sherpur) 132 kV ine-1 & 2 | 2020-04-03 19:01 | 2020-04-03 22:29 | 3:28 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Natore | Natore-Bogura (O) 132 kV line | 2020-04-03 19:14 | 2020-04-03 20:32 | 1:18 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Sherpur | Sherpur-Bogura 132 kV line-1 | 2020-04-12 12:29 | 2020-04-12 14:26 | 1:57 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur Confidence 132 kV line-1 | 2020-04-15 09:11 | 2020-04-15 10:25 | 1:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Saidpur | Saidpur-Joldhaka 132 kV line-1 & 2 | 2020-04-15 10:03 | 2020-04-15 10:25 | 0:22 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-04-15 09:56 | 2020-04-15 14:41 | 4:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Nattore | Nattore-Rajshahi 132 kV line-2 | 2020-04-15 11:35 | 2020-04-16 00:27 | 12:52 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2020-04-18 03:14 | 2020-04-18 07:50 | 4:36 | T | Tripped showing dist. relay | 10 | 46 | Power interruption
Palashbari | Palashbari-Rangpur Confidence 132 kV line-1 | 2020-04-18 03:13 | 2020-04-18 04:02 | 0:49 | T | Tripped showing dist.& O/C relay | 0 | 0 | No interruption
Saidpur | Saidpur-Joldhaka 132 kV line-2 | 2020-04-18 17:45 | 2020-04-18 18:12 | 0:27 | T | Tripped showing dist.relay | 0 | 0 | No interruption
| Saidpur-Joldhaka 132 kV line-2 | 2020-04-18 18:51 | 2020-04-18 19:29 | 0:38 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-04-20 02:22 | 2020-04-20 02:22 | 0:00 | T | Tripped showing SOTF relay | 0 | 0 | No interruption
| Bogura-Barapukuria 230 kV line-1 | 2020-04-20 02:35 | 2020-04-20 07:08 | 4:33 | T | Tripped showing O/C & E/F.relay | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur Confidence 132 kV line-1 | 2020-04-21 11:22 | 2020-04-21 11:49 | 0:27 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Rangpur | Rangpur-Kurigram 132 kV line | 2020-04-29 20:40 | 2020-04-29 21:50 | 1:10 | E/O | Due to red-hot maintenance | 38 | 44.3333 | Power interruption
|  |  | Total : | 47:16 |  | Unserved Energy: |  | 90.3333
Others :
BSRM | BSRM-GPH 230 kV line-2 | 2020-04-17 12:23 | 2020-04-17 13:05 | 0:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:42 |  |  |  | 0
Unserved Energy:
Total outage period of Sub-station Equipment : |  |  |  | 189:01 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:April 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132 kV main Bus | 2020-04-08 09:11 | 2020-04-08 11:40 | 2:29 | S/O | Due to isolator problem | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2020-04-09 09:54 | 2020-04-09 11:23 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-04-10 12:23 | 2020-04-10 15:26 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2020-04-10 23:18 | 2020-04-10 23:32 | 0:14 | S/O | Due to relay problem | 15 | 3.5 | Power interruption
Kabirpur | 132/33 kV Transformers-T2 & T3 | 2020-04-11 23:55 | 2020-04-12 01:12 | 1:17 | S/O | Due to loop(Y-phase) changing | 20 | 25.6667 | Power interruption
Agargaon | 230/132 kV Transformer-T2 | 2020-04-14 08:55 | 2020-04-14 11:26 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2020-04-15 09:21 | 2020-04-15 09:49 | 0:28 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2020-04-15 08:41 | 2020-04-15 14:18 | 5:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T2 | 2020-04-16 13:33 | 2020-04-16 17:40 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus & Transformer | 2020-04-17 08:58 | 2020-04-17 14:56 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T3 | 2020-04-19 10:13 | 2020-04-19 13:32 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2020-04-21 10:24 | 2020-04-21 10:40 | 0:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 & 132 kV reserve Bus | 2020-04-22 09:47 | 2020-04-22 17:13 | 7:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2020-04-24 10:25 | 2020-04-24 20:15 | 9:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-04-24 09:36 | 2020-04-24 12:46 | 3:10 | S/O | Due to maintenance work at 33 kV feeder | 0 | 0 | No interruption
|  |  | Total : | 51:14 |  | Unserved Energy: |  | 29.1667
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformer-T2 | 2020-04-04 09:06 | 2020-04-04 12:42 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2020-04-04 12:45 | 2020-04-04 13:48 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132/33 kV Transformer-T2 | 2020-04-17 09:33 | 2020-04-17 14:00 | 4:27 | S/O | Due to DPDC work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T2 | 2020-04-19 12:24 | 2020-04-19 12:33 | 0:09 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2020-04-23 09:45 | 2020-04-23 15:28 | 5:43 | S/O | Due to replacement work | 0 | 0 | No interruption
Mehnaghat | 230 kV Bus-1 | 2020-04-23 07:44 | 2020-04-23 07:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T1 | 2020-04-23 11:45 | 2020-04-23 22:15 | 10:30 | S/O | Due to replacement work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T1 | 2020-04-26 12:36 | 2020-04-26 15:28 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 28:20 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Rangamati | 132/33 kV Transformer-T2 | 2020-04-02 15:10 | 2020-04-02 16:24 | 1:14 | S/O | Due to problem of R-phase DS at 33 kV side | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-MT04 | 2020-04-04 08:25 | 2020-04-04 09:32 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T3 | 2020-04-07 06:07 | 2020-04-07 07:50 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(O) | 132 kV Bus-A | 2020-04-09 08:30 | 2020-04-09 12:00 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhohazari | 132/33 kV Transformer-T2 | 2020-04-12 17:35 | 2020-04-12 17:55 | 0:20 | S/O | Due to Fuse change | 20 | 6.6667 | Power interruption
Madunaghat | 132/33 kV Transformer-T2 | 2020-04-22 06:27 | 2020-04-22 06:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 7:54 |  | Unserved Energy : |  | 6.6667
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:April 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Cumilla(S) | 132/33 kV Transformer-T4 | 2020-04-04 08:44 | 2020-04-04 09:05 | 0:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2020-04-14 08:10 | 2020-04-14 11:15 | 3:05 | S/O | Due to high temperature | 20 | 61.6667 | Power interruption
Sylhet | 33 kV Bus-2 | 2020-04-14 11:08 | 2020-04-14 12:26 | 1:18 | S/O | Due to CB maintenance work | 13 | 16.9 | Power interruption
Ranganj | 132/33 kV Transformer-T1 | 2020-04-15 08:30 | 2020-04-15 11:15 | 2:45 | S/O | Due to high temperature | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-04-16 10:10 | 2020-04-16 10:20 | 0:10 | S/O | Due to ICSR testing | 8 | 1.3333 | Power interruption
Ranganj | 132/33 kV Transformer-T2 | 2020-04-22 07:05 | 2020-04-22 07:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2020-04-22 07:18 | 2020-04-22 08:51 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformer-T5 |  | 2020-04-27 16:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 9:12 |  | Unserved Energy : |  | 79.9
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T1 | 2020-04-02 07:15 | 2020-04-02 09:32 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kV Transformers-T1 & T2 with 33 kV Bus | 2020-04-02 07:45 | 2020-04-02 07:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T1 | 2020-04-23 16:06 | 2020-04-23 16:44 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2020-04-23 18:21 | 2020-04-23 19:38 | 1:17 | S/O | Due to reparing work at 33 kV U/G cable work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2020-04-23 06:40 | 2020-04-23 23:25 | 16:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV Transformer-T2 | 2020-04-24 08:11 | 2020-04-24 10:07 | 1:56 | S/O | Due to 33 kV cable maintenance | 0 | 0 | No interruption
|  |  | Total : | 22:53 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
Shahjadpur | 132/33 kV Transformer-T1 |  | 2020-04-14 18:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T01 | 2020-04-16 11:36 | 2020-04-16 12:23 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus & Transformer | 2020-04-18 10:18 | 2020-04-18 12:03 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 2:32 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Rajshahi | 230/132 kV Transformer-T-01 | 2020-04-01 12:22 | 2020-04-01 12:33 | 0:11 | S/O | Due to DS problem | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T2 | 2020-04-10 09:36 | 2020-04-10 16:56 | 7:20 | S/O | Due to OLTC refile | 0 | 0 | No interruption
| 132 kV main Bus | 2020-04-16 10:25 | 2020-04-16 14:22 | 3:57 | S/O | Due maintenance work | 0 | 0 | No interruption
Palashbari | 132/33 kV Transformer-T1 | 2020-04-19 10:20 | 2020-04-19 11:42 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | 230/132 kV Transformer-T01 |  | 2020-04-20 14:03 |  | S/O | After maintenance work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T3 | 2020-04-20 13:35 | 2020-04-20 14:12 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T4 | 2020-04-23 09:50 | 2020-04-23 22:47 | 12:57 | S/O | Due maintenance work at 33 kV side | 14 | 181.3 | Power interruption
Pabna | 132/33 kV Transformer-T3 | 2020-04-23 09:36 | 2020-04-23 12:46 | 3:10 | S/O |  | 0 | 0 | No interruption
Purbasadipur | Capacitor Bank 33 kV |  | 2020-04-24 16:10 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 29:34 |  | Unserved Energy : |  | 181.3
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 151:39 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2020-04-08 07:50 | 2020-04-08 11:40 | 3:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | Uttara-Mirpur 132 kV line | 2020-04-11 12:20 | 2020-04-11 13:45 | 1:25 | S/O | Due to removing bird nest | 0 | 0 | No interruption
| Mirpur-Uttara 3rd phase 132 kV ine | 2020-04-11 13:49 | 2020-04-11 15:06 | 1:17 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Sherpur | Sherpur-Mymensingh united 132 line |  | 2020-04-11 23:18 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-04-15 14:32 | 2020-04-15 15:09 | 0:37 | S/O | Due to removing bird nest | 70 | 43.1667 | Power interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2020-04-18 14:28 | 2020-04-18 15:44 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-04-19 11:30 | 2020-04-19 12:10 | 0:40 | S/O | Due to removing kie | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-1 | 2020-04-23 14:57 | 2020-04-23 16:53 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 11:01 |  | Unserved Energy: |  | 43.1667
Dhaka (South) Grid Circle :
Rampura | Rampura-Bashundhara 132 kV line-2 |  | 2020-04-02 11:49 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bangabhaban | Bangabhaban-Maniknagar 132 kV line-2 |  | 2020-04-02 14:27 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 | 2020-04-11 09:10 | 2020-04-11 11:01 | 1:51 | S/O | Due to removing kite | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-2 | 2020-04-14 11:59 | 2020-04-14 16:08 | 4:09 | S/O | Due to tree trimming | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV line | 2020-04-16 08:20 | 2020-04-16 13:12 | 4:52 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-1 | 2020-04-18 08:46 | 2020-04-18 13:29 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV line-2 | 2020-04-18 13:36 | 2020-04-18 16:02 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Narsinghdi 132 kV line |  | 2020-04-20 10:11 |  | S/O | After maintenance work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Bus-1 | 2020-04-23 07:42 | 2020-04-23 07:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-2 | 2020-04-23 13:07 | 2020-04-23 18:45 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:39 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar | Halishahar-Khulshi 132 kV line-1 | 2020-04-05 13:14 | 2020-04-05 13:28 | 0:14 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2020-04-13 13:52 | 2020-04-13 14:35 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2020-04-14 12:10 | 2020-04-14 12:24 | 0:14 | S/O | Due to removing nest | 0 | 0 | No interruption
| Khulshi-Halishahar 132 kV line-1 | 2020-04-21 08:30 | 2020-04-21 10:11 | 1:41 | S/O | Due to replacement work | 0 | 0 | No interruption
| Khulshi-Halishahar 132 kV line-2 | 2020-04-21 10:07 | 2020-04-21 10:35 | 0:28 | S/O |  | 0 | 0 | No interruption
Halishahar | Halishahar-Baraulia 132 kV line | 2020-04-21 10:54 | 2020-04-21 11:20 | 0:26 | S/O | Due to relay test | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV line-1 | 2020-04-22 14:43 | 2020-04-22 17:47 | 3:04 | S/O | Due to safety to cut 11 kV Pole under this 132 kV line
| Juldah-Shahmirpur 132 kV line-1 | 2020-04-23 10:03 | 2020-04-23 12:50 | 2:47 | S/O | Due to repairing work | 0 | 0 | No interruption
|  |  | Total : | 9:37 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj 132 kV line | 2020-04-06 15:45 | 2020-04-06 17:10 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sylhet-Chatak 132 kV line | 2020-04-21 09:10 | 2020-04-21 13:15 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur P/S 132 kV line | 2020-04-26 10:09 | 2020-04-26 13:45 | 3:36 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 9:06 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj(N) | Gopalganj-Payra 400 kV line-2 | 2020-04-04 08:11 | 2020-04-04 12:50 | 4:39 | S/O | Due to C/M work | 31 | 144.15 | Power interruption 08:37 to 08:44
| Gopalganj(N)- Faridpur 132 kV line | 2020-04-04 08:24 | 2020-04-04 12:23 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj(N)-Madaripur all 132 kV line | 2020-04-04 08:17 | 2020-04-04 12:40 | 4:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Gopalganj(N)-Gopalganj(O) 132 kV line | 2020-04-04 08:18 | 2020-04-04 12:33 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | Noapara-Banglatrac P/P 132 kV ine | 2020-04-21 11:59 | 2020-04-21 14:30 | 2:31 | S/O | Due to tree trimming | 0 | 0 | No interruption
| Noapara-Jessore 132 kV ine-2 | 2020-04-21 15:23 | 2020-04-21 21:06 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-1 | 2020-04-22 09:36 | 2020-04-22 14:27 | 4:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2020-04-24 07:13 | 2020-04-24 07:13 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Barishal (N) 132 kV line-1 | 2020-04-30 07:34 | 2020-04-30 07:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 30:21 |  | Unserved Energy: |  | 144.15
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishwardi | Ishwardi-Ghorashal 230 kV Ckt-2 | 2020-04-01 09:34 | 2020-04-01 11:15 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-1 | 2020-04-04 10:16 | 2020-04-04 11:34 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Rajshahi 230 kV line-1 |  | 2020-04-20 09:57 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bheramara HVDC-Rajshahi 230 kV line-2 |  | 2020-04-20 13:38 |  | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 2:59 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Sherpur | Sherpur-Bogura(N) 132 kV line-1 & 2 | 2020-04-13 12:24 | 2020-04-13 21:47 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Lalmonirhat 132 kV line | 2020-04-18 06:35 | 2020-04-18 07:45 | 1:10 | S/O | Due to repairing work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 132 kV line | 2020-04-24 06:55 | 2020-04-24 06:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 10:33 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Haripur-Siddhirganj 132 kV line | 2020-04-11 15:58 | 2020-04-11 16:28 | 0:30 | S/O | Due to Isolated of Ullon S/S | 70 | 35 | Power interruption
|  |  | Total : | 0:30 |  | Unserved Energy: |  | 35
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 97:46 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April' 2020
| Area | Previous Month (March 2020) |  |  |  | Current Month (April 2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 13 | 2 | 76 | 91 | 30 | 8 | 23 | 61
2 | Dhaka (South) Grid Circle. | 17 | 5 | 27 | 49 | 27 | 3 | 17 | 47
3 | Chattogram Grid Circle. | 4 | 3 | 23 | 30 | 21 | 2 | 14 | 37
4 | Cumilla Grid Circle. | 13 | 4 | 20 | 37 | 34 | 10 | 11 | 55
5 | Khulna Grid Circle. | 11 | 7 | 36 | 54 | 29 | 7 | 15 | 51
6 | Bheramara HVDC Grid Circle | 2 | 1 | 13 | 16 | 5 | 4 | 7 | 16
7 | Bogura Grid Circle. | 11 | 13 | 18 | 42 | 18 | 24 | 12 | 54
8 | Others | 2 |  |  | 2 | 1 | 1 | 1 | 3
9 | Total | 73 | 35 | 213 | 321 | 165 | 59 | 100 | 324
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April' 2020
| Area | Previous Month (March 2020) |  |  |  | Current Month (April 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 162.77 |  | 2703.88 | 2866.65 | 436.3833 | 118.6667 | 72.3333 | 627.3833
2 | Dhaka (South) Grid Circle. | 401.85 |  | 80.42 | 482.27 | 46.5333 | 0 | 0 | 46.5333
3 | Chattogram Grid Circle. |  |  |  | 0 | 443.15 | 74.8 | 6.67 | 524.62
4 | Cumilla Grid Circle. | 69.27 |  | 30.75 | 100.02 | 63.8 | 139.43 | 79.9 | 283.13
5 | Khulna Grid Circle. | 20.7 | 20.9 | 932.5 | 974.1 | 371.27 | 76.07 | 144.15 | 591.49
6 | Bheramara HVDC Grid Circle |  |  | 359.57 | 359.57 | 9.6 | 55.33 |  | 64.93
7 | Bogura Grid Circle. | 1374.78 | 135.58 | 198.53 | 1708.89 | 10.67 | 236.58 | 181.3 | 428.55
8 | Others | 11.27 |  |  | 11.27 |  | 46.67 | 35 | 81.67
9 | Total | 2040.64 | 156.48 | 4305.65 | 6502.77 | 1381.4067 | 747.5467 | 519.3533 | 2648.3067
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 8 | 2 | 10 | 4 | 2 | 4 | 323.47
2 | Dhaka (South) | 5031.6 | 2 |  | 2 | 2 |  |  | 40.8333
3 | Chattogram | 2042 | 4 | 2 | 6 | 4 |  | 2 | 327.07
4 | Khulna | 2434 | 6 |  | 6 | 3 |  | 3 | 325.0333
5 | Bheramara (HVDC) | 2423.3 | 1 |  | 1 |  |  | 1 | 55.3333
6 | Bogura | 3145.6 | 8 | 1 | 9 | 1 | 2 | 6 | 338.22
7 | Cumilla | 2981 | 8 | 3 | 11 | 5 | 2 | 4 | 273.68
8 | Others | - | 1 |  | 1 |  | 1 |  | 46.47
| Total | 23365.5 | [6 empty] | 1730.11
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.91%
4 | Khulna | 99.9%
5 | Bheramara (HVDC) | 99.97% | [6 empty] | Executive Engineer
6 | Bogura | 99.89% | [6 empty] | Information Management Division
7 | Cumilla | 99.91% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 3 | 1 | 4 | 2 | 2 |  | 303.92
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | 1 |  | - | 5.7
3 | Chattogram | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - | - | 197.55
4 | Khulna | 1238.4 | 21 | 8 | 1 | 9 | 8 |  | 1 | 266.45
5 | Bheramara (HVDC) | 598.7 |  | 1 |  | 1 | 1 | - |  | 9.6
6 | Bogura | 1803.3 | 38 | 2 |  | 2 |  |  | 2 | 90.3333
7 | Cumilla | 1648.16 | 17 | 1 |  | 1 |  | - | 1 | 9.45
7 | Others | - |  | 1 | - | 1 | 1 | - | - | 35
| Total | 8862.13 | 174 | [6 empty] | 918.0033
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.92%
3 | Chattogram | 99.98%
4 | Khulna | 99.94%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.88% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-04-18 | 18 | - | - | - | 1 | 1hour 10 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:April' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 2:00 | 55 | 110 | Due to tripping 33 kV feeder fault
Kishoreganj | 1 | 1:42 | 50 | 85 | Due to re-hot maintenance 132/33 kV Transformers T1 & T2
Mymensingh | 1 | 0:08 | 110 | 14.6667 | Due to tripping 33 kV feeder fault
Jamalpur | 1 | 0:29 | 50 | 24.1667
| 1 | 2:15 | 12 | 27
Netrakona | 1 | 0:40 | 10 | 6.6667 | Due to red-hot maintenance of PBS feeder
Jamalpur | 1 | 0:18 | 60 | 18 | Due to tripping 33 kV feeder fault
Kabirpur | 1 | 0:12 | 44 | 8.8
Tongi | 1 | 0:41 | 100 | 68.3333 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
Mymensingh | 1 | 0:17 | 635 | 179.9167 | Due to tripping of Mymensingh-Kishoreganj 132 kV line-1 & 2
Tongi | 1 | 0:15 | 50 | 12.5 | Due to tripping of Tongi-Kabirpur 132 kV line-2
Netrakona | 1 | 0:14 | 15 | 3.5 | Due to S/D of132/33 kV Transformer-T3
Kabirpur | 1 | 1:17 | 20 | 25.6667 | Due to S/D of132/33 kV Transformer-T2 & T3
Mymensingh | 1 | 0:37 | 70 | 43.1667 | Due to S/D of Mynensingh- Kishoreganj 132 kV line-2
Siddhirganj | 2 | 0:21 | 80 | 28 | Due to trippnig of 132/33 kV Transformers-T1 & T2
|  | 0:11 | 70 | 12.8333
Lalbagh | 1 | 0:19 | 18 | 5.7 | Due to tripping of Lalagh-Hasnabad 132 kV line
Ullon | 2 | 0:30 | 70 | 35 | Due to S/D of Ullon-Haripur-Siddhirganj 132 kV line
|  | 0:56 | 50 | 46.6667 | Due to tripping of 132/33 kV Transformers-T1 ,T2 & T3
Halishahar | 1 | 0:20 | 29 | 9.6667 | Due to tripping of 132/33 kV Transformers-T1 ,T2 & T3
Madunaghat | 1 | 3:07 | 24 | 74.8 | Due to red-hot maintenance of 132/33 kV Transformer T1
Khulshi | 1 | 0:29 | 30 | 14.5 | Due to tripping of 132/33 kV Transformer-T2 & T3
Rangamati | 1 | 8:19 | 26 | 216.2333 | Due to tripping of 132/33 kV Transformer-T1
Halishahar | 1 | 0:12 | 26 | 5.2 | Due to tripping 33 kV feeder fault
Khulshi | 1 | 0:27 | 439 | 197.55 | Due to tripping of Khulshi-Bakulia 132 kV line
Dhohazari | 1 | 0:20 | 20 | 6.6667 | Due to S/D of 132/33 kV Transformer-T2
Chattak | 1 | 0:13 | 2 | 0.43333 | Due to trippnig of 132/33 kV Transformer-T1
Cumilla (N) | 1 | 0:27 | 32 | 14.4 | Due to tripping of 132/33 kV Transformers-T3 & T4
Sumamganj | 1 | 0:16 | 18 | 4.8 | Due to trippnig of 132/33 kV Transformer-T1
Feni |  | 1:09 | 24 | 27.6 | Due to red-hot maintenance of 132/33 kV Transformer T1
Shahjibazar | 1 | 0:11 | 25 | 4.5833 | Due to trippnig of 132/33 kV Transformer-T2
Sylhet | 1 | 0:49 | 90 | 73.5 | Due to 33kV feeder incoming Breaker burst
B.Baria | 1 | 0:46 | 50 | 38.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Kulaura | ! | 1:53 | 16 | 30.1333 | Due to trippnig of 132/33 kV Transformer-T1
Sylhet |  | 1:03 | 9 | 9.45 | Due to tripping of Sylhet -Fenchuganj 132 kV line
Ramganj | 1 | 3:05 | 20 | 61.6667 | Due to S/D of 132/33 kV Transformer T2
Sylhet | 2 | 1:18 | 13 | 16.9 | Due to S/D of Bus-2
|  | 0:10 | 8 | 1.3333 | Due to S/D of 132/33 kV Transformer T2
Bagerhat | 2 | 0:10 | 10 | 1.6667 | Due to tripping of 132/33 kV Transformers T1 & T3
|  | 0:06 | 13 | 1.3 | Due to tripping of 33 kV feeder
Bhandaria | 1 | 2:59 | 80 | 238.6667 | Due to tripping of 132/33 kV Transformer T1
Shariatpur |  | 1:16 | 25 | 31.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Madaripur | 2 | 5:33 | 8 | 44.4 | Due to red-hot maintenance of 132/33 kV Transformer T3
|  | 0:11 | 40 | 7.3333 | Due to tripping of 132/33 kV Transformers T1 & T2
Bagerhat | 1 | 0:20 | 32 | 10.6667 | Due to tripping of Bagerhat-Mongla 132 kV line
Barisal(S) | 1 | 0:30 | 112 | 56 | Due to tripping of Barisal(S)-Barisal(N) 132 kV line-1 & 2
Gopalganj(New) | 1 | 0:28 | 55 | 25.6667 | Due to tripping of Gopalganj(N)-Gopalganj (O) 132 kV line
Bagerhat | 1 | 0:20 | 26 | 8.6667 | Due to tripping of Bagerhat-Mongla 132 kV line
| 1 | 0:18 | 6 | 1.8
Barisal | 1 | 0:14 | 35 | 8.1667 | Due to tripping of Barisal-Bhandaria 132 kV line
Gopalganj(New) | 1 | 0:20 | 28 | 9.3333 | Due to tripping of Gopalganj(N)-Gopalganj (O) 132 kV line
Barisal | 1 | 0:05 | 24 | 2 | Due to tripping of Barisal-Bhandaria 132 kV line
Gopalganj(N) | 1 | 4:39 | 31 | 144.15 | Due to S/D of Gopalganj(N)-Payra 400 kV line-2
Bottail | 1 | 1:23 | 40 | 55.3333 | Due to red-hot maintenance of 132/33 kV Transformer T2 & 33 kV Bus
Baghabari | 1 | 0:09 | 64 | 9.6 | Due to tripping of Baghabari-Shahjadpur 132 kV line-2
Barapukuria | 1 | 1:40 | 20 | 33.3333 | Due to red-hot maintenance of 132/33 kV Transformer T4
Purbasadipur | 1 | 0:08 | 80 | 10.6667 | Due to tripping of 132/33 kV Transformers T2 & T3
Panchagar | 1 | 0:48 | 20 | 16 | Due to Oil lealage of Transformers T1, T2 & T3
Naogaon | 1 | 2:35 | 18 | 46.5 | Due to red-hot maintenance of 132/33 kV Transformer T2 & 33 kV Bus
Bogura (O) | 2 | 0:35 | 20 | 11.6667 | Due to red-hot maintenance of 132/33 kV Transformer T4 & 33 kV Bus
|  | 2:10 | 15 | 32.5 | Due to red-hot maintenance of 132/33 kV Transformer T3
Narail | 2 | 1:04 | 3 | 3.2 | Due to red-hot maintenance of 132/33 kV Transformer T2
|  | 1:01 | 3 | 3.05 | Due to red-hot maintenance of 132/33 kV Transformer T4
Rangpur | 2 | 4:36 | 10 | 46 | Due to tripping of Rangpur-Kurigram 132 kV line
|  | 1:10 | 38 | 44.3333 | Due to red-hot maintenance of Rangpur-Kurigram 132 kV line
C.nawabganj | 1 | 12:57 | 14 | 181.3 | Due to S/D of Transformer 132/33 kV Transformer T4 & 33 kV Bus
| Total Unserved energy : |  |  | 2648.3 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 100 | 2 | 2020-04-03 | 15:00
2 | Munsiganj | 112 | 2 | 2020-04-03 | 19:00
3 | Sonargaon | 65 | 5 | 2020-04-03 | 14:00
4 | Shyampur | 150 | 28 | 2020-04-03 | 0.083333
5 | Bhulta | 99 | 29 | 2020-04-03 | 0:00
6 | Madanganj | 53 | 4 | 2020-04-03 | 24:00
7 | Shitalakhya | 77 | 5 | 2020-04-03 | 11:00
8 | Rahim steel | 11 | 23 | 2020-04-03 | 18:30
9 | Matuail | 54 | 4 | 2020-04-03 | 0.95833
10 | Ghorasal | 62 | 14 | 2020-04-03 | 19:30
11 | Narsingdi | 106 | 1 | 2020-04-03 | 19:00
12 | Haripur (SBU) | 63 | 7 | 2020-04-03 | 19:00
13 | Ullon | 64 | 2 | 2020-04-03 | 0.041667
14 | Hasnabad | 161 | 18 | 2020-04-03 | 0.8125
15 | Magbazar | 135 | 2 | 2020-04-03 | 4:00
16 | Maniknagar | 80 | 11 | 2020-04-03 | 0.58333
17 | Bangabhaban | 16 | 1 | 2020-04-03 | 0.66667
18 | Narinda | 68 | 7 | 2020-04-03 | 1899-12-31
19 | Dhanmondi | 86 | 11 | 2020-04-03 | 0.77083
20 | Lalbag | 53 | 30 | 2020-04-03 | 13:00
21 | Madartek | 65 | 11 | 2020-04-03 | 19:30
22 | Dhaka University | - | - | - | -
23 | Mirpur | 80 | 7 | 2020-04-03 | 0.77083
24 | Kalyanpur | 78 | 14 | 2020-04-03 | 22:00
25 | Gulshan | 82 | 15 | 2020-04-03 | 11:00
26 | Uttara | 61 | 14 | 2020-04-03 | 1899-12-31
27 | Uttara(new) | 22 | 2 | 2020-04-03 | 0.8125
28 | Kamrangirchar | 61 | 14 | 2020-04-03 | 21:00
29 | Savar | 92 | 7 | 2020-04-03 | 18:30
30 | Bhasantec | 118 | 7 | 2020-04-03 | 19:00
31 | Agargaon | 42 | 1 | 2020-04-03 | 0.8125
32 | Satmosjid | 85 | 14 | 2020-04-03 | 0.95833
33 | Tongi | 97 | 9 | 2020-04-03 | 18:00
34 | Kabirpur | 126 | 2 | 2020-04-03 | 0.77083
35 | Basundhara | 103 | 14 | 2020-04-03 | 21:00
36 | Manikganj | 81 | 14 | 2020-04-03 | 21:00
37 | Joydevpur | 120 | 30 | 2020-04-03 | 14:00
38 | New Tongi | 72 | 8 | 2020-04-03 | 18:30
39 | Kodda | 136 | 5 | 2020-04-03 | 15:00
40 | Dhamrai | 62 | 1 | 2020-04-03 | 19:00
41 | Rajendrapur | 66 | 4 | 2020-04-03 | 20:00
42 | Valuka | 66 | 5 | 2020-04-03 | 0.79167
43 | Tangail | 208 | 9 | 2020-04-03 | 19:00
44 | Mymensing | 230 | 7 | 2020-04-03 | 19:00
45 | Kishorganj | 134 | 10 | 2020-04-03 | 19:00
46 | Netrokona | 123 | 27 | 2020-04-03 | 19:00
47 | Jamalpur | 144 | 8 | 2020-04-03 | 19:00
48 | Sherpur | 116 | 8 | 2020-04-03 | 19:30
49 | Srimongal | 41 | 10 | 2020-04-03 | 0.8125
50 | Shahjibazar | 90 | 7 | 2020-04-03 | 19:30
51 | Fenchuganj | 37 | 10 | 2020-04-03 | 19:00
52 | Kulawara | 43 | 14 | 2020-04-03 | 20:00
53 | Sylhet | 109 | 8 | 2020-04-03 | 19:30
54 | Chatak | 31 | 10 | 2020-04-03 | 20:00
55 | Sunamganj | 37 | 8 | 2020-04-03 | 19:30
56 | Bianibazar | 60 | 10 | 2020-04-03 | 19:30
57 | Cumilla (S) | 144 | 2 | 2020-04-03 | 0.79167
58 | Cumilla(N) | 127 | 9 | 2020-04-03 | 19:30
59 | Chandpur | 102 | 19 | 2020-04-03 | 20:00
60 | Feni | 115 | 14 | 2020-04-03 | 20:00
61 | Chowmuhani | 163 | 18 | 2020-04-03 | 19:00
62 | Ashuganj | 55 | 14 | 2020-04-03 | 19:30
63 | Daudkandi | 132 | 7 | 2020-04-03 | 0.83333
64 | B.Baria | 154 | 7 | 2020-04-03 | 21:00
65 | Ramganj | 106 | 14 | 2020-04-03 | 19:30
66 | Chaddagram | 50 | 22 | 2020-04-03 | 19:00
67 | PHP | 11 | 19 | 2020-04-03 | 23:00
68 | Madanhat | 57 | 17 | 2020-04-03 | 19:30
69 | Hathazari | 86 | 2 | 2020-04-03 | 0.79167
70 | Khulshi | 168 | 2 | 2020-04-03 | 23:00
71 | Halishahar | 118 | 20 | 2020-04-03 | 19:30
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Baraulia | 146 | 4 | 2020-04-03 | 20:00
73 | Sikalbaha | 27 | 19 | 2020-04-03 | 19:30
74 | Dohazari | 102 | 9 | 2020-04-03 | 19:30
75 | Cox'sbazar | 92 | 3 | 2020-04-03 | 18:30
76 | Chandraghona | 34 | 23 | 2020-04-03 | 18:30
77 | Kaptai | 8 | 17 | 2020-04-03 | 22:00
78 | A. Khaer Stl. | 23 | 1 | 2020-04-03 | 10:00
79 | Bakulia | 78 | 2 | 2020-04-03 | 0.95833
80 | Julda | 20 | 6 | 2020-04-03 | 0.58333
81 | TK chemical | 17 | 14 | 2020-04-03 | 18:30
82 | Modern Steel | 17 | 30 | 2020-04-03 | 11:00
83 | Shahmirpur | 27 | 29 | 2020-04-03 | 21:00
84 | Khagrachhari | 22 | 2 | 2020-04-03 | 19:00
85 | Matarbari | 31.5 | 7 | 2020-04-03 | 19:00
86 | Baroiar Hat | 40 | 21 | 2020-04-03 | 18:30
87 | Rangamati | 10 | 1 | 2020-04-03 | 0.77083
88 | Abul Khair 230 | 30 | 4 | 2020-04-03 | 22:00
89 | BSRM | 156 | 3 | 2020-04-03 | 10:00
90 | GPH Ispat | 16 | 14 | 2020-04-03 | 20:00
91 | Goalpara | 31 | 4 | 2020-04-03 | 13:00
92 | Central s/s | 78 | 10 | 2020-04-03 | 21:00
93 | Noapara | 54 | 14 | 2020-04-03 | 0.83333
94 | Jashore | 132 | 14 | 2020-04-03 | 21:00
95 | Benapol | 48 | 3 | 2020-04-03 | 21:00
96 | Jhenidah | 114 | 18 | 2020-04-03 | 19:00
97 | Bottail | 106 | 18 | 2020-04-03 | 19:30
98 | G.K Project | 58 | 14 | 2020-04-03 | 21:00
99 | Faridpur | 170 | 18 | 2020-04-03 | 20:00
100 | Madaripur | 95 | 14 | 2020-04-03 | 21:00
101 | Sariatpur | 58 | 14 | 2020-04-03 | 19:30
102 | Gopalganj | 93 | 14 | 2020-04-03 | 19:30
103 | Bagerhat | 86 | 7 | 2020-04-03 | 19:30
104 | Mongla | 46 | 5 | 2020-04-03 | 10:00
105 | Satkhira | 111 | 10 | 2020-04-03 | 21:00
106 | Gallamari | 50 | 5 | 2020-04-03 | 13:00
107 | Magura | 52 | 14 | 2020-04-03 | 19:00
108 | Norail | 40 | 2 | 2020-04-03 | 22:00
109 | Chuadanga | 85 | 2 | 2020-04-03 | 21:00
110 | Barsal(N) | 42 | 14 | 2020-04-03 | 19:30
111 | Barsal(S) | 86 | 13 | 2020-04-03 | 21:00
112 | Patuakhali | 101 | 18 | 2020-04-03 | 21:00
113 | Bhandaria | 50 | 2 | 2020-04-03 | 19:30
114 | Borhan Uddin | 38 | 14 | 2020-04-03 | 21:00
115 | Ishurdi | 58 | 14 | 2020-04-03 | 19:30
116 | Ruppur Paromanobik | 2 | 2 | 2020-04-03 | 0.70833
117 | Natore | 134 | 10 | 2020-04-03 | 19:30
118 | Bogura | 163 | 13 | 2020-04-03 | 20:00
119 | Naogaon | 130 | 9 | 2020-04-03 | 20:00
120 | Rajshahi | 141 | 13 | 2020-04-03 | 19:30
121 | Rajshahi New | 14 | 2 | 2020-04-03 | 0.83333
122 | C.Nawabganj | 85 | 10 | 2020-04-03 | 20:00
123 | Amnura | 60 | 9 | 2020-04-03 | 21:00
124 | Pabna | 106 | 14 | 2020-04-03 | 19:30
125 | Shahjadpur | 100 | 7 | 2020-04-03 | 20:00
126 | Serajganj | 92 | 8 | 2020-04-03 | 19:30
127 | Niyamatpur | 91 | 9 | 2020-04-03 | 0.83333
128 | Joypurhat | 66 | 2 | 2020-04-03 | 21:00
129 | Sherpur(Bogura) | 49 | 2 | 2020-04-03 | 19:00
130 | Mohastangar | 48 | 9 | 2020-04-03 | 19:00
131 | Rangpur | 145 | 14 | 2020-04-03 | 19:00
132 | Lalmonirhat | 60 | 14 | 2020-04-03 | 19:30
133 | Saidpur | 112 | 11 | 2020-04-03 | 19:00
134 | Purbasadipur | 110 | 7 | 2020-04-03 | 10:00
135 | Thakurgaon | 77 | 6 | 2020-04-03 | 19:00
136 | Palshbari | 126 | 10 | 2020-04-03 | 0.83333
137 | Barapukuria | 66 | 1 | 2020-04-03 | 12:00
138 | Panchugar | 44 | 4 | 2020-04-03 | 0.79167
139 | Joldhaka | 31 | 8 | 2020-04-03 | 0.79167
140 | Kurigram | 58 | 9 | 2020-04-03 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 2845 | 05.04.2020 | 14:00
Chattogram | 1104 | 02.04.2020 | 21:00
Khulna | 1408 | 14.04.2020 | 19:30
Rajshahi | 1285 | 10.04.2020 | 20:00
Cumilla | 1081 | 14.04.2020 | 19:30
Mymensingh | 970 | 10.04.2020 | 19:30
Sylhet | 904 | 07.04.2020 | 18:00
Barisal | 315 | 08.04.2020 | 24:00
Rangpur | 780 | 14.04.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 413 | 11 | 2020-04-03 | 20:00 | 389 | 14 | 2020-04-03 | 24:00:
2 | Bheramara | 400 | 410 | 10 | 2020-04-03 | 7:00 | 383 | 2 | 2020-04-03 | 21:00
3 | Ashuganj(N) | 400 | 410 | 30 | 2020-04-03 | 6:00 | 385 | 14 | 2020-04-03 | 24:00
4 | Payra | 400 | 419 | 11 | 2020-04-03 | 6:00 | 390 | 9 | 2020-04-03 | 18:30
5 | Kaliakoir | 400 | 412 | 30 | 2020-04-03 | 6:00 | 370 | 14 | 2020-04-03 | 18:30
6 | Bhulta | 400 | 404 | 25 | 2020-04-03 | 6:00 | 377 | 30 | 2020-04-03 | 17:00
7 | Gopalganj | 400 | 417 | 23 | 2020-04-03 | 17:00 | 366 | 9 | 2020-04-03 | 18:30
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 1 | 2020-04-03 | 1:00 | 232 | 19 | 2020-04-03 | 23:00
2 | Ishurdi | 230 | 240 | 4 | 2020-04-03 | 23:00 | 224 | 10 | 2020-04-03 | 12:00
3 | Ashuganj | 230 | 242 | 1 | 2020-04-03 | 5:00 | 230 | 14 | 2020-04-03 | 24:00
4 | Serajganj | 230 | 236 | 20 | 2020-04-03 | 5:00 | 221 | 30 | 2020-04-03 | 21:00
5 | Baghabari | 230 | 247 | 20 | 2020-04-03 | 3:00 | 217 | 30 | 2020-04-03 | 21:00
6 | Barapukuria | 230 | 241 | 21 | 2020-04-03 | 11:00 | 213 | 30 | 2020-04-03 | 21:00
7 | Bogura | 230 | 242 | 20 | 2020-04-03 | 4:00 | 208 | 10 | 2020-04-03 | 19:00
8 | Rajshahi | 230 | 232 | 30 | 2020-04-03 | 5:00 | 210 | 25 | 2020-04-03 | 19:30
9 | Khulna South | 230 | 244 | 21 | 2020-04-03 | 9:00 | 204 | 18 | 2020-04-03 | 13:00
10 | Rampura | 230 | 235 | 11 | 2020-04-03 | 20:00 | 225 | 14 | 2020-04-03 | 22:00
11 | Haripur | 230 | 236 | 20 | 2020-04-03 | 4:00 | 225 | 14 | 2020-04-03 | 22:00
12 | Hasnabad | 230 | 238 | 27 | 2020-04-03 | 2:00 | 226 | 14 | 2020-04-03 | 19:30
13 | Shyampur | 230 | 238 | 11 | 2020-04-03 | 20:00 | 223 | 5 | 2020-04-03 | 12:00
14 | Aminbazar | 230 | 241 | 11 | 2020-04-03 | 20:00 | 225 | 5 | 2020-04-03 | 12:00
15 | Tongi | 230 | 240 | 11 | 2020-04-03 | 20:00 | 213 | 30 | 2020-04-03 | 7:00
16 | Comilla (N) | 230 | 240 | 11 | 2020-04-03 | 20:00 | 225 | 23 | 2020-04-03 | 15:00
17 | Hathazari | 230 | 242 | 30 | 2020-04-03 | 1:00 | 212 | 9 | 2020-04-03 | 16:00
18 | Megnaghat | 230 | 242 | 23 | 2020-04-03 | 17:00 | 228 | 14 | 2020-04-03 | 23:00
19 | Fenchuganj | 230 | 247 | 21 | 2020-04-03 | 21:00 | 231 | 30 | 2020-04-03 | 12:00
20 | Siddhirganj | 230 | 240 | 11 | 2020-04-03 | 20:00 | 227 | 14 | 2020-04-03 | 24:00
21 | Maniknagar | 230 | 246 | 30 | 2020-04-03 | 5:00 | 226 | 5 | 2020-04-03 | 12:00
22 | Old Airport | 230 | 241 | 11 | 2020-04-03 | 20:00 | 214 | 30 | 2020-04-03 | 10:00
23 | Barisal | 230 | 253 | 23 | 2020-04-03 | 17:00 | 218 | 30 | 2020-04-03 | 9:00
24 | AKSML | 230 | 229 | 19 | 2020-04-03 | 1:00 | 210 | 7 | 2020-04-03 | 3:00
25 | BSRM | 230 | 239 | 30 | 2020-04-03 | 2:00 | 212 | 23 | 2020-04-03 | 19:00
26 | Bibiyana | 230 | 243 | 11 | 2020-04-03 | 20:00 | 231 | 9 | 2020-04-03 | 20:00
27 | Bhulta | 230 | 241 | 11 | 2020-04-03 | 20:00 | 226 | 14 | 2020-04-03 | 12:00
28 | Ashuganj (S) | 230 | 241 | 25 | 2020-04-03 | 6:00 | 226 | 30 | 2020-04-03 | 14:00
29 | Kaliakoir | 230 | 246 | 11 | 2020-04-03 | 20:00 | 225 | 14 | 2020-04-03 | 18:30
30 | GPH | 230 | 238 | 25 | 2020-04-03 | 5:00 | 209 | 23 | 2020-04-03 | 15:00
132 kV Substation
1 | Siddhirganj | 132 | 137 | 11 | 2020-04-03 | 0.83333 | 128 | 5 | 2020-04-03 | 0.5
2 | Munsiganj | 132 | 139 | 5 | 2020-04-03 | 0.79167 | 127 | 5 | 2020-04-03 | 0.5
3 | Sonargaon | 132 | 137 | 11 | 2020-04-03 | 0.875 | 127 | 5 | 2020-04-03 | 0.5
4 | Shyampur | 132 | 143 | 11 | 2020-04-03 | 0.83333 | 131 | 5 | 2020-04-03 | 0.5
5 | Bhulta | 132 | 132 | 11 | 2020-04-03 | 0.83333 | 123 | 5 | 2020-04-03 | 0.5
6 | Madanganj | 132 | 142 | 11 | 2020-04-03 | 20:00 | 127 | 23 | 2020-04-03 | 0.58333
7 | Shitalakhya | 132 | 143 | 11 | 2020-04-03 | 0.83333 | 128 | 5 | 2020-04-03 | 0.58333
8 | Rahim Steal | 132 | 137 | 11 | 2020-04-03 | 21:00 | 129 | 5 | 2020-04-03 | 0.5
9 | Matuail | 132 | 137 | 11 | 2020-04-03 | 0.875 | 128 | 5 | 2020-04-03 | 0.5
10 | Ghorasal | 132 | 146 | 15 | 2020-04-03 | 0.54167 | 134 | 15 | 2020-04-03 | 0.29167
11 | Narsinghdi | 132 | 141 | 11 | 2020-04-03 | 0.91667 | 125 | 10 | 2020-04-03 | 0.79167
12 | Haripur (SBU) | 132 | 137 | 11 | 2020-04-03 | 0.83333 | 128 | 5 | 2020-04-03 | 0
13 | Ullon | 132 | 138 | 11 | 2020-04-03 | 0.79167 | 126 | 14 | 2020-04-03 | 0.875
14 | Hasnabad | 132 | 142 | 11 | 2020-04-03 | 0.83333 | 127 | 15 | 2020-04-03 | 0.041667
15 | Magbazar | 132 | 139 | 11 | 2020-04-03 | 0.83333 | 126 | 14 | 2020-04-03 | 0.91667
16 | Maniknagar | 132 | 140 | 20 | 2020-04-03 | 0.16667 | 130 | 7 | 2020-04-03 | 0.5
17 | Bangabhaban | 132 | 140 | 20 | 2020-04-03 | 0.16667 | 130 | 7 | 2020-04-03 | 0.5
18 | Narinda | 132 | 140 | 20 | 2020-04-03 | 0.16667 | 130 | 7 | 2020-04-03 | 0.5
19 | Dhanmondi | 132 | 138 | 11 | 2020-04-03 | 0.79167 | 126 | 14 | 2020-04-03 | 0.875
20 | Lalbag | 132 | 144 | 11 | 2020-04-03 | 20:00 | 129 | 30 | 2020-04-03 | 0.58333
21 | Madartek | 132 | 138 | 11 | 2020-04-03 | 0.83333 | 126 | 14 | 2020-04-03 | 0.875
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Mirpur | 132 | 139 | 11 | 2020-04-03 | 0.83333 | 128 | 14 | 2020-04-03 | 23:0
24 | Kalyanpur | 132 | 140 | 11 | 2020-04-03 | 0.83333 | 129 | 30 | 2020-04-03 | 0.875
25 | Gulshan | 132 | 138 | 11 | 2020-04-03 | 0.83333 | 125 | 14 | 2020-04-03 | 0.95833
26 | Uttara | 132 | 145 | 11 | 2020-04-03 | 0.83333 | 131 | 9 | 2020-04-03 | 0.8125
27 | Uttara(New) | 132 | 138 | 11 | 2020-04-03 | 0.83333 | 128 | 5 | 2020-04-03 | 0.5
28 | Kamrangirchar | 132 | 140 | 23 | 2020-04-03 | 0.70833 | 127 | 5 | 2020-04-03 | 0.5
29 | Savar | 132 | 140 | 11 | 2020-04-03 | 0.83333 | 127 | 5 | 2020-04-03 | 0.5
30 | Bhasantec | 132 | 139 | 11 | 2020-04-03 | 0.83333 | 126 | 14 | 2020-04-03 | 0.875
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Agargaon | 132 | 139 | 11 | 2020-04-03 | 0.83333 | 128 | 5 | 2020-04-03 | 0.5
32 | Satmosjid | 132 | 139 | 11 | 2020-04-03 | 0.83333 | 127 | 14 | 2020-04-03 | 1899-12-31
33 | Tongi | 132 | 148 | 11 | 2020-04-03 | 0.83333 | 130 | 1 | 2020-04-03 | 0.041667
34 | Kabirpur | 132 | 140 | 11 | 2020-04-03 | 0.8125 | 123 | 13 | 2020-04-03 | 0.58333
35 | Basundhara | 132 | 139 | 23 | 2020-04-03 | 17:00 | 125 | 14 | 2020-04-03 | 1899-12-31
36 | Manikganj | 132 | 146 | 11 | 2020-04-03 | 20:00 | 125 | 9 | 2020-04-03 | 0.83333
37 | Joydevpur | 132 | 145 | 15 | 2020-04-03 | 1899-12-31 | 132 | 5 | 2020-04-03 | 0.5
38 | New Tongi | 132 | 147 | 11 | 2020-04-03 | 0.83333 | 130 | 14 | 2020-04-03 | 0.91667
39 | Kodda | 132 | 145 | 11 | 2020-04-03 | 0.875 | 124 | 14 | 2020-04-03 | 0.91667
40 | Dhamrai | 132 | 138 | 11 | 2020-04-03 | 0.8125 | 122 | 13 | 2020-04-03 | 0.58333
41 | Rajendrapur | 132 | 146 | 11 | 2020-04-03 | 0.83333 | 123 | 14 | 2020-04-03 | 0.91667
42 | Valuka | 132 | 143 | 11 | 2020-04-03 | 0.875 | 111 | 6 | 2020-04-03 | 0.625
43 | Tangail | 132 | 140 | 11 | 2020-04-03 | 0.875 | 121 | 10 | 2020-04-03 | 0.79167
44 | Mymensing | 132 | 142 | 11 | 2020-04-03 | 0.83333 | 114 | 6 | 2020-04-03 | 0.625
45 | Kishorganj | 132 | 143 | 16 | 2020-04-03 | 0.041667 | 118 | 10 | 2020-04-03 | 0.8125
46 | Netrokona | 132 | 142 | 11 | 2020-04-03 | 0.875 | 110 | 6 | 2020-04-03 | 0.625
47 | Jamalpur | 132 | 142 | 11 | 2020-04-03 | 0.875 | 115 | 11 | 2020-04-03 | 6:00
48 | Sherpur | 132 | 143 | 11 | 2020-04-03 | 0.875 | 111 | 6 | 2020-04-03 | 7:00
49 | Srimongal | 132 | 142 | 11 | 2020-04-03 | 0.875 | 133 | 14 | 2020-04-03 | 0.83333
50 | Shahjibazar | 132 | 142 | 11 | 2020-04-03 | 23:00 | 130 | 1 | 2020-04-03 | 0.77083
51 | Fenchuganj | 132 | 140 | 11 | 2020-04-03 | 0.95833 | 133 | 10 | 2020-04-03 | 20:00
52 | Khulawara | 132 | 139 | 11 | 2020-04-03 | 0.91667 | 132 | 6 | 2020-04-03 | 0.77083
53 | Sylhet | 132 | 138 | 11 | 2020-04-03 | 0.83333 | 127 | 6 | 2020-04-03 | 0.54167
54 | Chattak | 132 | 138 | 11 | 2020-04-03 | 0.91667 | 125 | 6 | 2020-04-03 | 0.54167
55 | Sunamganj | 132 | 139 | 15 | 2020-04-03 | 0.625 | 124 | 6 | 2020-04-03 | 0.58333
56 | Biani Bazar | 132 | 139 | 11 | 2020-04-03 | 0.91667 | 126 | 6 | 2020-04-03 | 0.58333
57 | Comilla(South) | 132 | 138 | 11 | 2020-04-03 | 0.91667 | 122 | 14 | 2020-04-03 | 0.79167
58 | Comilla (North) | 132 | 142 | 3 | 2020-04-03 | 0.70833 | 128 | 14 | 2020-04-03 | 0.70833
59 | Chandpur | 132 | 142 | 3 | 2020-04-03 | 18:30 | 120 | 1 | 2020-04-03 | 0.79167
60 | Feni | 132 | 138 | 3 | 2020-04-03 | 0.79167 | 121 | 9 | 2020-04-03 | 0.625
61 | Chowmuhani | 132 | 135 | 3 | 2020-04-03 | 0.75 | 113 | 13 | 2020-04-03 | 0.625
62 | Ashuganj | 132 | 144 | 15 | 2020-04-03 | 0.625 | 132 | 9 | 2020-04-03 | 0.95833
63 | Daudkandi | 132 | 139 | 11 | 2020-04-03 | 0.875 | 124 | 16 | 2020-04-03 | 0.875
64 | Brahminbaria | 132 | 142 | 11 | 2020-04-03 | 0.875 | 126 | 9 | 2020-04-03 | 0.95833
65 | Ramganj | 132 | 137 | 11 | 2020-04-03 | 0.95833 | 108 | 10 | 2020-04-03 | 0.625
66 | Chaddagram | 132 | 139 | 3 | 2020-04-03 | 0.75 | 122 | 9 | 2020-04-03 | 0.625
67 | PHP | 132 | 136 | 3 | 2020-04-03 | 0.75 | 119 | 14 | 2020-04-03 | 0.625
68 | Madanhat | 132 | 138 | 21 | 2020-04-03 | 0.77083 | 126 | 7 | 2020-04-03 | 0.125
69 | Hathazari | 132 | 135 | 19 | 2020-04-03 | 0.125 | 103 | 18 | 2020-04-03 | 0.29167
70 | Khulshi | 132 | 133 | 21 | 2020-04-03 | 0.5 | 120 | 7 | 2020-04-03 | 0.125
71 | Halishahar | 132 | 135 | 7 | 2020-04-03 | 0.79167 | 120 | 7 | 2020-04-03 | 0.125
72 | Baraulia | 132 | 135 | 19 | 2020-04-03 | 0.041667 | 123 | 29 | 2020-04-03 | 0.45833
73 | Sikalbaha | 132 | 134 | 19 | 2020-04-03 | 0.041667 | 123 | 29 | 2020-04-03 | 0.45833
74 | Dohazari | 132 | 135 | 21 | 2020-04-03 | 0.5 | 118 | 23 | 2020-04-03 | 0.77083
75 | Cox'sbazar | 132 | 132 | 7 | 2020-04-03 | 0.16667 | 110 | 23 | 2020-04-03 | 0.77083
76 | Chandraghona | 132 | 136 | 19 | 2020-04-03 | 0.041667 | 122 | 7 | 2020-04-03 | 0.125
77 | Kaptai | 132 | 134 | 17 | 2020-04-03 | 0.54167 | 125 | 8 | 2020-04-03 | 0.77083
78 | A. Khaer Stl. | 132 | 132 | 8 | 2020-04-03 | 0.79167 | 123 | 7 | 2020-04-03 | 0.125
79 | Bakulia | 132 | 134 | 7 | 2020-04-03 | 0.79167 | 119 | 2 | 2020-04-03 | 0.66667
80 | Julda | 132 | 134 | 7 | 2020-04-03 | 0.77083 | 119 | 7 | 2020-04-03 | 0.125
81 | TK Chemical | 132 | 135 | 7 | 2020-04-03 | 0.79167 | 123 | 23 | 2020-04-03 | 0.77083
82 | Modern Steel | 132 | 136 | 21 | 2020-04-03 | 0.5 | 120 | 7 | 2020-04-03 | 0.125
83 | Shahmirpur | 132 | 134 | 7 | 2020-04-03 | 0.77083 | 116 | 5 | 2020-04-03 | 0.5
84 | Khagrachhari | 132 | 136 | 19 | 2020-04-03 | 0.041667 | 122 | 7 | 2020-04-03 | 0.125
85 | Matarbari | 132 | 133 | 26 | 2020-04-03 | 0.29167 | 111 | 11 | 2020-04-03 | 21:00
86 | Baroiar Hat | 132 | 137 | 19 | 2020-04-03 | 0.25 | 121 | 1 | 2020-04-03 | 0.625
87 | Rangamati | 132 | 136 | 21 | 2020-04-03 | 0.5 | 123 | 7 | 2020-04-03 | 0.16667
88 | Goalpara | 132 | 145 | 21 | 2020-04-03 | 0.375 | 122 | 10 | 2020-04-03 | 14:00
89 | Khulna Central | 132 | 144 | 21 | 2020-04-03 | 0.375 | 120 | 20 | 2020-04-03 | 14:00
90 | Noapara | 132 | 142 | 21 | 2020-04-03 | 0.375 | 118 | 18 | 2020-04-03 | 13:00
91 | Jessore | 132 | 137 | 21 | 2020-04-03 | 0.375 | 112 | 14 | 2020-04-03 | 0.77083
92 | Benapol | 132 | 139 | 30 | 2020-04-03 | 0.20833 | 113 | 20 | 2020-04-03 | 0.58333
93 | Jhenida | 132 | 138 | 11 | 2020-04-03 | 0.8125 | 109 | 13 | 2020-04-03 | 0.79167
94 | Bottail | 132 | 140 | 11 | 2020-04-03 | 0.8125 | 122 | 13 | 2020-04-03 | 0.79167
95 | G.K Project | 132 | 143 | 11 | 2020-04-03 | 0.8125 | 133 | 1 | 2020-04-03 | 0.79167
96 | Faridpur | 132 | 141 | 11 | 2020-04-03 | 0.83333 | 123 | 4 | 2020-04-03 | 0.5
97 | Madaripur | 132 | 143 | 23 | 2020-04-03 | 0.70833 | 126 | 4 | 2020-04-03 | 0.5
98 | Sariatpur | 132 | 143 | 11 | 2020-04-03 | 0.875 | 123 | 19 | 2020-04-03 | 0.79167
99 | Gopalganj | 132 | 147 | 11 | 2020-04-03 | 0.83333 | 124 | 14 | 2020-04-03 | 0.79167
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Bagerhat | 132 | 152 | 21 | 2020-04-03 | 0.375 | 115 | 11 | 2020-04-03 | 0.77083
101 | Mongla | 132 | 150 | 21 | 2020-04-03 | 0.375 | 114 | 20 | 2020-04-03 | 0.58333
102 | Satkhira | 132 | 147 | 21 | 2020-04-03 | 0.375 | 118 | 20 | 2020-04-03 | 0.5
103 | Gallamari | 132 | 145 | 21 | 2020-04-03 | 0.375 | 121 | 20 | 2020-04-03 | 0.5
104 | Magura | 132 | 140 | 21 | 2020-04-03 | 0.375 | 108 | 14 | 2020-04-03 | 0.83333
105 | Norail | 132 | 137 | 21 | 2020-04-03 | 0.375 | 103 | 13 | 2020-04-03 | 0.79167
106 | Chuadanga | 132 | 138 | 11 | 2020-04-03 | 0.8125 | 99 | 13 | 2020-04-03 | 0.79167
107 | Barisal(N) | 132 | 144 | 23 | 2020-04-03 | 0.70833 | 125 | 14 | 2020-04-03 | 0.8125
108 | Barisal(S) | 132 | 142 | 3 | 2020-04-03 | 0.77083 | 123 | 14 | 2020-04-03 | 0.83333
109 | Patuakhali | 132 | 141 | 23 | 2020-04-03 | 0.70833 | 117 | 14 | 2020-04-03 | 0.875
110 | Bhandaria | 132 | 142 | 23 | 2020-04-03 | 0.70833 | 116 | 11 | 2020-04-03 | 0.79167
111 | Ishurdi | 132 | 140 | 25 | 2020-04-03 | 0.25 | 128 | 5 | 2020-04-03 | 0.79167
112 | Ruppur paromanobik | 132 | 140 | 21 | 2020-04-03 | 0.375 | 128 | 1 | 2020-04-03 | 0.79167
113 | Natore | 132 | 143 | 20 | 2020-04-03 | 0.125 | 119 | 13 | 2020-04-03 | 0.5
114 | Bogra | 132 | 143 | 20 | 2020-04-03 | 0.125 | 121 | 10 | 2020-04-03 | 18:30
115 | Noagaon | 132 | 143 | 20 | 2020-04-03 | 0.125 | 111 | 10 | 2020-04-03 | 0.8125
116 | Rajshahi | 132 | 142 | 20 | 2020-04-03 | 0.125 | 115 | 13 | 2020-04-03 | 0.5
117 | Rajshahi New | 132 | 140 | 20 | 2020-04-03 | 0.16667 | 116 | 12 | 2020-04-03 | 0.58333
118 | C.Nawabganj | 132 | 140 | 20 | 2020-04-03 | 0.083333 | 110 | 13 | 2020-04-03 | 0.5
119 | Amnura | 132 | 140 | 20 | 2020-04-03 | 0.125 | 110 | 13 | 2020-04-03 | 0.5
120 | Pabna | 132 | 139 | 11 | 2020-04-03 | 0.75 | 125 | 7 | 2020-04-03 | 0.8125
121 | Shahjadpur | 132 | 145 | 20 | 2020-04-03 | 3:00 | 126 | 8 | 2020-04-03 | 20:00
122 | Serajganj | 132 | 147 | 20 | 2020-04-03 | 0.125 | 125 | 10 | 2020-04-03 | 18:30
123 | Niyamatpur | 132 | 145 | 20 | 2020-04-03 | 0.125 | 106 | 10 | 2020-04-03 | 0.8125
124 | Joypurhat | 132 | 145 | 20 | 2020-04-03 | 0.125 | 109 | 7 | 2020-04-03 | 0.79167
125 | Sherpur(Bogura) | 132 | 142 | 20 | 2020-04-03 | 0.125 | 119 | 10 | 2020-04-03 | 0.79167
126 | Mohastangor | 132 | 142 | 15 | 2020-04-03 | 0.41667 | 118 | 10 | 2020-04-03 | 0.79167
127 | Rangpur | 132 | 144 | 15 | 2020-04-03 | 0.41667 | 114 | 10 | 2020-04-03 | 0.79167
128 | Lalmonirhat | 132 | 140 | 15 | 2020-04-03 | 0.41667 | 109 | 10 | 2020-04-03 | 0.79167
129 | Saidpur | 132 | 144 | 15 | 2020-04-03 | 0.41667 | 112 | 8 | 2020-04-03 | 0.79167
130 | Purbasadipur | 132 | 139 | 15 | 2020-04-03 | 0.41667 | 104 | 10 | 2020-04-03 | 0.79167
131 | Thakurgaon | 132 | 144 | 15 | 2020-04-03 | 0.41667 | 104 | 7 | 2020-04-03 | 0.79167
132 | Palashbari | 132 | 142 | 15 | 2020-04-03 | 0.625 | 114 | 14 | 2020-04-03 | 0.5
133 | Barapukuria | 132 | 146 | 15 | 2020-04-03 | 0.41667 | 117 | 5 | 2020-04-03 | 0.77083
134 | Panchagar | 132 | 146 | 15 | 2020-04-03 | 0.41667 | 100 | 7 | 2020-04-03 | 0.79167
135 | Joldhaka | 132 | 145 | 15 | 2020-04-03 | 0.41667 | 107 | 10 | 2020-04-03 | 0.79167
136 | Kurigram | 132 | 144 | 15 | 2020-04-03 | 0.41667 | 109 | 14 | 2020-04-03 | 0.79167
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 120 | 290
Hasnabad | TR2 | 225 | 108 | 290 | 23.04.2020 | 14:00
| TR3 | 225 | 105 | 290
| TR1 | 225 | 145 | 400
Tongi | TR2 | 225 | 145 | 400 | 01.04.2020 | 21:00
| TR3 | 225 | 145 | 400
Haripur | TR1 | 225 | 107 | 275 | 06.04.2020 | 23:00
| TR3 | 225 | 107 | 275
| TR1 | 225 | 125 | 340
Rampura | TR2 | 225 | 125 | 340 | 14.04.2020 | 22:00
| TR3 | 225 | 125 | 340
| TR1 | 225 | 85 | 235
Aminbazar | TR2 | 225 | 85 | 235 | 07.04.2020 | 22:00
| TR3 | 225 | 88 | 245
Maniknagar | TR1 | 300 | 75 | 210 | 11.04.2020 | 19:30
| TR2 | 300 | 75 | 210
Cumilla (N) | TR1 | 225 | 207 | 590 | 11.04.2020 | 19:30
| TR2 | 225 | 207 | 588
Fenchuganj | TR1 | 300 | 136 | 330 | 08.04.2020 | 11':00
| MT1 | 150 | 100 | 285
Hathazari | MT2 | 150 | 100 | 285 | 11.04.2020 | 19:00
| MT3 | 150 | 100 | 285
| MT4 | 150 | 100 | 285
| TR1 | 225 | 140 | 330
Ishurdi | TR2 | 225 | 140 | 330 | 18.04.2020 | 22:00
| TR3 | 225 | 140 | 330
Khulna(S) | TR1 | 225 | 119 | 352
| TR2 | 225 | 119 | 352 | 18.04.2020 | 24:00
| TR3 | 300 | 155 | 446
Bogra | TR1 | 225 | 154 | 464 | 10.04.2020 | 20:00
| TR2 | 225 | 154 | 464
| TR3 | 225 | 209 | 618
Baghabari | TR1 | 300 | 110 | 300 | 10.04.2020 | 9:00
| TR2 | 225 | 80 | 220
Barapukuria | TR1 | 225 | 154 | 750 | 01.04.2020 | 19:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 155 | 760 |  |  | 132 kV current is being provided
| TR6 | 300 | 200 | 981
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:March' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 155.6 | 287 | 15.04.2020 | 23:30
| TR2(400/230 kV) | 520 | 155.6 | 287
| TR1(400/132 kV) | 325 | 196.1 | 328 | 27.04.2020 | 20:30
| TR2(400/132 kV) | 325 | 196.1 | 328
Bibiyana | ICT1(400/230 kV) | 520 | 123 | 327 | 02.04.2020 | 11:00
| ICT2(400/230kV) | 520 | 122 | 328
Bhulta | ATR1(400/230 kV) | 520 | 186 | 321 | 15.04.2020 | 22:00
| ATR2(400/230kV) | 520 | 186 | 321
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-04-20 | 10113 | 10113 | - | - | - | - | - | - | - | - | - | - | - | - | 01-04-20 | 7793.1 | 7793.1 | - | - | - | - | - | - | - | - | - | - | - | -
02-04-20 | 8815 | 8815 | - | - | - | - | - | - | - | - | - | - | - | - | 02-04-20 | 8326.56 | 8326.56 | - | - | - | - | - | - | - | - | - | - | - | -
03-04-20 | 8734 | 8734 | - | - | - | - | - | - | - | - | - | - | - | - | 03-04-20 | 7822.2 | 7822.2 | - | - | - | - | - | - | - | - | - | - | - | -
04-04-20 | 9828 | 9828 | - | - | - | - | - | - | - | - | - | - | - | - | 04-04-20 | 7905.3 | 7905.3 | - | - | - | - | - | - | - | - | - | - | - | -
05-04-20 | 9454 | 9454 | - | - | - | - | - | - | - | - | - | - | - | - | 05-04-20 | 8389.7 | 8389.7 | - | - | - | - | - | - | - | - | - | - | - | -
06-04-20 | 10009 | 10009 | - | - | - | - | - | - | - | - | - | - | - | - | 06-04-20 | 8234 | 8234 | - | - | - | - | - | - | - | - | - | - | - | -
07-04-20 | 10308 | 10308 | - | - | - | - | - | - | - | - | - | - | - | - | 07-04-20 | 8287.4 | 8287.4 | - | - | - | - | - | - | - | - | - | - | - | -
08-04-20 | 10158 | 10158 | - | - | - | - | - | - | - | - | - | - | - | - | 08-04-20 | 7941.2 | 7941.2 | - | - | - | - | - | - | - | - | - | - | - | -
09-04-20 | 10019 | 10019 | - | - | - | - | - | - | - | - | - | - | - | - | 09-04-20 | 8034.3 | 8034.3 | - | - | - | - | - | - | - | - | - | - | - | -
10-04-20 | 10095 | 10095 | - | - | - | - | - | - | - | - | - | - | - | - | 10-04-20 | 7632 | 7632 | - | - | - | - | - | - | - | - | - | - | - | -
11-04-20 | 7375 | 7375 | - | - | - | - | - | - | - | - | - | - | - | - | 11-04-20 | 8127.36 | 8127.36 | - | - | - | - | - | - | - | - | - | - | - | -
12-04-20 | 8865 | 8865 | - | - | - | - | - | - | - | - | - | - | - | - | 12-04-20 | 6074.8 | 6074.8 | - | - | - | - | - | - | - | - | - | - | - | -
13-04-20 | 9967 | 9967 | - | - | - | - | - | - | - | - | - | - | - | - | 13-04-20 | 7472 | 7472 | - | - | - | - | - | - | - | - | - | - | - | -
14-04-20 | 10344 | 10344 | - | - | - | - | - | - | - | - | - | - | - | - | 14-04-20 | 7847.1 | 7847.1 | - | - | - | - | - | - | - | - | - | - | - | -
15-04-20 | 7769 | 7769 | - | - | - | - | - | - | - | - | - | - | - | - | 15-04-20 | 7001.03 | 7001.03 | - | - | - | - | - | - | - | - | - | - | - | -
16-04-20 | 9358 | 9358 | - | - | - | - | - | - | - | - | - | - | - | - | 16-04-20 | 6516.4 | 6516.4 | - | - | - | - | - | - | - | - | - | - | - | -
17-04-20 | 8830 | 8830 | - | - | - | - | - | - | - | - | - | - | - | - | 17-04-20 | 5671.3 | 5671.3 | - | - | - | - | - | - | - | - | - | - | - | -
18-04-20 | 8804 | 8804 | - | - | - | - | - | - | - | - | - | - | - | - | 18-04-20 | 6605.4 | 6605.4 | - | - | - | - | - | - | - | - | - | - | - | -
19-04-20 | 9455 | 9455 | - | - | - | - | - | - | - | - | - | - | - | - | 19-04-20 | 6723.6 | 6723.6 | - | - | - | - | - | - | - | - | - | - | - | -
20-04-20 | 8635 | 8635 | - | - | - | - | - | - | - | - | - | - | - | - | 20-04-20 | 6400.6 | 6400.6 | - | - | - | - | - | - | - | - | - | - | - | -
21-04-20 | 8041 | 8041 | - | - | - | - | - | - | - | - | - | - | - | - | 21-04-20 | 5542.8 | 5542.8 | - | - | - | - | - | - | - | - | - | - | - | -
22-04-20 | 8461 | 8461 | - | - | - | - | - | - | - | - | - | - | - | - | 22-04-20 | 6136.6 | 6136.6 | - | - | - | - | - | - | - | - | - | - | - | -
23-04-20 | 7017 | 7017 | - | - | - | - | - | - | - | - | - | - | - | - | 23-04-20 | 6715.4 | 6715.4 | - | - | - | - | - | - | - | - | - | - | - | -
24-04-20 | 7189 | 7189 | - | - | - | - | - | - | - | - | - | - | - | - | 24-04-20 | 5768.6 | 5768.6 | - | - | - | - | - | - | - | - | - | - | - | -
25-04-20 | 7969 | 7969 | - | - | - | - | - | - | - | - | - | - | - | - | 25-04-20 | 6068.7 | 6068.7 | - | - | - | - | - | - | - | - | - | - | - | -
26-04-20 | 7256 | 7256 | - | - | - | - | - | - | - | - | - | - | - | - | 26-04-20 | 6076.5 | 6076.5 | - | - | - | - | - | - | - | - | - | - | - | -
27-04-20 | 8999 | 8999 | - | - | - | - | - | - | - | - | - | - | - | - | 27-04-20 | 6353.6 | 6353.6 | - | - | - | - | - | - | - | - | - | - | - | -
28-04-20 | 7640 | 7640 | - | - | - | - | - | - | - | - | - | - | - | - | 28-04-20 | 6279.8 | 6279.8 | - | - | - | - | - | - | - | - | - | - | - | -
29-04-20 | 8743 | 8743 | - | - | - | - | - | - | - | - | - | - | - | - | 29-04-20 | 6501.4 | 6501.4 | - | - | - | - | - | - | - | - | - | - | - | -
30-04-20 | 8658 | 8658 | - | - | - | - | - | - | - | - | - | - | - | - | 30-04-20 | 6706.8 | 6706.8 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10344 | 14/04/20 | 21:00
2 | Maximum Day Peak Genaration | MW | 8389.7 | 05/04/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 10344 | 14/04/20 | 21:00
4 | Minimum Generation | MW | 4292.2 | 25/04/20 | 6:00
5 | Average of the daily evening peak Genaration | MW | 8896.9333
6 | Average of the daily day peak Genaration | MW | 7031.8517
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5232.0891
12 | Total Generation by BPDB | MKWH | 3300.8626 | % of total Gen. | 63.09%
13 | Total Generation by IPP | MKWH | 1089.3401 | '' | 20.82%
14 | A) Total Generation by RPCL | MKWH | 134.1374 | '' | 2.564%
| B) Total Generation by REB | MKWH | 101.3435 | " | 1.937%
| C) Total Generation by RENTAL | MKWH | 202.4975 | " | 3.87%
| D) Total Imported from India (HVDC) | MKWH | 335.2814 | " | 6.408%
| E) Total Imported from Tripura, India (A.C) | MKWH | 68.6266 | " | 1.312%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3983.5017 | % of total Gen. | 76.14%
| B) Oil | MKWH | 397.8787 | '' | 7.605%
| C) Hydro | MKWH | 24.8805 | '' | 0.4755%
| D) Solar | MKWH | 5.7632 | '' | 0.1102%
| E) Coal | MKWH | 416.1569 | '' | 7.954%
| F) HVDC (Import from India) | MKWH | 335.2814 | '' | 6.408%
| G) A.C (Import from Tripura, India) | MKWH | 68.6266 | '' | 1.312%
16 | Maximun of the daily total Generation . | MKWH | 251.8769 | 14/04/2020
17 | Monthly Load factor | % | 70.2513
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 9060.2191
| A) Gas | M.Taka | 4464.2446
| B) Liquid fuel | M.Taka | 2581.658
| C) Coal | M.Taka | 2014.3165
| D) HVDC (Import from India) | M.Taka | 1709.9354
| E) Tripura(Import from India) | M.Taka | 514.6992
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 458.7345 | 07/04/2020
| A) Gas | M.Taka | 170.9531 | 05/04/2020
| B) Liquid fuel | M.Taka | 232.3216 | 07/04/2020
| C) Coal | M.Taka | 91.4589 | 14/04/2020
| D) HVDC (Import from India) | M.Taka | 69.3897 | 09-04-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.3533
| B) Excluding Hydro & Solar | Taka/KWHR | 2.3668
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 78.89 | 30/04/2020 | 06:00
b) | Actual | FT (MSL) | 82.2 | 30/04/2020 | 06:00
22 | Peak Genaration of April 2019 | MW | 12200 | 29/04/19 | 19:30
23 | Peak Demand of April 2019 | MW | 12200 | 29/04/19 | 19:30
24 | Maximum peak Generation recorded upto 30/04/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 30/04/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 30/04/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.