## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-08-30 | Friday
|  | Date (day): | 2019-08-30 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13292 | MW |  |  | (b) At Evening Peak Hour : |  | 14911 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-08-29 | 2019-08-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 184 | 184 | 209 | 209
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 330 | 380 | 350 | 350
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 | 78 |  | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 346 | 350 | 350 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 351 | 350 | 350
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 370 | 360 | 360 |  | 90 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 87 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 240 | 240 | 290 | 290 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 100 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 81 | 10 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 92 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 44 | 219 | 150 | 218
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 101 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 12 | 46 | 46 | 46 |  | 5 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 133 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 72 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 51 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 34 | 286 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 136 | 134 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 106 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 3100 | 3836 | 3870 | 4538 | 501 | 489
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 100 | 100 | 80 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 14 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 208 | 215 | 214 | 214
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 148 | 130 | 130 | 130
| Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 50 | 85
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 26 | 10 | 25
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 79 | 91 | 95 | 97 |  | 11 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.13 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 88 | 177 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 56 | 0 | 37 | 37
53 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 113 | 113
| Chattogram area Total |  |  |  |  | 2172 | 2112 | 1213.13 | 1367 | 1665.4 | 1773 | 160 | 109
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 215 | 225 | 225
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 345 | 360 | 360 |  |  | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 305 | 0 | 0 |  |  | Under S/D
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 30 | 33 | 33 |  | 12 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 53 | 55 | 55
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 35 | 8 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 50 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 133 | 127 | 140 | 140
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 70 | 200 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 154 | 184 | 141 | 183
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 2 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1572 | 1795 | 1653 | 1945 | 425 | 25
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 137 | 123 | 204 | 204
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 89 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 70 | 170 | 200 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 107 | 107 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 427.1 | 517 | 637.6 | 636 | 0 | 0
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 31 | 31 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 144 | 146 | 160 | 160 |  |  | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 46 | 48 | 50 | 50
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 67 | 63 | 63 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 76 | 77 | 77
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 46 | 45 | 45 |  | 5 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 98 | 69 | 110
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 45 | 46 | 47
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  |  | Under S/D
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1089 | 1172 | 1205 | 1267 | 0 | 5
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 907 | 909 | 909
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 0 | 42
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 75
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 300 | 380 | 410
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 90 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 36 | 81 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1348 | 1723 | 1929 | 2128 | 0 | 0
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 40 | 25 | 35
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 180 | 167 | 180 | 180
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 295 | 415 | 370 | 450 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60 | 11 |  | Gas Shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 40 | 50
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 42 | 50 | 50
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 47 | 47
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 198 | 205 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 207 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 370 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 35
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 7 | 16 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 23 | 94 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 939 | 1356 | 1561 | 1665 | 231 | 100
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 98
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 270 | 220 | 280 | 280
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 14 | 0 | 18
134 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 111 | 113 | 113 |  |  | On test
135 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 389 | 345 | 401 | 509 | 0 | 105
| Total |  |  |  |  | 19141 | 18618 | 10372.23 | 12526 | 13292 | 14911 | 1317 | 833
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9842.2741 | 11886 | 12612.8622 | 14149.1415
A. |  | 2019-08-29 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 12526 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9335.057 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12526 | MW
3 | Day peak Generation : |  |  | 10372.23 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11886 | MW
4 | Evening peak Generation : |  |  | 12526 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 270.4339 | MKWHr | By Solar | 0.2274 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 161.601 | MKWHr |  | By Oil: | 71.3928 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 6.5997 | MKWHr |  | By Hydro: | 4.921 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1317 | MW | Dhaka | 4230 | 4230 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 833 | MW | Chittagong | 1136 | 1136 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2150 | MW | Khulna | 1524 | 1524 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1360.45 | MMCFD |  |  | Rajshahi | 1301 | 1301 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 151079579.608 | ii) Oil : | Taka | 633850244.03 | Comilla | 1116 | 1116 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 27907899.98 | Total | Taka | 812837723.618 | Mymensingh | 958 | 958 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.982 | MKWHr. | Sylhet | 530 | 530 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -276 | MW (E to W) at | 21:00 | hrs | Barisal | 353 | 353 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -276 | MW at | 21:00 | hrs | Rangpur | 738 | 738 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.7° C |  |  | Total | 11886 | 11886 |  | 0
B. |  | 2019-08-30 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14911 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 2811 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 261.2366 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8870.9 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7695 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.9226 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.58 |  | (b) Today: | 105.41 |  | (c) Rule Curve: |  | 98.01
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-08-29
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 345 | 333 |  | 0 | 360 | 282 | 97 | 0 | 55 | 120 | 0 | 0 | 0 | 0 | 93 | 133 | 0 | 72 | 0 | 17 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 121 | 90 | 100 | 100 | 25 | 206 | 0 | 130 | 0 |  | 0 | 0 | 34 | 50 | 97 | 50 | 22 | 40 | 0 | 0 | 100 | 270 | 300 | 216 | 35 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 174 | 140 | 95 | 22 | 0 | 60 | 30 | 49 | 49 | 130 | 147 | 67 | 75 | 44 | 68 | 18 | 46 | 10 | 285 | 24 | 11 | 0 | 243 | 0 | 0 | 192 | 0 | 135 | 0 | 100 | 199 | 100 | 0 | 115 | 106 | 0 | 0 | 107 | 56 | 0 |  | 907 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 19 | 50 | 40 | 179 | 38 | 110 | 0 | 0 | 55 | 50 | 25 | 94 | 12 | 42 | 44 | 52 | 21 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 15 | 189 | 0 | 0 | 0 | 98 | 50 | 189 | 0 | 330 | 89 | 0 | 113 | 104 | 114 | 0 | 0 |  | 8182 | 3770 | 11952 | 4407 | 907 | 2055 | 3374 | 339 | 211 | 485 | 174 | 0 | 0 | 105.6
2:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 345 | 333 |  | 0 | 360 | 280 | 100 | 0 | 30 | 120 | 0 | 0 | 0 | 0 | 90 | 133 | 0 | 72 | 0 | 12 | 53 | 55 | 35 | 19 | 25 | 24 | 33 | 33 | 52 | 0 | 118 | 90 | 100 | 100 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 97 | 50 | 22 | 40 | 0 | 0 | 100 | 270 | 300 | 216 | 35 | 132 | 30 | 55 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 164 | 154 | 95 | 22 | 0 | 60 | 30 | 50 | 49 | 130 | 145 | 67 | 76 | 45 | 68 | 18 | 46 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 135 | 0 | 100 | 199 | 100 | 0 | 115 | 106 | 0 | 0 | 107 | 56 | 0 |  | 907 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 19 | 2 | 24 | 179 | 38 | 110 | 0 | 0 | 55 | 42 | 25 | 94 | 12 | 42 | 0 | 52 | 21 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 15 | 180 | 0 | 0 | 0 | 97 | 0 | 188 | 0 | 330 | 89 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7826 | 3561 | 11387 | 4404 | 907 | 2053 | 2961 | 339 | 208 | 351 | 164 | 0 | 0 | 105.6
3:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 349 | 334 |  | 0 | 360 | 278 | 45 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 50 | 133 | 0 | 72 | 0 | 12 | 53 | 55 | 35 | 19 | 25 | 24 | 33 | 33 | 52 | 0 | 118 | 90 | 100 | 100 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 92 | 50 | 22 | 40 | 0 | 0 | 100 | 325 | 300 | 215 | 35 | 132 | 30 | 55 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 160 | 155 | 95 | 22 | 0 | 60 | 30 | 50 | 49 | 130 | 146 | 67 | 76 | 45 | 68 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 80 | 0 | 100 | 199 | 100 | 0 | 115 | 106 | 0 | 0 | 107 | 56 | 0 |  | 907 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 179 | 38 | 110 | 0 | 0 | 55 | 42 | 16 | 94 | 12 | 42 | 0 | 52 | 21 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 15 | 188 | 0 | 0 | 0 | 98 | 0 | 195 | 0 | 330 | 89 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7716 | 3547 | 11263 | 4479 | 907 | 2075 | 2774 | 339 | 208 | 321 | 160 | 0 | 0 | 105.59
4:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 349 | 334 |  | 0 | 360 | 284 | 7 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 7 | 110 | 0 | 72 | 0 | 12 | 53 | 55 | 17 | 19 | 25 | 24 | 33 | 33 | 52 | 0 | 118 | 90 | 100 | 100 | 25 | 207 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 97 | 50 | 22 | 40 | 0 | 0 | 100 | 330 | 305 | 216 | 35 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 160 | 155 | 89 | 22 | 0 | 60 | 30 | 50 | 49 | 130 | 146 | 67 | 76 | 45 | 69 | 18 | 46 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 18 | 0 | 100 | 199 | 100 | 0 | 115 | 106 | 0 | 0 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 180 | 38 | 80 | 0 | 0 | 55 | 42 | 0 | 94 | 12 | 25 | 0 | 52 | 21 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 0 | 189 | 0 | 0 | 0 | 95 | 0 | 195 | 0 | 330 | 89 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7542 | 3468 | 11010 | 4496 | 907 | 2081 | 2552 | 339 | 208 | 267 | 160 | 0 | 0 | 105.59
5:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 357 | 334 |  | 0 | 360 | 288 | 7 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 7 | 84 | 0 | 72 | 0 | 13 | 53 | 55 | 17 | 19 | 25 | 24 | 33 | 33 | 52 | 0 | 121 | 90 | 100 | 100 | 25 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 97 | 48 | 22 | 40 | 0 | 0 | 100 | 220 | 295 | 217 | 35 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 142 | 155 | 90 | 22 | 0 | 60 | 30 | 50 | 49 | 130 | 145 | 67 | 76 | 45 | 69 | 18 | 46 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 100 | 199 | 100 | 0 | 115 | 106 | 0 | 0 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 179 | 30 | 80 | 0 | 0 | 55 | 42 | 0 | 94 | 12 | 25 | 0 | 52 | 21 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 0 | 194 | 0 | 0 | 0 | 95 | 0 | 201 | 0 | 330 | 90 | 0 | 113 | 104 | 114 | 0 | 0 |  | 7354 | 3471 | 10825 | 4393 | 907 | 2073 | 2519 | 339 | 211 | 241 | 142 | 0 | 0 | 105.58
6:00 | 70 | 183 | 0 | 110 | 280 | 0 | 0 | 348 | 303 |  | 0 | 360 | 252 | 7 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 72 | 0 | 12 | 35 | 55 | 17 | 19 | 25 | 24 | 33 | 33 | 34 | 0 | 125 | 90 | 100 | 100 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 12 | 46 | 22 | 40 | 0 | 0 | 100 | 220 | 300 | 179 | 35 | 126 | 30 | 55 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 140 | 157 | 66 | 22 | 0 | 60 | 30 | 50 | 49 | 100 | 144 | 67 | 76 | 45 | 69 | 18 | 47 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 100 | 185 | 50 | 0 | 115 | 106 | 0 | 0.122 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 94 | 12 | 25 | 0 | 16 | 0 | 22 | 14 | 11 | 69 | 0 | 270 | 0 | 0 | 188 | 0 | 0 | 0 | 93 | 0 | 191 | 0 | 300 | 70 | 0 | 113 | 104 | 114 | 0 | 0 |  | 6721.122 | 3190 | 9911.122 | 4301 | 907 | 1948 | 1917 | 339 | 215 | 144 | 140 | 0.122 | 0 | 105.58
7:00 | 70 | 184 | 0 | 110 | 280 | 0 | 0 | 352 | 304 |  | 0 | 360 | 270 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 35 | 0 | 0 | 19 | 25 | 24 | 33 | 33 | 34 | 0 | 125 | 90 | 100 | 100 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 46 | 22 | 37 | 0 | 0 | 100 | 220 | 300 | 188 | 35 | 132 | 30 | 55 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 33 | 8 | 134 | 155 | 75 | 22 | 0.3 | 58 | 30 | 50 | 49 | 100 | 144 | 67 | 75 | 45 | 70 | 18 | 46 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 100 | 50 | 50 | 0 | 115 | 106 | 0 | 0.757 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 270 | 0 | 0 | 166 | 0 | 0 | 0 | 96 | 0 | 198 | 0 | 300 | 53 | 0 | 113 | 70 | 114 | 0 | 0 |  | 6443.057 | 2892 | 9335.057 | 4291 | 907 | 1957 | 1532 | 270 | 215 | 23 | 134 | 6.057 | 0 | 105.57
8:00 | 70 | 184 | 0 | 110 | 280 | 0 | 0 | 345 | 283 |  | 0 | 360 | 250 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 12 | 35 | 0 | 0 | 19 | 25 | 24 | 33 | 33 | 34 | 0 | 125 | 90 | 100 | 100 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 46 | 22 | 13 | 0 | 0 | 100 | 295 | 265 | 180 | 35 | 132 | 27 | 54 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 8 | 138 | 155 | 90 | 22 | 0.3 | 58 | 30 | 47 | 49 | 100 | 146 | 67 | 40 | 45 | 67 | 18 | 46 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 58 | 10 | 100 | 50 | 50 | 0 | 115 | 105 | 0 | 3 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 270 | 0 | 0 | 189 | 0 | 0 | 0 | 95 | 0 | 172 | 0 | 300 | 53 | 0 | 113 | 69 | 114 | 0 | 2 |  | 6463.3 | 2876 | 9339.3 | 4294 | 907 | 1860 | 1617 | 270 | 215 | 23 | 138 | 15.3 | 0 | 105.57
9:00 | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 361 | 282 |  | 0 | 360 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 72 | 0 | 12 | 35 | 17 | 17 | 19 | 25 | 24 | 33 | 33 | 34 | 0 | 125 | 90 | 100 | 100 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 46 | 22 | 5 | 0 | 0 | 100 | 265 | 275 | 193 | 35 | 132 | 30 | 54 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 0 | 138 | 153 | 89 | 22 | 0.5 | 60 | 30 | 47 | 46 | 130 | 146 | 65 | 40 | 44 | 77 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 58 | 0 | 90 | 15 | 100 | 50 | 50 | 0 | 115 | 105 | 0 | 5.57 | 88 | 56 | 0 |  | 907 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 15 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 0 | 270 | 0 | 0 | 198 | 0 | 0 | 0 | 94 | 0 | 167 | 0 | 300 | 70 | 0 | 113 | 35 | 114 | 0 | 3.7 |  | 6577.07 | 2847.7 | 9424.77 | 4250 | 907 | 1880 | 1717 | 270 | 215 | 23 | 138 | 24.77 | 0 | 105.56
10:00 | 70 | 183 | 0 | 110 | 330 | 0 | 0 | 371 | 302 |  | 0 | 360 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 72 | 0 | 12 | 35 | 17 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 100 | 100 | 0 | 207 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 10 | 46 | 22 | 5 | 0 | 0 | 100 | 300 | 300 | 197 | 35 | 132 | 30 | 52 | 0 | 43 | 0 | 0 | 0 | 19 | 5 | 33 | 0 | 144 | 152 | 90 | 22 | 2 | 60 | 30 | 47 | 45 | 130 | 145 | 65 | 70 | 43 | 76 | 18 | 44 | 10 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 131 | 17 | 100 | 50 | 56 | 0 | 107 | 105 | 0 | 2.65 | 88 | 56 | 0 |  | 907 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 203 | 0 | 0 | 0 | 91 | 0 | 184 | 0 | 300 | 70 | 0 | 113 | 35 | 114 | 0 | 2.6 |  | 6820.65 | 2934.6 | 9755.25 | 4400 | 907 | 1945 | 1811 | 270 | 215 | 39 | 144 | 24.25 | 0 | 105.56
11:00 | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 355 | 343 |  | 0 | 320 | 240 | 18 | 0 | 0 | 48 | 0 | 0 | 0 | 22 | 40 | 16 | 29 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 100 | 100 | 0 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 10 | 50 | 46 | 22 | 2 | 0 | 0 | 100 | 325 | 260 | 183 | 35 | 130 | 30 | 53 | 0 | 43 | 0 | 0 | 2 | 19 | 5 | 33 | 20 | 144 | 138 | 90 | 22 | 2.5 | 60 | 20 | 47 | 46 | 100 | 145 | 65 | 70 | 43 | 67 | 18 | 43 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 70 | 0 | 136 | 20 | 100 | 105 | 50 | 0 | 107 | 105 | 0 | 3.17 | 106 | 56 | 0 |  | 907 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 202 | 0 | 0 | 0 | 94 | 0 | 203 | 0 | 300 | 70 | 0 | 113 | 35 | 113 | 0 | 3.8 |  | 6997.67 | 3013.8 | 10011.47 | 4428 | 907 | 1910 | 2069 | 270 | 215 | 39 | 144 | 29.47 | 0 | 105.56
12:00 | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 360 | 345 |  | 0 | 320 | 240 | 87 | 0 | 55 | 44 | 0 | 0 | 0 | 92 | 84 | 16 | 81 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 118 | 90 | 100 | 100 | 14 | 217 | 0 | 148 | 0 |  | 0 | 0 | 0 | 10 | 79 | 46 | 21 | 4 | 0 | 0 | 100 | 345 | 320 | 200 | 35 | 133 | 30 | 53 | 0 | 43 | 0 | 0 | 2 | 19 | 5 | 33 | 20 | 154 | 137 | 89 | 22 | 2.1 | 60 | 31 | 44 | 46 | 100 | 144 | 65 | 72 | 43 | 78 | 18 | 43 | 10 | 300 | 24 | 11 | 0 | 34 | 0 | 0 | 70 | 0 | 136 | 20 | 100 | 70 | 10 | 0 | 107 | 105 | 0 | 2.13 | 88 | 56 | 0 |  | 907 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 21 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 198 | 0 | 0 | 0 | 92 | 0 | 177 | 0 | 300 | 70 | 0 | 113 | 36 | 113 | 0 | 6 |  | 7401.23 | 2971 | 10372.23 | 4504 | 907 | 1901 | 2359 | 270 | 208 | 39 | 154 | 30.23 | 0 | 105.55
13:00 | 70 | 183 | 0 | 110 | 330 | 0 | 0 | 371 | 342 |  | 0 | 320 | 240 | 86 | 0 | 55 | 38 | 0 | 0 | 0 | 94 | 92 | 32 | 100 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 118 | 90 | 95 | 120 | 24 | 205 | 0 | 150 | 0 |  | 0 | 0 | 0 | 40 | 84 | 46 | 21 | 2 | 0 | 0 | 100 | 335 | 310 | 182 | 35 | 133 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 156 | 137 | 89 | 22 | 0.9 | 60 | 30 | 47 | 48 | 100 | 146 | 65 | 73 | 43 | 68 | 18 | 42 | 10 | 320 | 24 | 11 | 0 | 45 | 0 | 0 | 80 | 0 | 135 | 20 | 100 | 85 | 10 | 0 | 106 | 89 | 0 | 4.94 | 88 | 56 | 0 |  | 907 | 0 | 300 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 40 | 169 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 8 | 0 | 21 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 201 | 0 | 0 | 0 | 93 | 0 | 180 | 0 | 350 | 70 | 0 | 113 | 36 | 106 | 0 | 7 |  | 7505.84 | 3099 | 10604.84 | 4497 | 907 | 1975 | 2504 | 270 | 208 | 55 | 156 | 32.84 | 0 | 105.55
14:00 | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 350 | 320 |  | 0 | 320 | 240 | 95 | 0 | 55 | 38 | 0 | 0 | 0 | 90 | 101 | 32 | 100 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 46 | 0 | 118 | 90 | 95 | 120 | 24 | 205 | 0 | 120 | 0 |  | 0 | 0 | 0 | 50 | 86 | 48 | 21 | 7 | 0 | 0 | 100 | 300 | 280 | 180 | 35 | 131 | 27 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 162 | 122 | 82 | 22 | 0.2 | 60 | 31 | 47 | 46 | 100 | 146 | 65 | 75 | 43 | 78 | 18 | 42 | 10 | 290 | 24 | 11 | 0 | 102 | 0 | 0 | 90 | 0 | 133 | 20 | 100 | 140 | 10 | 0 | 107 | 89 | 0 | 5 | 88 | 56 | 0 |  | 907 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 172 | 26 | 16 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 8 | 0 | 21 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 202 | 0 | 0 | 0 | 92 | 0 | 171 | 0 | 300 | 90 | 0 | 113 | 36 | 107 | 0 | 6.5 |  | 7480.2 | 3073.5 | 10553.7 | 4366 | 907 | 1874 | 2680 | 270 | 208 | 55 | 162 | 31.7 | 0 | 105.55
15:00 | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 375 | 342 |  | 0 | 320 | 240 | 98 | 0 | 55 | 34 | 0 | 0 | 0 | 91 | 101 | 32 | 100 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 117 | 90 | 95 | 120 | 24 | 208 | 0 | 135 | 0 |  | 0 | 0 | 0 | 50 | 91 | 50 | 19 | 2 | 0 | 0 | 100 | 350 | 310 | 200 | 35 | 132 | 27 | 48 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 168 | 120 | 90 | 22 | 1.2 | 58 | 31 | 47 | 46 | 163 | 155 | 65 | 76 | 45 | 83 | 18 | 42 | 10 | 315 | 24 | 11 | 0 | 145 | 0 | 0 | 90 | 0 | 95 | 16 | 100 | 140 | 10 | 0 | 107 | 106 | 0 | 0.5 | 92 | 56 | 0 |  | 907 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 26 | 16 | 0 | 0 | 50 | 0 | 0 | 23 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 8 | 0 | 0 | 260 | 0 | 0 | 203 | 0 | 0 | 0 | 93 | 0 | 195 | 0 | 360 | 90 | 0 | 113 | 35 | 107 | 0 | 5.8 |  | 7731.7 | 3168.8 | 10900.5 | 4542 | 907 | 2042 | 2696 | 260 | 207 | 55 | 168 | 23.5 | 0 | 105.54
16:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 365 | 340 |  | 0 | 320 | 280 | 75 | 0 | 55 | 33 | 0 | 0 | 0 | 85 | 101 | 100 | 50 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 117 | 90 | 95 | 120 | 24 | 204 | 0 | 145 | 0 |  | 0 | 0 | 0 | 50 | 91 | 50 | 19 | 4 | 0 | 0 | 100 | 325 | 280 | 181 | 35 | 132 | 27 | 49 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 170 | 120 | 90 | 22 | 1.1 | 60 | 31 | 47 | 49 | 130 | 147 | 65 | 74 | 46 | 67 | 18 | 43 | 10 | 310 | 24 | 11 | 0 | 180 | 0 | 0 | 90 | 0 | 0 | 2.29 | 100 | 178 | 50 | 0 | 107 | 106 | 0 | 0.4 | 107 | 56 | 0 |  | 908 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 16 | 0 | 0 | 50 | 0 | 0 | 23 | 12 | 42 | 0 | 25 | 0 | 18 | 7 | 8 | 0 | 0 | 217 | 0 | 0 | 205 | 0 | 0 | 0 | 93 | 0 | 204 | 0 | 360 | 70 | 0 | 113 | 36 | 114 | 0 | 3.96 |  | 7616.79 | 3175.96 | 10792.75 | 4462 | 908 | 2003 | 2695 | 217 | 207 | 123 | 170 | 7.75 | 0 | 105.54
17:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 349 | 273 |  | 0 | 320 | 280 | 95 | 0 | 55 | 30 | 0 | 0 | 0 | 50 | 101 | 100 | 50 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 2 | 0 | 120 | 90 | 95 | 120 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 91 | 50 | 22 | 2 | 0 | 0 | 100 | 300 | 270 | 192 | 0 | 132 | 30 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 164 | 134 | 90 | 22 | 0.5 | 60 | 31 | 47 | 43 | 100 | 144 | 63 | 75 | 45 | 70 | 18 | 14 | 9 | 300 | 24 | 8 | 0 | 210 | 0 | 0 | 90 | 0 | 41 | 2.4 | 100 | 200 | 50 | 0 | 115 | 106 | 0 | 1.8 | 107 | 56 | 0 |  | 908 | 0 | 270 | 0 | 35 | 0 | 0 | 0 | 0 | 13 | 8 | 180 | 24 | 16 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 42 | 0 | 25 | 0 | 22 | 7 | 8 | 0 | 0 | 235 | 0 | 0 | 202 | 0 | 0 | 0 | 51 | 0 | 188 | 0 | 320 | 70 | 0 | 113 | 35 | 113 | 0 | 1.92 |  | 7416.7 | 2976.92 | 10393.62 | 4335 | 908 | 1745 | 2654 | 235 | 210 | 136 | 164 | 6.62 | 0 | 105.54
18:00 | 70 | 184 | 0 | 110 | 270 | 0 | 0 | 300 | 273 |  | 0 | 300 | 260 | 75 | 0 | 55 | 29 | 0 | 0 | 0 | 50 | 101 | 100 | 50 | 72 | 0 | 18 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 33 | 0 | 122 | 90 | 95 | 120 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 91 | 50 | 22 | 2 | 0 | 0 | 100 | 260 | 270 | 162 | 8 | 126 | 30 | 20 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 156 | 136 | 90 | 22 | 0 | 60 | 31 | 13 | 10 | 100 | 144 | 65 | 30 | 10 | 70 | 18 | 14 | 10 | 280 | 24 | 11 | 0 | 210 | 0 | 0 | 100 | 0 | 112 | 0 | 100 | 200 | 50 | 0 | 106 | 106 | 0 | 0 | 156 | 0 | 0 |  | 908 | 0 | 220 | 0 | 40 | 0 | 0 | 0 | 6 | 43 | 8 | 173 | 23 | 16 | 0 | 0 | 55 | 0 | 5 | 23 | 12 | 42 | 0 | 25 | 0 | 22 | 7 | 8 | 0 | 0 | 260 | 0 | 0 | 188 | 0 | 0 | 0 | 54 | 0 | 172 | 0 | 250 | 90 | 0 | 113 | 36 | 108 | 0 | 0 |  | 7079 | 2907 | 9986 | 4068 | 908 | 1469 | 2736 | 260 | 212 | 177 | 156 | 0 | 0 | 105.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 300 | 344 |  | 0 | 370 | 275 | 85 | 15 | 55 | 29 | 0 | 0 | 0 | 72 | 101 | 133 | 70 | 72 | 0 | 20 | 53 | 55 | 35 | 22 | 25 | 19 | 33 | 33 | 34 | 0 | 125 | 90 | 95 | 120 | 11 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 50 | 91 | 50 | 22 | 19 | 0 | 0 | 100 | 345 | 290 | 212 | 8 | 133 | 30 | 20 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 188 | 137 | 95 | 0 | 0 | 60 | 31 | 49 | 26 | 163 | 144 | 65 | 75 | 45 | 80 | 18 | 44 | 10 | 290 | 24 | 11 | 30 | 220 | 0 | 30 | 139 | 32 | 127 | 0 | 100 | 200 | 94 | 0 | 107 | 106 | 0 | 0 | 174 | 0 | 0 |  | 908 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 31 | 65 | 40 | 179 | 37 | 110 | 0 | 0 | 55 | 43 | 30 | 94 | 40 | 42 | 38 | 52 | 27 | 22 | 7 | 8 | 0 | 0 | 238 | 0 | 15 | 195 | 0 | 0 | 0 | 95 | 48 | 190 | 0 | 350 | 90 | 0 | 113 | 84 | 111 | 0 | 0 |  | 8209 | 3796 | 12005 | 4426 | 908 | 2017 | 3452 | 238 | 215 | 561 | 188 | 0 | 0 | 105.52
19:30 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 345 | 350 |  | 0 | 370 | 253 | 100 | 40 | 55 | 28 | 0 | 0 | 0 | 90 | 101 | 133 | 89 | 72 | 0 | 34 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 87 | 91 | 50 | 22 | 22 | 0 | 0 | 100 | 345 | 290 | 215 | 8 | 126 | 30 | 33 | 0 | 43 | 0 | 50 | 52 | 19 | 11 | 33 | 20 | 182 | 123 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 130 | 145 | 67 | 76 | 45 | 100 | 18 | 45 | 10 | 290 | 24 | 11 | 30 | 270 | 0 | 30 | 139 | 31 | 127 | 0 | 100 | 200 | 98 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 0 |  | 906 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 27 | 60 | 40 | 170 | 37 | 110 | 0 | 0 | 55 | 43 | 31 | 94 | 40 | 42 | 38 | 52 | 30 | 22 | 7 | 11 | 0 | 0 | 230 | 0 | 15 | 209 | 0 | 0 | 0 | 96 | 100 | 208 | 0 | 350 | 90 | 0 | 113 | 89 | 113 | 0 | 0 |  | 8555 | 3867 | 12422 | 4528 | 906 | 2032 | 3723 | 230 | 215 | 606 | 182 | 0 | 0 | 0
20:00 | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 345 | 350 |  | 0 | 370 | 253 | 100 | 70 | 55 | 29 | 0 | 0 | 0 | 100 | 101 | 133 | 87 | 72 | 0 | 39 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 100 | 91 | 50 | 19 | 25 | 0 | 0 | 100 | 345 | 290 | 215 | 8 | 126 | 30 | 54 | 0 | 43 | 0 | 50 | 52 | 19 | 11 | 33 | 20 | 188 | 125 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 130 | 145 | 67 | 76 | 46 | 98 | 18 | 45 | 10 | 280 | 24 | 11 | 30 | 288 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 200 | 50 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 17 |  | 907 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 31 | 60 | 40 | 169 | 38 | 110 | 0 | 0 | 55 | 43 | 31 | 94 | 40 | 42 | 39 | 52 | 27 | 22 | 7 | 11 | 0 | 0 | 230 | 0 | 14 | 200 | 0 | 0 | 0 | 96 | 100 | 208 | 0 | 350 | 90 | 0 | 113 | 92 | 111 | 0 | 0 |  | 8622 | 3841 | 12463 | 4496 | 907 | 2048 | 3772 | 230 | 215 | 607 | 188 | 0 | 0 | 105.51
21:00 | 70 | 184 | 0 | 110 | 380 | 0 | 0 | 346 | 351 |  | 0 | 370 | 240 | 100 | 100 | 55 | 219 | 0 | 0 | 0 | 100 | 101 | 133 | 10 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 91 | 50 | 22 | 26 | 0 | 0 | 100 | 345 | 305 | 215 | 8 | 127 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 184 | 123 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 163 | 146 | 67 | 76 | 46 | 98 | 18 | 45 | 10 | 290 | 24 | 0 | 0 | 286 | 0 | 0 | 170 | 0 | 134 | 0 | 100 | 200 | 50 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 17 |  | 907 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 30 | 60 | 40 | 167 | 40 | 110 | 0 | 0 | 55 | 43 | 31 | 94 | 40 | 42 | 37 | 52 | 27 | 22 | 7 | 11 | 0 | 0 | 220 | 0 | 14 | 205 | 0 | 0 | 0 | 98 | 100 | 207 | 0 | 370 | 90 | 0 | 113 | 81 | 111 | 0 | 0 |  | 8687 | 3839 | 12526 | 4756 | 907 | 2116 | 3574 | 220 | 215 | 554 | 184 | 0 | 0 | 105.5
22:00 | 70 | 184 | 0 | 110 | 380 | 0 | 0 | 347 | 350 |  | 0 | 370 | 278 | 100 | 15 | 15 | 218 | 0 | 0 | 0 | 7 | 102 | 133 | 10 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 91 | 50 | 22 | 26 | 0 | 0 | 100 | 345 | 305 | 215 | 8 | 132 | 30 | 52 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 188 | 124 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 163 | 147 | 65 | 76 | 46 | 96 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 210 | 0 | 0 | 150 | 0 | 131 | 0 | 100 | 199 | 50 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 17 |  | 907 | 0 | 330 | 0 | 115 | 0 | 0 | 0 | 30 | 60 | 40 | 179 | 40 | 110 | 0 | 0 | 55 | 42 | 31 | 94 | 40 | 42 | 37 | 52 | 20 | 22 | 7 | 11 | 0 | 0 | 220 | 0 | 14 | 207 | 0 | 0 | 0 | 96 | 100 | 208 | 0 | 370 | 90 | 0 | 113 | 105 | 111 | 0 | 0 |  | 8443 | 3898 | 12341 | 4815 | 907 | 2123 | 3327 | 220 | 215 | 546 | 188 | 0 | 0 | 105.49
23:00 | 70 | 184 | 0 | 110 | 380 | 0 | 0 | 344 | 350 |  | 0 | 370 | 274 | 100 | 15 | 15 | 219 | 0 | 0 | 0 | 7 | 102 | 133 | 10 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 124 | 90 | 95 | 120 | 25 | 212 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 91 | 50 | 22 | 31 | 0 | 0 | 100 | 345 | 305 | 215 | 8 | 128 | 30 | 53 | 0 | 43 | 0 | 0 | 14 | 19 | 11 | 33 | 20 | 188 | 126 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 163 | 145 | 67 | 77 | 45 | 88 | 17 | 46 | 10 | 300 | 24 | 11 | 0 | 210 | 0 | 0 | 150 | 0 | 132 | 0 | 100 | 199 | 50 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 17 |  | 907 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 30 | 54 | 40 | 176 | 37 | 110 | 0 | 0 | 55 | 43 | 24 | 92 | 40 | 42 | 36 | 52 | 21 | 22 | 7 | 11 | 0 | 0 | 219 | 0 | 14 | 200 | 0 | 0 | 0 | 97 | 100 | 208 | 0 | 416 | 90 | 0 | 113 | 105 | 111 | 0 | 0 |  | 8403 | 3947 | 12350 | 4830 | 907 | 2173 | 3287 | 219 | 214 | 532 | 188 | 0 | 0 | 105.48
24:00 | 70 | 194 | 0 | 110 | 380 | 0 | 0 | 341 | 353 |  | 0 | 370 | 273 | 100 | 15 | 15 | 220 | 0 | 0 | 0 | 7 | 102 | 133 | 10 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 52 | 0 | 124 | 90 | 95 | 120 | 25 | 205 | 0 | 130 | 0 |  | 0 | 0 | 85 | 10 | 91 | 50 | 22 | 39 | 0 | 0 | 100 | 345 | 305 | 215 | 8 | 129 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 184 | 140 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 163 | 144 | 67 | 77 | 46 | 88 | 17 | 46 | 10 | 300 | 24 | 11 | 0 | 212 | 0 | 0 | 150 | 0 | 132 | 0 | 100 | 199 | 50 | 0 | 107 | 106 | 0 | 0 | 180 | 0 | 17 |  | 907 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 30 | 54 | 40 | 180 | 33 | 110 | 0 | 0 | 55 | 43 | 24 | 92 | 40 | 42 | 36 | 52 | 22 | 22 | 7 | 11 | 0 | 0 | 220 | 0 | 14 | 201 | 0 | 0 | 0 | 95 | 100 | 201 | 0 | 421 | 90 | 0 | 113 | 105 | 111 | 0 | 0 |  | 8423 | 3946 | 12369 | 4843 | 907 | 2183 | 3285 | 220 | 214 | 533 | 184 | 0 | 0 | 105.47
KWH | 1575000 | 4683400 | 0 | 2614500 | 7521382 | 0 | 0 | 8528900 | 7766000 |  | 0 | 8407375 | 6462080 | 1521600 | 295824 | 721404 | 2273237 | 0 | 0 | 0 | 925440 | 1645776 | 1863840 | 935970 | 1718400 | 0 | 491424 | 1227960 | 1128349 | 760759 | 432180 | 600000 | 5423400 | 806900 | 785200 | 977424 | 0 | 2761004 | 2160000 | 2300000 | 2700000 | 395419 | 4912396 | 0 | 3150562 | 0 |  | 0 | 0 | 533246 | 617400 | 1814400 | 1177440 | 514320 | 503040 | 0 | 0 | 2394302 | 7725600 | 7239000 | 4852000 | 702545 | 3114230 | 663192 | 1229280 | 0 | 1028018 | 0 | 62984 | 583666 | 459936 | 223380 | 817600 | 449780 | 3922560 | 3250280 | 2200320 | 479412 | 10900 | 1418000 | 742500 | 1101600 | 1100736 | 3151669 | 3267000 | 1567680 | 1690560 | 1000440 | 1940820 | 430254 | 1021800 | 245520 | 7462200 | 567816 | 253056 | 44160 | 2782580 | 0 | 40565 | 3002400 | 37687 | 2240640 | 141885 | 2413440 | 3791520 | 1518836 | 0 | 2625600 | 2495784 | 0 | 31440 | 2792618 | 993595 | 80290 |  | 21769455 | 0 | 7257600 | 0 | 1553280 | 0 | 0 | 0 | 219840 | 447488 | 567000 | 4337914 | 683889 | 1303680 | 0 | 0 | 1310000 | 485280 | 224365 | 1356404 | 473580 | 813475 | 271982 | 670560 | 229040 | 503040 | 217872 | 227214 | 401454 | 0 | 6198200 | 0 | 131000 | 5022800 | 0 | 0 | 0 | 2199695 | 653760 | 4828473 | 0 | 7924545 | 1954560 | 0 | 2741184 | 1688400 | 2687040 | 0 | 43175 |  | 189036627 | 81397244 | 270433871 | 113661216 | 21769455 | 47939824 | 65567289 | 6599654 | 4921004 | 5825469 | 3922560 | 227400 | 0
Fuel Cost | 1764000 | 5058072 | 0 | 2928240 | 5565822.68 | 0 | 0 | 6140808 | 5902160 |  | 0 | 6725900 | 5815872 | 15520320 | 3203773.92 | 7401605.04 | 2818813.88 | 0 | 0 | 0 | 10272384 | 16721084.16 | 18470654.4 | 9808965.6 | 15637440 | 0 | 4599728.64 | 11776136.4 | 10764449.46 | 7577159.64 | 324135 | 450000 | 0 | 0 | 0 | 9363721.92 | 0 | 717861.04 | 561600 | 3519000 | 4131000 | 3799976.59 | 5158015.8 | 0 | 4001213.74 | 0 |  | 0 | 0 | 5593750.54 | 6353046 | 17254944 | 11020838.4 | 473174.4 | 1398451.2 | 0 | 0 | 2514017.1 | 5716944 | 6080760 | 4463840 | 688494.1 | 4141925.9 | 543817.44 | 1266158.4 | 0 | 1470065.74 | 0 | 738172.48 | 5486460.4 | 469134.72 | 167535 | 1545264 | 337335 | 27065664 | 2665229.6 | 20925043.2 | 489000.24 | 178760 | 1928480 | 1009800 | 1498176 | 1375920 | 3908069.56 | 3005640 | 2335843.2 | 2975385.6 | 1110488.4 | 2950046.4 | 684103.86 | 1195506 | 576972 | 5298162 | 425862 | 192322.56 | 743654.4 | 29133612.6 | 0 | 677435.5 | 28883088 | 629372.9 | 22608057.6 | 1637352.9 | 22493260.8 | 35564457.6 | 14231493.32 | 0 | 23026512 | 22237435.44 | 0 | 0 | 25747937.96 | 0 | 0 |  | 58777528.5 | 0 | 5660928 | 0 | 14973619.2 | 0 | 0 | 0 | 2550144 | 5862092.8 | 5607630 | 3470331.2 | 1060027.95 | 14001523.2 | 0 | 0 | 2462800 | 5406019.2 | 2748471.25 | 13428399.6 | 4911024.6 | 9525792.25 | 3277383.1 | 6678777.6 | 2256044 | 553344 | 359488.8 | 172000.998 | 2557261.98 | 0 | 25350638 | 0 | 3698130 | 4420064 | 0 | 0 | 0 | 3497515.05 | 11048544 | 4249056.24 | 0 | 5784917.85 | 18490137.6 | 0 | 25164069.12 | 15043644 | 25096953.6 | 0 | 0 |  | 593632188.37 | 308144301.688 | 901776490.058 | 104434376.958 | 58777528.5 | 46645202.65 | 569820982.66 | 27907899.98 | 1279461.04 | 64029261.37 | 27065664 | 1816112.9 | 0
Yesterday Day Peak | 70 | 184 | 0 | 110 | 330 | 0 | 0 | 360 | 345 |  | 0 | 320 | 240 | 87 | 0 | 55 | 44 | 0 | 0 | 0 | 92 | 84 | 16 | 81 | 72 | 0 | 12 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 118 | 90 | 100 | 100 | 14 | 217 | 0 | 148 | 0 |  | 0 | 0 | 0 | 10 | 79 | 46 | 21 | 4 | 0 | 0 | 100 | 345 | 320 | 200 | 35 | 133 | 30 | 53 | 0 | 43 | 0 | 0 | 2 | 19 | 5 | 33 | 20 | 154 | 137 | 89 | 22 | 2.1 | 60 | 31 | 44 | 46 | 100 | 144 | 65 | 72 | 43 | 78 | 18 | 43 | 10 | 300 | 24 | 11 | 0 | 34 | 0 | 0 | 70 | 0 | 136 | 20 | 100 | 70 | 10 | 0 | 107 | 105 | 0 | 2.13 | 88 | 56 | 0 |  | 907 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 180 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 23 | 12 | 25 | 0 | 0 | 0 | 21 | 7 | 8 | 0 | 0 | 270 | 0 | 0 | 198 | 0 | 0 | 0 | 92 | 0 | 177 | 0 | 300 | 70 | 0 | 113 | 36 | 113 | 0 | 6 |  | 10372.23 | DayPeak
Yesterday Evening Peak | 70 | 184 | 0 | 110 | 380 | 0 | 0 | 346 | 351 | 0 | 0 | 370 | 240 | 100 | 100 | 55 | 219 | 0 | 0 | 0 | 100 | 101 | 133 | 10 | 72 | 0 | 46 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 125 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 10 | 91 | 50 | 22 | 26 | 0 | 0 | 100 | 345 | 305 | 215 | 8 | 127 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 184 | 123 | 95 | 22 | 0 | 60 | 31 | 50 | 48 | 163 | 146 | 67 | 76 | 46 | 98 | 18 | 45 | 10 | 290 | 24 | 0 | 0 | 286 | 0 | 0 | 170 | 0 | 134 | 0 | 100 | 200 | 50 | 0 | 107 | 106 | 0 | 0 | 177 | 0 | 17 |  | 907 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 30 | 60 | 40 | 167 | 40 | 110 | 0 | 0 | 55 | 43 | 31 | 94 | 40 | 42 | 37 | 52 | 27 | 22 | 7 | 11 | 0 | 0 | 220 | 0 | 14 | 205 | 0 | 0 | 0 | 98 | 100 | 207 | 0 | 370 | 90 | 0 | 113 | 81 | 111 | 0 | 0 |  | 12526 | EvPeak
Forecast for Evening | 70 | 209 | 0 | 110 | 350 | 0 | 0 | 350 | 350 | 0 | 0 | 360 | 290 | 100 | 100 | 55 | 218 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 100 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 85 | 100 | 97 | 50 | 22 | 25 | 0 | 0 | 100 | 360 | 0 | 225 | 68 | 140 | 33 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 183 | 204 | 95 | 22 | 0 | 60 | 58 | 51 | 50 | 163 | 160 | 63 | 77 | 45 | 110 | 18 | 47 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 260 | 37 | 113 |  | 909 | 32 | 410 | 0 | 115 | 200 | 0 | 0 | 42 | 75 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 50 | 50 | 47 | 52 | 35 | 22 | 15 | 11 | 98 | 0 | 280 | 0 | 18 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 70 | 209 | 0 | 110 | 350 | 0 | 0 | 350 | 350 | 0 | 0 | 360 | 290 | 100 | 100 | 55 | 150 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 46 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 124 | 90 | 100 | 100 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 95 | 50 | 22 | 10 | 0 | 0 | 100 | 360 | 0 | 225 | 68 | 140 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 141 | 204 | 95 | 22 | 1.6 | 60 | 58 | 51 | 50 | 163 | 160 | 63 | 77 | 45 | 69 | 18 | 46 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 50 | 4.4 | 230 | 37 | 113 |  | 909 | 0 | 380 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 50 | 47 | 52 | 0 | 22 | 16 | 11 | 0 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 70 | 184 | 0 | 110 | 300 | 0 | 0 | 345 | 303 | 0 | 0 | 340 | 290 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 0 | 0 | 0 | 22 | 25 | 23 | 33 | 33 | 43 | 0 | 124 | 90 | 100 | 120 | 0 | 206 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 24 | 21 | 40 | 0 | 0 | 100 | 260 | 260 | 181 | 8 | 132 | 30 | 54 | 0 | 5 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 130 | 155 | 95 | 22 | 1.3 | 60 | 31 | 11 | 10 | 100 | 145 | 67 | 77 | 46 | 69 | 17 | 20 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 10 | 20 | 17 | 0 | 0 | 108 | 106 | 0 | 2.6 | 106 | 0 | 0 | 0 | 907 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 24 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 42 | 0 | 0 | 0 | 22 | 7 | 8 | 0 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 73 | 0 | 158 | 0 | 300 | 17 | 0 | 109 | 105 | 36 | 0 | 0 | 0
199
| Minimum Generation |  | 9335.057 | 7:00
| Highest Generation |  | 12526 | 21:00
| Day Peak Generation |  | 10372.23 | 12:00
| Evening Peak Generation |  | 12526 | 21:00
| HVDC Max Flow |  | 908 | 16:00
| HVDC EvPeak Flow |  | 907 | 21:00
| Load factor L.F |  | 89.96%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-08-30
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-08-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10372.23 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8870.9 | MW
Evening Peak Generation : |  | 12526 | MW Hour : | 21:00 | Available Max Generation : |  | 14911 | MW
E.P. Demand (at gen end) : |  | 12526 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12100 | MW
Maximum Generation : |  | 12526 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2811 | MW
Total Gen. (MKWH) : |  | 270.4339 | System Load Factor : | 89.96% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -276 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-08-30
Actual : | 105.41 | Ft.(MSL) , | Rule curve : | 98.01 | Ft.( MSL )
Gas Consumed : | Total = | 1360.45 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151079579.608
|  | Coal : | 27907899.98 | Oil : | 633850244.03 | Total : | 812837723.618
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4271.2438 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1454.8032 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1303.8731 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1178.3076 |  |  | 0 | 0%
) | 0 | 0:00 | 1064.7378 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 859.2116 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 477.4126 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.1441 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 662.6811 |  |  | 0 | 0%
Total | 0 |  | 11493.4149 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorashal Unit-4
|  |  |  | 2) Khulna ST 110 MW | 8) Sirajganj Unit-2
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ashuganj #3
4) Siddhirganj ST
5) Ashuganj #4
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ghorashal-Ishurdi 230 kV Ckt-2 was under shut down from 08:25 to 15:30 for D/W.
b) Ullon 132/33 kV T-2 transformer was under shut down from 09:07 to 11:32 for spark at isolator of B-phase..
c) Ullon-Rampura 132 kV (cable) Ckt-2 was under shut down from 11:40 to 15:41 for C/M.
d) Siddhirganj 335 MW was shut down at 08:31 for ST commissioning and was synchronized at 10:40.
e) Bogura-Bogura Confidence-1 132 kV Ckt was under shut down from 12:17 to 15:01 for Energy meter work.
f) Sylhet-Fenchuganj (P/S) 132 kV Ckt was switched on at 23:10.
g) Ashuganj-Kishorganj 132 kV Ckt-1 was shut down at 06:30(30/8/19) for D/W.
h) Sonargaon 132/33 kV T-2 transformer along with 33 kV Bus was under shut down from 07:07(30/8/19) to 10 :20 |  |  |  |  | About 35 MW power interruption occurred under Sonargaon S/S
For R/H maintenance. |  |  |  |  | area from 07:07(30/8/19) to 10 :20.
i) Cox-Bazar 132/33 kV T-1 transformer was under shut down from 06:11(30/8/19) to 08:24 for R/H maintenance.
j) Rampura 230/132 kV T-1 transformer was under shut down from 06:04(30/8/19) to 09:54 for R/H maintenance.
k) Khulshi 132/33 kV T-2 transformer was under shut down from 06:57(30/8/19) to 09:39 for C/M. |  |  |  |  | About 30 MW power interruption occurred under Khulshi S/S
area from 06:57(30/8/19) to 09:39.
l) Barishal-Bhandaria 132 kV Ckt tripped at 05:55(30/8/19) from both ends showing distance Z1 at A,B,C-phase of
Bhandaria end and distance Z1 at A-phase of Barishal end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-08-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1575000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 184 | 4683400 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2614500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 7521382
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8528900 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7766000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8407375 | Machine problem
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1521600
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6462080 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 100 | 295824
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 721404
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 935970 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 432180
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 925440
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 219 | 2273237 | ST Commissioning
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 101 | 1645776
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 46 | 491424
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1227960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1863840 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1128349
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 760759 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1718400 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 6023400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 806900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 785200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 977424
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 2782580
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 40565 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 37687 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 134 | 2240640
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 106 | 2495784
| Dhaka area Total |  |  |  | 5693 | 3836 | 79690980
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2700000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 395419
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 141885
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1177440
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 215 | 4921004
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4912396 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3150562 | FGMO
| Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | Contract Expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer overload.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 533246
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 617400 | Line O/L
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2413440
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 514320
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 503040
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 1814400 | Engine problem
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 177 | 2792618 | Transformer overload.
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 993595 | on test
53 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 80290 | Transformer overload.
| Chattogram area Total |  |  |  | 2112 | 1367 | 29992495
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2394302 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4852000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7725600 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7239000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 663192 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1229280
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 702545 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1028018 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1518836 | Transformer overload.
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 62984 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 127 | 3114230
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3791520
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 459936
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223380
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 184 | 3922560
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817600
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 583666
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 449780 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 44160 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1795 | 40822589
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 123 | 3250280 | Gas shortage
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 479412
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 2200320
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10900
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 3002400 | Engine problem
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 107 | 2625600
| Mymensingh Area Total |  |  |  | 637 | 517 | 11568912
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1418000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 742500
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3151669
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 146 | 3267000 | GT-2 under maint.
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1101600
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 1100736
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 253056 | Machine tripped.
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 67 | 1567680 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1690560 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 46 | 1000440
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 98 | 1940820
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 430254
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 45 | 1021800
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 567816
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7462200 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Test
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245520
| Sylhet Area Total |  |  |  | 1834 | 1172 | 26961651
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21769455
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1553280
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 219840 | Low demand
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 447488
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7257600 | Line O/L
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 567000
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 653760
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1954560 | Engine problem
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 81 | 1688400
| Khulna Area Total |  |  |  | 2314 | 1723 | 36111383
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1303680
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 40 | 683889
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 167 | 4337914
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 2199695
| Barisal Area Total |  |  |  | 462 | 415 | 8525178
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1310000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 485280
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 224365
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 473580
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 813475 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 271982
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 205 | 5022800 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 207 | 4828473 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 7924545 | Gas shortage
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 229040
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 503040
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 7 | 217872
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227214
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 670560
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 1356404
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2741184
| Rajshahi Area Total |  |  |  | 2070 | 1356 | 27299814
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 401454 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 6198200
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 14 | 131000
134 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 2687040
135 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43175
| Rangpur Area Total |  |  |  | 605 | 345 | 9460869
| Total |  |  |  | 18618 | 12526 | 270433871
| Eastern Grid Total |  |  |  | 13167 | 8687 | 189036627
| Western Grid Total |  |  |  | 5451 | 3839 | 81397244
| National Grid Total |  |  |  | 18618 | 12526 | 270433871
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-08-29
(a) ENTIRE EASTERN GRID : |  | 7970 | MW | (b) ENTIRE WESTERN GRID : |  | 3916 | MW
i) Dhaka area |  | 4230 | MW | i) Khulna area |  | 1524 | MW
ii) Chittagong area |  | 1136 | MW | ii) Rajshahi area |  | 1301 | MW
iii) Comilla area |  | 1116 | MW | iii) Barisal area |  | 353 | MW
iv) Mymensingh area |  | 958 | MW | iv) Rangpur area |  | 738 | MW
v) Sylhet area |  | 530 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11886 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 134 | 1500 | Sherpur | 112 | 2200 | Jhenida | 115 | 1930
Munsiganj | 130 | 2100 | Srimongal | 43 | 1930 | Bottail | 132 | 1930
Sonargaon | 86 | 1900 | Shahjibazar | 124 | 2200 | G.K Project | 69 | 1900
Shyampur | 200 | 100 | Fenchuganj | 53 | 1930 | Faridpur | 184 | 2300
Bhulta | 189 | 2400 | Kulawara | 48 | 2100 | Madaripur | 120 | 2100
Madanganj | 56 | 200 | Sylhet | 157 | 2100 | Sariatpur | 46 | 2200
Shitalakhya | 112 | 1500 | Chatak | 28 | 2100 | Gopalganj | 96 | 2100
Rahim steel | 3 | 100 | Sunamganj | 47 | 2100 | Bagerhat | 87 | 2000
Matuail | 98 | 1200 | Biani Bazar | 58 | 2100 | Mongla | 40 | 2100
Ghorasal | 83 | 1930 | Comilla (S) | 188 | 2100 | Satkhira | 99 | 2100
Narsingdi | 152 | 2200 | Comilla(N) | 125 | 1900 | Gallamari | 48 | 100
Haripur (SBU) | 95 | 2100 | Chandpur | 109 | 2200 | Magura | 56 | 1930
Ullon | 80 | 1930 | Feni | 131 | 1900 | Norail | 24 | 1930
Hasnabad | 203 | 2100 | Chowmuhani | 182 | 2100 | Chuadanga | 88 | 2100
Magbazar | 147 | 1600 | Ashuganj | 61 | 2300 | Barisal(N) | 44 | 2200
Maniknagar | 116 | 1200 | Daudkandi | 138 | 2300 | Barisal (S) | 110 | 2100
Bangabhaban | 40 | 1300 | B.Baria | 140 | 2400 | Patuakhali | 115 | 2200
Narinda | 102 | 1200 | Ramganj | 100 | 2100 | Bhandaria | 54 | 2100
Dhanmondi | 179 | 1200 | Madunaghat | 58 | 2100 | Borhan Uddin | 37 | 100
Lalbag | 93 | 1200 | Hathazari | 105 | 1930 | Ishurdi | 71 | 2100
Madartek | 57 | 1930 | Khulshi | 200 | 1500 | Ruppur Paromanobik | 2 | 1900
Mirpur | 117 | 1500 | Halishahar | 137 | 1100 | Natore | 133 | 2200
Kalyanpur | 120 | 2000 | Baraulia | 167 | 1900 | Bogra | 253 | 1930
Gulshan | 178 | 1600 | Sikalbaha | 26 | 1930 | Noagaon | 125 | 2100
Uttara | 91 | 1600 | Dohazari | 90 | 1900 | Rajshahi | 166 | 2100
Uttara New | 17 | 1700 | Cox'sbazar | 93 | 2100 | C.Nawabganj | 80 | 2200
Kamrangirchar | 76 | 1900 | Chandraghona | 26 | 1900 | Amnura | 39 | 2100
Savar | 143 | 1500 | Kaptai | 5 | 1900 | Pabna | 119 | 1930
Bhasantec | 177 | 1500 | A. Khaer Stl. | 0 | 100 | Shahjadpur | 109 | 2000
Agargaon | 67 | 1300 | Bakulia | 102 | 1830 | Serajganj | 102 | 2000
Satmosjid | 114 | 1930 | Julda | 20 | 100 | Niyamatpur | 65 | 2200
Tongi | 169 | 1500 | TK chemical | 17 | 1600 | Joypurhat | 54 | 2000
Kabirpur | 229 | 1500 | Modern Steel | 16 | 1000 | Mohastangor | 16 | 100
Basundhara | 140 | 1830 | Shahmirpur | 32 | 1830 | Rangpur | 148 | 1930
Manikganj | 94 | 2100 | Khagrachhari | 22 | 1900 | Lalmonirhat | 72 | 2000
Joydevpur | 231 | 2000 | Matarbari | 29 | 1930 | Saidpur | 118 | 1930
New Tongi | 107 | 1500 | Baroiar Hat | 38 | 1900 | Purbasadipur | 95 | 2000
Korda | 234 | 1400 | Rangamati | 12 | 1830 | Thakurgaon | 73 | 200
Dhamrai | 78 | 2000 | Abul Khair 230 | 141 | 1300 | Palashbari | 114 | 100
Valuka | 94 | 2000 | BSRM | 141 | 500 | Barapukuria | 55 | 2100
Tangail | 197 | 2200 | Goalpara | 28 | 1930 | Panchagar | 45 | 1900
Mymensing | 258 | 2000 | Central s/s | 96 | 1900 | Joldhaka | 19 | 2000
Kishorganj | 138 | 2100 | Noapara | 89 | 1930 | Kurigram | 40 | 2300
Netrokona | 111 | 1930 | Jessore | 118 | 1900
Jamalpur | 130 | 100 | Benapol | 44 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-08-29 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 1:00 | 376 | 10:00 | Kaliakoir | 365 | 1:00 | 350 | 10:00
Bheramara | 399 | 7:00 | 390 | 20:00 | Bhulta | 381 | 1:00 | 364 | 10:00
Ashuganj(N) | 384 | 1:00 | 372 | 9:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 10:00
Ghorasal | 230 | 1:00 | 222 | 16:00 | Hathazari | 220 | 1:00 | 216 | 10:00
Ishurdi | 236 | 18:00 | 226 | 19:00 | Megnaghat | 222 | 1:00 | 212 | 10:00
Ashuganj | 235 | 1:00 | 230 | 9:00 | Fenchuganj | 233 | 6:00 | 229 | 10:00
Serajganj | 230 | 6:00 | 224 | 19:30 | Siddhirganj | 219 | 1:00 | 209 | 10:00
Baghabari | 232 | 3:00 | 228 | 19:30 | Maniknagar | 218 | 1:00 | 207 | 10:00
Barapukuria | 237 | 9:00 | 219 | 22:00 | Old Airport | 218 | 1:00 | 205 | 10:00
Bogra | 225 | 9:00 | 207 | 22:00 | Barisal | 230 | 24:00 | 220 | 15:00
Khulna South | 230 | 18:00 | 213 | 7:00 | AKSML | 217 | 1:00 | 212 | 11:00
Rampura | 220 | 1:00 | 210 | 10:00 | BSRM | 218 | 1:00 | 213 | 10:00
Haripur | 220 | 1:00 | 210 | 10:00 | Bibiyana | 230 | 1:00 | 224 | 9:00
Hasnabad | 220 | 1:00 | 210 | 11:00 | Bhulta | 221 | 1:00 | 209 | 10:00
Aminbazar | 219 | 1:00 | 210 | 8:00 | Ashuganj (S) | 233 | 1:00 | 226 | 10:00
Tongi | 221 | 1:00 | 210 | 9:00 | Kaliakoir | 222 | 23:00 | 206 | 10:00
Comilla (N) | 227 | 3:00 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 132 | 1930 | 123 | 1000 | Khulshi | 129 | 100 | 126 | 1000
Munsiganj | 134 | 1930 | 122 | 1000 | Halishahar | 132 | 100 | 129 | 1000
Megnaghat | 130 | 1830 | 122 | 1000 | Baraulia | 130 | 2200 | 126 | 900
Shyampur | 131 | 1830 | 122 | 1000 | Sikalbaha | 132 | 100 | 129 | 1000
Bhulta | 124 | 1830 | 116 | 1000 | Dohazari | 130 | 100 | 126 | 1400
Madanganj | 136 | 1930 | 122 | 1000 | Cox'sbazar | 123 | 700 | 116 | 1500
Shitalakhya | 138 | 1930 | 122 | 1000 | Chandraghona | 132 | 2100 | 130 | 300
Rahim steal | 132 | 2000 | 124 | 1000 | Kaptai | 132 | 100 | 130 | 1000
Matuail | 131 | 1900 | 122 | 1000 | A. Khaer Stl. | 129 | 200 | 126 | 1000
Ghorasal | 135 | 100 | 132 | 1000 | Bakulia | 130 | 100 | 128 | 1000
Narsinghdi | 130 | 700 | 124 | 1830 | Julda | 131 | 100 | 128 | 1000
Haripur (SBU) | 132 | 1930 | 124 | 1000 | TK Chemical | 132 | 100 | 129 | 1000
Ullon | 131 | 100 | 121 | 1500 | Modern Steel | 132 | 100 | 128 | 900
Hasnabad | 135 | 1900 | 128 | 800 | Shahmirpur | 131 | 300 | 128 | 1200
Magbazar | 132 | 200 | 121 | 1000 | Khagrachhari | 131 | 500 | 129 | 1000
Maniknagar | 133 | 400 | 125 | 1000 | Matarbari | 129 | 800 | 120 | 200
Bangabhaban | 133 | 400 | 125 | 1000 | Baroiar Hat | 129 | 500 | 122 | 2300
Narinda | 133 | 400 | 125 | 1000 | Rangamati | 131 | 100 | 129 | 1200
Dhanmondi | 131 | 100 | 121 | 1500 | Goalpara | 139 | 1800 | 130 | 1000
Lalbag | 130 | 600 | 126 | 900 | Central s/s | 136 | 1800 | 130 | 1900
Madartek | 132 | 600 | 121 | 1500 | Noapara | 134 | 1800 | 125 | 1000
Mirpur | 134 | 300 | 124 | 1600 | Jessore | 128 | 1830 | 118 | 2100
Kalyanpur | 135 | 200 | 126 | 1000 | Benapol | 131 | 1800 | 118 | 2100
Gulshan | 131 | 100 | 121 | 1000 | Jhenida | 128 | 1800 | 112 | 2100
Uttara | 132 | 600 | 121 | 1000 | Bottail | 134 | 1800 | 123 | 2100
Uttara New | 132 | 2000 | 125 | 1200 | G.K Project | 141 | 1800 | 134 | 1930
Kamrangirchar | 133 | 1900 | 120 | 1000 | Faridpur | 128 | 800 | 118 | 2100
Savar | 132 | 400 | 122 | 1000 | Madaripur | 135 | 1800 | 124 | 1500
Bhasantec | 131 | 100 | 122 | 1000 | Sariatpur | 138 | 1830 | 122 | 1600
Agargaon | 133 | 600 | 123 | 1000 | Gopalganj | 140 | 1800 | 126 | 1500
Satmosjid | 132 | 600 | 123 | 1000 | Bagerhat | 135 | 500 | 125 | 2000
Tongi | 135 | 1930 | 128 | 900 | Mongla | 134 | 400 | 125 | 1200
Kabirpur | 129 | 1800 | 123 | 900 | Satkhira | 138 | 1800 | 125 | 2000
Basundhara | 131 | 2100 | 126 | 1500 | Gallamari | 138 | 100 | 128 | 700
Manikganj | 138 | 1800 | 132 | 1500 | Magura | 125 | 600 | 110 | 2100
Joydevpur | 138 | 100 | 127 | 1100 | Norail | 127 | 1800 | 108 | 2100
New Tongi | 134 | 100 | 127 | 1300 | Chuadanga | 124 | 1800 | 102 | 2100
Kodda | 138 | 1830 | 130 | 800 | Barisal(N) | 136 | 1800 | 128 | 1500
Dhamrai | 129 | 800 | 124 | 2200 | Barisal (S) | 136 | 1830 | 127 | 1500
Valuka | 122 | 500 | 110 | 2200 | Patuakhali | 133 | 1830 | 121 | 1500
Tangail | 127 | 700 | 120 | 2100 | Bhandaria | 134 | 1800 | 127 | 700
Mymensing | 125 | 600 | 113 | 2200 | Ishurdi | 139 | 1800 | 132 | 1400
Kishorganj | 127 | 1800 | 116 | 2100 | Ruppur Paromanobik | 139 | 1800 | 132 | 1930
Netrokona | 126 | 1800 | 110 | 2100 | Natore | 136 | 1800 | 126 | 1500
Jamalpur | 139 | 1700 | 128 | 2100 | Bogra | 136 | 1800 | 123 | 1930
Sherpur | 137 | 1400 | 127 | 2200 | Noagaon | 130 | 600 | 115 | 2100
Srimongal | 135 | 600 | 131 | 1830 | Rajshahi | 133 | 1800 | 121 | 1500
Shahjibazar | 134 | 600 | 129 | 1900 | C.Nawabganj | 130 | 600 | 118 | 1500
Fenchuganj | 134 | 700 | 130 | 1830 | Amnura | 133 | 1800 | 119 | 1500
Khulawara | 132 | 500 | 129 | 1830 | Pabna | 136 | 1800 | 130 | 1900
Sylhet | 133 | 500 | 128 | 1830 | Shahjadpur | 140 | 600 | 133 | 1930
Chatak | 132 | 500 | 126 | 1830 | Serajganj | 135 | 1800 | 126 | 2000
Sunamganj | 130 | 600 | 123 | 1900 | Niyamatpur | 130 | 1800 | 111 | 2100
Biani Bazar | 131 | 600 | 124 | 2100 | Joypurhat | 130 | 1800 | 112 | 2100
Comilla(s) | 135 | 600 | 117 | 2200 | Mohastangor | 135 | 800 | 121 | 2000
Comilla(n) | 133 | 1830 | 121 | 900 | Rangpur | 133 | 800 | 112 | 2000
Chandpur | 132 | 1700 | 130 | 700 | Lalmonirhat | 130 | 600 | 105 | 2100
Feni | 127 | 1800 | 120 | 2300 | Saidpur | 132 | 800 | 111 | 1900
Chowmuhani | 127 | 1800 | 117 | 2300 | Purbasadipur | 134 | 900 | 108 | 2200
Ashuganj | 135 | 800 | 130 | 2400 | Thakurgaon | 130 | 900 | 100 | 1900
Daudkandi | 130 | 1900 | 122 | 1000 | Palashbari | 135 | 800 | 115 | 1900
B.Baria | 130 | 700 | 125 | 2100 | Barapukuria | 137 | 900 | 119 | 1900
Ramganj | 128 | 1830 | 118 | 2300 | Panchagar | 125 | 800 | 91 | 2300
Madanhat | 131 | 100 | 130 | 900 | Joldhaka | 133 | 800 | 110 | 1900
Hathazari | 130 | 100 | 129 | 1100 | Kurigram | 131 | 800 | 107 | 2200
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-08-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 58 | 8423 | 3946 | 12369 |  |  |  | QF-LDC-12
0:30 | 116 | 8302.5 | 3858 | 12160.5 | Date: | 2019-08-29
1:00 | 174 | 8182 | 3770 | 11952
1:30 | 182 | 8004 | 3665.5 | 11669.5
2:00 | 190 | 7826 | 3561 | 11387
2:30 | 165 | 7771 | 3554 | 11325 | [5 empty] | Gen. at Eve. Peak | 12526 | 12526 MW (21:00 )
3:00 | 140 | 7716 | 3547 | 11263 | [6 empty] | 21:00
3:30 | 130 | 7629 | 3507.5 | 11136.5 | [5 empty] | Gen. at Day Peak | 10372.23 | 10372.23 MW (12:00 )
4:00 | 120 | 7542 | 3468 | 11010 | [6 empty] | 12:00
4:30 | 116 | 7448 | 3469.5 | 10917.5 | [5 empty] | Highest Generation | 12526
5:00 | 112 | 7354 | 3471 | 10825 | [6 empty] | 21:00
5:30 | 71 | 7037.561 | 3330.5 | 10368.061
6:00 | 30 | 6721.122 | 3190 | 9911.122
6:30 | 30 | 6582.0895 | 3041 | 9623.0895
7:00 | 30 | 6443.057 | 2892 | 9335.057
7:30 | 85 | 6453.1785 | 2884 | 9337.1785
8:00 | 140 | 6463.3 | 2876 | 9339.3
8:30 | 240 | 6520.185 | 2861.85 | 9382.035
9:00 | 340 | 6577.07 | 2847.7 | 9424.77
9:30 | 320 | 6698.86 | 2891.15 | 9590.01
10:00 | 300 | 6820.65 | 2934.6 | 9755.25
10:30 | 267.5 | 6909.16 | 2974.2 | 9883.36
11:00 | 235 | 6997.67 | 3013.8 | 10011.47
11:30 | 151 | 7199.45 | 2992.4 | 10191.85
12:00 | 67 | 7401.23 | 2971 | 10372.23
12:30 | 72 | 7453.535 | 3035 | 10488.535
13:00 | 77 | 7505.84 | 3099 | 10604.84
13:30 | 60 | 7493.02 | 3086.25 | 10579.27
14:00 | 43 | 7480.2 | 3073.5 | 10553.7
14:30 | 54 | 7605.95 | 3121.15 | 10727.1
15:00 | 65 | 7731.7 | 3168.8 | 10900.5
15:30 | 100.5 | 7674.245 | 3172.38 | 10846.625
16:00 | 136 | 7616.79 | 3175.96 | 10792.75
16:30 | 118 | 7516.745 | 3076.44 | 10593.185
17:00 | 100 | 7416.7 | 2976.92 | 10393.62
17:30 | 113 | 7247.85 | 2941.96 | 10189.81
18:00 | 126 | 7079 | 2907 | 9986
18:30 | 118 | 7644 | 3351.5 | 10995.5
19:00 | 110 | 8209 | 3796 | 12005
19:30 | 198 | 8555 | 3867 | 12422
20:00 | 218 | 8622 | 3841 | 12463 |  |  |  | Executive Engineer
20:30 | 247 | 8654.5 | 3840 | 12494.5 |  |  |  | Network Operation Division
21:00 | 276 | 8687 | 3839 | 12526
21:30 | 248 | 8565 | 3868.5 | 12433.5
22:00 | 220 | 8443 | 3898 | 12341 |  |  |  |  | Page 6 of 7
22:30 | 155 | 8423 | 3922.5 | 12345.5
23:00 | 90 | 8403 | 3947 | 12350
23:30 | 74 | 8413 | 3946.5 | 12359.5
24:00 | 58 | 8423 | 3946 | 12369
12526 MW (21:00 )
10372.23 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-08-29 |  | Energy | 270433871
[10 empty] | 2019-08-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4843 | 907 | 2183 | 3285 | 220 | 214 | 533 | 0 | 184
0:30 | 4625 | 907 | 2119 | 3329.5 | 279.5 | 212.5 | 509 | 0 | 179 | Date: | 2019-08-29
1:00 | 4407 | 907 | 2055 | 3374 | 339 | 211 | 485 | 0 | 174
1:30 | 4405.5 | 907 | 2054 | 3167.5 | 339 | 209.5 | 418 | 0 | 169 | [7 empty] | Total Energy | 270.4339 | Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
2:00 | 4404 | 907 | 2053 | 2961 | 339 | 208 | 351 | 0 | 164 | [7 empty] | Energy not Served | 0
2:30 | 4441.5 | 907 | 2064 | 2867.5 | 339 | 208 | 336 | 0 | 162 | [7 empty] | Energy Requirement | 270.4339
3:00 | 4479 | 907 | 2075 | 2774 | 339 | 208 | 321 | 0 | 160
3:30 | 4487.5 | 907 | 2078 | 2663 | 339 | 208 | 294 | 0 | 160 | [6 empty] | Shortage
4:00 | 4496 | 907 | 2081 | 2552 | 339 | 208 | 267 | 0 | 160
4:30 | 4444.5 | 907 | 2077 | 2535.5 | 339 | 209.5 | 254 | 0 | 151
5:00 | 4393 | 907 | 2073 | 2519 | 339 | 211 | 241 | 0 | 142
5:30 | 4347 | 907 | 2010.5 | 2218 | 339 | 213 | 192.5 | 0 | 141
6:00 | 4301 | 907 | 1948 | 1917 | 339 | 215 | 144 | 0 | 140
6:30 | 4296 | 907 | 1952.5 | 1724.5 | 304.5 | 215 | 83.5 | 0 | 137 |  |  |  |  | Coal
7:00 | 4291 | 907 | 1957 | 1532 | 270 | 215 | 23 | 0 | 134
7:30 | 4292.5 | 907 | 1908.5 | 1574.5 | 270 | 215 | 23 | 0 | 136 |  |  |  | Oil |  |  |  | ,
8:00 | 4294 | 907 | 1860 | 1617 | 270 | 215 | 23 | 0 | 138
8:30 | 4272 | 907 | 1870 | 1667 | 270 | 215 | 23 | 0 | 138
9:00 | 4250 | 907 | 1880 | 1717 | 270 | 215 | 23 | 0 | 138
9:30 | 4325 | 907 | 1912.5 | 1764 | 270 | 215 | 31 | 0 | 141
10:00 | 4400 | 907 | 1945 | 1811 | 270 | 215 | 39 | 0 | 144
10:30 | 4414 | 907 | 1927.5 | 1940 | 270 | 215 | 39 | 0 | 144
11:00 | 4428 | 907 | 1910 | 2069 | 270 | 215 | 39 | 0 | 144
11:30 | 4466 | 907 | 1905.5 | 2214 | 270 | 211.5 | 39 | 0 | 149
12:00 | 4504 | 907 | 1901 | 2359 | 270 | 208 | 39 | 0 | 154
12:30 | 4500.5 | 907 | 1938 | 2431.5 | 270 | 208 | 47 | 0 | 155
13:00 | 4497 | 907 | 1975 | 2504 | 270 | 208 | 55 | 0 | 156
13:30 | 4497 | 907 | 1975 | 2504 | 270 | 208 | 55 | 0 | 156
14:00 | 4497 | 907 | 1975 | 2504 | 270 | 208 | 55 | 0 | 156
14:30 | 4519.5 | 907 | 2008.5 | 2600 | 265 | 207.5 | 55 | 0 | 162
15:00 | 4542 | 907 | 2042 | 2696 | 260 | 207 | 55 | 0 | 168
15:30 | 4502 | 907.5 | 2022.5 | 2695.5 | 238.5 | 207 | 89 | 0 | 169
16:00 | 4462 | 908 | 2003 | 2695 | 217 | 207 | 123 | 0 | 170
16:30 | 4398.5 | 908 | 1874 | 2674.5 | 226 | 208.5 | 129.5 | 0 | 167
17:00 | 4335 | 908 | 1745 | 2654 | 235 | 210 | 136 | 0 | 164
17:30 | 4201.5 | 908 | 1607 | 2695 | 247.5 | 211 | 156.5 | 0 | 160
18:00 | 4068 | 908 | 1469 | 2736 | 260 | 212 | 177 | 0 | 156
18:30 | 4247 | 908 | 1743 | 3094 | 249 | 213.5 | 369 | 0 | 172
19:00 | 4426 | 908 | 2017 | 3452 | 238 | 215 | 561 | 0 | 188
19:30 | 4528 | 906 | 2032 | 3723 | 230 | 215 | 606 | 0 | 182
20:00 | 4496 | 907 | 2048 | 3772 | 230 | 215 | 607 | 0 | 188
20:30 | 4626 | 907 | 2082 | 3673 | 225 | 215 | 580.5 | 0 | 186
21:00 | 4756 | 907 | 2116 | 3574 | 220 | 215 | 554 | 0 | 184
21:30 | 4785.5 | 907 | 2119.5 | 3450.5 | 220 | 215 | 550 | 0 | 186
22:00 | 4815 | 907 | 2123 | 3327 | 220 | 215 | 546 | 0 | 188
22:30 | 4822.5 | 907 | 2148 | 3307 | 219.5 | 214.5 | 539 | 0 | 188
23:00 | 4830 | 907 | 2173 | 3287 | 219 | 214 | 532 | 0 | 188
23:30 | 4836.5 | 907 | 2178 | 3286 | 219.5 | 214 | 532.5 | 0 | 186 | Max Temp. in Dhaka |  | 35.7° C
24:00 | 4843 | 907 | 2183 | 3285 | 220 | 214 | 533 | 0 | 184
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 187.552 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 187.552 MKWHr
Note on W13: Author:

## Generation
2019-08-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 121 | 118 | 118 | 118 | 121 | 125 | 125 | 125 | 125 | 125 | 125 | 118 | 118 | 118 | 117 | 117 | 120 | 122 |  | 125 | 125 | 125 | 125 | 125 | 124 | 124 | 2761004
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2160000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2300000
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2700000
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 0 |  |  |  |  | 0 | 14 | 24 | 24 | 24 | 24 | 0 | 0 |  | 11 | 25 | 25 | 25 | 25 | 25 | 25 | 395419
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 10 | 15 | 17 | 20 | 20 | 20 | 20 | 16 | 2.29 | 2.4 | 0 | [8 empty] | 141885
6 | Sikalbaha 225MW CCPP (Gas) | 206 | 204 | 204 | 207 | 206 | 203 | 203 | 204 | 204 | 207 | 204 | 217 | 205 | 205 | 208 | 204 | 204 | 203 |  | 204 | 204 | 204 | 204 | 204 | 212 | 205 | 4912396
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 145 | 148 | 150 | 120 | 135 | 145 | 130 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3150562
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 0 | [15 empty] | 0 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 533246
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 0 |  | 30 | 30 | 30 | 0 |  |  |  | 44160
14 | Titas 50 MW Peaking PP | [19 empty] | 0 | 50 | 50 | 0 |  |  |  | 62984
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 0 | 0 | 48 | 44 | 38 | 38 | 34 | 33 | 30 | 29 |  | 29 | 28 | 29 | 219 | 218 | 219 | 220 | 2273237
18 | Kodda 300 MW PP Unit-2 (Summit) | 243 | 0 | [8 empty] | 0 | 34 | 45 | 102 | 145 | 180 | 210 | 210 |  | 220 | 270 | 288 | 286 | 210 | 210 | 212 | 2782580
19 | Ashuganj 195MW PP (APSCL-United) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 702545
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1575000
21 | Ghorasal Repowered CCPP Unit-3 | 184 | 184 | 184 | 184 | 184 | 183 | 184 | 184 | 184 | 183 | 184 | 184 | 183 | 184 | 184 | 184 | 184 | 184 |  | 184 | 184 | 184 | 184 | 184 | 184 | 194 | 4683400
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2614500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 270 |  | 300 | 300 | 300 | 380 | 380 | 380 | 380 | 7521382
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394302
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 30 | 30 | 30 | 30 | 30 | 27 | 27 | 27 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 663192
33 | Ashuganj 225 MW CCPP | 216 | 216 | 215 | 216 | 217 | 179 | 188 | 180 | 193 | 197 | 183 | 200 | 182 | 180 | 200 | 181 | 192 | 162 |  | 212 | 215 | 215 | 215 | 215 | 215 | 215 | 4852000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 305 | 295 | 300 | 300 | 265 | 275 | 300 | 260 | 320 | 310 | 280 | 310 | 280 | 270 | 270 |  | 290 | 290 | 290 | 305 | 305 | 305 | 305 | 7239000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 325 | 330 | 220 | 220 | 220 | 295 | 265 | 300 | 325 | 345 | 335 | 300 | 350 | 325 | 300 | 260 |  | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 7725600
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 55 | 54 | 54 | 55 | 55 | 54 | 54 | 52 | 53 | 53 | 53 | 50 | 48 | 49 | 50 | 20 |  | 20 | 33 | 54 | 53 | 52 | 53 | 52 | 1229280
36 | Chandpur 150 MW CCPP | 132 | 132 | 132 | 132 | 132 | 126 | 132 | 132 | 132 | 132 | 130 | 133 | 133 | 131 | 132 | 132 | 132 | 126 |  | 133 | 126 | 126 | 127 | 132 | 128 | 129 | 3114230
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 345 | 349 | 349 | 357 | 348 | 352 | 345 | 361 | 371 | 355 | 360 | 371 | 350 | 375 | 365 | 349 | 300 |  | 300 | 345 | 345 | 346 | 347 | 344 | 341 | 8528900
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 300 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 8407375
41 | Haripur 360MW CCPP(HPL) | 333 | 333 | 334 | 334 | 334 | 303 | 304 | 283 | 282 | 302 | 343 | 345 | 342 | 320 | 342 | 340 | 273 | 273 |  | 344 | 350 | 350 | 351 | 350 | 350 | 353 | 7766000
42 | RPCL 210MW CCPP | 140 | 154 | 155 | 155 | 155 | 157 | 155 | 155 | 153 | 152 | 138 | 137 | 137 | 122 | 120 | 120 | 134 | 136 |  | 137 | 123 | 125 | 123 | 124 | 126 | 140 | 3250280
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1418000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 31 | 30 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 742500
46 | Shajibazar 330 MW CCPP | 147 | 145 | 146 | 146 | 145 | 144 | 144 | 146 | 146 | 145 | 145 | 144 | 146 | 146 | 155 | 147 | 144 | 144 |  | 144 | 145 | 145 | 146 | 147 | 145 | 144 | 3267000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 63 | 65 |  | 65 | 67 | 67 | 67 | 65 | 67 | 67 | 1567680
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 76 | 76 | 76 | 76 | 76 | 75 | 40 | 40 | 70 | 70 | 72 | 73 | 75 | 76 | 74 | 75 | 30 |  | 75 | 76 | 76 | 76 | 76 | 77 | 77 | 1690560
49 | Shahjibazar 50MW PP (EPL) | 44 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 43 | 43 | 43 | 43 | 43 | 45 | 46 | 45 | 10 |  | 45 | 45 | 46 | 46 | 46 | 45 | 46 | 1000440
50 | Sylhet 150 MW CCPP | 68 | 68 | 68 | 69 | 69 | 69 | 70 | 67 | 77 | 76 | 67 | 78 | 68 | 78 | 83 | 67 | 70 | 70 |  | 80 | 100 | 98 | 98 | 96 | 88 | 88 | 1940820
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 430254
52 | Sylhet 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 47 | 46 | 46 | 46 | 44 | 43 | 43 | 42 | 42 | 42 | 43 | 14 | 14 |  | 44 | 45 | 45 | 45 | 46 | 46 | 46 | 1021800
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245520
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 |  | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 253056
55 | Fenchugonj 51 MW PP (Barakatullah) | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 13 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 1101600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 567816
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 300 | 310 | 310 | 280 | 290 | 280 | 300 | 325 | 310 | 300 | 320 | 290 | 315 | 310 | 300 | 280 |  | 290 | 290 | 280 | 290 | 300 | 300 | 300 | 7462200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 17 | 17 | 17 | 0 | 0 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 760759
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 19 | 19 | 22 | 22 |  | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 514320
61 | Narshingdi 22 MW PP (Doreen) | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 432180
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 479412
63 | Impoprt (Tripura) | 174 | 164 | 160 | 160 | 142 | 140 | 134 | 138 | 138 | 144 | 144 | 154 | 156 | 162 | 168 | 170 | 164 | 156 |  | 188 | 182 | 188 | 184 | 188 | 188 | 184 | 3922560
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 13 | 5 | 5 | 2 | 4 | 2 | 7 | 2 | 4 | 2 | 2 |  | 19 | 22 | 25 | 26 | 26 | 31 | 39 | 503040
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 459936
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223380
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 8 | 8 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 449780
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 19 | 24 | 24 | 24 | 24 | 24 | 24 | 5423400
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 785200
73 | Ghorashal 108MW PP (Regent)
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 0 | 22 | 92 | 94 | 90 | 91 | 85 | 50 | 50 |  | 72 | 90 | 100 | 100 | 7 | 7 | 7 | 925440
78 | Gazipur 52 MW PP | 52 | 52 | 52 | 52 | 52 | 34 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 46 | 0 | 0 | 2 | 33 |  | 34 | 43 | 43 | 43 | 51 | 52 | 52 | 977424
79 | Kodda 150MW PP | 133 | 133 | 133 | 110 | 84 | 50 | 0 |  | 0 | 16 | 16 | 16 | 32 | 32 | 32 | 100 | 100 | 100 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 1863840
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 89 | 90 | 66 | 75 | 90 | 89 | 90 | 90 | 89 | 89 | 82 | 90 | 90 | 90 | 90 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200320
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 8 | 0 |  |  | 0 | 2 | 2 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 52 | 52 | 52 | 52 | 14 | 8 | 583666
| Gazipur 100 MW PP | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 105 | 105 | 105 | 105 | 105 | 89 | 89 | 106 | 106 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2495784
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0.122 | 0.757 | 3 | 5.57 | 2.65 | 3.17 | 2.13 | 4.94 | 5 | 0.5 | 0.4 | 1.8 | 0 | [8 empty] | 31440
| Jodiac Power | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 0 | [7 empty] | 0 | 993595
| Karnaphuli Power Ltd. | [20 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 80290
82 | Madanganj 102 PP(Summit) | [17 empty] | 0 |  | 15 | 40 | 70 | 100 | 15 | 15 | 15 | 295824
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 0 | 29 | 81 | 100 | 100 | 100 | 50 | 50 | 50 |  | 70 | 89 | 87 | 10 | 10 | 10 | 10 | 935970
86 | Meghnaghat CCPP(Summit) | 282 | 280 | 278 | 284 | 288 | 252 | 270 | 250 | 280 | 285 | 240 | 240 | 240 | 240 | 240 | 280 | 280 | 260 |  | 275 | 253 | 253 | 240 | 278 | 274 | 273 | 6462080
87 | Meghnaghat 100 MW(IEL) | 97 | 100 | 45 | 7 | 7 | 7 | 0 |  |  | 0 | 18 | 87 | 86 | 95 | 98 | 75 | 95 | 75 |  | 85 | 100 | 100 | 100 | 100 | 100 | 100 | 1521600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 50 | 50 | 50 | 10 | 10 |  | 50 | 87 | 100 | 10 | 10 | 10 | 10 | 617400
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 45 | 46 | 46 | 48 | 46 | 46 | 49 | 43 | 10 |  | 26 | 48 | 48 | 48 | 48 | 48 | 48 | 1100736
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1028018
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 90 | 50 | 7 | 7 | 0 |  | 0 | 24 | 24 | 40 | 84 | 92 | 101 | 101 | 101 | 101 | 101 |  | 101 | 101 | 101 | 101 | 102 | 102 | 102 | 1645776
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 48 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1177440
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 92 | 97 | 97 | 12 | 10 | 10 | 10 | 10 | 50 | 79 | 84 | 86 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 1814400
97 | Katpotti 52 MW PP (Sinha) | 17 | 12 | 12 | 12 | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 18 |  | 20 | 34 | 39 | 46 | 46 | 46 | 46 | 491424
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1718400
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 0 | [7 empty] | 0 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 721404
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 0 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1128349
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 163 | 130 | 100 | 100 |  | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 3151669
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.3 | 0.3 | 0.5 | 2 | 2.5 | 2.1 | 0.9 | 0.2 | 1.2 | 1.1 | 0.5 | 0 | [8 empty] | 10900
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1227960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 0 |  | 30 | 30 | 0 |  |  |  | 0 | 40565
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 172 | 55 | 16 | 50 | 58 | 70 | 70 | 70 | 80 | 90 | 90 | 90 | 90 | 100 |  | 139 | 139 | 200 | 170 | 150 | 150 | 150 | 3002400
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 0 |  | 32 | 31 | 0 |  |  |  |  | 37687
114 | Kodda 149 MW PP Unit-1 (Summit) | 135 | 135 | 80 | 18 | 0 |  | 0 | 58 | 90 | 131 | 136 | 136 | 135 | 133 | 95 | 0 | 41 | 112 |  | 127 | 127 | 132 | 134 | 131 | 132 | 132 | 2240640
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2413440
116 | Chandpur 200MW (Desh energy) | 199 | 199 | 199 | 199 | 199 | 185 | 50 | 50 | 50 | 50 | 105 | 70 | 85 | 140 | 140 | 178 | 200 | 200 |  | 200 | 200 | 200 | 200 | 199 | 199 | 199 | 3791520
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 56 | 50 | 10 | 10 | 10 | 10 | 50 | 50 | 50 |  | 94 | 98 | 50 | 50 | 50 | 50 | 50 | 1518836
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 107 | 107 | 107 | 106 | 107 | 107 | 107 | 115 | 106 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2625600
| Anwara 300 MW PP (United) | 107 | 107 | 107 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 106 | 88 | 88 | 88 | 92 | 107 | 107 | 156 |  | 174 | 177 | 177 | 177 | 177 | 177 | 180 | 2792618
120 | Eastern Zone Total | 8182 | 7826 | 7716 | 7542 | 7354 | 6721.122 | 6443.057 | 6463.3 | 6577.07 | 6820.65 | 6997.67 | 7401.23 | 7505.84 | 7480.2 | 7731.7 | 7616.79 | 7416.7 | 7079 |  | 8209 | 8555 | 8622 | 8687 | 8443 | 8403 | 8423 | 189036627
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 83 | 83 | 83 | 83 | 66 | 0 |  |  | 0 | 49 | 49 | 56 | 66 | 66 | 66 | 35 | 40 |  | 99 | 99 | 99 | 115 | 115 | 115 | 115 | 1553280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 0 | [13 empty] | 0 | 6 |  | 31 | 27 | 31 | 30 | 30 | 30 | 30 | 219840
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 89 | 89 | 89 | 89 | 90 | 70 | 53 | 53 | 70 | 70 | 70 | 70 | 70 | 90 | 90 | 70 | 70 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1954560
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 80 | 80 | 16 | 0 |  |  |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1303680
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 98 | 97 | 98 | 95 | 95 | 93 | 96 | 95 | 94 | 91 | 94 | 92 | 93 | 92 | 93 | 93 | 51 | 54 |  | 95 | 96 | 96 | 98 | 96 | 97 | 95 | 2199695
| Bhola 225 MW CCPP | 179 | 179 | 179 | 180 | 179 | 174 | 180 | 169 | 179 | 179 | 180 | 180 | 169 | 172 | 180 | 180 | 180 | 173 |  | 179 | 170 | 169 | 167 | 179 | 176 | 180 | 4337914
140 | Bhola 33 MW PP (Venture) | 38 | 38 | 38 | 38 | 30 | 26 | 26 | 24 | 13 | 14 | 22 | 23 | 26 | 26 | 26 | 25 | 24 | 23 |  | 37 | 37 | 38 | 40 | 40 | 37 | 33 | 683889
141 | Noapara 100 MW PP (Bangla Trac) | 50 | 0 | [15 empty] | 0 |  | 48 | 100 | 100 | 100 | 100 | 100 | 100 | 653760
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 24 | 24 | 24 | 24 | 0 |  |  |  |  | 0 | 16 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 567000
143 | Gopalganj 100 MW Peaking PP | 50 | 2 | 0 | [12 empty] | 0 | 13 | 43 |  | 65 | 60 | 60 | 60 | 60 | 54 | 54 | 447488
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 104 | 104 | 104 | 104 | 104 | 104 | 70 | 69 | 35 | 35 | 35 | 36 | 36 | 36 | 35 | 36 | 35 | 36 |  | 84 | 89 | 92 | 81 | 105 | 105 | 105 | 1688400
146 | Bheramara HVDC | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 908 | 908 | 908 |  | 908 | 906 | 907 | 907 | 907 | 907 | 907 | 21769455
147 | Bheramara 360 MW CCPP | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 300 | 300 | 270 | 300 | 300 | 300 | 340 | 270 | 220 |  | 340 | 340 | 320 | 300 | 330 | 360 | 360 | 7257600
148
149
150 | Barapukuria TPP Unit-1 | 69 | 69 | 69 | 69 | 69 | 69 | 0 | [19 empty] | 401454
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 260 | 217 | 235 | 260 |  | 238 | 230 | 230 | 220 | 220 | 219 | 220 | 6198200
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 50 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1310000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 42 | 42 | 42 | 42 | 0 | [11 empty] | 0 |  | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 485280
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 189 | 180 | 188 | 189 | 194 | 188 | 166 | 189 | 198 | 203 | 202 | 198 | 201 | 202 | 203 | 205 | 202 | 188 |  | 195 | 209 | 200 | 205 | 207 | 200 | 201 | 5022800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 188 | 195 | 195 | 201 | 191 | 198 | 172 | 167 | 184 | 203 | 177 | 180 | 171 | 195 | 204 | 188 | 172 |  | 190 | 208 | 208 | 207 | 208 | 208 | 201 | 4828473
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 300 | 360 | 360 | 320 | 250 |  | 350 | 350 | 350 | 370 | 370 | 416 | 421 | 7924545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 25 | 25 | 16 | 0 | [12 empty] | 0 | 5 |  | 30 | 31 | 31 | 31 | 31 | 24 | 24 | 224365
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 18 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503040
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 217872
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 227214
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 473580
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 25 | 25 | 25 | 25 | 25 | 15 | 25 | 25 | 25 | 25 | 25 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 813475
167 | Katakhali 50 MW Peaking PP | 44 | 0 | [15 empty] | 0 |  | 38 | 38 | 39 | 37 | 37 | 36 | 36 | 271982
168 | Santahar 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 0 | [11 empty] | 0 |  | 27 | 30 | 27 | 27 | 20 | 21 | 22 | 229040
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 16 | 0 |  |  |  |  | 0 | 8 | 8 | 8 | 25 | 25 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 670560
170 | Chapainawabganj 100 MW Peaking PP | 94 | 94 | 94 | 94 | 94 | 94 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 94 | 94 | 94 | 94 | 94 | 92 | 92 | 1356404
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2741184
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 15 | 15 | 15 | 0 | [13 empty] | 0 |  | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 131000
176 | Rangpur 113 MW PP (Confidence) | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 113 | 113 | 106 | 107 | 107 | 114 | 113 | 108 |  | 111 | 113 | 111 | 111 | 111 | 111 | 111 | 2687040
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3.7 | 2.6 | 3.8 | 6 | 7 | 6.5 | 5.8 | 3.96 | 1.92 | 0 | [8 empty] | 43175
178
178