## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-23 | Tuesday
|  | Date (day): | 2020-06-23 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12718.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14198 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-22 | 2020-06-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 260 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 65 | 66 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 101 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 26/06/2020
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 347 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 260 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 97 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 94 | 100 | 100 | 110 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 97 | 98 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 212 | 220 | 220 |  | 115 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 68 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 48 | 48 | 51
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 0 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 6 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 194 | 270 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 130 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 108 | 88 | 88 |  | 17 | Engine problem
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 2712 | 3208 | 3762 | 4099 | 323 | 1294
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 90 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10.8 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 99 | 100 | 100 | 130 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 139 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 34 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 10 | 35
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 31 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.8 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 288 | 308 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 3 | 54 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 863.6 | 1139 | 1402 | 1546 | 390 | 225
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 120 | 100 | 100 | 35 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 120 | 100 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 198 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 345 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 38 | 38 | 38 |  | 7 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 20 | 50 | 50
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 55 | 55 | 140 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 25 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 23 | 143 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 0 | 162 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 32 | 32
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 20 | 21
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 54 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 73 | 95 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1071 | 1516 | 1996 | 2169 | 358 | 88
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 134 | 133 | 150 | 150 | 52 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 40 | 72 | 60 | 95
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.6 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 53 | 170 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 365.6 | 510 | 518.6 | 582 | 52 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 60 | 60 | 60
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 250 | 317 | 330 | 330
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 42 | 40 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 59 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 79 | 76 | 76
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 295 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1230 | 1282 | 1369 | 1375 | 0 | 460
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 943 | 947 | 959 | 959
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 24 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 21 | 0 | 30
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 285 | 275 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 33 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 67 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1285 | 1655 | 1789 | 2165 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 50 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 31 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 68 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 76 | 79 | 78 | 78 |  | 17 | Engine problem
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 600 | 450 | 0 | 0 |  |  | Under S/D
| Barisal GT PP Unit-1& 2 |  | HSD | PDB |  |  |  |  | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 775 | 724 | 226 | 289 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 43 | 43
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 163 | 177 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 166 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 404 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 20 | 21
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 50 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 778 | 1186 | 1428 | 1690 | 381 | 19
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 40 | 107 | 70 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 196.7 | 256 | 228 | 283 | 170 | 0
| Total |  |  |  |  | 20279 | 19788 | 9276.9 | 11476 | 12718.6 | 14198 | 1674 | 2229
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8868.6711 | 10971 | 12158.9195 | 13573.2187
A. |  | 2020-06-22 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11501 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7985.1 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11476 | MW
3 | Day peak Generation : |  |  | 9276.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10971 | MW
4 | Evening peak Generation : |  |  | 11476 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 232.6142 | MKWHr | By Solar | 0.17046 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 131.7114 | MKWHr |  | By Oil: | 59.416 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 14.1738 | MKWHr |  | By Hydro: | 2.2887 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1674 | MW | Dhaka | 3678 | 3678 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2229 | MW | Chittagong | 1072 | 1072 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3903 | MW | Khulna | 1469 | 1469 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1132.68 | MMCFD |  |  | Rajshahi | 1221 | 1221 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 155269411.056 | ii) Oil : | Taka | 444062369.6 | Comilla | 1069 | 1069 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 66004421 | Total | Taka | 665336201.656 | Mymensingh | 915 | 915 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.4025 | MKWHr. | Sylhet | 462 | 462 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -157 | MW (E to W) at | 21:00 | hrs | Barisal | 334 | 334 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -293 | MW at | 24:00 | hrs | Rangpur | 751 | 751 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 10971 | 10971 |  | 0
B. |  | 2020-06-23 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14198 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 2498 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 236.6391 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8500.1 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.6538 | MKWHr. | ii) HVDC Flow at Peak Time |  | 947 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2 | MKWHr. | iii) Maximum HVDC Flow : |  | 949 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.99 |  | (b) Today: | 84 |  | (c) Rule Curve: |  | 81.84
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-06-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 99 | 69 | 0 | 354 |  | 0 | 420 | 250 | 100 | 97 | 41 | 216 | 0 | 96 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 34 | 20 | 25 | 135 | 120 | 0 | 310 | 0 | 182 | 8 | 90 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 114 | 139 | 48 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 247 | 61 | 77 | 0 | 150 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 252 | 0 | 0 | 200 | 0 | 132 | 0 | 100 | 0 | 148 | 0 | 108 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 947 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 28 | 96 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 12 | 0 | 0 | 188 | 0 | 78 | 0 | 187 | 0 | 414 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 197 |  | 7034 | 3133 | 10167 | 3526 | 947 | 2192 | 2793 | 346 | 100 | 149 | 114 | 0 | 0 | 83.99
2:00 | 35 | 0 | 0 | 0 | 300 | 99 | 68 | 0 | 353 |  | 0 | 420 | 260 | 100 | 97 | 30 | 218 | 0 | 95 | 0 | 99 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 20 | 32 | 100 | 120 | 0 | 310 | 0 | 165 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 124 | 140 | 40 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 251 | 61 | 77 | 0 | 150 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 252 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 100 | 0 | 107 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 |  | 948 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 78 | 0 | 187 | 0 | 418 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 300 |  | 6883 | 3037 | 9920 | 3485 | 948 | 2210 | 2516 | 449 | 98 | 90 | 124 | 0 | 0 | 83.99
3:00 | 35 | 0 | 0 | 0 | 300 | 99 | 69 | 0 | 352 |  | 0 | 390 | 260 | 100 | 97 | 30 | 215 | 0 | 63 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 32 | 80 | 120 | 0 | 345 | 0 | 182 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 118 | 139 | 40 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 260 | 61 | 77 | 0 | 150 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 130 | 0 | 0 | 200 | 0 | 133 | 0 | 100 | 0 | 50 | 0 | 107 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 |  | 941 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 78 | 0 | 187 | 0 | 413 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 349 |  | 6611 | 3026 | 9637 | 3502 | 941 | 2170 | 2303 | 498 | 97 | 8 | 118 | 0 | 0 | 83.99
4:00 | 35 | 0 | 0 | 0 | 300 | 96 | 69 | 0 | 351 |  | 0 | 420 | 265 | 100 | 97 | 15 | 180 | 0 | 94 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 62 | 35 | 95 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 80 | 120 | 0 | 345 | 0 | 181 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 110 | 139 | 40 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 252 | 61 | 77 | 0 | 150 | 0 | 0 | 10 | 315 | 24 | 11 | 0 | 130 | 0 | 0 | 160 | 0 | 132 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 84 | 100 | 0 |  | 941 | 0 | 345 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 202 | 0 | 76 | 0 | 187 | 0 | 410 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 350 |  | 6486 | 2923 | 9409 | 3484 | 941 | 2200 | 2078 | 499 | 97 | 0 | 110 | 0 | 0 | 83.99
5:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 355 |  | 0 | 420 | 260 | 100 | 97 | 15 | 220 | 0 | 91 | 0 | 99 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 35 | 95 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 80 | 120 | 0 | 310 | 0 | 187 | 8 | 80 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 98 | 141 | 40 | 22 | 0 | 59 | 30 | 50 | 43 | 130 | 248 | 62 | 77 | 0 | 150 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 70 | 100 | 0 |  | 941 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 64 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 197 | 0 | 76 | 0 | 187 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 |  | 6355 | 2846 | 9201 | 3466 | 941 | 2185 | 1915 | 498 | 98 | 0 | 98 | 0 | 0 | 83.99
6:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 329 |  | 0 | 390 | 260 | 60 | 30 | 15 | 218 | 0 | 96 | 0 | 60 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 95 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 33 | 80 | 120 | 0 | 310 | 0 | 184 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 80 | 140 | 40 | 22 | 0.1 | 59 | 30 | 50 | 43 | 100 | 252 | 61 | 77 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 1.9 | 40 | 0 | 0 | 0 | 115 | 0 | 0 | 0.2 | 142 | 0 | 0 | 0 | 0 | 100 | 0 |  | 941 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 77 | 0 | 187 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 401 |  | 5409.2 | 2825.2 | 8234.4 | 3469 | 941 | 2089 | 1004 | 550 | 99 | 0 | 80 | 2.4 | 0 | 83.99
7:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 309 |  | 0 | 360 | 260 | 7 | 30 | 0 | 216 | 0 | 95 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 35 | 95 | 0 | 16 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 80 | 120 | 0 | 330 | 0 | 173 | 8 | 91 | 38 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 14 | 96 | 139 | 40 | 22 | 0.2 | 59 | 30 | 50 | 43 | 100 | 257 | 60 | 74 | 0 | 150 | 0 | 0 | 10 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6.2 | 20 | 0 | 0 | 0 | 115 | 0 | 0 | 1.5 | 141 | 0 | 0 | 0 | 0 | 70 | 0 |  | 941 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 76 | 0 | 187 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 400 |  | 5169.9 | 2815.2 | 7985.1 | 3469 | 941 | 2030 | 793 | 549 | 98 | 0 | 96 | 9.1 | 0 | 84
8:00 | 35 | 0 | 0 | 0 | 300 | 95 | 68 | 0 | 309 |  | 0 | 390 | 275 | 7 | 30 | 0 | 217 | 0 | 95 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 35 | 95 | 0 | 16 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 80 | 120 | 0 | 335 | 0 | 155 | 8 | 92 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 14 | 102 | 139 | 40 | 22 | 0.7 | 59 | 30 | 47 | 43 | 100 | 255 | 61 | 74 | 0 | 150 | 0 | 0 | 10 | 320 | 24 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5.7 | 50 | 0 | 0 | 0 | 115 | 0 | 0 | 2 | 142 | 0 | 0 | 0 | 0 | 100 | 0 |  | 941 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 203 | 0 | 77 | 0 | 187 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 495 |  | 5271.4 | 2925 | 8196.4 | 3465 | 941 | 2065 | 869 | 645 | 98 | 0 | 102 | 11.4 | 0 | 84
9:00 | 35 | 0 | 0 | 0 | 300 | 96 | 68 | 0 | 351 |  | 0 | 420 | 285 | 14 | 30 | 0 | 215 | 0 | 37 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 95 | 0 | 8 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 80 | 120 | 0 | 335 | 0 | 189 | 8 | 91 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 106 | 139 | 40 | 22 | 0.5 | 59 | 30 | 47 | 43 | 130 | 262 | 59 | 77 | 0 | 150 | 0 | 0 | 10 | 320 | 24 | 5 | 0 | 9 | 0 | 0 | 0 | 0 | 88 | 6.5 | 98 | 0 | 0 | 0 | 115 | 0 | 0 | 4.3 | 215 | 0 | 0 | 0 | 0 | 100 | 0 |  | 941 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 206 | 0 | 79 | 0 | 186 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 | 550 |  | 5530.3 | 2952.4 | 8482.7 | 3407 | 941 | 2156 | 1059 | 700 | 99 | 0 | 106 | 14.7 | 0 | 84
10:00 | 35 | 0 | 0 | 0 | 300 | 96 | 67 | 0 | 349 |  | 0 | 450 | 270 | 68 | 40 | 20 | 180 | 0 | 37 | 0 | 60 | 64 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 95 | 0 | 8 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 80 | 120 | 0 | 310 | 0 | 198 | 8 | 91 | 33 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 104 | 137 | 40 | 22 | 1.9 | 58 | 30 | 47 | 43 | 163 | 252 | 59 | 76 | 0 | 150 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 31 | 0 | 0 | 19 | 0 | 116 | 11.3 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 4 | 252 | 0 | 0 | 0 | 2 | 100 | 0 |  | 941 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 202 | 0 | 79 | 0 | 185 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0 | 604 |  | 5831.2 | 3043.2 | 8874.4 | 3317 | 941 | 2214 | 1424 | 754 | 99 | 0 | 104 | 21.4 | 0 | 84
11:00 | 35 | 0 | 0 | 0 | 300 | 96 | 66 | 0 | 349 |  | 0 | 450 | 255 | 100 | 60 | 41 | 180 | 0 | 37 | 0 | 95 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 0 | 25 | 30 | 33 | 25 | 0 | 0 | 65 | 35 | 95 | 0 | 8 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 80 | 120 | 0 | 360 | 0 | 191 | 8 | 87 | 36 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 0 | 136 | 40 | 22 | 0 | 58 | 30 | 47 | 42 | 163 | 248 | 59 | 76 | 0 | 150 | 0 | 0 | 9 | 305 | 24 | 5 | 0 | 91 | 0 | 0 | 40 | 0 | 129 | 19.7 | 100 | 0 | 3 | 0 | 115 | 0 | 0 | 6.1 | 252 | 0 | 0 | 0 | 37 | 100 | 0 |  | 941 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 78 | 0 | 170 | 0 | 408 | 0 | 0 | 0 | 0 | 14 | 0 | 6.8 | 0 | 580 |  | 6046.8 | 2968.8 | 9015.6 | 3294 | 941 | 2199 | 1719 | 730 | 100 | 0 | 0 | 32.6 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 94 | 65 | 0 | 347 |  | 0 | 450 | 265 | 100 | 80 | 41 | 180 | 0 | 37 | 0 | 97 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 6 | 0 | 25 | 30 | 8 | 25 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 80 | 120 | 0 | 315 | 0 | 201 | 8 | 90 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 20 | 8 | 25 | 18 | 0 | 134 | 40 | 22 | 1.6 | 57 | 30 | 47 | 42 | 163 | 250 | 59 | 76 | 0 | 150 | 0 | 0 | 9 | 315 | 24 | 8 | 0 | 194 | 0 | 0 | 53 | 0 | 132 | 10.8 | 100 | 0 | 23 | 0 | 115 | 0 | 0 | 5.8 | 288 | 3 | 0 | 0 | 73 | 100 | 0 |  | 943 | 0 | 285 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 76 | 0 | 173 | 0 | 409 | 0 | 0 | 0 | 0 | 40 | 0 | 6.7 | 0 | 600 |  | 6242.2 | 3034.7 | 9276.9 | 3231 | 943 | 2204 | 2024 | 750 | 100 | 0 | 0 | 24.9 | 0 | 84
13:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 347 |  | 0 | 450 | 265 | 100 | 85 | 41 | 180 | 0 | 37 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 0 | 25 | 20 | 33 | 25 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 80 | 120 | 0 | 315 | 0 | 196 | 8 | 90 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 60 | 133 | 40 | 20 | 1.2 | 57 | 30 | 50 | 42 | 163 | 208 | 59 | 76 | 0 | 150 | 0 | 0 | 9 | 310 | 24 | 8 | 0 | 265 | 0 | 0 | 64 | 0 | 133 | 5 | 100 | 0 | 55 | 0 | 115 | 0 | 0 | 0.2 | 306 | 17 | 0 | 0 | 105 | 100 | 0 |  | 943 | 0 | 270 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 170 | 0 | 400 | 0 | 0 | 0 | 0 | 70 | 0 | 7.2 | 0 | 600 |  | 6461.4 | 3090.2 | 9551.6 | 3197 | 943 | 2199 | 2273 | 750 | 101 | 15 | 60 | 13.6 | 0 | 84
14:00 | 35 | 0 | 0 | 0 | 300 | 95 | 67 | 0 | 322 |  | 0 | 420 | 280 | 100 | 80 | 41 | 206 | 0 | 0 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 21 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 6 | 80 | 120 | 0 | 345 | 0 | 198 | 8 | 90 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 68 | 120 | 40 | 20 | 2.2 | 58 | 30 | 50 | 42 | 130 | 155 | 57 | 74 | 0 | 150 | 0 | 0 | 10 | 305 | 24 | 8 | 0 | 260 | 0 | 0 | 80 | 0 | 132 | 7.9 | 100 | 0 | 85 | 0 | 115 | 0 | 0 | 1.8 | 307 | 17 | 0 | 0 | 105 | 100 | 0 |  | 944 | 0 | 260 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 64 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 77 | 0 | 170 | 0 | 402 | 0 | 0 | 0 | 0 | 80 | 0 | 7.2 | 0 | 601 |  | 6461.9 | 3115.2 | 9577.1 | 3167 | 944 | 2116 | 2372 | 751 | 99 | 41 | 68 | 19.1 | 0 | 84
15:00 | 35 | 0 | 0 | 0 | 300 | 96 | 65 | 0 | 344 |  | 0 | 450 | 285 | 100 | 80 | 41 | 210 | 0 | 37 | 0 | 97 | 67 | 0 | 8 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 20 | 0 | 3 | 20 | 2 | 100 | 100 | 0 | 310 | 0 | 177 | 8 | 85 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 0 | 122 | 120 | 40 | 20 | 1.8 | 58 | 30 | 50 | 42 | 163 | 145 | 60 | 76 | 0 | 150 | 0 | 0 | 10 | 310 | 16 | 9 | 0 | 264 | 0 | 0 | 100 | 0 | 131 | 15.7 | 100 | 0 | 105 | 0 | 115 | 4 | 0 | 3 | 308 | 30 | 0 | 0 | 104 | 100 | 0 |  | 944 | 0 | 250 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 79 | 0 | 167 | 0 | 409 | 0 | 0 | 11 | 0 | 113 | 0 | 6.6 | 0 | 629 |  | 6611.5 | 3267.6 | 9879.1 | 3094 | 944 | 2211 | 2554 | 779 | 98 | 50 | 122 | 27.1 | 0 | 84
16:00 | 35 | 0 | 0 | 0 | 300 | 96 | 65 | 0 | 341 |  | 0 | 450 | 270 | 100 | 79 | 41 | 212 | 0 | 32 | 0 | 97 | 67 | 0 | 10 | 0 | 0 | 11 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 20 | 0 | 12 | 20 | 5 | 100 | 100 | 0 | 310 | 0 | 201 | 8 | 80 | 35 | 40 | 0 | 25 | 0 | 0 | 10 | 20 | 8 | 25 | 5 | 122 | 124 | 68 | 20 | 0.5 | 60 | 30 | 50 | 42 | 110 | 162 | 51 | 76 | 0 | 150 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 264 | 0 | 0 | 40 | 0 | 132 | 8.6 | 100 | 0 | 125 | 0 | 115 | 17 | 0 | 0.2 | 270 | 54 | 0 | 0 | 104 | 100 | 0 |  | 944 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 78 | 0 | 166 | 0 | 397 | 0 | 0 | 35 | 0 | 88 | 0 | 3.6 | 0 | 450 |  | 6603.3 | 3074.6 | 9677.9 | 3135 | 944 | 2155 | 2563 | 600 | 96 | 50 | 122 | 12.9 | 0 | 84
17:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 314 |  | 0 | 450 | 260 | 100 | 82 | 30 | 212 | 0 | 32 | 0 | 97 | 67 | 0 | 10 | 0 | 0 | 14 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 11 | 12 | 20 | 10 | 100 | 100 | 0 | 310 | 0 | 182 | 8 | 85 | 37 | 40 | 0 | 25 | 0 | 0 | 8 | 21 | 8 | 25 | 21 | 110 | 139 | 64 | 20 | 0.5 | 60 | 30 | 50 | 10 | 110 | 199 | 52 | 77 | 0 | 100 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 8 | 0 | 118 | 2.5 | 100 | 0 | 60 | 0 | 75 | 17 | 0 | 0.4 | 248 | 17 | 0 | 0 | 84 | 100 | 0 |  | 948 | 0 | 250 | 0 | 49 | 0 | 0 | 0 | 0 | 1 | 40 | 65 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 77 | 0 | 166 | 0 | 345 | 0 | 0 | 35 | 0 | 48 | 0 | 0.1 | 0 | 450 |  | 6216.4 | 2914.1 | 9130.5 | 3142 | 948 | 2037 | 2143 | 600 | 96 | 51 | 110 | 3.5 | 0 | 84
18:00 | 35 | 0 | 0 | 0 | 260 | 23 | 40 | 0 | 252 |  | 0 | 350 | 260 | 70 | 90 | 30 | 180 | 0 | 33 | 0 | 60 | 68 | 0 | 10 | 0 | 0 | 14 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 62 | 35 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 30 | 12 | 20 | 12 | 100 | 100 | 0 | 290 | 0 | 183 | 8 | 90 | 37 | 10 | 0 | 25 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 114 | 138 | 64 | 20 | 0.1 | 60 | 30 | 14 | 10 | 110 | 288 | 40 | 10 | 0 | 70 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 200 | 0 | 0 | 8 | 0 | 101 | 0.4 | 100 | 0 | 60 | 0 | 75 | 17 | 0 | 0.1 | 105 | 17 | 0 | 0 | 55 | 100 | 0 |  | 949 | 0 | 270 | 0 | 30 | 0 | 0 | 0 | 2 | 3 | 40 | 68 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 34 | 0 | 167 | 0 | 367 | 0 | 0 | 35 | 0 | 35 | 0 | 0.2 | 0 | 448 |  | 5488.6 | 2884.2 | 8372.8 | 3072 | 949 | 1604 | 1883 | 598 | 97 | 55 | 114 | 0.8 | 0 | 84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 260 | 54 | 40 | 0 | 275 |  | 0 | 350 | 285 | 77 | 95 | 30 | 200 | 0 | 65 | 0 | 70 | 68 | 55 | 35 | 0 | 0 | 13 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 2 | 0 | 62 | 35 | 90 | 0 | 2 | 0 | 0 | 145 | 0 |  | 0 | 0 | 74 | 10 | 30 | 16 | 20 | 17 | 100 | 100 | 0 | 320 | 0 | 209 | 8 | 90 | 38 | 10 | 0 | 25 | 0 | 0 | 8 | 21 | 8 | 8 | 21 | 150 | 138 | 48 | 20 | 0 | 59 | 30 | 14 | 21 | 163 | 319 | 59 | 10 | 0 | 70 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 215 | 0 | 0 | 16 | 0 | 102 | 0 | 100 | 10 | 72 | 0 | 98 | 32 | 5 | 0 | 155 | 24 | 0 | 17 | 62 | 100 | 0 |  | 948 | 0 | 275 | 0 | 69 | 0 | 0 | 0 | 21 | 6 | 40 | 65 | 25 | 66 | 0 | 0 | 0 | 17 | 8 | 75 | 0 | 8 | 20 | 23 | 32 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 34 | 0 | 166 | 0 | 395 | 43 | 0 | 42 | 15 | 56 | 0 | 0 | 15 | 450 |  | 6210 | 3243 | 9453 | 3236 | 948 | 1777 | 2337 | 600 | 97 | 308 | 150 | 0 | 0 | 84
19:30 | 35 | 0 | 0 | 0 | 260 | 92 | 66 | 0 | 354 |  | 0 | 450 | 240 | 100 | 97 | 55 | 215 | 0 | 33 | 0 | 88 | 68 | 64 | 100 | 0 | 0 | 13 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 25 | 0 | 63 | 35 | 90 | 0 | 8 | 0 | 0 | 104 | 0 |  | 0 | 0 | 102 | 10 | 42 | 50 | 20 | 10 | 100 | 100 | 0 | 265 | 0 | 216 | 8 | 82 | 38 | 10 | 0 | 25 | 0 | 14 | 12 | 21 | 8 | 25 | 21 | 160 | 140 | 60 | 20 | 0 | 60 | 30 | 50 | 40 | 110 | 300 | 40 | 79 | 0 | 131 | 0 | 0 | 10 | 275 | 24 | 0 | 0 | 268 | 0 | 0 | 110 | 26 | 110 | 0 | 100 | 34 | 148 | 0 | 115 | 70 | 34 | 0 | 304 | 27 | 0 | 114 | 104 | 100 | 0 |  | 948 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 57 | 30 | 96 | 0 | 0 | 0 | 17 | 10 | 10 | 0 | 24 | 35 | 43 | 33 | 19 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 73 | 100 | 165 | 0 | 302 | 90 | 0 | 105 | 67 | 107 | 0 | 0 | 70 | 440 |  | 7315 | 3624 | 10939 | 3173 | 948 | 2014 | 3652 | 590 | 98 | 304 | 160 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 260 | 100 | 66 | 0 | 352 |  | 0 | 450 | 260 | 100 | 97 | 55 | 180 | 0 | 32 | 0 | 88 | 68 | 64 | 95 | 0 | 0 | 26 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 35 | 0 | 62 | 35 | 90 | 0 | 8 | 0 | 0 | 104 | 0 |  | 0 | 0 | 102 | 0 | 50 | 47 | 20 | 18 | 120 | 100 | 0 | 260 | 0 | 181 | 8 | 80 | 38 | 20 | 0 | 25 | 0 | 16 | 25 | 21 | 8 | 25 | 21 | 160 | 140 | 72 | 20 | 0 | 60 | 30 | 50 | 40 | 110 | 288 | 40 | 79 | 0 | 140 | 0 | 0 | 10 | 275 | 24 | 0 | 0 | 270 | 0 | 0 | 140 | 0 | 122 | 0 | 100 | 17 | 132 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 114 | 104 | 100 | 0 |  | 946 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 63 | 30 | 96 | 0 | 0 | 0 | 17 | 26 | 100 | 0 | 24 | 40 | 43 | 34 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 82 | 81 | 166 | 0 | 313 | 90 | 0 | 110 | 67 | 107 | 0 | 0 | 70 | 438 |  | 7401 | 3752 | 11153 | 3135 | 946 | 2059 | 3750 | 588 | 97 | 418 | 160 | 0 | 0 | 84
21:00 | 35 | 0 | 0 | 0 | 260 | 101 | 66 | 0 | 347 |  | 0 | 450 | 260 | 100 | 97 | 55 | 212 | 0 | 94 | 0 | 98 | 68 | 64 | 100 | 0 | 0 | 48 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 31 | 50 | 20 | 12 | 120 | 100 | 0 | 345 | 0 | 198 | 8 | 91 | 38 | 20 | 0 | 25 | 0 | 8 | 34 | 21 | 8 | 25 | 21 | 162 | 133 | 72 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 317 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 295 | 24 | 5 | 0 | 270 | 0 | 0 | 170 | 0 | 130 | 0 | 100 | 0 | 143 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 54 | 95 | 100 | 0 |  | 947 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 21 | 0 | 40 | 68 | 31 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 100 | 166 | 0 | 404 | 90 | 0 | 113 | 67 | 107 | 0 | 0 | 70 | 450 |  | 7655 | 3821 | 11476 | 3447 | 947 | 2212 | 3645 | 599 | 99 | 365 | 162 | 0 | 0 | 84
22:00 | 35 | 0 | 0 | 0 | 260 | 101 | 66 | 0 | 349 |  | 0 | 450 | 260 | 100 | 97 | 55 | 214 | 0 | 94 | 0 | 98 | 102 | 64 | 70 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 31 | 50 | 20 | 19 | 120 | 100 | 0 | 310 | 0 | 192 | 8 | 91 | 38 | 20 | 0 | 25 | 0 | 12 | 34 | 21 | 8 | 25 | 21 | 166 | 135 | 40 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 302 | 60 | 79 | 0 | 150 | 0 | 0 | 10 | 320 | 24 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 130 | 0 | 100 | 0 | 148 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 54 | 101 | 100 | 0 |  | 943 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 21 | 0 | 40 | 67 | 31 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 100 | 166 | 0 | 408 | 90 | 0 | 113 | 67 | 106 | 0 | 0 | 70 | 450 |  | 7686 | 3815 | 11501 | 3396 | 943 | 2250 | 3678 | 600 | 99 | 369 | 166 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 260 | 102 | 68 | 0 | 354 |  | 0 | 450 | 260 | 100 | 97 | 55 | 218 | 0 | 97 | 0 | 98 | 102 | 64 | 69 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 7 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 20 | 49 | 50 | 20 | 23 | 135 | 100 | 0 | 310 | 0 | 181 | 8 | 82 | 38 | 20 | 0 | 25 | 0 | 16 | 43 | 21 | 8 | 25 | 21 | 162 | 140 | 32 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 294 | 63 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 0 | 0 | 185 | 0 | 132 | 0 | 100 | 2 | 148 | 0 | 115 | 108 | 34 | 0 | 307 | 54 | 0 | 102 | 105 | 100 | 0 |  | 943 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 21 | 0 | 40 | 62 | 33 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 100 | 165 | 0 | 374 | 105 | 0 | 113 | 105 | 107 | 0 | 0 | 70 | 302 |  | 7782 | 3683 | 11465 | 3392 | 943 | 2195 | 3847 | 452 | 101 | 373 | 162 | 0 | 0 | 84
24:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 353 |  | 0 | 400 | 260 | 100 | 97 | 41 | 218 | 0 | 35 | 0 | 99 | 102 | 64 | 100 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 26 | 33 | 25 | 52 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 102 | 20 | 95 | 50 | 20 | 28 | 135 | 100 | 0 | 310 | 0 | 181 | 8 | 87 | 41 | 51 | 0 | 25 | 0 | 16 | 52 | 21 | 8 | 25 | 20 | 90 | 140 | 32 | 20 | 0 | 58 | 30 | 50 | 37 | 163 | 292 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 0 | 0 | 190 | 0 | 130 | 0 | 100 | 17 | 147 | 0 | 108 | 108 | 34 | 0 | 307 | 54 | 0 | 102 | 105 | 100 | 0 |  | 943 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 67 | 34 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 70 | 165 | 0 | 355 | 105 | 0 | 113 | 105 | 108 | 0 | 0 | 70 | 199 |  | 7716 | 3536 | 11252 | 3297 | 943 | 2155 | 3946 | 349 | 101 | 371 | 90 | 0 | 0 | 76.33
KWH | 765000 | 0 | 0 | 0 | 6974791 | 2190227 | 1516256 | 0 | 8055000 |  | 0 | 9658500 | 6437993 | 2048640 | 1939968 | 816153 | 5116875 | 0 | 1631000 | 0 | 1971840 | 1841184 | 401280 | 530296 | 0 | 0 | 274992 | 1065240 | 1030918 | 694721 | 374544 | 600000 | 661860 | 781600 | 638900 | 115068 | 0 | 1444664 | 844000 | 2200000 | 0 | 91873 | 0 | 0 | 3248474 | 0 |  | 0 | 0 | 645617 | 99960 | 342720 | 342240 | 464832 | 420960 | 2402298 | 2661755 | 0 | 7955600 | 0 | 4546000 | 200727 | 2105540 | 841464 | 722880 | 0 | 629064 | 0 | 69448 | 240677 | 494244 | 188280 | 585600 | 488920 | 2200000 | 3177120 | 1152000 | 433980 | 12800 | 1391000 | 719880 | 1119600 | 955008 | 3293182 | 5624000 | 1375104 | 1717440 | 0 | 3427750 | 15000 | 0 | 232200 | 7506200 | 558672 | 194112 | 0 | 4413489 | 0 | 0 | 2373600 | 16947 | 2903040 | 87885 | 2230080 | 72480 | 1709527 | 0 | 2628000 | 607848 | 192363 | 26280 | 6272727 | 476390 | 0 | 376200 | 1768200 | 2378880 | 0 |  | 22653818 | 0 | 7422336 | 0 | 1315200 | 0 | 0 | 0 | 111840 | 10624 | 768375 | 1560000 | 541720 | 922176 | 0 | 0 | 30000 | 33091 | 26117 | 913968 | 0 | 23371 | 169175 | 219360 | 212669 | 479280 | 237852 | 170838 | 0 | 0 | 3671300 | 0 | 17000 | 0 | 0 | 4558927 | 0 | 1811045 | 526080 | 4459109 | 0 | 9578872 | 480480 | 0 | 826272 | 420480 | 1469760 | 0 | 43494 | 377376 | 10502500 |  | 156049667 | 76564505 | 232614172 | 80845405 | 22653818 | 50866013 | 56805184 | 14173800 | 2288664 | 2610829 | 2200000 | 170459 | 0
Fuel Cost | 1254600 | 0 | 0 | 0 | 7742018.01 | 2891099.64 | 2577635.2 | 0 | 8296650 |  | 0 | 10527765 | 7146172.23 | 15549177.6 | 13366379.52 | 6904654.38 | 5321550 | 0 | 2821630 | 0 | 14847955.2 | 16791598.08 | 3948595.2 | 4889329.12 | 0 | 0 | 2499677.28 | 7776252 | 7968996.14 | 6849949.06 | 280908 | 450000 | 0 | 0 | 0 | 1112707.56 | 0 | 390059.28 | 227880 | 3982000 | 0 | 853500.17 | 0 | 0 | 5522405.8 | 0 |  | 0 | 0 | 6262484.9 | 954618 | 2981664 | 2710540.8 | 585688.32 | 1250251.2 | 3555401.04 | 3939397.4 | 0 | 5887144 | 0 | 4182320 | 258937.83 | 2421371 | 950854.32 | 1012032 | 0 | 1075699.44 | 0 | 701424.8 | 2298465.35 | 627689.88 | 141210 | 1024800 | 366690 | 16500000 | 3367747.2 | 10460160 | 551154.6 | 204032 | 2281240 | 1151808 | 1992888 | 1489812.48 | 3754227.48 | 5848960 | 2708954.88 | 3280310.4 | 0 | 5930007.5 | 32850 | 0 | 473688 | 7581262 | 419004 | 147525.12 | 0 | 33365976.84 | 0 | 0 | 12342720 | 283353.84 | 28565913.6 | 1027375.65 | 18175152 | 786408 | 12052165.35 | 0 | 23967360 | 5744163.6 | 1675481.73 | 0 | 47421816.12 | 4149356.9 | 0 | 3754476 | 15153474 | 15843340.8 | 0 |  | 130485991.68 | 0 | 7793452.8 | 0 | 10337472 | 0 | 0 | 0 | 1173201.6 | 111339.52 | 8006467.5 | 1762800 | 839666 | 9000437.76 | 0 | 0 | 61500 | 325615.44 | 265348.72 | 8088616.8 | 0 | 315975.92 | 1639305.75 | 2125598.4 | 2062889.3 | 920217.6 | 368670.6 | 129324.366 | 0 | 0 | 19898446 | 0 | 485010 | 0 | 0 | 6017783.64 | 0 | 2716567.5 | 8948620.8 | 5217157.53 | 0 | 9483083.28 | 5016211.2 | 0 | 7841321.28 | 3969331.2 | 11405337.6 | 0 | 480608.7 | 2788808.64 | 46105975 |  | 498463994.84 | 316188154.126 | 814652148.966 | 94478947.406 | 130485991.68 | 60790463.65 | 418998537.57 | 66004421 | 617939.28 | 25063832.03 | 16500000 | 1712016.35 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 94 | 65 | 0 | 347 |  | 0 | 450 | 265 | 100 | 80 | 41 | 180 | 0 | 37 | 0 | 97 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 6 | 0 | 25 | 30 | 8 | 25 | 0 | 0 | 65 | 35 | 95 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 80 | 120 | 0 | 315 | 0 | 201 | 8 | 90 | 35 | 30 | 0 | 25 | 0 | 0 | 0 | 20 | 8 | 25 | 18 | 0 | 134 | 40 | 22 | 1.6 | 57 | 30 | 47 | 42 | 163 | 250 | 59 | 76 | 0 | 150 | 0 | 0 | 9 | 315 | 24 | 8 | 0 | 194 | 0 | 0 | 53 | 0 | 132 | 10.8 | 100 | 0 | 23 | 0 | 115 | 0 | 0 | 5.8 | 288 | 3 | 0 | 0 | 73 | 100 | 0 |  | 943 | 0 | 285 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 76 | 0 | 173 | 0 | 409 | 0 | 0 | 0 | 0 | 40 | 0 | 6.7 | 0 | 600 |  | 9276.9 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 260 | 101 | 66 | 0 | 347 | 0 | 0 | 450 | 260 | 100 | 97 | 55 | 212 | 0 | 94 | 0 | 98 | 68 | 64 | 100 | 0 | 0 | 48 | 0 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 64 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 102 | 0 | 31 | 50 | 20 | 12 | 120 | 100 | 0 | 345 | 0 | 198 | 8 | 91 | 38 | 20 | 0 | 25 | 0 | 8 | 34 | 21 | 8 | 25 | 21 | 162 | 133 | 72 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 317 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 295 | 24 | 5 | 0 | 270 | 0 | 0 | 170 | 0 | 130 | 0 | 100 | 0 | 143 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 54 | 95 | 100 | 0 |  | 947 | 0 | 275 | 0 | 115 | 0 | 0 | 0 | 21 | 0 | 40 | 68 | 31 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 79 | 100 | 166 | 0 | 404 | 90 | 0 | 113 | 67 | 107 | 0 | 0 | 70 | 450 |  | 11476 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 51 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 22 | 35 | 100 | 80 | 0 | 360 | 0 | 215 | 55 | 90 | 38 | 50 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 32 | 21 | 173 | 150 | 95 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 330 | 66 | 76 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 88 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  |  | 959 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 50 | 43 | 43 | 35 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 20 | 0 | 0 | 200 | 0 | 78 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 0
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 55 | 220 | 0 | 100 | 0 | 100 | 102 | 100 | 100 | 0 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 65 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 22 | 10 | 100 | 80 | 0 | 360 | 0 | 215 | 55 | 90 | 38 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 32 | 20 | 154 | 150 | 60 | 22 | 1.6 | 60 | 30 | 51 | 44 | 163 | 330 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 88 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  |  | 959 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 50 | 43 | 43 | 0 | 20 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 70 | 0 | 8 | 70 | 0
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 333 | 0 | 0 | 400 | 265 | 0 | 97 | 41 | 219 | 0 | 36 | 0 | 98 | 94 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 100 | 100 | 0 | 310 | 0 | 182 | 8 | 80 | 37 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 0 | 120 | 138 | 73 | 20 | 1.2 | 59 | 30 | 42 | 37 | 163 | 291 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 106 | 0 | 0 | 100 | 0 | 133 | 4.4 | 100 | 0 | 5 | 0 | 115 | 0 | 0 | 1.4 | 251 | 0 | 0 | 0 | 63 | 100 | 0 | 0 | 944 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 167 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0
199
| Minimum Generation |  | 7985.1 | 7:00
| Highest Generation |  | 11501 | 22:00
| Day Peak Generation |  | 9276.9 | 12:00
| Evening Peak Generation |  | 11476 | 21:00
| HVDC Max Flow |  | 949 | 18:00
| HVDC EvPeak Flow |  | 947 | 21:00
| Load factor L.F |  | 84.27%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-23
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9276.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8500.1 | MW
Evening Peak Generation : |  | 11476 | MW Hour : | 21:00 | Available Max Generation : |  | 14198 | MW
E.P. Demand (at gen end) : |  | 11476 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11700 | MW
Maximum Generation : |  | 11501 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2498 | MW
Total Gen. (MKWH) : |  | 232.6142 | System Load Factor : | 84.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -293 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-23
Actual : | 84 | Ft.(MSL) , | Rule curve : | 81.84 | Ft.( MSL )
Gas Consumed : | Total = | 1132.68 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155269411.056
: |  | Coal : | 66004421 | Oil : | 444062369.6 | Total : | 665336201.656
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4161.6134 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1416.728 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1269.6173 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1147.3044 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1036.7483 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 836.6231 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 465.805 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 215.3552 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 645.2548 |  |  | 0 | 0%
Total | 0 |  | 11195.0495 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj(S) 360 MW
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Baghabari-100, 71 MW
9) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Sreemangal 132/33 kV T-2 transformer was under shut down from 10:50 to 11:13 to Switched on T-3.
b) Comilla(S)-SM Nagar Tripura 132 kV Ckt-1 tripped at 10:52 due to SM Nagar to Palatona Ckt tripped and |  |  |  |  | About 104 MW power interruption occurred under Comilla(S) S/S area
was switched on at 12:08. |  |  |  |  | from 10:52 to 12:08.
c) Kabirpur 132/33 kV T-1 and T-2 transformers tripped at 10:50 showing O/C, E/F relay and were switched on |  |  |  |  | About 50 MW power interruption occurred under Kabirpur S/S area
at 10:58 and 11:02 respectively. |  |  |  |  | from 10:50 to 11:02.
AKSTL-Hathazari 230 kV Ckt was under shut down from 08:38 to 10:50 for C/M.
e) Munshiganj 132/33 kV T-2 transformer was under shut down from 10:09 to 14:16 for C/M.
f) Comilla(S)-SM Nagar Tripura 132 kV was under shut down from 09:15 to 12:48 for C/M.
g) Madunaghat 132/33 kV T-2 transformer was under shut down from 08:32 to 11:38 for C/M.
h) Siddhirganj (peaking) GT-1 tripped at 13:18 due to false fire alarm and was synchronized at 15:56.
i) Munshiganj 132/33 kV T-1 transformer was under shut down from 14:17 to 18:01 for Tan-Delta test.
j) Shahjibazar 330 MW Gt-2 was synchronized at 15:49.
k) Payra unit-1 was shut down at 00:30(23/06/2020) for auxiliary steam heater leakage.
l) Sonargaon-Meghna IEL 132 kV Ckt was shut down at 07:38(23/06/2020) for C/M.
m) Meghna-Haripur 132 Ckt-2 was shut down at 07:35(23/06/2020) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 765000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 6974791
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1516256 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 2190227
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 347 | 8055000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9658500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2048640
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6437993 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 97 | 1939968
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 816153
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 530296
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 374544
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 94 | 1631000 | Low demand
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 98 | 1971840
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 212 | 5116875 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 68 | 1841184 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 274992
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 1065240 | Reserve
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 401280 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1030918
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 694721
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1261860 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 781600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 638900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 115068 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 270 | 4413489
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 16947 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 2903040 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 108 | 607848
| Dhaka area Total |  |  |  | 5791 | 3208 | 66074170
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2200000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 91873 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 87885
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 342240
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 99 | 2288664 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 139 | 3248474 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 192363 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 645617
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 99960 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2230080
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 464832
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 420960
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 31 | 342720 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26280
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 308 | 6272727
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 476390
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2378880
| Chattogram area Total |  |  |  | 2266 | 1139 | 21809945
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2402298
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2661755 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 198 | 4546000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7955600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 841464 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 722880 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 25 | 629064 | Low demand
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 1709527
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 8 | 69448 | Low demand
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2105540
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 72480 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 494244
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 188280 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 2200000
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 585600 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 240677 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 488920 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 54 | 376200 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1768200
| Cumilla Area Total |  |  |  | 2980 | 1516 | 30258904
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 133 | 3177120 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 433980
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 72 | 1152000
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 2373600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2628000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 510 | 9777500
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1391000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719880
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3293182
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 317 | 5624000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1119600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 40 | 955008
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 194112
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1375104 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1717440 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3427750
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 15000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 558672
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7506200 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232200
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1282 | 28129148
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 947 | 22653818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1315200
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 111840 | Low demand
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 10624 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 275 | 7422336 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 768375
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 526080
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 480480 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 67 | 420480
| Khulna Area Total |  |  |  | 2284 | 1655 | 33709233
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 922176
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 541720
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1560000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 79 | 1811045 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 450 | 10502500
| Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 0
| Barisal Area Total |  |  |  | 1084 | 724 | 15337441
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 30000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 33091
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 26117
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 23371 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 169175
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4558927 | Gas shortage.
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 166 | 4459109 | Gas shortage.
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 404 | 9578872
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 212669
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 479280
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 237852
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 170838
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 219360 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 913968
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 826272
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 377376 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1186 | 22316277
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3671300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 17000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1469760
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43494
| Rangpur Area Total |  |  |  | 605 | 256 | 5201554
| Total |  |  |  | 19818 | 11476 | 232614172
| Eastern Grid Total |  |  |  | 13662 | 7655 | 156049667
| Western Grid Total |  |  |  | 6156 | 3821 | 76564505
| National Grid Total |  |  |  | 19818 | 11476 | 232614172
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-22
(a) ENTIRE EASTERN GRID : |  | 7196 | MW | (b) ENTIRE WESTERN GRID : |  | 3775 | MW
i) Dhaka area |  | 3678 | MW | i) Khulna area |  | 1469 | MW
ii) Chittagong area |  | 1072 | MW | ii) Rajshahi area |  | 1221 | MW
iii) Comilla area |  | 1069 | MW | iii) Barisal area |  | 334 | MW
iv) Mymensingh area |  | 915 | MW | iv) Rangpur area |  | 751 | MW
v) Sylhet area |  | 462 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10971 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 12:00 | Sherpur | 108 | 20:00 | Benapol | 46 | 20:00
Munsiganj | 120 | 23:00 | Srimongal | 43 | 19:30 | Jhenida | 108 | 19:30
Sonargaon | 71 | 24:00 | Shahjibazar | 113 | 23:00 | Bottail | 128 | 19:30
Shyampur | 184 | 24:00 | Fenchuganj | 43 | 21:00 | G.K Project | 54 | 20:00
Bhulta | 183 | 1:00 | Kulawara | 46 | 22:00 | Faridpur | 188 | 0.875
Madanganj | 48 | 2:00 | Sylhet | 119 | 20:00 | Madaripur | 93 | 0.875
Shitalakhya | 104 | 16:00 | Chatak | 27 | 19:30 | Sariatpur | 64 | 21:00
Rahim steel | 19 | 18:00 | Sunamganj | 40 | 24:00 | Gopalganj | 97 | 21:00
Matuail | 84 | 10:00 | Biani Bazar | 58 | 21:00 | Bagerhat | 90 | 0.83333
Ghorasal | 72 | 22:00 | Comilla (S) | 166 | 22:00 | Mongla | 38 | 1:00
Narsingdi | 158 | 23:00 | Comilla(N) | 125 | 14:00 | Satkhira | 100 | 0.91667
Haripur (SBU) | 101 | 13:00 | Chandpur | 100 | 22:00 | Gallamari | 47 | 19:30
Ullon | 62 | 15:00 | Feni | 115 | 23:00 | Magura | 52 | 0.875
Hasnabad | 196 | 21:00 | Chowmuhani | 172 | 23:00 | Norail | 39 | 20:00
Magbazar | 96 | 15:00 | Ashuganj | 61 | 23:00 | Chuadanga | 88 | 19:30
Maniknagar | 96 | 12:00 | Daudkandi | 132 | 0:00 | Barisal(N) | 44 | 0.91667
Bangabhaban | 28 | 10:00 | B.Baria | 146 | 21:00 | Barisal (S) | 96 | 0.95833
Narinda | 90 | 12:00 | Ramganj | 14 | 22:00 | Patuakhali | 112 | 0.95833
Dhanmondi | 145 | 13:00 | Chaddagram | 34 | 19:00 | Bhandaria | 42 | 21:00
Lalbag | 85 | 12:00 | PHP | 10 | 8:00 | Borhan Uddin
Madartek | 66 | 22:00 | Madunaghat | 53 | 19:30 | Ishurdi | 137 | 18:00
Dhaka University |  |  | Hathazari | 94 | 0.83333 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 96 | 15:00 | Khulshi | 192 | 0.5 | Natore | 119 | 21:00
Kalyanpur | 84 | 19:30 | Halishahar | 124 | 0.58333 | Bogra | 159 | 20:0
Gulshan | 114 | 15:00 | Baraulia | 130 | 0.16667 | Noagaon | 125 | 20:00
Uttara | 78 | 15:00 | Sikalbaha | 23 | 0.8125 | Rajshahi | 144 | 21:00
Uttara New | 22 | 9:00 | Dohazari | 92 | 0.83333 | Rajshahi New | 10 | 19:30
Kamrangirchar | 84 | 13:00 | Cox'sbazar | 86 | 0.8125 | C.Nawabganj | 69 | 20:00
Savar | 143 | 16:00 | Chandraghona | 30 | 0.875 | Amnura | 38 | 1:00
Bhasantec | 137 | 15:00 | Kaptai | 4 | 0.79167 | Pabna | 120 | 21:00
Agargaon | 60 | 13:00 | A. Khaer Stl. | 9 | 0.45833 | Shahjadpur | 96 | 19:30
Satmosjid | 89 | 15:00 | Bakulia | 91 | 0.45833 | Serajganj | 101 | 20:00
Tongi | 131 | 0.45833 | Julda | 21 | 0.41667 | Niyamatpur | 51 | 20:00
Kabirpur | 181 | 8:00 | TK chemical | 15.5 | 0.8125 | Joypurhat | 41 | 21:00
Basundhara | 109 | 13:00 | Modern Steel | 14 | 0.125 | Sherpur(Bogura) | 48 | 21:00
Manikganj | 64 | 21:00 | Shahmirpur | 27 | 0.83333 | Mohastangor | 52 | 20:0
Joydevpur | 151 | 19:30 | Khagrachhari | 24 | 0.8125 | Rangpur | 140 | 21:00
New Tongi | 98 | 15:00 | Matarbari | 31.5 | 0.83333 | Lalmonirhat | 54 | 19:30
Kodda | 231 | 20:00 | Baroiar Hat | 36 | 0.79167 | Saidpur | 107 | 20:00
Dhamrai | 84 | 21:00 | Rangamati | 10 | 0.54167 | Purbasadipur | 104 | 19:30
Rajendrapur | 86 | 22:00 | Abul Khair 230 | 30 | 0.45833 | Thakurgaon | 78 | 19:30
Valuka | 86 | 19:30 | BSRM | 155 | 0.58333 | Palashbari | 113 | 20:00
Tangail | 177 | 23:00 | GPH Ispat | 68 | 0.875 | Barapukuria | 50 | 21:00
Mymensing | 212 | 21:00 | Goalpara | 19 | 19:30 | Panchagar | 48 | 20:00
Kishorganj | 136 | 22:00 | Central s/s | 87 | 19:30 | Joldhaka | 27 | 20:00
Netrokona | 105 | 20:00 | Noapara | 61 | 20:00 | Kurigram | 53 | 19:30
Jamalpur | 136 | 20:00 | Jessore | 108 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 400 | 5:00 | 390 | 9:00 | Kaliakoir | 382 | 0.083333 | 368 | 0.375
| Bheramara | 396 | 6:00 | 390 | 20:00 | Bhulta | 391 | 0.083333 | 375 | 0.375
| Ashuganj(N) | 396 | 1:00 | 383 | 10:00 | Gopalganj | 412 | 0.77083 | 390 | 0.58333
| Payra | 414 | 17:00 | 401 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 24:00 | 230 | 7:00 | Comilla (N) | 236 | 3:00 | 226 | 10:00
| Ishurdi | 235 | 16:00 | 224 | 22:00 | Hathazari | 228 | 20:00 | 220 | 11:00
| Ashuganj | 236 | 19:30 | 228 | 10:00 | Megnaghat | 235 | 1:00 | 224 | 9:00
| Serajganj | 231 | 17:00 | 225 | 1:00 | Fenchuganj | 238 | 4:00 | 234 | 12:00
| Baghabari | 240 | 16:00 | 232 | 1:00 | Siddhirganj | 233 | 2:00 | 223 | 9:00
| Barapukuria | 232 | 16:00 | 221 | 21:00 | Maniknagar | 231 | 4:00 | 221 | 9:00
| Bogra | 227 | 17:00 | 215 | 21:00 | Agargaon | 230 | 5:00 | 217 | 10:00
| Rajshahi | 233 | 18:00 | 219 | 21:00 | Barisal | 245 | 17:00 | 235 | 2:00
| Khulna South | 229 | 16:00 | 209 | 9:00 | AKSML | 225 | 21:00 | 218 | 11:00
| Rampura | 228 | 1:00 | 220 | 10:00 | BSRM | 226 | 20:00 | 218 | 11:00
| Haripur | 230 | 1:00 | 222 | 9:00 | Bibiyana | 237 | 1:00 | 232 | 9:00
| Hasnabad | 230 | 1:00 | 220 | 9:00 | Bhulta | 233 | 5:00 | 223 | 9:00
| Shyampur | 227 | 2:00 | 216 | 10:00 | Ashuganj (S) | 235 | 1:00 | 228 | 9:00
| Aminbazar | 230 | 1:00 | 219 | 10:00 | Kaliakoir | 234 | 2:00 | 222 | 9:00
| Tongi | 228 | 19:30 | 215 | 9:00 | GPH | 224 | 2:00 | 215 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 3:00 | 126 | 9:00 | Hathazari | 135 | 0.8125 | 131 | 0.375
| Munsiganj | 136 | 19:00 | 125 | 9:00 | Khulshi | 134 | 0.8125 | 128 | 0.41667
| Sonargaon | 132 | 1:00 | 125 | 9:00 | Halishahar | 137 | 0.8125 | 130 | 0.41667
| Shyampur | 137 | 5:00 | 130 | 9:00 | Baraulia | 134 | 0.8125 | 129 | 0.33333
| Bhulta | 126 | 4:00 | 119 | 9:00 | Sikalbaha | 138 | 20:00 | 131 | 0.375
| Madanganj | 131 | 5:00 | 128 | 23:00 | Dohazari | 134 | 19:30 | 128 | 0.16667
| Shitalakhya | 142 | 1:00 | 129 | 8:00 | Cox'sbazar | 123 | 0.5 | 111 | 0.875
| Rahim steal | 133 | 19:30 | 126 | 9:00 | Chandraghona | 136 | 0.83333 | 132 | 0.33333
| Matuail | 133 | 3:00 | 126 | 9:00 | Kaptai | 134 | 1:00 | 132 | 0.375
| Ghorasal | 138 | 8:00 | 134 | 1:00 | A. Khaer Stl. | 135 | 0.83333 | 130 | 9:00
| Narsinghdi | 128 | 20:00 | 121 | 9:00 | Bakulia | 136 | 0.8125 | 130 | 0.33333
| Haripur (SBU) | 132 | 2:00 | 125 | 9:00 | Julda | 134 | 0.041667 | 131 | 0.29167
| Ullon | 136 | 2:00 | 129 | 10:00 | TK Chemical | 137 | 0.83333 | 131 | 9:00
| Hasnabad | 138 | 22:00 | 129 | 9:00 | Modern Steel | 136 | 0.83333 | 130 | 0.33333
| Magbazar | 135 | 4:00 | 128 | 10:00 | Shahmirpur | 137 | 0.83333 | 131 | 0.29167
| Maniknagar | 134 | 1:00 | 128 | 11:00 | Khagrachhari | 134 | 0.16667 | 131 | 0.29167
| Bangabhaban | 134 | 1:00 | 128 | 11:00 | Matarbari | 127 | 0.41667 | 119 | 0.77083
| Narinda | 134 | 1:00 | 128 | 11:00 | Baroiar Hat | 136 | 0.83333 | 127 | 0.375
| Dhanmondi | 136 | 2:00 | 129 | 10:00 | Rangamati | 135 | 0.8125 | 131 | 9:00
| Lalbag | 138 | 23:00 | 125 | 10:00 | Goalpara S/S | 140 | 16:00 | 125 | 11:00
| Madartek | 135 | 2:00 | 128 | 10:00 | Khulna Central S/S | 139 | 0.66667 | 125 | 11:00
| Dhaka University |  |  |  |  | Noapara | 136 | 16:00 | 123 | 11:00
| Mirpur | 134 | 5:00 | 126 | 15:00 | Jessore | 132 | 18:00 | 119 | 12:00
| Kalyanpur | 134 | 4:00 | 125 | 10:00 | Benapol | 132 | 18:00 | 120 | 11:00
| Gulshan | 135 | 5:00 | 128 | 10:00 | Jhenida | 128 | 0.75 | 114 | 21:00
| Uttara | 132 | 5:00 | 122 | 10:00 | Bottail | 132 | 16:00 | 122 | 21:00
| Uttara New | 132 | 4:00 | 122 | 10:00 | G.K Project | 139 | 0.75 | 129 | 6:00
| Kamrangirchar | 136 | 6:00 | 126 | 12:00 | Faridpur | 133 | 18:00 | 122 | 10:00
| Savar | 133 | 4:00 | 123 | 10:00 | Madaripur | 137 | 0.77083 | 130 | 12:00
| Bhasantec | 133 | 5:00 | 122 | 10:00 | Shariyatpur S/S | 136 | 0.70833 | 128 | 13:00
| Agargaon | 133 | 6:00 | 124 | 10:00 | Gopalganj | 141 | 18:30 | 127 | 10:00
| Satmosjid | 131 | 5:00 | 123 | 10:00 | Bagerhat | 137 | 0.8125 | 120 | 9:00
| Tongi | 137 | 0.875 | 127 | 9:00 | Mongla | 135 | 0.8125 | 117 | 9:00
| Kabirpur | 133 | 18:00 | 128 | 22:00 | Satkhira | 137 | 0.66667 | 124 | 11:00
| Basundhara | 135 | 2:00 | 128 | 13:00 | Gallamari | 140 | 16:00 | 126 | 11:00
| Manikganj | 140 | 24:00 | 130 | 10:00 | Magura | 127 | 0.77083 | 112 | 21:00
| Joydevpur | 139 | 19:30 | 133 | 12:00 | Norail | 125 | 0.75 | 108 | 21:00
| New Tongi | 137 | 1904-01-02 | 126 | 8:00 | Chuadanga | 123 | 18:00 | 103 | 21:00
| Kodda | 137 | 23:00 | 122 | 0.33333 | Barisal(N) | 138 | 18:00 | 132 | 2:00
| Dhamrai | 133 | 5:00 | 127 | 22:00 | Barisal (S) | 136 | 0.8125 | 130 | 13:00
| Rajendrapur | 132 | 21:00 | 119 | 9:00 | Patuakhali | 136 | 0.75 | 124 | 13:00
| Valuka | 127 | 16:00 | 113 | 22:00 | Bhandaria | 135 | 17:00 | 125 | 2:00
| Tangail | 135 | 4:00 | 125 | 23:00 | Ishurdi | 137 | 18:00 | 130 | 11:00
| Mymensing | 129 | 16:00 | 115 | 22:00 | Ruppur Paromanobik | 136 | 18:30 | 130 | 12:00
| Kishorganj | 129 | 16:00 | 118 | 22:00 | Natore | 134 | 19:00 | 127 | 1:00
| Netrokona | 128 | 16:00 | 111 | 22:00 | Bogra | 133 | 19:00 | 124 | 2:00
| Jamalpur | 139 | 16:00 | 127 | 19:00 | Noagaon | 129 | 19:00 | 119 | 4:00
| Sherpur | 137 | 19:30 | 126 | 0.91667 | Rajshahi | 132 | 18:00 | 125 | 3:00
| Srimongal | 137 | 7:00 | 132 | 0.91667 | Rajshahi New | 134 | 18:00 | 125 | 2:00
| Shahjibazar | 135 | 6:00 | 129 | 0.91667 | C.Nawabganj | 132 | 18:00 | 122 | 11:00
| Fenchuganj | 135 | 6:00 | 132 | 0.70833 | Amnura | 133 | 18:00 | 121 | 12:00
| Khulawara | 134 | 4:00 | 130 | 0.91667 | Pabna | 134 | 18:00 | 127 | 21:00
| Sylhet | 133 | 6:00 | 129 | 0.91667 | Shahjadpur | 136 | 18:00 | 133 | 2:00
| Chatak | 132 | 5:00 | 128 | 21:00 | Serajganj | 132 | 18:30 | 125 | 21:00
| Sunamganj | 131 | 6:00 | 126 | 0.041667 | Niyamatpur | 127 | 18:00 | 117 | 21:00
| Biani Bazar | 132 | 7:00 | 126 | 0.875 | Joypurhat | 130 | 19:00 | 119 | 1:00
| Comilla(s) | 127 | 6:00 | 120 | 10:00 | Sherpur(Bogura) | 133 | 19:00 | 125 | 1:00
| Comilla(n) | 137 | 20:00 | 132 | 10:00 | Mohastangor | 131 | 18:00 | 121 | 2:0
| Chandpur | 133 | 19:30 | 127 | 9:00 | Rangpur | 130 | 15:00 | 115 | 21:00
| Feni | 135 | 20:00 | 128 | 10:00 | Lalmonirhat | 125 | 15:00 | 112 | 3:00
| Chowmuhani | 131 | 20:00 | 125 | 15:00 | Saidpur | 128 | 15:00 | 112 | 21:00
| Ashuganj | 135 | 10:00 | 131 | 11:00 | Purbasadipur | 125 | 17:00 | 105 | 19:30
| Daudkandi | 132 | 19:30 | 125 | 9:00 | Thakurgaon | 122 | 17:00 | 102 | 20:00
| B.Baria | 132 | 6:00 | 125 | 22:00 | Palashbari | 125 | 14:00 | 113 | 21:00
| Ramganj | 123 | 18:00 | 118 | 20:00 | Barapukuria | 132 | 16:00 | 121 | 21:00
| Chaddagram | 136 | 20:00 | 127 | 9:00 | Panchagar | 121 | 6:00 | 96 | 20:0
| PHP | 134 | 20:00 | 126 | 10:00 | Joldhaka | 125 | 15:00 | 107 | 21:00
| Madanhat | 138 | 20:00 | 132 | 10:00 | Kurigram | 125 | 15:00 | 108 | 21:00

## L-Curve
Date | 2020-06-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 293 | 7716 | 3536 | 11252 |  |  |  | QF-LDC-12
0:30 | 252 | 7375 | 3334.5 | 10709.5 | Date: | 2020-06-22
1:00 | 211 | 7034 | 3133 | 10167
1:30 | 204.5 | 6958.5 | 3085 | 10043.5
2:00 | 198 | 6883 | 3037 | 9920
2:30 | 179 | 6747 | 3031.5 | 9778.5 | [5 empty] | Gen. at Eve. Peak | 11476 | 11476 MW (21:00 )
3:00 | 160 | 6611 | 3026 | 9637 | [6 empty] | 21:00
3:30 | 157.5 | 6548.5 | 2974.5 | 9523 | [5 empty] | Gen. at Day Peak | 9276.9 | 9276.9 MW (12:00 )
4:00 | 155 | 6486 | 2923 | 9409 | [6 empty] | 12:00
4:30 | 92.5 | 6420.5 | 2884.5 | 9305 | [5 empty] | Highest Generation | 11501
5:00 | 30 | 6355 | 2846 | 9201 | [6 empty] | 22:00
5:30 | 143.5 | 5882.1 | 2835.6 | 8717.7
6:00 | 257 | 5409.2 | 2825.2 | 8234.4
6:30 | 263.5 | 5289.55 | 2820.2 | 8109.75
7:00 | 270 | 5169.9 | 2815.2 | 7985.1
7:30 | 342.5 | 5220.65 | 2870.1 | 8090.75
8:00 | 415 | 5271.4 | 2925 | 8196.4
8:30 | 404.5 | 5400.85 | 2938.7 | 8339.55
9:00 | 394 | 5530.3 | 2952.4 | 8482.7
9:30 | 395 | 5680.75 | 2997.8 | 8678.55
10:00 | 396 | 5831.2 | 3043.2 | 8874.4
10:30 | 360 | 5939 | 3006 | 8945
11:00 | 324 | 6046.8 | 2968.8 | 9015.6
11:30 | 298.5 | 6144.5 | 3001.75 | 9146.25
12:00 | 273 | 6242.2 | 3034.7 | 9276.9
12:30 | 237 | 6351.8 | 3062.45 | 9414.25
13:00 | 201 | 6461.4 | 3090.2 | 9551.6
13:30 | 226 | 6461.65 | 3102.7 | 9564.35
14:00 | 251 | 6461.9 | 3115.2 | 9577.1
14:30 | 295.5 | 6536.7 | 3191.4 | 9728.1
15:00 | 340 | 6611.5 | 3267.6 | 9879.1
15:30 | 283.5 | 6607.4 | 3171.1 | 9778.5
16:00 | 227 | 6603.3 | 3074.6 | 9677.9
16:30 | 252 | 6409.85 | 2994.35 | 9404.2
17:00 | 277 | 6216.4 | 2914.1 | 9130.5
17:30 | 316.5 | 5852.5 | 2899.15 | 8751.65
18:00 | 356 | 5488.6 | 2884.2 | 8372.8
18:30 | 281.5 | 5849.3 | 3063.6 | 8912.9
19:00 | 207 | 6210 | 3243 | 9453
19:30 | 130 | 7315 | 3624 | 10939
20:00 | 177 | 7401 | 3752 | 11153 |  |  |  | Executive Engineer
20:30 | 167 | 7528 | 3786.5 | 11314.5 |  |  |  | Network Operation Division
21:00 | 157 | 7655 | 3821 | 11476
21:30 | 155 | 7670.5 | 3818 | 11488.5
22:00 | 153 | 7686 | 3815 | 11501 |  |  |  |  | Page 6 of 7
22:30 | 186.5 | 7734 | 3749 | 11483
23:00 | 220 | 7782 | 3683 | 11465
23:30 | 256.5 | 7749 | 3609.5 | 11358.5
24:00 | 293 | 7716 | 3536 | 11252
11476 MW (21:00 )
9276.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-22 |  | Energy | 232614172
[10 empty] | 2020-06-22 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3297 | 943 | 2155 | 3847 | 349 | 101 | 371 | 0 | 90
0:30 | 3411.5 | 945 | 2173.5 | 3320 | 347.5 | 100.5 | 260 | 0 | 102 | Date: | 2020-06-22
1:00 | 3526 | 947 | 2192 | 2793 | 346 | 100 | 149 | 0 | 114
1:30 | 3505.5 | 947.5 | 2201 | 2654.5 | 397.5 | 99 | 119.5 | 0 | 119 | [7 empty] | Total Energy | 232.6142 | Total Energy Gen 232.614 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.614 MKWHr
2:00 | 3485 | 948 | 2210 | 2516 | 449 | 98 | 90 | 0 | 124 | [7 empty] | Energy not Served | 0
2:30 | 3493.5 | 944.5 | 2190 | 2409.5 | 473.5 | 97.5 | 49 | 0 | 121 | [7 empty] | Energy Requirement | 232.6142
3:00 | 3502 | 941 | 2170 | 2303 | 498 | 97 | 8 | 0 | 118
3:30 | 3493 | 941 | 2185 | 2190.5 | 498.5 | 97 | 4 | 0 | 114 | [6 empty] | Shortage
4:00 | 3484 | 941 | 2200 | 2078 | 499 | 97 | 0 | 0 | 110
4:30 | 3475 | 941 | 2192.5 | 1996.5 | 498.5 | 97.5 | 0 | 0 | 104
5:00 | 3466 | 941 | 2185 | 1915 | 498 | 98 | 0 | 0 | 98
5:30 | 3467.5 | 941 | 2137 | 1459.5 | 524 | 98.5 | 0 | 0 | 89
6:00 | 3469 | 941 | 2089 | 1004 | 550 | 99 | 0 | 0 | 80
6:30 | 3469 | 941 | 2059.5 | 898.5 | 549.5 | 98.5 | 0 | 0 | 88 |  |  |  |  | Coal
7:00 | 3469 | 941 | 2030 | 793 | 549 | 98 | 0 | 0 | 96
7:30 | 3467 | 941 | 2047.5 | 831 | 597 | 98 | 0 | 0 | 99 |  |  |  | Oil |  |  |  | ,
8:00 | 3465 | 941 | 2065 | 869 | 645 | 98 | 0 | 0 | 102
8:30 | 3436 | 941 | 2110.5 | 964 | 672.5 | 98.5 | 0 | 0 | 104
9:00 | 3407 | 941 | 2156 | 1059 | 700 | 99 | 0 | 0 | 106
9:30 | 3362 | 941 | 2185 | 1241.5 | 727 | 99 | 0 | 0 | 105
10:00 | 3317 | 941 | 2214 | 1424 | 754 | 99 | 0 | 0 | 104
10:30 | 3305.5 | 941 | 2206.5 | 1571.5 | 742 | 99.5 | 0 | 0 | 52
11:00 | 3294 | 941 | 2199 | 1719 | 730 | 100 | 0 | 0 | 0
11:30 | 3262.5 | 942 | 2201.5 | 1871.5 | 740 | 100 | 0 | 0 | 0
12:00 | 3231 | 943 | 2204 | 2024 | 750 | 100 | 0 | 0 | 0
12:30 | 3214 | 943 | 2201.5 | 2148.5 | 750 | 100.5 | 7.5 | 0 | 30
13:00 | 3197 | 943 | 2199 | 2273 | 750 | 101 | 15 | 0 | 60
13:30 | 3197 | 943 | 2199 | 2273 | 750 | 101 | 15 | 0 | 60
14:00 | 3197 | 943 | 2199 | 2273 | 750 | 101 | 15 | 0 | 60
14:30 | 3145.5 | 943.5 | 2205 | 2413.5 | 764.5 | 99.5 | 32.5 | 0 | 91
15:00 | 3094 | 944 | 2211 | 2554 | 779 | 98 | 50 | 0 | 122
15:30 | 3114.5 | 944 | 2183 | 2558.5 | 689.5 | 97 | 50 | 0 | 122
16:00 | 3135 | 944 | 2155 | 2563 | 600 | 96 | 50 | 0 | 122
16:30 | 3138.5 | 946 | 2096 | 2353 | 600 | 96 | 50.5 | 0 | 116
17:00 | 3142 | 948 | 2037 | 2143 | 600 | 96 | 51 | 0 | 110
17:30 | 3107 | 948.5 | 1820.5 | 2013 | 599 | 96.5 | 53 | 0 | 112
18:00 | 3072 | 949 | 1604 | 1883 | 598 | 97 | 55 | 0 | 114
18:30 | 3154 | 948.5 | 1690.5 | 2110 | 599 | 97 | 181.5 | 0 | 132
19:00 | 3236 | 948 | 1777 | 2337 | 600 | 97 | 308 | 0 | 150
19:30 | 3173 | 948 | 2014 | 3652 | 590 | 98 | 304 | 0 | 160
20:00 | 3135 | 946 | 2059 | 3750 | 588 | 97 | 418 | 0 | 160
20:30 | 3291 | 946.5 | 2135.5 | 3697.5 | 593.5 | 98 | 391.5 | 0 | 161
21:00 | 3447 | 947 | 2212 | 3645 | 599 | 99 | 365 | 0 | 162
21:30 | 3421.5 | 945 | 2231 | 3661.5 | 599.5 | 99 | 367 | 0 | 164
22:00 | 3396 | 943 | 2250 | 3678 | 600 | 99 | 369 | 0 | 166
22:30 | 3394 | 943 | 2222.5 | 3762.5 | 526 | 100 | 371 | 0 | 164
23:00 | 3392 | 943 | 2195 | 3847 | 452 | 101 | 373 | 0 | 162
23:30 | 3344.5 | 943 | 2175 | 3847 | 400.5 | 101 | 372 | 0 | 126 | Max Temp. in Dhaka |  | 33.2° C
24:00 | 3297 | 943 | 2155 | 3847 | 349 | 101 | 371 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 232.614 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.614 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 65 | 63 | 62 | 62 | 63 | 64 | 63 | 63 | 64 | 64 | 65 | 65 | 66 | 64 | 63 | 61 | 61 | 62 |  | 62 | 63 | 62 | 64 | 64 | 66 | 66 | 1444664
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [5 empty] | 8 | 16 | 16 | 8 | 8 | 8 | [8 empty] | 2 | 8 | 8 |  |  |  | 0 | 91873
| Teknaf 20MW PP (Solartech) | [5 empty] | 1.9 | 6.2 | 5.7 | 6.5 | 11.3 | 19.7 | 10.8 | 5 | 7.9 | 15.7 | 8.6 | 2.5 | 0.4 | [8 empty] | 87885
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 146 | 143 | 140 | 140 | 146 | 139 | 139 | 139 | 139 | 139 | 139 | 145 | 139 | 139 | 139 | 104 |  | 145 | 104 | 104 | 139 | 139 | 139 | 104 | 3248474
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 8 | [16 empty] | 74 | 102 | 102 | 102 | 102 | 102 | 102 | 645617
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 5 | 34 | 34 | 34 | 34 | 34 | 34 | 192363
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [20 empty] | 14 | 16 | 8 | 12 | 16 | 16 | 69448
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 96 | 95 | 63 | 94 | 91 | 96 | 95 | 95 | 37 | 37 | 37 | 37 | 37 | 0 | 37 | 32 | 32 | 33 |  | 65 | 33 | 32 | 94 | 94 | 97 | 35 | 1631000
17 | Siddhirganj 335 MW CCPP | 216 | 218 | 215 | 180 | 220 | 218 | 216 | 217 | 215 | 180 | 180 | 180 | 180 | 206 | 210 | 212 | 212 | 180 |  | 200 | 215 | 180 | 212 | 214 | 218 | 218 | 5116875
18 | Kodda 300 MW PP Unit-2 (Summit) | 252 | 252 | 130 | 130 | 95 |  |  |  | 9 | 31 | 91 | 194 | 265 | 260 | 264 | 264 | 200 | 200 |  | 215 | 268 | 270 | 270 | 268 | 268 | 268 | 4413489
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 765000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6974791
26
28 | Ashuganj TPP Unit- 3 | 135 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 |  | 100 | 100 | 120 | 120 | 120 | 135 | 135 | 2402298
29 | Ashuganj TPP Unit- 4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2661755
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 33 | 36 | 35 | 35 | 35 | 35 | 35 | 37 | 37 |  | 38 | 38 | 38 | 38 | 38 | 38 | 41 | 841464
33 | Ashuganj 225 MW CCPP | 182 | 165 | 182 | 181 | 187 | 184 | 173 | 155 | 189 | 198 | 191 | 201 | 196 | 198 | 177 | 201 | 182 | 183 |  | 209 | 216 | 181 | 198 | 192 | 181 | 181 | 4546000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 345 | 345 | 310 | 310 | 330 | 335 | 335 | 310 | 360 | 315 | 315 | 345 | 310 | 310 | 310 | 290 |  | 320 | 265 | 260 | 345 | 310 | 310 | 310 | 7955600
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 10 |  | 10 | 10 | 20 | 20 | 20 | 20 | 51 | 722880
36 | Chandpur 150 MW CCPP | 90 | 91 | 91 | 91 | 80 | 91 | 91 | 92 | 91 | 91 | 87 | 90 | 90 | 90 | 85 | 80 | 85 | 90 |  | 90 | 82 | 80 | 91 | 91 | 82 | 87 | 2105540
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 390 | 420 | 420 | 390 | 360 | 390 | 420 | 450 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 350 |  | 350 | 450 | 450 | 450 | 450 | 450 | 400 | 9658500
41 | Haripur 360MW CCPP(HPL) | 354 | 353 | 352 | 351 | 355 | 329 | 309 | 309 | 351 | 349 | 349 | 347 | 347 | 322 | 344 | 341 | 314 | 252 |  | 275 | 354 | 352 | 347 | 349 | 354 | 353 | 8055000
42 | RPCL 210MW CCPP | 139 | 140 | 139 | 139 | 141 | 140 | 139 | 139 | 139 | 137 | 136 | 134 | 133 | 120 | 120 | 124 | 139 | 138 |  | 138 | 140 | 140 | 133 | 135 | 140 | 140 | 3177120
43
44 | Fenchugonj CCPP Phase-1 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 57 | 57 | 58 | 58 | 60 | 60 | 60 |  | 59 | 60 | 60 | 60 | 60 | 60 | 58 | 1391000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719880
46 | Shajibazar 330 MW CCPP | 247 | 251 | 260 | 252 | 248 | 252 | 257 | 255 | 262 | 252 | 248 | 250 | 208 | 155 | 145 | 162 | 199 | 288 |  | 319 | 300 | 288 | 317 | 302 | 294 | 292 | 5624000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 62 | 61 | 60 | 61 | 59 | 59 | 59 | 59 | 59 | 57 | 60 | 51 | 52 | 40 |  | 59 | 40 | 40 | 59 | 60 | 63 | 61 | 1375104
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 77 | 77 | 77 | 77 | 77 | 74 | 74 | 77 | 76 | 76 | 76 | 76 | 74 | 76 | 76 | 77 | 10 |  | 10 | 79 | 79 | 79 | 79 | 79 | 79 | 1717440
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 100 | 70 |  | 70 | 131 | 140 | 150 | 150 | 150 | 150 | 3427750
51 | Sylhet 20 MW GTPP | [25 empty] | 0 | 15000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232200
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 9 | 11 | 11 | 11 |  | 8 | 0 |  | 5 | 11 | 11 | 11 | 194112
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 14 |  | 14 | 50 | 50 | 50 | 50 | 50 | 50 | 1119600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 558672
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 305 | 315 | 310 | 285 | 290 | 320 | 320 | 310 | 305 | 315 | 310 | 305 | 310 | 310 | 300 | 280 |  | 295 | 275 | 275 | 295 | 320 | 285 | 285 | 7506200
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 17 | [9 empty] | 6 | 17 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 694721
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 464832
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [5 empty] | 21 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 374544
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 433980
63 | Impoprt (Tripura) | 114 | 124 | 118 | 110 | 98 | 80 | 96 | 102 | 106 | 104 | 0 | 0 | 60 | 68 | 122 | 122 | 110 | 114 |  | 150 | 160 | 160 | 162 | 166 | 162 | 90 | 2200000
64 | Malancha, Ctg. EPZ (United) | 25 | 32 | 32 | 32 | 33 | 33 | 30 | 10 | 4 | 2 | 2 | 2 | 4 | 6 | 2 | 5 | 10 | 12 |  | 17 | 10 | 18 | 12 | 19 | 23 | 28 | 420960
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 21 | 21 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 494244
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 188280
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 |  | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 585600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 18 | 14 | 14 | 18 | 18 | 18 | 18 | 21 | 21 |  | 5 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 488920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 30 | 30 | 30 | 30 | 30 |  | 20 | 20 | 30 | 30 | 30 | 30 | 26 | 661860
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 781600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 638900
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 96 | 96 | 96 | 96 | 95 | 96 | 96 | 96 | 94 | 95 | 95 | 96 | 96 | 95 | 23 |  | 54 | 92 | 100 | 101 | 101 | 102 | 99 | 2190227
| Feni Lanka Power | [19 empty] | 17 | 114 | 114 | 54 | 54 | 102 | 102 | 376200
| Chowmuhani 113 MW | 113 | 113 | 104 | 84 | 70 |  |  |  |  | 2 | 37 | 73 | 105 | 105 | 104 | 104 | 84 | 55 |  | 62 | 104 | 104 | 95 | 101 | 105 | 105 | 1768200
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 99 | 99 | 99 | 99 | 99 | 60 | 7 | 7 | 8 | 60 | 95 | 97 | 97 | 97 | 97 | 97 | 97 | 60 |  | 70 | 88 | 88 | 98 | 98 | 98 | 99 | 1971840
78 | Gazipur 52 MW PP | [19 empty] | 2 | 25 | 35 |  |  | 7 | 52 | 115068
79 | Kodda 150MW PP | 16 | 16 | [17 empty] | 55 | 64 | 64 | 64 | 64 | 64 | 64 | 401280
80 | Jamalpur 95 MW PP(Powerpac) | 48 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 68 | 64 | 64 |  | 48 | 60 | 72 | 72 | 40 | 32 | 32 | 1152000
81 | Jangalia 52 MW PP (Lakdanavi) | [15 empty] | 10 | 8 | 8 |  | 8 | 12 | 25 | 34 | 34 | 43 | 52 | 240677
| Gazipur 100 MW PP | [14 empty] | 4 | 17 | 17 | 17 |  | 32 | 70 | 108 | 108 | 108 | 108 | 108 | 607848
| Kaptai 7 MW Solar PP | [5 empty] | 0.2 | 1.5 | 2 | 4.3 | 4 | 6.1 | 5.8 | 0.2 | 1.8 | 3 | 0.2 | 0.4 | 0.1 | [8 empty] | 26280
| Jodiac Power | [11 empty] | 3 | 17 | 17 | 30 | 54 | 17 | 17 |  | 24 | 27 | 54 | 54 | 54 | 54 | 54 | 476390
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 30 | 30 | 30 | 30 | 40 | 60 | 80 | 85 | 80 | 80 | 79 | 82 | 90 |  | 95 | 97 | 97 | 97 | 97 | 97 | 97 | 1939968
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [14 empty] | 8 | 10 | 10 | 10 |  | 35 | 100 | 95 | 100 | 70 | 69 | 100 | 530296
86 | Meghnaghat CCPP(Summit) | 250 | 260 | 260 | 265 | 260 | 260 | 260 | 275 | 285 | 270 | 255 | 265 | 265 | 280 | 285 | 270 | 260 | 260 |  | 285 | 240 | 260 | 260 | 260 | 260 | 260 | 6437993
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 60 | 7 | 7 | 14 | 68 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 77 | 100 | 100 | 100 | 100 | 100 | 100 | 2048640
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 68 | 69 | 69 | 68 | 68 | 68 | 68 | 68 | 67 | 66 | 65 | 66 | 67 | 65 | 65 | 66 | 40 |  | 40 | 66 | 66 | 66 | 66 | 68 | 67 | 1516256
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [14 empty] | 20 | 20 | 10 | 10 |  | 10 | 10 |  |  |  | 20 | 20 | 99960
92 | Fenchuganj 44MW (Energyprima) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 10 | 10 |  | 21 | 40 | 40 | 40 | 40 | 40 | 37 | 955008
93 | Ashuganj 51 MW PP (Midland) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 629064
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 32 | 7 | 7 | 32 | 64 | 102 | 93 | 102 | 102 | 67 | 67 | 67 | 68 |  | 68 | 68 | 68 | 68 | 102 | 102 | 102 | 1841184
95 | Patenga 50MW PP (Baraka) | 34 | [13 empty] | 3 | 12 | 12 | 12 |  | 16 | 50 | 47 | 50 | 50 | 50 | 50 | 342240
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 11 | 30 |  | 30 | 42 | 50 | 31 | 31 | 49 | 95 | 342720
97 | Katpotti 52 MW PP (Sinha) | [15 empty] | 11 | 14 | 14 |  | 13 | 13 | 26 | 48 | 48 | 48 | 48 | 274992
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 41 | 30 | 30 | 15 | 15 | 15 |  |  |  | 20 | 41 | 41 | 41 | 41 | 41 | 41 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 55 | 41 | 816153
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 |  |  |  |  | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1030918
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 163 | 130 | 163 | 110 | 110 | 110 |  | 163 | 110 | 110 | 163 | 163 | 163 | 163 | 3293182
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.2 | 0.7 | 0.5 | 1.9 | 0 | 1.6 | 1.2 | 2.2 | 1.8 | 0.5 | 0.5 | 0.1 | [8 empty] | 12800
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 |  |  |  | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 |  | 53 | 53 | 53 | 1065240
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 160 | 120 |  |  |  |  | 19 | 40 | 53 | 64 | 80 | 100 | 40 | 8 | 8 |  | 16 | 110 | 140 | 170 | 170 | 185 | 190 | 2373600
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 26 |  |  |  |  | 0 | 16947
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 133 | 133 | 132 | 133 | 102 | 80 | 80 | 88 | 116 | 129 | 132 | 133 | 132 | 131 | 132 | 118 | 101 |  | 102 | 110 | 122 | 130 | 130 | 132 | 130 | 2903040
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 40 | 20 | 50 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2230080
116 | Chandpur 200MW (Desh energy) | [19 empty] | 10 | 34 | 17 |  |  | 2 | 17 | 72480
117 | Ashuganj 150MW PP (Midland) | 148 | 100 | 50 | [7 empty] | 3 | 23 | 55 | 85 | 105 | 125 | 60 | 60 |  | 72 | 148 | 132 | 143 | 148 | 148 | 147 | 1709527
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 108 | 107 | 107 | 107 | 107 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 75 | 75 |  | 98 | 115 | 115 | 115 | 115 | 115 | 108 | 2628000
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 288 | 142 | 141 | 142 | 215 | 252 | 252 | 288 | 306 | 307 | 308 | 270 | 248 | 105 |  | 155 | 304 | 308 | 308 | 308 | 307 | 307 | 6272727
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2378880
120 | Eastern Zone Total | 7034 | 6883 | 6611 | 6486 | 6355 | 5409.2 | 5169.9 | 5271.4 | 5530.3 | 5831.2 | 6046.8 | 6242.2 | 6461.4 | 6461.9 | 6611.5 | 6603.3 | 6216.4 | 5488.6 |  | 6210 | 7315 | 7401 | 7655 | 7686 | 7782 | 7716 | 156049667
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 66 | 66 | 39 | 32 | [6 empty] | 24 | 32 | 32 | 109 | 115 | 49 | 30 |  | 69 | 115 | 115 | 115 | 115 | 115 | 115 | 1315200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 2 |  | 21 | 19 | 19 | 21 | 21 | 21 | 19 | 111840
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [19 empty] | 43 | 90 | 90 | 90 | 90 | 105 | 105 | 480480
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 32 | 32 | 16 | 16 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 66 | 96 | 96 | 96 | 96 | 96 | 96 | 922176
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 78 | 76 | 76 | 77 | 76 | 77 | 79 | 79 | 78 | 76 | 75 | 77 | 79 | 78 | 77 | 34 |  | 34 | 73 | 82 | 79 | 79 | 79 | 79 | 1811045
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 64 | 65 | 65 | 65 | 64 | 65 | 65 | 65 | 65 | 64 | 65 | 65 | 65 | 68 |  | 65 | 57 | 63 | 68 | 67 | 62 | 67 | 1560000
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 27 | 26 | 24 | 20 | 17 | 15 | 14 | 18 | 17 | 18 | 19 | 22 | 21 | 21 | 19 | 18 |  | 25 | 30 | 30 | 31 | 31 | 33 | 34 | 541720
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 100 | 81 | 100 | 100 | 100 | 70 | 526080
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 33 |  |  |  |  | 33 | 33 | 33 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 768375
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 1 | 3 |  | 6 | [5 empty] | 0 | 10624
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 15 | 67 | 67 | 67 | 67 | 105 | 105 | 420480
146 | Bheramara HVDC | 947 | 948 | 941 | 941 | 941 | 941 | 941 | 941 | 941 | 941 | 941 | 943 | 943 | 944 | 944 | 944 | 948 | 949 |  | 948 | 948 | 946 | 947 | 943 | 943 | 943 | 22653818
147 | Bheramara 410 MW CCPP | 345 | 345 | 350 | 345 | 340 | 345 | 340 | 340 | 320 | 300 | 295 | 285 | 270 | 260 | 250 | 250 | 250 | 270 |  | 275 | 275 | 275 | 275 | 270 | 270 | 270 | 7422336
148 | Payra 1320 MW | 197 | 300 | 349 | 350 | 349 | 401 | 400 | 495 | 550 | 604 | 580 | 600 | 600 | 601 | 629 | 450 | 450 | 448 |  | 450 | 440 | 438 | 450 | 450 | 302 | 199 | 10502500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 3671300
153 | Baghabari 71 MW GTPP | [26 empty] | 30000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 17 | 17 | 17 |  |  |  |  | 33091
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 189 | 191 | 202 | 197 | 187 | 190 | 203 | 206 | 202 | 162 | 163 | 180 | 170 | 172 | 170 | 169 | 166 |  | 140 | 165 | 168 | 177 | 177 | 177 | 177 | 4558927
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 186 | 185 | 170 | 173 | 170 | 170 | 167 | 166 | 166 | 167 |  | 166 | 165 | 166 | 166 | 166 | 165 | 165 | 4459109
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 418 | 413 | 410 | 398 | 418 | 414 | 413 | 404 | 413 | 408 | 409 | 400 | 402 | 409 | 397 | 345 | 367 |  | 395 | 302 | 313 | 404 | 408 | 374 | 355 | 9578872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 8 | 10 | 26 |  |  |  |  | 26117
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 19 | 20 | 21 | 21 | 21 | 21 | 479280
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 10 | 10 | 8 | 8 | 8 | 10 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 237852
164 | Ullapara 11 MW PP (Summit) | 5 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 5 | 5 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 170838
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 24 | 24 |  |  |  |  | 23371
167 | Katakhali 50 MW Peaking PP | [19 empty] | 20 | 35 | 40 | 37 | 37 | 37 | 37 | 169175
168 | Santahar 50 MW Peaking PP | [19 empty] | 32 | 33 | 34 | 33 | 33 | 33 | 33 | 212669
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 23 | 43 | 43 | 43 | 43 | 43 | 43 | 219360
170 | Chapainawabganj 100 MW Peaking PP | 87 | 40 | [10 empty] | 15 | 41 | 50 | 50 | 50 | 50 |  | 75 | 10 | 100 | 100 | 100 | 100 | 100 | 913968
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | [13 empty] | 11 | 35 | 35 | 35 |  | 42 | 105 | 110 | 113 | 113 | 113 | 113 | 826272
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 15 | 70 | 70 | 70 | 70 | 70 | 70 | 377376
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 12 | [25 empty] | 17000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 98 | 37 | [6 empty] | 14 | 40 | 70 | 80 | 113 | 88 | 48 | 35 |  | 56 | 107 | 107 | 107 | 106 | 107 | 108 | 1469760
177 | Sympa Solar Power 8MW | [5 empty] | 0.2 | 1.2 | 3 | 3.4 | 4.2 | 6.8 | 6.7 | 7.2 | 7.2 | 6.6 | 3.6 | 0.1 | 0.2 | [8 empty] | 43494
178
178