## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-24 | Wednesday
|  | Date (day): | 2020-06-24 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12669.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14790 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-23 | 2020-06-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 65 | 66 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 95 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint. |  | 26/06/2020
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 353 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 255 | 270 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 95 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 41 | 41 | 42 |  | 14 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 87 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 94 | 0 | 100 | 110 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 80 | 97 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 213 | 170 | 220 | 220 |  | 115 | ST-under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 0 | 49 | 52
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 133 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 20 | 43 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 268 | 283 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 70 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 131 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 108 | 108 | 100 | 100
| Sonargoan 104 MW (Orion) |  | HFO | IPP | 18.5*6 | 104 MW | 104 MW | 30 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 3078 | 3335 | 3661 | 4099 | 323 | 1291
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 4 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15.56 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 19 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 99 | 98 | 100 | 100 | 130 |  | Low water level
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 139 | 140 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 34 | 34 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 10 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 27 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 95 | 51 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 307 | 308 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 1154.66 | 1178 | 1392 | 1531 | 400 | 225
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100 | 35 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 188 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 315 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 42 | 38 | 42 |  | 3 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 52 | 50 | 50
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 26 | 26 | 169 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 26 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 143 | 148 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 91 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 105 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 11 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 164 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 32 | 32
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 12 | 21 | 22
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 104 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1345 | 1675 | 1988 | 2165 | 367 | 444
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 136 | 156 | 150 | 160 | 42 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 33 | 25 | 25 | 30
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.5 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 170 | 185 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 467.5 | 501 | 483.6 | 527 | 42 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 59 | 60 | 60
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 292 | 302 | 330 | 330
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 39 | 40 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 53 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 79 | 80 | 80
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 300 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1247 | 1288 | 1373 | 1379 | 0 | 460
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 561 | 938 | 959 | 959
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 22 | 0 | 30
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 20 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 345 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 60 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 105 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 917 | 1755 | 1789 | 2165 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 96 | 110 | 80 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 38 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 68 | 67 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 78 | 78 | 78 | 78 |  | 17 | Engine problem
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 0 | 0 | 0 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 258 | 293 | 256 | 949 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 40 |  | 10 | Engine problem
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 43 | 45
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 198 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 192 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 399 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 21 | 21
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 36 | 43 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 50 | 100 | 100 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 113 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 1011 | 1376 | 1479 | 1692 | 381 | 19
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 90 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6.3 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 269.3 | 272 | 248 | 283 | 170 | 0
| Total |  |  |  |  | 20279 | 19788 | 9747.46 | 11673 | 12669.6 | 14790 | 1683 | 2582
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9251.4443 | 11079 | 12024.8864 | 14037.3863
A. |  | 2020-06-23 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11693 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8500.1 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11673 | MW
3 | Day peak Generation : |  |  | 9747.46 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11079 | MW
4 | Evening peak Generation : |  |  | 11673 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 243.0219 | MKWHr | By Solar | 0.15824 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 132.6708 | MKWHr |  | By Oil: | 80.0454 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 3.6659 | MKWHr |  | By Hydro: | 2.2206 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1683 | MW | Dhaka | 3751 | 3751 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2582 | MW | Chittagong | 1095 | 1095 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 4265 | MW | Khulna | 1431 | 1431 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1155.99 | MMCFD |  |  | Rajshahi | 1217 | 1217 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 156127240.796 | ii) Oil : | Taka | 621767292.9 | Comilla | 1080 | 1080 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 19869178 | Total | Taka | 797763711.696 | Mymensingh | 924 | 924 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4.0205 | MKWHr. | Sylhet | 475 | 475 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -306 | MW (E to W) at | 21:00 | hrs | Barisal | 348 | 348 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -438 | MW at | 1:00 | hrs | Rangpur | 758 | 758 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 11079 | 11079 |  | 0
B. |  | 2020-06-24 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14790 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 2790 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 249.4024 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8976.9 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.8778 | MKWHr. | ii) HVDC Flow at Peak Time |  | 938 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.383 | MKWHr. | iii) Maximum HVDC Flow : |  | 948 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84 |  | (b) Today: | 83.98 |  | (c) Rule Curve: |  | 82.11
.

## YesterdayGen
2020-06-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Sonargoan 104 MW (Orion) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 351 |  | 0 | 400 | 260 | 100 | 97 | 41 | 218 | 0 | 36 | 0 | 97 | 102 | 64 | 68 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 52 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 98 | 50 | 20 | 32 | 135 | 100 | 0 | 310 | 0 | 188 | 8 | 90 | 40 | 52 | 0 | 25 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 154 | 138 | 32 | 20 | 0 | 59 | 30 | 50 | 37 | 163 | 315 | 62 | 79 | 0 | 151 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 268 | 0 | 0 | 195 | 0 | 132 | 0 | 100 | 0 | 148 | 0 | 108 | 108 | 0 | 0 | 307 | 54 | 0 | 101 | 104 | 100 | 0 | 0 |  | 943 | 0 | 280 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 67 | 32 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 36 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 0 | 165 | 0 | 385 | 35 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7750 | 3166 | 10916 | 3381 | 943 | 2189 | 3645 | 149 | 101 | 354 | 154 | 0 | 0 | 84
2:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 356 |  | 0 | 400 | 260 | 100 | 97 | 41 | 220 | 0 | 36 | 0 | 97 | 102 | 32 | 84 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 62 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 60 | 50 | 20 | 32 | 135 | 100 | 0 | 310 | 0 | 183 | 8 | 80 | 40 | 52 | 0 | 25 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 150 | 141 | 32 | 20 | 0 | 59 | 30 | 50 | 37 | 163 | 292 | 62 | 79 | 0 | 150 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 268 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 150 | 0 | 107 | 108 | 0 | 0 | 307 | 52 | 0 | 0 | 105 | 100 | 0 | 0 |  | 944 | 0 | 295 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 66 | 32 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 35 | 43 | 25 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 0 | 165 | 0 | 344 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7495 | 3166 | 10661 | 3361 | 944 | 2153 | 3494 | 149 | 97 | 313 | 150 | 0 | 0 | 84
3:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 356 |  | 0 | 400 | 260 | 100 | 97 | 41 | 218 | 0 | 36 | 0 | 97 | 102 | 16 | 0 | 0 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 62 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 62 | 39 | 20 | 40 | 135 | 100 | 0 | 310 | 0 | 183 | 8 | 85 | 40 | 52 | 0 | 25 | 0 | 0 | 43 | 21 | 8 | 25 | 21 | 146 | 140 | 32 | 20 | 0 | 59 | 30 | 50 | 37 | 163 | 308 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 148 | 0 | 108 | 108 | 0 | 0 | 307 | 52 | 0 | 0 | 105 | 100 | 0 | 0 |  | 944 | 0 | 305 | 0 | 115 | 0 | 0 | 0 | 19 | 0 | 40 | 67 | 30 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 0 | 165 | 0 | 358 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7392 | 3083 | 10475 | 3386 | 944 | 2168 | 3348 | 149 | 97 | 237 | 146 | 0 | 0 | 84
4:00 | 35 | 0 | 0 | 0 | 260 | 99 | 68 | 0 | 355 |  | 0 | 400 | 260 | 100 | 97 | 41 | 218 | 0 | 36 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 18 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 43 | 0 | 20 | 40 | 135 | 100 | 0 | 310 | 0 | 183 | 8 | 85 | 40 | 51 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 148 | 141 | 32 | 20 | 0 | 59 | 30 | 50 | 37 | 130 | 304 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 148 | 0 | 108 | 18 | 0 | 0 | 307 | 44 | 0 | 0 | 105 | 100 | 0 | 0 |  | 944 | 0 | 320 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 27 | 96 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 77 | 0 | 165 | 0 | 381 | 50 | 0 | 35 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7112 | 2951 | 10063 | 3399 | 944 | 2154 | 3021 | 149 | 96 | 152 | 148 | 0 | 0 | 84
5:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 353 |  | 0 | 400 | 260 | 100 | 97 | 41 | 219 | 0 | 36 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 60 | 35 | 90 | 0 | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 64 | 0 | 45 | 0 | 20 | 41 | 100 | 100 | 0 | 310 | 0 | 182 | 8 | 80 | 40 | 52 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 140 | 141 | 32 | 20 | 0 | 59 | 30 | 47 | 37 | 130 | 290 | 61 | 80 | 0 | 150 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 268 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 148 | 0 | 108 | 18 | 0 | 0 | 307 | 34 | 0 | 0 | 105 | 100 | 0 | 0 |  | 943 | 0 | 325 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 24 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 76 | 0 | 166 | 0 | 363 | 0 | 0 | 35 | 95 | 113 | 0 | 0 | 0 | 0 |  | 6956 | 2824 | 9780 | 3360 | 943 | 2149 | 2880 | 149 | 95 | 64 | 140 | 0 | 0 | 84
6:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 354 |  | 0 | 370 | 260 | 74 | 97 | 41 | 217 | 0 | 36 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 41 | 100 | 100 | 0 | 320 | 0 | 194 | 8 | 90 | 40 | 53 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 0 | 120 | 140 | 32 | 20 | 0.1 | 59 | 30 | 47 | 37 | 130 | 298 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 130 | 0 | 0 | 150 | 0 | 131 | 0.8 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0.3 | 253 | 0 | 0 | 0 | 75 | 100 | 0 | 0 |  | 943 | 0 | 340 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 18 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 78 | 0 | 166 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 6331.2 | 2404.1 | 8735.3 | 3369 | 943 | 2059 | 1981 | 149 | 96 | 17 | 120 | 1.3 | 0 | 84
7:00 | 35 | 0 | 0 | 0 | 260 | 99 | 67 | 0 | 307 |  | 0 | 370 | 260 | 41 | 97 | 41 | 214 | 0 | 36 | 0 | 89 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 33 | 100 | 100 | 0 | 340 | 0 | 204 | 8 | 90 | 40 | 51 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 0 | 116 | 138 | 34 | 20 | 0.3 | 59 | 30 | 46 | 37 | 163 | 307 | 61 | 80 | 0 | 100 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 100 | 0 | 131 | 2.7 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 1.9 | 199 | 0 | 0 | 0 | 46 | 100 | 0 | 0 |  | 943 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 68 | 15 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 78 | 0 | 166 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 |  | 6096.9 | 2403.2 | 8500.1 | 3365 | 943 | 2064 | 1762 | 149 | 96 | 0 | 116 | 5.1 | 0 | 84
8:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 333 |  | 0 | 400 | 265 | 0 | 97 | 41 | 219 | 0 | 36 | 0 | 98 | 94 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 100 | 100 | 0 | 310 | 0 | 182 | 8 | 80 | 37 | 50 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 0 | 120 | 138 | 73 | 20 | 1.2 | 59 | 30 | 42 | 37 | 163 | 291 | 61 | 79 | 0 | 150 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 106 | 0 | 0 | 100 | 0 | 133 | 4.4 | 100 | 0 | 5 | 0 | 115 | 0 | 0 | 1.4 | 251 | 0 | 0 | 0 | 63 | 100 | 0 | 0 |  | 944 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 77 | 0 | 167 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 |  | 6219 | 2419.4 | 8638.4 | 3370 | 944 | 2139 | 1813 | 149 | 96 | 0 | 120 | 7.4 | 0 | 84
9:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 353 |  | 0 | 400 | 280 | 0 | 97 | 41 | 219 | 0 | 35 | 0 | 94 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 0 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 100 | 100 | 0 | 310 | 0 | 182 | 8 | 90 | 37 | 48 | 0 | 25 | 0 | 0 | 0 | 21 | 5 | 25 | 0 | 122 | 138 | 88 | 20 | 0.8 | 59 | 30 | 42 | 37 | 163 | 295 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 193 | 0 | 0 | 100 | 0 | 131 | 5.2 | 100 | 0 | 28 | 0 | 115 | 0 | 0 | 4.8 | 272 | 0 | 0 | 0 | 101 | 100 | 0 | 0 |  | 948 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 77 | 0 | 166 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 |  | 6419.8 | 2434.8 | 8854.6 | 3344 | 948 | 2169 | 2014 | 149 | 96 | 0 | 122 | 12.6 | 0 | 84
10:00 | 35 | 0 | 0 | 0 | 300 | 95 | 67 | 0 | 325 |  | 0 | 450 | 265 | 0 | 97 | 41 | 180 | 0 | 85 | 0 | 97 | 102 | 0 | 8 | 0 | 0 | 0 | 35 | 55 | 52 | 22 | 25 | 30 | 33 | 33 | 4 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 21 | 1 | 18 | 2 | 100 | 100 | 0 | 270 | 0 | 195 | 8 | 82 | 39 | 48 | 0 | 25 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 120 | 136 | 32 | 20 | 1.6 | 59 | 30 | 42 | 37 | 130 | 292 | 60 | 79 | 0 | 150 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 270 | 0 | 0 | 137 | 0 | 131 | 1.67 | 100 | 0 | 80 | 0 | 108 | 24 | 4 | 2.8 | 306 | 20 | 0 | 0 | 105 | 100 | 0 | 0 |  | 948 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 192 | 0 | 76 | 0 | 165 | 0 | 346 | 0 | 0 | 6 | 0 | 55 | 0 | 3.5 | 0 | 0 |  | 6670.07 | 2494.5 | 9164.57 | 3399 | 948 | 2091 | 2352 | 149 | 96 | 0 | 120 | 9.57 | 0 | 84
11:00 | 35 | 0 | 0 | 0 | 300 | 92 | 67 | 0 | 344 |  | 0 | 450 | 285 | 0 | 96 | 41 | 213 | 0 | 35 | 0 | 40 | 102 | 0 | 61 | 0 | 0 | 3 | 35 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 17 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 90 | 6 | 20 | 2 | 100 | 100 | 0 | 285 | 0 | 186 | 8 | 90 | 39 | 45 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 120 | 135 | 33 | 20 | 1.6 | 58 | 30 | 45 | 38 | 130 | 290 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 268 | 0 | 0 | 170 | 0 | 132 | 4.77 | 100 | 0 | 110 | 0 | 108 | 52 | 34 | 4 | 307 | 54 | 0 | 0 | 105 | 100 | 0 | 22 |  | 562 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 17 | 96 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 78 | 0 | 171 | 0 | 398 | 0 | 0 | 38 | 0 | 110 | 0 | 5.3 | 0 | 0 |  | 6937.37 | 2282.3 | 9219.67 | 3367 | 562 | 2152 | 2725 | 150 | 98 | 30 | 120 | 15.67 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 90 | 65 | 0 | 347 |  | 0 | 390 | 255 | 0 | 95 | 41 | 213 | 0 | 35 | 0 | 80 | 102 | 0 | 87 | 0 | 0 | 13 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 20 | 0 | 64 | 35 | 90 | 0 | 4 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 60 | 95 | 31 | 20 | 2 | 100 | 100 | 0 | 310 | 0 | 184 | 8 | 85 | 38 | 49 | 0 | 25 | 0 | 0 | 8 | 11 | 5 | 25 | 21 | 128 | 136 | 33 | 20 | 0.5 | 58 | 30 | 47 | 39 | 163 | 292 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 70 | 0 | 170 | 0 | 131 | 15.56 | 100 | 0 | 143 | 0 | 108 | 108 | 34 | 4.1 | 307 | 54 | 0 | 0 | 105 | 100 | 0 | 30 |  | 561 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 16 | 96 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 36 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 78 | 0 | 196 | 0 | 398 | 0 | 0 | 108 | 0 | 113 | 0 | 6.3 | 0 | 0 |  | 7292.16 | 2455.3 | 9747.46 | 3429 | 561 | 2120 | 3184 | 150 | 99 | 50 | 128 | 26.46 | 0 | 84
13:00 | 35 | 0 | 0 | 0 | 300 | 92 | 64 | 0 | 324 |  | 0 | 390 | 265 | 28 | 95 | 41 | 170 | 0 | 35 | 0 | 96 | 102 | 70 | 94 | 0 | 0 | 14 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 40 | 0 | 64 | 35 | 90 | 0 | 16 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 50 | 97 | 46 | 20 | 8 | 100 | 100 | 0 | 310 | 0 | 184 | 8 | 84 | 38 | 48 | 0 | 25 | 0 | 0 | 43 | 18 | 8 | 25 | 21 | 120 | 123 | 33 | 20 | 2.5 | 58 | 30 | 47 | 39 | 130 | 291 | 59 | 79 | 0 | 70 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 270 | 50 | 0 | 170 | 0 | 128 | 17.12 | 100 | 0 | 145 | 0 | 108 | 108 | 34 | 5 | 307 | 54 | 0 | 0 | 105 | 100 | 0 | 24 |  | 542 | 0 | 330 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 66 | 20 | 96 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 78 | 0 | 205 | 0 | 406 | 0 | 0 | 113 | 0 | 113 | 0 | 6.3 | 0 | 0 |  | 7299.62 | 2501.3 | 9800.92 | 3287 | 542 | 2087 | 3365 | 150 | 99 | 120 | 120 | 30.92 | 0 | 84
14:00 | 35 | 0 | 0 | 0 | 300 | 95 | 63 | 0 | 346 |  | 0 | 400 | 277 | 90 | 93 | 41 | 170 | 0 | 34 | 0 | 96 | 102 | 98 | 87 | 0 | 0 | 14 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 63 | 35 | 90 | 0 | 24 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 50 | 97 | 47 | 20 | 2 | 100 | 100 | 0 | 330 | 0 | 202 | 8 | 90 | 38 | 47 | 0 | 25 | 0 | 0 | 52 | 18 | 8 | 25 | 5 | 146 | 122 | 33 | 20 | 0 | 58 | 30 | 47 | 39 | 130 | 306 | 60 | 76 | 0 | 15 | 0 | 0 | 10 | 305 | 24 | 11 | 0 | 275 | 0 | 0 | 170 | 0 | 133 | 16.8 | 100 | 0 | 145 | 0 | 108 | 108 | 34 | 1.4 | 307 | 54 | 0 | 17 | 104 | 100 | 0 | 60 |  | 490 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 22 | 96 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 20 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 78 | 0 | 195 | 0 | 399 | 0 | 0 | 113 | 15 | 113 | 0 | 0 | 0 | 0 |  | 7457.2 | 2458 | 9915.2 | 3252 | 490 | 2123 | 3473 | 150 | 98 | 165 | 146 | 18.2 | 0 | 84
15:00 | 35 | 0 | 0 | 0 | 300 | 95 | 65 | 0 | 345 |  | 0 | 400 | 240 | 100 | 93 | 41 | 211 | 0 | 32 | 0 | 96 | 102 | 98 | 87 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 62 | 35 | 90 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 50 | 97 | 45 | 20 | 2 | 100 | 100 | 0 | 310 | 0 | 201 | 8 | 82 | 35 | 47 | 0 | 25 | 0 | 0 | 52 | 20 | 8 | 25 | 21 | 148 | 124 | 33 | 20 | 0.7 | 60 | 30 | 47 | 39 | 163 | 290 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 310 | 24 | 11 | 0 | 285 | 0 | 0 | 150 | 0 | 130 | 13.6 | 100 | 0 | 145 | 0 | 107 | 108 | 34 | 3 | 307 | 54 | 0 | 51 | 105 | 100 | 0 | 28 |  | 683 | 0 | 320 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 59 | 24 | 96 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 76 | 0 | 201 | 0 | 382 | 0 | 0 | 113 | 50 | 107 | 0 | 0 | 0 | 0 |  | 7613.3 | 2706 | 10319.3 | 3412 | 683 | 2146 | 3469 | 149 | 97 | 198 | 148 | 17.3 | 0 | 84
16:00 | 35 | 0 | 0 | 0 | 280 | 93 | 64 | 0 | 323 |  | 0 | 400 | 275 | 100 | 93 | 30 | 212 | 0 | 35 | 0 | 96 | 102 | 98 | 40 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 8 | 0 | 62 | 35 | 90 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 10 | 65 | 33 | 20 | 5 | 100 | 100 | 0 | 310 | 0 | 201 | 8 | 88 | 35 | 49 | 0 | 25 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 142 | 119 | 25 | 20 | 0.7 | 60 | 30 | 47 | 36 | 130 | 302 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 283 | 0 | 0 | 150 | 0 | 130 | 9.2 | 100 | 0 | 100 | 0 | 108 | 52 | 34 | 2.6 | 270 | 53 | 0 | 51 | 104 | 100 | 0 | 20 |  | 930 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 20 | 96 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 169 | 0 | 76 | 0 | 196 | 0 | 389 | 0 | 0 | 70 | 50 | 105 | 0 | 0 | 0 | 0 |  | 7154.5 | 2829 | 9983.5 | 3394 | 930 | 2063 | 2998 | 149 | 97 | 198 | 142 | 12.5 | 0 | 84
17:00 | 35 | 0 | 0 | 0 | 280 | 54 | 50 | 0 | 283 |  | 0 | 360 | 255 | 80 | 93 | 41 | 170 | 0 | 32 | 0 | 75 | 102 | 48 | 10 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 30 | 33 | 16 | 8 | 0 | 59 | 35 | 90 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 10 | 50 | 19 | 20 | 11 | 100 | 100 | 0 | 290 | 0 | 193 | 8 | 84 | 39 | 48 | 0 | 25 | 0 | 0 | 5 | 21 | 8 | 25 | 18 | 132 | 133 | 25 | 20 | 0.4 | 60 | 30 | 24 | 20 | 130 | 290 | 59 | 79 | 0 | 130 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 220 | 0 | 0 | 100 | 0 | 131 | 4 | 100 | 0 | 100 | 0 | 115 | 52 | 34 | 1.7 | 181 | 54 | 0 | 17 | 94 | 100 | 0 | 36 |  | 930 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 24 | 61 | 20 | 96 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 19 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 168 | 0 | 76 | 0 | 178 | 0 | 370 | 0 | 0 | 70 | 15 | 71 | 0 | 2.5 | 0 | 0 |  | 6477.1 | 2728.5 | 9205.6 | 3240 | 930 | 1893 | 2595 | 149 | 94 | 164 | 132 | 8.6 | 0 | 84
18:00 | 35 | 0 | 0 | 0 | 280 | 54 | 40 | 0 | 283 |  | 0 | 320 | 245 | 50 | 96 | 41 | 170 | 0 | 32 | 0 | 50 | 102 | 48 | 10 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 16 | 8 | 0 | 60 | 35 | 90 | 0 | 25 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 10 | 51 | 18 | 20 | 10 | 100 | 100 | 0 | 270 | 0 | 177 | 8 | 80 | 41 | 48 | 0 | 25 | 0 | 0 | 8 | 21 | 8 | 25 | 18 | 120 | 137 | 25 | 20 | 0.1 | 60 | 30 | 22 | 20 | 100 | 290 | 59 | 30 | 0 | 100 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 220 | 0 | 0 | 100 | 0 | 131 | 0.6 | 100 | 0 | 100 | 0 | 115 | 52 | 34 | 0.3 | 179 | 54 | 0 | 17 | 46 | 100 | 0 | 5 |  | 936 | 0 | 320 | 0 | 16 | 0 | 0 | 0 | 8 | 44 | 8 | 64 | 18 | 96 | 0 | 0 | 0 | 50 | 8 | 58 | 0 | 8 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 78 | 0 | 166 | 0 | 347 | 0 | 0 | 70 | 15 | 71 | 0 | 1.2 | 0 | 0 |  | 6102 | 2732.2 | 8834.2 | 3140 | 936 | 1729 | 2447 | 149 | 95 | 216 | 120 | 2.2 | 0 | 84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 300 | 87 | 40 | 0 | 304 |  | 0 | 370 | 305 | 57 | 96 | 41 | 170 | 0 | 82 | 0 | 55 | 102 | 48 | 31 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 16 | 9 | 0 | 61 | 35 | 90 | 0 | 25 | 0 | 0 | 116 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 20 | 100 | 100 | 0 | 340 | 0 | 204 | 8 | 90 | 41 | 50 | 0 | 25 | 0 | 31 | 8 | 21 | 8 | 25 | 20 | 160 | 128 | 25 | 20 | 0 | 60 | 30 | 22 | 25 | 100 | 323 | 59 | 79 | 0 | 90 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 230 | 0 | 0 | 100 | 0 | 130 | 0 | 100 | 0 | 115 | 0 | 115 | 70 | 34 | 0 | 179 | 54 | 0 | 17 | 59 | 100 | 0 | 36 |  | 937 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 21 | 74 | 8 | 65 | 31 | 96 | 0 | 0 | 0 | 50 | 29 | 90 | 0 | 8 | 30 | 15 | 30 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 78 | 0 | 167 | 0 | 399 | 0 | 0 | 80 | 15 | 73 | 0 | 0 | 0 | 0 |  | 6824 | 3038 | 9862 | 3386 | 937 | 1949 | 2680 | 149 | 96 | 505 | 160 | 0 | 0 | 84
19:30 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 349 |  | 0 | 420 | 277 | 100 | 96 | 41 | 170 | 0 | 93 | 0 | 90 | 102 | 55 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 40 | 0 | 61 | 35 | 90 | 0 | 25 | 0 | 0 | 143 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 22 | 100 | 100 | 0 | 305 | 0 | 196 | 8 | 90 | 41 | 50 | 0 | 25 | 0 | 50 | 16 | 21 | 8 | 25 | 20 | 160 | 155 | 25 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 319 | 59 | 79 | 0 | 150 | 18 | 0 | 10 | 330 | 24 | 11 | 0 | 285 | 0 | 0 | 148 | 0 | 130 | 0 | 100 | 0 | 150 | 0 | 115 | 108 | 34 | 0 | 303 | 27 | 0 | 75 | 105 | 100 | 0 | 36 |  | 937 | 0 | 345 | 0 | 85 | 0 | 0 | 0 | 22 | 65 | 40 | 66 | 27 | 96 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 20 | 42 | 43 | 33 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 193 | 0 | 79 | 100 | 190 | 0 | 400 | 35 | 0 | 113 | 50 | 113 | 0 | 0 | 25 | 0 |  | 7787 | 3511 | 11298 | 3551 | 937 | 2244 | 3591 | 149 | 96 | 570 | 160 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 352 |  | 0 | 420 | 255 | 100 | 96 | 41 | 170 | 0 | 95 | 0 | 96 | 102 | 120 | 90 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 45 | 0 | 61 | 35 | 90 | 0 | 25 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 22 | 100 | 100 | 0 | 310 | 0 | 198 | 8 | 90 | 41 | 52 | 0 | 26 | 0 | 34 | 49 | 21 | 8 | 25 | 21 | 162 | 154 | 25 | 20 | 0 | 60 | 30 | 50 | 40 | 163 | 301 | 60 | 79 | 0 | 150 | 17 | 0 | 10 | 310 | 24 | 11 | 0 | 285 | 0 | 0 | 180 | 0 | 131 | 0 | 100 | 25 | 148 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 114 | 105 | 100 | 0 | 36 |  | 937 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 22 | 65 | 40 | 67 | 27 | 98 | 0 | 0 | 0 | 50 | 42 | 100 | 0 | 50 | 46 | 43 | 34 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 193 | 0 | 78 | 86 | 191 | 0 | 400 | 70 | 0 | 113 | 67 | 113 | 0 | 0 | 50 | 0 |  | 7950 | 3627 | 11577 | 3540 | 937 | 2229 | 3839 | 149 | 96 | 625 | 162 | 0 | 0 | 84
21:00 | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 353 |  | 0 | 420 | 270 | 100 | 96 | 41 | 170 | 0 | 94 | 0 | 97 | 102 | 133 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 63 | 35 | 90 | 0 | 25 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 27 | 100 | 100 | 0 | 315 | 0 | 188 | 8 | 91 | 42 | 52 | 0 | 26 | 0 | 0 | 52 | 21 | 8 | 25 | 12 | 164 | 156 | 25 | 20 | 0 | 59 | 30 | 50 | 40 | 163 | 302 | 53 | 79 | 0 | 150 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 283 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 105 | 148 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 114 | 104 | 100 | 0 | 0 |  | 938 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 22 | 20 | 40 | 67 | 38 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 50 | 44 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 198 | 0 | 78 | 100 | 192 | 0 | 399 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 70 | 0 |  | 7977 | 3696 | 11673 | 3521 | 938 | 2236 | 4012 | 149 | 98 | 555 | 164 | 0 | 0 | 84
22:00 | 35 | 0 | 0 | 0 | 300 | 97 | 67 | 0 | 353 |  | 0 | 390 | 270 | 100 | 96 | 41 | 170 | 0 | 95 | 0 | 97 | 102 | 133 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 63 | 35 | 90 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 31 | 100 | 100 | 0 | 315 | 0 | 197 | 8 | 90 | 42 | 52 | 0 | 35 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 166 | 155 | 25 | 20 | 0 | 59 | 30 | 50 | 40 | 130 | 303 | 59 | 79 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 285 | 0 | 0 | 195 | 0 | 132 | 0 | 100 | 90 | 148 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 114 | 105 | 100 | 0 | 0 |  | 938 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 22 | 48 | 40 | 67 | 29 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 50 | 42 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 197 | 0 | 78 | 100 | 192 | 0 | 411 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 70 | 0 |  | 7964 | 3729 | 11693 | 3558 | 938 | 2202 | 4001 | 149 | 98 | 581 | 166 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 300 | 98 | 67 | 0 | 355 |  | 0 | 420 | 285 | 100 | 97 | 41 | 170 | 0 | 95 | 0 | 97 | 102 | 133 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 64 | 35 | 90 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 26 | 100 | 100 | 0 | 345 | 0 | 172 | 8 | 90 | 42 | 51 | 0 | 35 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 166 | 154 | 25 | 20 | 0 | 59 | 30 | 50 | 40 | 130 | 272 | 59 | 79 | 0 | 150 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 285 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 35 | 148 | 0 | 115 | 108 | 34 | 0 | 307 | 54 | 0 | 114 | 105 | 100 | 0 | 0 |  | 941 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 22 | 50 | 40 | 67 | 34 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 24 | 41 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 196 | 0 | 77 | 100 | 195 | 0 | 403 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 70 | 0 |  | 7935 | 3705 | 11640 | 3533 | 941 | 2235 | 3935 | 149 | 99 | 582 | 166 | 0 | 0 | 84
24:00 | 35 | 0 | 0 | 0 | 300 | 98 | 66 | 0 | 354 |  | 0 | 450 | 260 | 100 | 97 | 41 | 215 | 0 | 95 | 0 | 97 | 102 | 133 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 65 | 35 | 90 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 25 | 100 | 100 | 0 | 310 | 0 | 160 | 8 | 86 | 42 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 8 | 25 | 21 | 160 | 155 | 25 | 20 | 0 | 58 | 30 | 50 | 40 | 163 | 270 | 60 | 79 | 0 | 150 | 17 | 0 | 10 | 315 | 24 | 11 | 0 | 283 | 0 | 0 | 195 | 0 | 131 | 0 | 100 | 35 | 150 | 0 | 115 | 108 | 34 | 0 | 307 | 54 | 0 | 114 | 105 | 100 | 0 | 0 |  | 942 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 19 | 50 | 33 | 68 | 34 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 24 | 41 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 200 | 0 | 75 | 100 | 196 | 0 | 412 | 70 | 0 | 113 | 105 | 107 | 0 | 0 | 70 | 0 |  | 7961 | 3713 | 11674 | 3541 | 942 | 2306 | 3897 | 149 | 100 | 579 | 160 | 0 | 0 | 76.33
KWH | 750000 | 0 | 0 | 0 | 6814036 | 2186045 | 1488032 | 0 | 8019000 |  | 0 | 9390000 | 6332276 | 1669440 | 2308992 | 991835 | 4944166 | 0 | 1262000 | 0 | 2169600 | 2442096 | 1241760 | 1249875 | 0 | 0 | 236400 | 1283400 | 1327396 | 1016039 | 426780 | 600000 | 662580 | 808300 | 695500 | 550452 | 0 | 1384642 | 836000 | 2100000 | 0 | 261906 | 0 | 0 | 3270806 | 0 |  | 0 | 0 | 1055663 | 313200 | 1340160 | 506880 | 467136 | 441120 | 2609904 | 2384695 | 0 | 7810800 | 0 | 4582000 | 217454 | 2048140 | 904968 | 1192800 | 0 | 649948 | 0 | 58496 | 610013 | 457092 | 169920 | 614500 | 422990 | 3383040 | 3230000 | 842880 | 403776 | 11750 | 1404000 | 722760 | 1094400 | 880488 | 3547227 | 6737000 | 1430688 | 1808640 | 0 | 3207160 | 103000 | 0 | 244440 | 7396300 | 566832 | 264000 | 0 | 5989197 | 144237 | 0 | 3900000 | 0 | 3166560 | 90315 | 2438400 | 348960 | 2855345 | 0 | 2679600 | 1726476 | 557018 | 34800 | 6814691 | 1029241 | 0 | 853860 | 2297400 | 2435520 | 0 | 308160 |  | 20877818 | 0 | 8169984 | 0 | 1345920 | 0 | 0 | 0 | 179520 | 314624 | 636750 | 1577000 | 572219 | 2335776 | 0 | 0 | 0 | 491190 | 203813 | 1289040 | 0 | 184540 | 281283 | 504480 | 245711 | 462720 | 253404 | 194998 | 0 | 0 | 3665900 | 0 | 5000 | 0 | 0 | 4460173 | 0 | 1876115 | 509760 | 4542191 | 0 | 9130581 | 603360 | 0 | 1868928 | 1213776 | 2146560 | 0 | 21374 | 331968 | 0 |  | 172525394 | 70496476 | 243021870 | 81819875 | 20877818 | 50850933 | 74679323 | 3665900 | 2220642 | 5366100 | 3383040 | 158239 | 0
Fuel Cost | 1230000 | 0 | 0 | 0 | 7563579.96 | 2885579.4 | 2529654.4 | 0 | 8259570 |  | 0 | 10235100 | 7028826.36 | 12671049.6 | 15908954.88 | 8390924.1 | 5141932.64 | 0 | 2183260 | 0 | 16337088 | 22271915.52 | 12218918.4 | 11523847.5 | 0 | 0 | 2148876 | 9368820 | 10260771.08 | 10018144.54 | 320085 | 450000 | 0 | 0 | 0 | 5322870.84 | 0 | 373853.34 | 225720 | 3801000 | 0 | 2433106.74 | 0 | 0 | 5560370.2 | 0 |  | 0 | 0 | 10239931.1 | 2991060 | 11659392 | 4014489.6 | 588591.36 | 1310126.4 | 3862657.92 | 3529348.6 | 0 | 5779992 | 0 | 4215440 | 280515.66 | 2355361 | 1022613.84 | 1669920 | 0 | 1111411.08 | 0 | 590809.6 | 5825624.15 | 580506.84 | 127440 | 1075375 | 317242.5 | 25372800 | 3423800 | 7653350.4 | 512795.52 | 187295 | 2302560 | 1156416 | 1948032 | 1373561.28 | 4043838.78 | 7006480 | 2818455.36 | 3454502.4 | 0 | 5548386.8 | 225570 | 0 | 498657.6 | 7470263 | 425124 | 200640 | 0 | 45278329.32 | 2449144.26 | 0 | 20280000 | 0 | 31158950.4 | 1055782.35 | 19872960 | 3786216 | 20130182.25 | 0 | 24437952 | 16315198.2 | 4851626.78 | 0 | 51519063.96 | 8964689.11 | 0 | 8521522.8 | 19688718 | 16220563.2 | 0 | 0 |  | 120256231.68 | 0 | 8578483.2 | 0 | 10578931.2 | 0 | 0 | 0 | 1883164.8 | 3297259.52 | 6634935 | 1782010 | 886939.45 | 22797173.76 | 0 | 0 | 0 | 4833309.6 | 2070740.08 | 11408004 | 0 | 2494980.8 | 2725632.27 | 4888411.2 | 2383396.7 | 888422.4 | 392776.2 | 147613.486 | 0 | 0 | 19869178 | 0 | 142650 | 0 | 0 | 5887428.36 | 0 | 2814172.5 | 8671017.6 | 5314363.47 | 0 | 9039275.19 | 6299078.4 | 0 | 17736126.72 | 11458045.44 | 16657305.6 | 0 | 236182.7 | 2453243.52 | 0 |  | 629965093.92 | 315506482.846 | 945471576.766 | 95034923.056 | 120256231.68 | 61092317.74 | 569973476.83 | 19869178 | 599573.34 | 51793816.07 | 25372800 | 1479260.05 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 90 | 65 | 0 | 347 |  | 0 | 390 | 255 | 0 | 95 | 41 | 213 | 0 | 35 | 0 | 80 | 102 | 0 | 87 | 0 | 0 | 13 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 20 | 0 | 64 | 35 | 90 | 0 | 4 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 60 | 95 | 31 | 20 | 2 | 100 | 100 | 0 | 310 | 0 | 184 | 8 | 85 | 38 | 49 | 0 | 25 | 0 | 0 | 8 | 11 | 5 | 25 | 21 | 128 | 136 | 33 | 20 | 0.5 | 58 | 30 | 47 | 39 | 163 | 292 | 59 | 79 | 0 | 150 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 268 | 70 | 0 | 170 | 0 | 131 | 15.56 | 100 | 0 | 143 | 0 | 108 | 108 | 34 | 4.1 | 307 | 54 | 0 | 0 | 105 | 100 | 0 | 30 |  | 561 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 16 | 96 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 36 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 78 | 0 | 196 | 0 | 398 | 0 | 0 | 108 | 0 | 113 | 0 | 6.3 | 0 | 0 |  | 9747.46 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 95 | 66 | 0 | 353 | 0 | 0 | 420 | 270 | 100 | 96 | 41 | 170 | 0 | 94 | 0 | 97 | 102 | 133 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 63 | 35 | 90 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 10 | 51 | 19 | 20 | 27 | 100 | 100 | 0 | 315 | 0 | 188 | 8 | 91 | 42 | 52 | 0 | 26 | 0 | 0 | 52 | 21 | 8 | 25 | 12 | 164 | 156 | 25 | 20 | 0 | 59 | 30 | 50 | 40 | 163 | 302 | 53 | 79 | 0 | 150 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 283 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 105 | 148 | 0 | 115 | 108 | 34 | 0 | 308 | 54 | 0 | 114 | 104 | 100 | 0 | 0 |  | 938 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 22 | 20 | 40 | 67 | 38 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 0 | 50 | 44 | 43 | 33 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 198 | 0 | 78 | 100 | 192 | 0 | 399 | 70 | 0 | 113 | 105 | 113 | 0 | 0 | 70 | 0 |  | 11673 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 42 | 220 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 52 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 65 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 22 | 30 | 100 | 100 | 0 | 360 | 0 | 215 | 26 | 90 | 42 | 50 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 32 | 22 | 173 | 160 | 30 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 330 | 66 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  |  |  | 959 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 50 | 45 | 43 | 35 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 20 | 0 | 0 | 200 | 0 | 78 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 41 | 220 | 0 | 0 | 0 | 100 | 102 | 100 | 100 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 65 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 22 | 10 | 100 | 100 | 0 | 360 | 0 | 215 | 26 | 90 | 38 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 32 | 21 | 154 | 150 | 25 | 22 | 1.6 | 60 | 30 | 51 | 44 | 163 | 330 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  |  |  | 959 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 50 | 43 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 90 | 0 | 8 | 70 | 0
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 98 | 65 | 0 | 353 | 0 | 0 | 450 | 265 | 65 | 97 | 0 | 214 | 0 | 0 | 0 | 60 | 70 | 0 | 4 | 0 | 0 | 0 | 35 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 20 | 5 | 100 | 100 | 0 | 270 | 0 | 183 | 8 | 90 | 38 | 48 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 21 | 130 | 157 | 24 | 20 | 1.1 | 59 | 30 | 50 | 40 | 163 | 256 | 61 | 79 | 0 | 150 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 95 | 0 | 0 | 108 | 0 | 98 | 9.2 | 100 | 0 | 65 | 0 | 115 | 34 | 0 | 2.4 | 233 | 0 | 0 | 0 | 57 | 100 | 0 | 0 | 0 | 941 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 77 | 0 | 187 | 0 | 407 | 0 | 0 | 35 | 0 | 92 | 0 | 1.2 | 0 | 0 | 0
199
| Minimum Generation |  | 8500.1 | 7:00
| Highest Generation |  | 11693 | 22:00
| Day Peak Generation |  | 9747.46 | 12:00
| Evening Peak Generation |  | 11673 | 21:00
| HVDC Max Flow |  | 948 | 9:00
| HVDC EvPeak Flow |  | 938 | 21:00
| Load factor L.F |  | 86.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-24
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9747.46 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8976.9 | MW
Evening Peak Generation : |  | 11673 | MW Hour : | 21:00 | Available Max Generation : |  | 14790 | MW
E.P. Demand (at gen end) : |  | 11673 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11693 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2790 | MW
Total Gen. (MKWH) : |  | 243.0219 | System Load Factor : | 86.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -438 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-24
Actual : | 83.98 | Ft.(MSL) , | Rule curve : | 82.11 | Ft.( MSL )
Gas Consumed : | Total = | 1155.99 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 156127240.796
: |  | Coal : | 19869178 | Oil : | 621767292.9 | Total : | 797763711.696
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4237.2748 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1443.0056 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1293.259 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1168.7013 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1056.0653 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 852.2126 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 473.816 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.3504 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 657.2816 |  |  | 0 | 0%
Total | 0 |  | 11400.9665 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10) Ashuganj(S) 360 MW
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Baghabari-100, 71 MW
9) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ishurdi-Pabna 132 kV Ckt tripped at 10:19 showing E/F relay and was switched on at 10:51.
b) Pabna-Shahjadpur 132 kV Ckt tripped at 10:19 showing dist.Z3,A/R at Pabna end & dist.Z1,BC-phase |  |  |  |  | About 90 MW power interruption occurred under Pabna S/S
at Shahjadpur end and was switched on at 11:51. |  |  |  |  | area from 10:19 to 10:51.
c) Matuail-Siddirganj 132 kV Ckt tripped at 10:29 showing O/C, AB-phase at Siddirganj end and was switched |  |  |  |  | About 78 MW power interruption occurred under Matuail S/S area
on at 10:40. |  |  |  |  | from 10:29 to 10:40.
d) Sylhet-150 MW tripped at 13:04 due to GT encloser ventilation fault and was synchronized at 13:54.
e) HVDC Bheramara pole-1 tripped at 10:45 due to external protection and was synchronized at 14:29.
f) Sonargaon-Daudkandi 132 kV Ckt-2 was under shut down from 11:40 to 14:03 for C/M.
g) Khulshi-Rampur 132 kV Ckt was under shut down from 17:56 to 17:58 for relay test.
h) After maintenance Madaripur 132/33 kV T-3 transformer was switched on at 16:19.
i) Cumilla(N)-Chowddagram 132 kV Ckt-2 tripped at 15:01 showing dist.A-phase, ARC at Cumilla(N) end &
dist.Z1,R-phase at Chowddagram end and was switched on at 15:28.
j) Chowmuhoni 132/33 kV T-1 transformer is under shut down since 06:30 to 11:35(24/6/20) for C/M. |  |  |  |  | About 25 MW power interruption occurred under Chowmuhoni S/S area
from 06:30 to 11:35(24/6/20).
k) Siddirganj peaking GT-1 tripped at 07:28(24/6/20) due to problem with exhaust valve.
l) Siddirganj 132/33 kV T-2 transformer was under shut down from 07:11 to 07:40(24/6/20) for C/M. |  |  |  |  | About 15 MW power interruption occurred under Siddirganj S/S area
m) Megnaghat-Haripur 230 kV Ckt-2 is under shut down since 07:56(24/6/20) for D/W. |  |  |  |  | from 07:11 to 07:40(24/6/20).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 750000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6814036
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1488032 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 2186045 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 8019000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9390000 | Frequency Control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1669440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6332276 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2308992
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 41 | 991835 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 1249875
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 426780
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 94 | 1262000 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 97 | 2169600
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 170 | 4944166 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2442096
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 236400 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1283400
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1241760 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1327396
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1016039
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1262580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 808300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 695500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 550452 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 283 | 5989197
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 144237 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 3166560 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 108 | 1726476
| Sonargoan 104 MW (Orion) |  | IPP | 18.5*6 | 104 MW | 0 | 308160
| Dhaka area Total |  |  |  | 5791 | 3335 | 72200630
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 261906
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 90315
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 506880 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 98 | 2220642 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3270806 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 34 | 557018 | Low demand
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1055663
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 313200 | Low demand
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2438400
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 467136
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 441120
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 1340160 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34800
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 308 | 6814691
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1029241
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2435520
| Chattogram area Total |  |  |  | 2266 | 1178 | 25377498
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2609904
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2384695 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 188 | 4582000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7810800 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 904968 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1192800
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 26 | 649948 | Gas shortage.
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 148 | 2855345
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 58496 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2048140
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 105 | 348960 | Low demand
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 457092
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 169920 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 164 | 3383040
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 614500 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 610013
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 12 | 422990 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 853860
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 2297400 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1675 | 34472325
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3230000 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 403776
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 25 | 842880 | Low demand
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11750
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 185 | 3900000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2679600 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 501 | 11068006
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1404000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 722760
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3547227
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 302 | 6737000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1094400
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 40 | 880488
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 53 | 1430688 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1808640 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3207160
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 103000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 566832
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7396300 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 244440
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1288 | 29406935
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 938 | 20877818
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1345920
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 22 | 179520
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 20 | 314624 | Low demand
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8169984 | Gas shortage.
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 636750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 509760
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 603360 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 105 | 1213776
| Khulna Area Total |  |  |  | 2284 | 1755 | 33851512
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 2335776
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 572219
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1577000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1876115 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 0 | 0 | Under maint.
| Barisal Area Total |  |  |  | 1054 | 293 | 6361110
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 491190
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 203813
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 184540
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 281283
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4460173 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 192 | 4542191 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 399 | 9130581 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 245711
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 462720
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 253404
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 194998
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 504480 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1289040
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1868928
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 331968 | Low demand
| Rajshahi Area Total |  |  |  | 2183 | 1376 | 24445020
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3665900 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 5000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2146560
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 21374
| Rangpur Area Total |  |  |  | 605 | 272 | 5838834
| Total |  |  |  | 19788 | 11673 | 243021870
| Eastern Grid Total |  |  |  | 13662 | 7977 | 172525394
| Western Grid Total |  |  |  | 6126 | 3696 | 70496476
| National Grid Total |  |  |  | 19788 | 11673 | 243021870
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-23
(a) ENTIRE EASTERN GRID : |  | 7325 | MW | (b) ENTIRE WESTERN GRID : |  | 3754 | MW
i) Dhaka area |  | 3751 | MW | i) Khulna area |  | 1431 | MW
ii) Chittagong area |  | 1095 | MW | ii) Rajshahi area |  | 1217 | MW
iii) Comilla area |  | 1080 | MW | iii) Barisal area |  | 348 | MW
iv) Mymensingh area |  | 924 | MW | iv) Rangpur area |  | 758 | MW
v) Sylhet area |  | 475 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11079 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 11:00 | Sherpur | 110 | 21:00 | Benapol | 48 | 19:30
Munsiganj | 112 | 1:00 | Srimongal | 47 | 21:00 | Jhenida | 102 | 22:00
Sonargaon | 71 | 1:00 | Shahjibazar | 108 | 23:00 | Bottail | 126 | 19:30
Shyampur | 184 | 24:00 | Fenchuganj | 45 | 20:00 | G.K Project | 58 | 20:00
Bhulta | 185 | 24:00 | Kulawara | 47 | 21:00 | Faridpur | 181 | 0.91667
Madanganj | 53 | 14:00 | Sylhet | 117 | 21:00 | Madaripur | 101 | 0.875
Shitalakhya | 111 | 15:00 | Chatak | 28 | 19:30 | Sariatpur | 66 | 22:00
Rahim steel | 22 | 10:00 | Sunamganj | 45 | 21:00 | Gopalganj | 94 | 19:30
Matuail | 85 | 12:00 | Biani Bazar | 60 | 19:30 | Bagerhat | 88 | 0.875
Ghorasal | 76 | 22:00 | Comilla (S) | 166 | 22:00 | Mongla | 36 | 10:00
Narsingdi | 159 | 23:00 | Comilla(N) | 99 | 20:00 | Satkhira | 103 | 0.91667
Haripur (SBU) | 101 | 13:00 | Chandpur | 98 | 23:00 | Gallamari | 41 | 20:00
Ullon | 58 | 21:00 | Feni | 114 | 22:00 | Magura | 52 | 0.875
Hasnabad | 190 | 21:00 | Chowmuhani | 166 | 22:00 | Norail | 40 | 20:00
Magbazar | 100 | 13:00 | Ashuganj | 64 | 24:00 | Chuadanga | 86 | 19:30
Maniknagar | 100 | 15:00 | Daudkandi | 138 | 23:00 | Barisal(N) | 40 | 0.875
Bangabhaban | 30 | 11:00 | B.Baria | 151 | 21:00 | Barisal (S) | 100 | 0.875
Narinda | 90 | 15:00 | Ramganj | 106 | 21:00 | Patuakhali | 117 | 0.875
Dhanmondi | 136 | 12:00 | Chaddagram | 34 | 21:00 | Bhandaria | 50 | 21:00
Lalbag | 87 | 13:00 | PHP | 10 | 7:00 | Borhan Uddin | 44 | 20:00
Madartek | 69 | 22:00 | Madunaghat | 52 | 19:30 | Ishurdi | 60 | 21:00
Dhaka University |  |  | Hathazari | 98 | 0.8125 | Ruppur Paromanobik | 2 | 8:00
Mirpur | 99 | 15:00 | Khulshi | 191 | 0.5 | Natore | 112 | 20:00
Kalyanpur | 84 | 21:00 | Halishahar | 137 | 0.625 | Bogra | 153 | 21:00
Gulshan | 120 | 15:00 | Baraulia | 137 | 0.625 | Noagaon | 136 | 21:00
Uttara | 81 | 15:00 | Sikalbaha | 23 | 0.875 | Rajshahi | 152 | 20:00
Uttara New | 22 | 16:00 | Dohazari | 96 | 0.83333 | Rajshahi New | 11 | 21:00
Kamrangirchar | 88 | 12:00 | Cox'sbazar | 93 | 0.83333 | C.Nawabganj | 76 | 21:00
Savar | 139 | 10:00 | Chandraghona | 30 | 0.8125 | Amnura | 42 | 20:00
Bhasantec | 145 | 15:00 | Kaptai | 4.2 | 0.79167 | Pabna | 127 | 21:00
Agargaon | 62 | 15:00 | A. Khaer Stl. | 11 | 0.875 | Shahjadpur | 101 | 21:00
Satmosjid | 92 | 15:00 | Bakulia | 104 | 0.45833 | Serajganj | 102 | 20:00
Tongi | 138 | 0.41667 | Julda | 19 | 0.58333 | Niyamatpur | 54 | 20:00
Kabirpur | 213 | 16:00 | TK chemical | 17.1 | 0.91667 | Joypurhat | 42 | 19:30
Basundhara | 116 | 14:00 | Modern Steel | 15 | 0.66667 | Sherpur(Bogura) | 45 | 21:00
Manikganj | 72 | 21:00 | Shahmirpur | 28.5 | 0.95833 | Mohastangor | 56 | 19:30
Joydevpur | 167 | 15:00 | Khagrachhari | 24 | 0.91667 | Rangpur | 145 | 19:30
New Tongi | 100 | 12:00 | Matarbari | 35 | 0.875 | Lalmonirhat | 57 | 21:00
Kodda | 236 | 14:00 | Baroiar Hat | 36 | 0.79167 | Saidpur | 109 | 21:00
Dhamrai | 90 | 19:30 | Rangamati | 12 | 0.8125 | Purbasadipur | 108 | 20:00
Rajendrapur | 94 | 19:00 | Abul Khair 230 | 33 | 0.41667 | Thakurgaon | 82 | 21:00
Valuka | 92 | 19:30 | BSRM | 158 | 0.33333 | Palashbari | 120 | 20:00
Tangail | 184 | 22:00 | GPH Ispat | 66 | 0.83333 | Barapukuria | 49 | 21:00
Mymensing | 224 | 20:00 | Goalpara | 19 | 13:00 | Panchagar | 44 | 19:30
Kishorganj | 138 | 21:00 | Central s/s | 92 | 20:00 | Joldhaka | 29 | 21:00
Netrokona | 111 | 20:00 | Noapara | 64 | 20:00 | Kurigram | 57 | 20:00
Jamalpur | 132 | 20:00 | Jessore | 108 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 399 | 8:00 | 393 | 16:00 | Kaliakoir | 382 | 0.125 | 375 | 0.375
| Bheramara | 409 | 11:00 | 384 | 21:00 | Bhulta | 392 | 0.125 | 383 | 0.66667
| Ashuganj(N) | 397 | 5:00 | 391 | 10:00 | Gopalganj | 417 | 0.75 | 383 | 0.79167
| Payra | 420 | 18:00 | 371 | 19:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 1:00 | 235 | 7:00 | Comilla (N) | 236 | 19:30 | 233 | 4:00
| Ishurdi | 235 | 11:00 | 223 | 22:00 | Hathazari | 229 | 18:00 | 224 | 9:00
| Ashuganj | 236 | 2:00 | 234 | 9:00 | Megnaghat | 235 | 18:30 | 230 | 15:00
| Serajganj | 232 | 18:00 | 225 | 21:00 | Fenchuganj | 240 | 12:00 | 236 | 1:00
| Baghabari | 240 | 11:00 | 235 | 21:00 | Siddhirganj | 233 | 2:00 | 228 | 10:00
| Barapukuria | 234 | 18:30 | 225 | 20:00 | Maniknagar | 231 | 4:00 | 225 | 11:00
| Bogra | 229 | 14:00 | 219 | 19:30 | Agargaon | 229 | 2:00 | 222 | 16:00
| Rajshahi | 232 | 18:00 | 220 | 22:00 | Barisal | 251 | 11:00 | 226 | 19:00
| Khulna South | 224 | 18:00 | 209 | 19:00 | AKSML | 227 | 18:00 | 221 | 3:00
| Rampura | 228 | 1:00 | 222 | 11:00 | BSRM | 226 | 18:00 | 221 | 3:00
| Haripur | 230 | 1:00 | 226 | 16:00 | Bibiyana | 241 | 15:00 | 234 | 12:00
| Hasnabad | 231 | 23:00 | 224 | 9:00 | Bhulta | 233 | 3:00 | 227 | 11:00
| Shyampur | 227 | 2:00 | 222 | 16:00 | Ashuganj (S) | 236 | 3:00 | 233 | 16:00
| Aminbazar | 230 | 1:00 | 224 | 10:00 | Kaliakoir | 234 | 5:00 | 228 | 16:00
| Tongi | 230 | 19:30 | 224 | 5:00 | GPH | 224 | 5:00 | 221 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 18:30 | 128 | 11:00 | Hathazari | 136 | 0.75 | 133 | 0.20833
| Munsiganj | 136 | 18:00 | 131 | 9:00 | Khulshi | 134 | 0.70833 | 129 | 0.375
| Sonargaon | 133 | 19:00 | 127 | 9:00 | Halishahar | 138 | 0.75 | 133 | 0.45833
| Shyampur | 137 | 2:00 | 132 | 11:00 | Baraulia | 134 | 0.041667 | 131 | 0.45833
| Bhulta | 127 | 19:00 | 121 | 11:00 | Sikalbaha | 138 | 18:00 | 134 | 0.29167
| Madanganj | 134 | 22:00 | 130 | 7:00 | Dohazari | 135 | 18:30 | 129 | 0.66667
| Shitalakhya | 142 | 2:00 | 136 | 9:00 | Cox'sbazar | 124 | 0 | 113 | 0.79167
| Rahim steal | 134 | 19:00 | 129 | 10:00 | Chandraghona | 137 | 0.77083 | 133 | 0.375
| Matuail | 133 | 18:30 | 128 | 11:00 | Kaptai | 135 | 8:00 | 132 | 0.041667
| Ghorasal | 138 | 1:00 | 133 | 7:00 | A. Khaer Stl. | 134 | 0.8125 | 132 | 3:00
| Narsinghdi | 129 | 5:00 | 123 | 23:00 | Bakulia | 136 | 0.75 | 132 | 0.125
| Haripur (SBU) | 132 | 5:00 | 130 | 14:00 | Julda | 138 | 0.75 | 133 | 0.625
| Ullon | 135 | 4:00 | 131 | 9:00 | TK Chemical | 137 | 0.5 | 132 | 8:00
| Hasnabad | 139 | 1:00 | 135 | 10:00 | Modern Steel | 136 | 0.75 | 132 | 0.29167
| Magbazar | 135 | 3:00 | 130 | 11:00 | Shahmirpur | 138 | 0.75 | 133 | 0.33333
| Maniknagar | 135 | 3:00 | 130 | 11:00 | Khagrachhari | 135 | 0.75 | 132 | 0.41667
| Bangabhaban | 135 | 3:00 | 130 | 11:00 | Matarbari | 128 | 0.75 | 119 | 0.79167
| Narinda | 135 | 3:00 | 130 | 11:00 | Baroiar Hat | 133 | 0.29167 | 130 | 0.66667
| Dhanmondi | 135 | 4:00 | 131 | 9:00 | Rangamati | 136 | 0.75 | 133 | 9:00
| Lalbag | 138 | 2:00 | 131 | 9:00 | Goalpara S/S | 136 | 1:00 | 127 | 7:00
| Madartek | 135 | 2:00 | 130 | 16:00 | Khulna Central S/S | 135 | 0.75 | 127 | 1:00
| Dhaka University |  |  |  |  | Noapara | 133 | 18:30 | 124 | 1:00
| Mirpur | 133 | 4:00 | 127 | 16:00 | Jessore | 127 | 5:00 | 117 | 21:00
| Kalyanpur | 134 | 4:00 | 129 | 16:00 | Benapol | 129 | 18:30 | 116 | 19:00
| Gulshan | 135 | 5:00 | 130 | 16:00 | Jhenida | 126 | 0.75 | 110 | 21:00
| Uttara | 133 | 6:00 | 127 | 15:00 | Bottail | 132 | 18:00 | 121 | 21:00
| Uttara New | 134 | 5:00 | 126 | 16:00 | G.K Project | 138 | 0.45833 | 130 | 21:00
| Kamrangirchar | 136 | 5:00 | 131 | 12:00 | Faridpur | 133 | 18:00 | 121 | 21:00
| Savar | 132 | 5:00 | 127 | 16:00 | Madaripur | 136 | 0.45833 | 121 | 19:00
| Bhasantec | 131 | 5:00 | 125 | 16:00 | Shariyatpur S/S | 139 | 0.75 | 125 | 19:00
| Agargaon | 132 | 5:00 | 127 | 15:00 | Gopalganj | 144 | 18:00 | 130 | 13:00
| Satmosjid | 131 | 5:00 | 125 | 16:00 | Bagerhat | 136 | 0.20833 | 120 | 22:00
| Tongi | 137 | 0.875 | 131 | 9:00 | Mongla | 131 | 0.75 | 116 | 19:00
| Kabirpur | 134 | 8:00 | 129 | 21:00 | Satkhira | 133 | 0.75 | 123 | 1:00
| Basundhara | 135 | 21:00 | 130 | 16:00 | Gallamari | 135 | 3:00 | 125 | 19:00
| Manikganj | 139 | 1:00 | 129 | 9:00 | Magura | 125 | 0.75 | 108 | 19:00
| Joydevpur | 142 | 14:00 | 136 | 12:00 | Norail | 124 | 0.75 | 104 | 21:00
| New Tongi | 136 | 0.875 | 130 | 16:00 | Chuadanga | 121 | 18:00 | 101 | 21:00
| Kodda | 138 | 2:00 | 124 | 0.375 | Barisal(N) | 142 | 11:00 | 128 | 19:00
| Dhamrai | 132 | 18:00 | 127 | 21:00 | Barisal (S) | 140 | 0.75 | 128 | 19:00
| Rajendrapur | 136 | 1:00 | 124 | 8:00 | Patuakhali | 136 | 0.75 | 125 | 19:00
| Valuka | 127 | 5:00 | 111 | 23:00 | Bhandaria | 135 | 11:00 | 116 | 21:00
| Tangail | 135 | 5:00 | 125 | 21:00 | Ishurdi | 137 | 11:00 | 130 | 21:00
| Mymensing | 130 | 8:00 | 114 | 23:00 | Ruppur Paromanobik | 135 | 6:00 | 131 | 21:00
| Kishorganj | 130 | 6:00 | 117 | 23:00 | Natore | 135 | 14:00 | 128 | 3:00
| Netrokona | 127 | 6:00 | 109 | 23:00 | Bogra | 138 | 18:00 | 128 | 21:00
| Jamalpur | 138 | 6:00 | 126 | 23:00 | Noagaon | 129 | 11:00 | 123 | 19:30
| Sherpur | 138 | 7:00 | 124 | 0.95833 | Rajshahi | 133 | 18:00 | 128 | 1:00
| Srimongal | 137 | 6:00 | 132 | 0.875 | Rajshahi New | 133 | 18:00 | 127 | 1:00
| Shahjibazar | 136 | 7:00 | 130 | 0.91667 | C.Nawabganj | 131 | 14:00 | 125 | 21:00
| Fenchuganj | 136 | 8:00 | 133 | 0.041667 | Amnura | 134 | 18:00 | 124 | 15:00
| Khulawara | 135 | 6:00 | 131 | 0.95833 | Pabna | 135 | 11:00 | 128 | 1:00
| Sylhet | 133 | 5:00 | 129 | 0.58333 | Shahjadpur | 139 | 18:00 | 134 | 11:00
| Chatak | 132 | 7:00 | 128 | 1:00 | Serajganj | 133 | 14:00 | 128 | 19:30
| Sunamganj | 131 | 8:00 | 125 | 0.95833 | Niyamatpur | 128 | 18:00 | 120 | 20:00
| Biani Bazar | 133 | 7:00 | 127 | 0.041667 | Joypurhat | 130 | 10:00 | 121 | 1:00
| Comilla(s) | 127 | 13:00 | 121 | 22:00 | Sherpur(Bogura) | 138 | 18:00 | 127 | 21:00
| Comilla(n) | 138 | 23:00 | 134 | 16:00 | Mohastangor | 133 | 18:00 | 125 | 1:00
| Chandpur | 135 | 20:00 | 130 | 8:00 | Rangpur | 131 | 11:00 | 119 | 21:00
| Feni | 137 | 20:00 | 130 | 17:00 | Lalmonirhat | 125 | 11:00 | 112 | 21:00
| Chowmuhani | 133 | 20:00 | 126 | 8:00 | Saidpur | 130 | 18:00 | 114 | 21:00
| Ashuganj | 136 | 12:00 | 131 | 24:00 | Purbasadipur | 126 | 17:00 | 110 | 19:30
| Daudkandi | 134 | 19:00 | 128 | 10:00 | Thakurgaon | 125 | 10:00 | 108 | 19:30
| B.Baria | 133 | 17:00 | 126 | 23:00 | Palashbari | 128 | 14:00 | 115 | 19:00
| Ramganj | 130 | 21:00 | 118 | 19:30 | Barapukuria | 134 | 18:30 | 125 | 21:00
| Chaddagram | 135 | 20:00 | 131 | 9:00 | Panchagar | 122 | 17:00 | 106 | 19:30
| PHP | 136 | 20:00 | 130 | 14:00 | Joldhaka | 129 | 18:30 | 112 | 20:00
| Madanhat | 139 | 18:00 | 135 | 7:00 | Kurigram | 129 | 10:00 | 113 | 20:00

## L-Curve
Date | 2020-06-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 181 | 7961 | 3713 | 11674 |  |  |  | QF-LDC-12
0:30 | 309.5 | 7855.5 | 3439.5 | 11295 | Date: | 2020-06-23
1:00 | 438 | 7750 | 3166 | 10916
1:30 | 413 | 7622.5 | 3166 | 10788.5
2:00 | 388 | 7495 | 3166 | 10661
2:30 | 373.5 | 7443.5 | 3124.5 | 10568 | [5 empty] | Gen. at Eve. Peak | 11673 | 11673 MW (21:00 )
3:00 | 359 | 7392 | 3083 | 10475 | [6 empty] | 21:00
3:30 | 373.5 | 7252 | 3017 | 10269 | [5 empty] | Gen. at Day Peak | 9747.46 | 9747.46 MW (12:00 )
4:00 | 388 | 7112 | 2951 | 10063 | [6 empty] | 12:00
4:30 | 359.5 | 7034 | 2887.5 | 9921.5 | [5 empty] | Highest Generation | 11693
5:00 | 331 | 6956 | 2824 | 9780 | [6 empty] | 22:00
5:30 | 280.5 | 6643.6 | 2614.05 | 9257.65
6:00 | 230 | 6331.2 | 2404.1 | 8735.3
6:30 | 217 | 6214.05 | 2403.65 | 8617.7
7:00 | 204 | 6096.9 | 2403.2 | 8500.1
7:30 | 188 | 6157.95 | 2411.3 | 8569.25
8:00 | 172 | 6219 | 2419.4 | 8638.4
8:30 | 155.5 | 6319.4 | 2427.1 | 8746.5
9:00 | 139 | 6419.8 | 2434.8 | 8854.6
9:30 | 103.5 | 6544.935 | 2464.65 | 9009.585
10:00 | 68 | 6670.07 | 2494.5 | 9164.57
10:30 | 131.5 | 6803.72 | 2388.4 | 9192.12
11:00 | 195 | 6937.37 | 2282.3 | 9219.67
11:30 | 250.5 | 7114.765 | 2368.8 | 9483.565
12:00 | 306 | 7292.16 | 2455.3 | 9747.46
12:30 | 341.5 | 7295.89 | 2478.3 | 9774.19
13:00 | 377 | 7299.62 | 2501.3 | 9800.92
13:30 | 368.5 | 7378.41 | 2479.65 | 9858.06
14:00 | 360 | 7457.2 | 2458 | 9915.2
14:30 | 200 | 7535.25 | 2582 | 10117.25
15:00 | 40 | 7613.3 | 2706 | 10319.3
15:30 | 35 | 7383.9 | 2767.5 | 10151.4
16:00 | 30 | 7154.5 | 2829 | 9983.5
16:30 | 51.5 | 6815.8 | 2778.75 | 9594.55
17:00 | 73 | 6477.1 | 2728.5 | 9205.6
17:30 | 103 | 6289.55 | 2730.35 | 9019.9
18:00 | 133 | 6102 | 2732.2 | 8834.2
18:30 | 74 | 6463 | 2885.1 | 9348.1
19:00 | 15 | 6824 | 3038 | 9862
19:30 | 262 | 7787 | 3511 | 11298
20:00 | 293 | 7950 | 3627 | 11577 |  |  |  | Executive Engineer
20:30 | 299.5 | 7963.5 | 3661.5 | 11625 |  |  |  | Network Operation Division
21:00 | 306 | 7977 | 3696 | 11673
21:30 | 271.5 | 7970.5 | 3712.5 | 11683
22:00 | 237 | 7964 | 3729 | 11693 |  |  |  |  | Page 6 of 7
22:30 | 229.5 | 7949.5 | 3717 | 11666.5
23:00 | 222 | 7935 | 3705 | 11640
23:30 | 201.5 | 7948 | 3709 | 11657
24:00 | 181 | 7961 | 3713 | 11674
11673 MW (21:00 )
9747.46 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-23 |  | Energy | 243021870
[10 empty] | 2020-06-23 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3541 | 942 | 2306 | 3935 | 149 | 100 | 579 | 0 | 160
0:30 | 3461 | 942.5 | 2247.5 | 3790 | 149 | 100.5 | 466.5 | 0 | 157 | Date: | 2020-06-23
1:00 | 3381 | 943 | 2189 | 3645 | 149 | 101 | 354 | 0 | 154
1:30 | 3371 | 943.5 | 2171 | 3569.5 | 149 | 99 | 333.5 | 0 | 152 | [7 empty] | Total Energy | 243.0219 | Total Energy Gen 243.022 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.022 MKWHr
2:00 | 3361 | 944 | 2153 | 3494 | 149 | 97 | 313 | 0 | 150 | [7 empty] | Energy not Served | 0
2:30 | 3373.5 | 944 | 2160.5 | 3421 | 149 | 97 | 275 | 0 | 148 | [7 empty] | Energy Requirement | 243.0219
3:00 | 3386 | 944 | 2168 | 3348 | 149 | 97 | 237 | 0 | 146
3:30 | 3392.5 | 944 | 2161 | 3184.5 | 149 | 96.5 | 194.5 | 0 | 147 | [6 empty] | Shortage
4:00 | 3399 | 944 | 2154 | 3021 | 149 | 96 | 152 | 0 | 148
4:30 | 3379.5 | 943.5 | 2151.5 | 2950.5 | 149 | 95.5 | 108 | 0 | 144
5:00 | 3360 | 943 | 2149 | 2880 | 149 | 95 | 64 | 0 | 140
5:30 | 3364.5 | 943 | 2104 | 2430.5 | 149 | 95.5 | 40.5 | 0 | 130
6:00 | 3369 | 943 | 2059 | 1981 | 149 | 96 | 17 | 0 | 120
6:30 | 3367 | 943 | 2061.5 | 1871.5 | 149 | 96 | 8.5 | 0 | 118 |  |  |  |  | Coal
7:00 | 3365 | 943 | 2064 | 1762 | 149 | 96 | 0 | 0 | 116
7:30 | 3367.5 | 943.5 | 2101.5 | 1787.5 | 149 | 96 | 0 | 0 | 118 |  |  |  | Oil |  |  |  | ,
8:00 | 3370 | 944 | 2139 | 1813 | 149 | 96 | 0 | 0 | 120
8:30 | 3357 | 946 | 2154 | 1913.5 | 149 | 96 | 0 | 0 | 121
9:00 | 3344 | 948 | 2169 | 2014 | 149 | 96 | 0 | 0 | 122
9:30 | 3371.5 | 948 | 2130 | 2183 | 149 | 96 | 0 | 0 | 121
10:00 | 3399 | 948 | 2091 | 2352 | 149 | 96 | 0 | 0 | 120
10:30 | 3383 | 755 | 2121.5 | 2538.5 | 149.5 | 97 | 15 | 0 | 120
11:00 | 3367 | 562 | 2152 | 2725 | 150 | 98 | 30 | 0 | 120
11:30 | 3398 | 561.5 | 2136 | 2954.5 | 150 | 98.5 | 40 | 0 | 124
12:00 | 3429 | 561 | 2120 | 3184 | 150 | 99 | 50 | 0 | 128
12:30 | 3358 | 551.5 | 2103.5 | 3274.5 | 150 | 99 | 85 | 0 | 124
13:00 | 3287 | 542 | 2087 | 3365 | 150 | 99 | 120 | 0 | 120
13:30 | 3287 | 542 | 2087 | 3365 | 150 | 99 | 120 | 0 | 120
14:00 | 3287 | 542 | 2087 | 3365 | 150 | 99 | 120 | 0 | 120
14:30 | 3349.5 | 612.5 | 2116.5 | 3417 | 149.5 | 98 | 159 | 0 | 134
15:00 | 3412 | 683 | 2146 | 3469 | 149 | 97 | 198 | 0 | 148
15:30 | 3403 | 806.5 | 2104.5 | 3233.5 | 149 | 97 | 198 | 0 | 145
16:00 | 3394 | 930 | 2063 | 2998 | 149 | 97 | 198 | 0 | 142
16:30 | 3317 | 930 | 1978 | 2796.5 | 149 | 95.5 | 181 | 0 | 137
17:00 | 3240 | 930 | 1893 | 2595 | 149 | 94 | 164 | 0 | 132
17:30 | 3190 | 933 | 1811 | 2521 | 149 | 94.5 | 190 | 0 | 126
18:00 | 3140 | 936 | 1729 | 2447 | 149 | 95 | 216 | 0 | 120
18:30 | 3263 | 936.5 | 1839 | 2563.5 | 149 | 95.5 | 360.5 | 0 | 140
19:00 | 3386 | 937 | 1949 | 2680 | 149 | 96 | 505 | 0 | 160
19:30 | 3551 | 937 | 2244 | 3591 | 149 | 96 | 570 | 0 | 160
20:00 | 3540 | 937 | 2229 | 3839 | 149 | 96 | 625 | 0 | 162
20:30 | 3530.5 | 937.5 | 2232.5 | 3925.5 | 149 | 97 | 590 | 0 | 163
21:00 | 3521 | 938 | 2236 | 4012 | 149 | 98 | 555 | 0 | 164
21:30 | 3539.5 | 938 | 2219 | 4006.5 | 149 | 98 | 568 | 0 | 165
22:00 | 3558 | 938 | 2202 | 4001 | 149 | 98 | 581 | 0 | 166
22:30 | 3545.5 | 939.5 | 2218.5 | 3968 | 149 | 98.5 | 581.5 | 0 | 166
23:00 | 3533 | 941 | 2235 | 3935 | 149 | 99 | 582 | 0 | 166
23:30 | 3537 | 941.5 | 2270.5 | 3935 | 149 | 99.5 | 580.5 | 0 | 163 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3541 | 942 | 2306 | 3935 | 149 | 100 | 579 | 0 | 160
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 243.022 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 243.022 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 66 | 62 | 62 | 61 | 60 | 61 | 61 | 61 | 61 | 61 | 63 | 64 | 64 | 63 | 62 | 62 | 59 | 60 |  | 61 | 61 | 61 | 63 | 63 | 64 | 65 | 1384642
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 4 | 16 | 24 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 261906
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.8 | 2.7 | 4.4 | 5.2 | 1.67 | 4.77 | 15.56 | 17.12 | 16.8 | 13.6 | 9.2 | 4 | 0.6 | [8 empty] | 90315
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 140 | 141 | 140 | 140 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 139 | 104 |  | 116 | 143 | 139 | 140 | 140 | 140 | 140 | 3270806
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 102 | 102 | 102 | 64 | 17 | [13 empty] | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1055663
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [9 empty] | 4 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 557018
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 31 | 50 | 34 |  |  |  |  | 58496
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 85 | 35 | 35 | 35 | 34 | 32 | 35 | 32 | 32 |  | 82 | 93 | 95 | 94 | 95 | 95 | 95 | 1262000
17 | Siddhirganj 335 MW CCPP | 218 | 220 | 218 | 218 | 219 | 217 | 214 | 219 | 219 | 180 | 213 | 213 | 170 | 170 | 211 | 212 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 215 | 4944166
18 | Kodda 300 MW PP Unit-2 (Summit) | 268 | 268 | 268 | 268 | 268 | 130 | 95 | 106 | 193 | 270 | 268 | 268 | 270 | 275 | 285 | 283 | 220 | 220 |  | 230 | 285 | 285 | 283 | 285 | 285 | 283 | 5989197
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 750000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6814036
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2609904
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384695
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 | 39 | 39 | 38 | 38 | 38 | 35 | 35 | 39 | 41 |  | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 904968
33 | Ashuganj 225 MW CCPP | 188 | 183 | 183 | 183 | 182 | 194 | 204 | 182 | 182 | 195 | 186 | 184 | 184 | 202 | 201 | 201 | 193 | 177 |  | 204 | 196 | 198 | 188 | 197 | 172 | 160 | 4582000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 320 | 340 | 310 | 310 | 270 | 285 | 310 | 310 | 330 | 310 | 310 | 290 | 270 |  | 340 | 305 | 310 | 315 | 315 | 345 | 310 | 7810800
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 51 | 52 | 53 | 51 | 50 | 48 | 48 | 45 | 49 | 48 | 47 | 47 | 49 | 48 | 48 |  | 50 | 50 | 52 | 52 | 52 | 51 | 52 | 1192800
36 | Chandpur 150 MW CCPP | 90 | 80 | 85 | 85 | 80 | 90 | 90 | 80 | 90 | 82 | 90 | 85 | 84 | 90 | 82 | 88 | 84 | 80 |  | 90 | 90 | 90 | 91 | 90 | 90 | 86 | 2048140
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 370 | 370 | 400 | 400 | 450 | 450 | 390 | 390 | 400 | 400 | 400 | 360 | 320 |  | 370 | 420 | 420 | 420 | 390 | 420 | 450 | 9390000
41 | Haripur 360MW CCPP(HPL) | 351 | 356 | 356 | 355 | 353 | 354 | 307 | 333 | 353 | 325 | 344 | 347 | 324 | 346 | 345 | 323 | 283 | 283 |  | 304 | 349 | 352 | 353 | 353 | 355 | 354 | 8019000
42 | RPCL 210MW CCPP | 138 | 141 | 140 | 141 | 141 | 140 | 138 | 138 | 138 | 136 | 135 | 136 | 123 | 122 | 124 | 119 | 133 | 137 |  | 128 | 155 | 154 | 156 | 155 | 154 | 155 | 3230000
43
44 | Fenchugonj CCPP Phase-1 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 59 | 59 | 59 | 58 | 1404000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 722760
46 | Shajibazar 330 MW CCPP | 315 | 292 | 308 | 304 | 290 | 298 | 307 | 291 | 295 | 292 | 290 | 292 | 291 | 306 | 290 | 302 | 290 | 290 |  | 323 | 319 | 301 | 302 | 303 | 272 | 270 | 6737000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 61 | 61 | 61 | 61 | 61 | 61 | 59 | 60 | 59 | 59 | 59 | 60 | 59 | 59 | 59 | 59 |  | 59 | 59 | 60 | 53 | 59 | 59 | 60 | 1430688
48 | Shahjibazar 86MW PP (Shahjibazar) | 79 | 79 | 79 | 79 | 80 | 79 | 80 | 79 | 79 | 79 | 79 | 79 | 79 | 76 | 79 | 79 | 79 | 30 |  | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 1808640
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 151 | 150 | 150 | 150 | 150 | 150 | 100 | 150 | 150 | 150 | 150 | 150 | 70 | 15 | 150 | 150 | 130 | 100 |  | 90 | 150 | 150 | 150 | 150 | 150 | 150 | 3207160
51 | Sylhet 20 MW GTPP | [19 empty] | 18 | 18 | 17 | 17 | 18 | 18 | 17 | 103000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244440
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 47 | 47 | 46 | 42 | 42 | 42 | 45 | 47 | 47 | 47 | 47 | 47 | 24 | 22 |  | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 1094400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566832
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 285 | 285 | 305 | 280 | 310 | 300 | 300 | 305 | 295 | 285 | 290 | 305 | 310 | 280 | 295 | 285 |  | 270 | 330 | 310 | 300 | 310 | 320 | 315 | 7396300
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | [5 empty] | 52 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1016039
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467136
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 426780
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 403776
63 | Impoprt (Tripura) | 154 | 150 | 146 | 148 | 140 | 120 | 116 | 120 | 122 | 120 | 120 | 128 | 120 | 146 | 148 | 142 | 132 | 120 |  | 160 | 160 | 162 | 164 | 166 | 166 | 160 | 3383040
64 | Malancha, Ctg. EPZ (United) | 32 | 32 | 40 | 40 | 41 | 41 | 33 | 10 | 3 | 2 | 2 | 2 | 8 | 2 | 2 | 5 | 11 | 10 |  | 20 | 22 | 22 | 27 | 31 | 26 | 25 | 441120
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 11 | 18 | 18 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 457092
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 169920
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 |  |  |  |  | 21 | 21 | 21 | 21 | 5 | 21 | 18 | 18 | 18 |  | 20 | 20 | 21 | 12 | 21 | 21 | 21 | 422990
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 662580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 808300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 |  | 16 | 33 | 33 | 25 | 33 | 33 | 33 | 695500
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 95 | 95 | 95 | 92 | 90 | 92 | 95 | 95 | 93 | 54 | 54 |  | 87 | 95 | 95 | 95 | 97 | 98 | 98 | 2186045
| Feni Lanka Power | 101 | [12 empty] | 17 | 51 | 51 | 17 | 17 |  | 17 | 75 | 114 | 114 | 114 | 114 | 114 | 853860
| Chowmuhani 113 MW | 104 | 105 | 105 | 105 | 105 | 75 | 46 | 63 | 101 | 105 | 105 | 105 | 105 | 104 | 105 | 104 | 94 | 46 |  | 59 | 105 | 105 | 104 | 105 | 105 | 105 | 2297400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 97 | 97 | 97 | 97 | 97 | 97 | 89 | 98 | 94 | 97 | 40 | 80 | 96 | 96 | 96 | 96 | 75 | 50 |  | 55 | 90 | 96 | 97 | 97 | 97 | 97 | 2169600
78 | Gazipur 52 MW PP | 52 | [8 empty] | 4 | 17 | 20 | 40 | 50 | 50 | 8 | 8 | 8 |  | 9 | 40 | 45 | 43 | 50 | 51 | 51 | 550452
79 | Kodda 150MW PP | 64 | 32 | 16 | [9 empty] | 70 | 98 | 98 | 98 | 48 | 48 |  | 48 | 55 | 120 | 133 | 133 | 133 | 133 | 1241760
80 | Jamalpur 95 MW PP(Powerpac) | 32 | 32 | 32 | 32 | 32 | 32 | 34 | 73 | 88 | 32 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 842880
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 43 | [8 empty] | 8 | 43 | 52 | 52 |  | 5 | 8 |  | 8 | 16 | 49 | 52 | 52 | 52 | 52 | 610013
| Gazipur 100 MW PP | 108 | 108 | 108 | 18 | 18 |  |  |  |  | 24 | 52 | 108 | 108 | 108 | 108 | 52 | 52 | 52 |  | 70 | 108 | 108 | 108 | 108 | 108 | 108 | 1726476
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 1.9 | 1.4 | 4.8 | 2.8 | 4 | 4.1 | 5 | 1.4 | 3 | 2.6 | 1.7 | 0.3 | [8 empty] | 34800
| Jodiac Power | 54 | 52 | 52 | 44 | 34 |  |  |  |  | 20 | 54 | 54 | 54 | 54 | 54 | 53 | 54 | 54 |  | 54 | 27 | 54 | 54 | 54 | 54 | 54 | 1029241
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 95 | 95 | 93 | 93 | 93 | 93 | 96 |  | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 2308992
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 68 | 84 | [7 empty] | 8 | 61 | 87 | 94 | 87 | 87 | 40 | 10 | 10 |  | 31 | 100 | 90 | 100 | 100 | 100 | 100 | 1249875
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 265 | 280 | 265 | 285 | 255 | 265 | 277 | 240 | 275 | 255 | 245 |  | 305 | 277 | 255 | 270 | 270 | 285 | 260 | 6332276
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 74 | 41 | [5 empty] | 28 | 90 | 100 | 100 | 80 | 50 |  | 57 | 100 | 100 | 100 | 100 | 100 | 100 | 1669440
| Sonargoan 104 MW (Orion) | [10 empty] | 22 | 30 | 24 | 60 | 28 | 20 | 36 | 5 |  | 36 | 36 | 36 |  |  |  |  | 308160
88 | Ghorashal 78.5 MW PP(MAX) | 67 | 67 | 67 | 68 | 67 | 67 | 67 | 66 | 66 | 67 | 67 | 65 | 64 | 63 | 65 | 64 | 50 | 40 |  | 40 | 66 | 66 | 66 | 67 | 67 | 66 | 1488032
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 60 | 50 | 50 | 50 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 313200
92 | Fenchuganj 44MW (Energyprima) | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 39 | 39 | 39 | 39 | 36 | 20 | 20 |  | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 880488
93 | Ashuganj 51 MW PP (Midland) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 26 | 26 | 35 | 35 | 43 | 649948
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 94 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2442096
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 39 | [6 empty] | 1 | 6 | 31 | 46 | 47 | 45 | 33 | 19 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 506880
96 | Chattogram 108 MW PP (ECPV) | 98 | 60 | 62 | 43 | 45 |  |  |  |  | 21 | 90 | 95 | 97 | 97 | 97 | 65 | 50 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1340160
97 | Katpotti 52 MW PP (Sinha) | 48 | 48 | 48 | 18 | [6 empty] | 3 | 13 | 14 | 14 | [12 empty] | 236400
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 30 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 991835
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1327396
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 130 | 130 | 163 | 130 | 130 | 163 | 130 | 130 | 100 |  | 100 | 163 | 163 | 163 | 130 | 130 | 163 | 3547227
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.3 | 1.2 | 0.8 | 1.6 | 1.6 | 0.5 | 2.5 |  | 0.7 | 0.7 | 0.4 | 0.1 | [8 empty] | 11750
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1283400
104 | Keranigonj 300 MW PP (APR) | [11 empty] | 70 | 50 | [13 empty] | 144237
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 195 | 185 | 185 | 185 | 185 | 150 | 100 | 100 | 100 | 137 | 170 | 170 | 170 | 170 | 150 | 150 | 100 | 100 |  | 100 | 148 | 180 | 185 | 195 | 195 | 195 | 3900000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 131 | 131 | 131 | 131 | 131 | 131 | 133 | 131 | 131 | 132 | 131 | 128 | 133 | 130 | 130 | 131 | 131 |  | 130 | 130 | 131 | 131 | 132 | 131 | 131 | 3166560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2438400
116 | Chandpur 200MW (Desh energy) | [21 empty] | 25 | 105 | 90 | 35 | 35 | 348960
117 | Ashuganj 150MW PP (Midland) | 148 | 150 | 148 | 148 | 148 |  |  | 5 | 28 | 80 | 110 | 143 | 145 | 145 | 145 | 100 | 100 | 100 |  | 115 | 150 | 148 | 148 | 148 | 148 | 150 | 2855345
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 108 | 107 | 108 | 108 | 108 | 115 | 115 | 115 | 115 | 108 | 108 | 108 | 108 | 108 | 107 | 108 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2679600
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 307 | 253 | 199 | 251 | 272 | 306 | 307 | 307 | 307 | 307 | 307 | 270 | 181 | 179 |  | 179 | 303 | 308 | 308 | 308 | 307 | 307 | 6814691
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2435520
120 | Eastern Zone Total | 7750 | 7495 | 7392 | 7112 | 6956 | 6331.2 | 6096.9 | 6219 | 6419.8 | 6670.07 | 6937.37 | 7292.16 | 7299.62 | 7457.2 | 7613.3 | 7154.5 | 6477.1 | 6102 |  | 6824 | 7787 | 7950 | 7977 | 7964 | 7935 | 7961 | 172525394
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 4 | [6 empty] | 34 | 49 | 49 | 16 | 16 | 16 |  | 49 | 85 | 99 | 115 | 115 | 115 | 115 | 1345920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 19 | [14 empty] | 8 |  | 21 | 22 | 22 | 22 | 22 | 22 | 19 | 179520
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 70 | 70 | 50 | [16 empty] | 35 | 70 | 70 | 70 | 70 | 70 | 603360
130
131
132
133
| Barisal 110 MW PP (Summit ) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 64 | 64 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 98 | 110 | 110 | 110 | 110 | 2335776
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 77 | 77 | 76 | 78 | 78 | 77 | 77 | 76 | 78 | 78 | 78 | 78 | 76 | 76 | 76 | 78 |  | 78 | 79 | 78 | 78 | 78 | 77 | 75 | 1876115
| Bhola 225 MW CCPP | 67 | 66 | 67 | 67 | 68 | 68 | 68 | 67 | 67 | 67 | 68 | 68 | 66 | 65 | 59 | 65 | 61 | 64 |  | 65 | 66 | 67 | 67 | 67 | 67 | 68 | 1577000
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 30 | 27 | 24 | 18 | 15 | 12 | 18 | 17 | 17 | 16 | 20 | 22 | 24 | 20 | 20 | 18 |  | 31 | 27 | 27 | 38 | 29 | 34 | 34 | 572219
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 100 | 86 | 100 | 100 | 100 | 100 | 509760
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 16 | 8 |  |  |  |  | 16 | 40 | 33 | 33 | 33 | 24 | 8 |  | 8 | 40 | 40 | 40 | 40 | 40 | 33 | 636750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 16 | 44 |  | 74 | 65 | 65 | 20 | 48 | 50 | 50 | 314624
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 95 | [8 empty] | 15 | 50 | 50 | 15 | 15 |  | 15 | 50 | 67 | 105 | 105 | 105 | 105 | 1213776
146 | Bheramara HVDC | 943 | 944 | 944 | 944 | 943 | 943 | 943 | 944 | 948 | 948 | 562 | 561 | 542 | 490 | 683 | 930 | 930 | 936 |  | 937 | 937 | 937 | 938 | 938 | 941 | 942 | 20877818
147 | Bheramara 410 MW CCPP | 280 | 295 | 305 | 320 | 325 | 340 | 350 | 350 | 345 | 340 | 340 | 340 | 330 | 325 | 320 | 320 | 320 | 320 |  | 345 | 345 | 345 | 345 | 350 | 350 | 360 | 8169984
148 | Payra 1320 MW | [26 empty] | 0
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3665900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 17 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 491190
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 177 | 177 | 177 | 177 | 179 | 158 | 160 | 152 | 149 | 192 | 182 | 186 | 172 | 166 | 184 | 169 | 168 | 154 |  | 157 | 193 | 193 | 198 | 197 | 196 | 200 | 4460173
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 165 | 165 | 165 | 165 | 166 | 166 | 166 | 167 | 166 | 165 | 171 | 196 | 205 | 195 | 201 | 196 | 178 | 166 |  | 167 | 190 | 191 | 192 | 192 | 195 | 196 | 4542191
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 385 | 344 | 358 | 381 | 363 | 331 | 333 | 400 | 413 | 346 | 398 | 398 | 406 | 399 | 382 | 389 | 370 | 347 |  | 399 | 400 | 400 | 399 | 411 | 403 | 412 | 9130581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 8 |  | 29 | 41 | 42 | 41 | 41 | 41 | 41 | 203813
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 20 | 18 | 18 | 19 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 462720
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253404
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 194998
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | 20 | 50 | 50 | 50 | 24 | 24 | 184540
167 | Katakhali 50 MW Peaking PP | 36 | 35 | [17 empty] | 30 | 42 | 46 | 44 | 42 | 41 | 41 | 281283
168 | Santahar 50 MW Peaking PP | 33 | 25 | [17 empty] | 30 | 33 | 34 | 33 | 33 | 33 | 33 | 245711
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | [9 empty] | 36 | 43 | 43 | 43 | 8 | 8 | 8 |  | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 504480
170 | Chapainawabganj 100 MW Peaking PP | 100 | 100 | 100 | 50 | [6 empty] | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 58 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1289040
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 35 | 35 |  |  |  |  | 6 | 38 | 108 | 113 | 113 | 113 | 70 | 70 | 70 |  | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 1868928
172 | Confidence Power Bogura Unit-1 113 MW | [20 empty] | 25 | 50 | 70 | 70 | 70 | 70 | 331968
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [20 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 5000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 |  |  |  |  | 55 | 110 | 113 | 113 | 113 | 107 | 105 | 71 | 71 |  | 73 | 113 | 113 | 113 | 113 | 113 | 107 | 2146560
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.2 | 0.4 | 1.8 | 3.5 | 5.3 | 6.3 | 6.3 |  |  |  | 2.5 | 1.2 | [8 empty] | 21374
178
178