## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-06-27 | Saturday
|  | Date (day): | 2020-06-27 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13684.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15398 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-06-26 | 2020-06-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 30 | 62 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 53 | 97 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 254 | 290 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 380 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 255 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 81 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 40 | 41 | 42 |  | 13 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 87 | 100 | 100 | 110 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 92 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 290 | 320 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 66 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 49 | 52
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 30 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 48 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 286 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 85 | 131 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 17 | 100 | 100
| Sonargoan 104 MW (Orion) |  | HFO | IPP | 18.5*6 | 0 | 0 | 108 | 108 | 0 | 0
| Dhaka area Total |  |  |  |  | 6015 | 5791 | 2209 | 2961 | 3861 | 4199 | 323 | 1175
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 66 | 67 | 105 | 105 | 125 |  | Low water level & Unit-2 under maint.
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 104 | 140 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 50 | 102 | 100 | 100
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 22 | 42 | 10 | 35
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2.6 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 52 | 307 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 596.6 | 968 | 1397 | 1541 | 395 | 225
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 100 | 135
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 80 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 216 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 295 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 100 | 360
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 40 | 40 | 42 |  | 3 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 50 | 50
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 26 | 26 | 169 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 135 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 90 | 90 |  | 73 | ST Under maint.
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 100 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 8 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 148 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 32 | 32
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 21 | 21 | 22
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 200 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 104 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1087 | 1435 | 2090 | 2560 | 332 | 84
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 154 | 156 | 150 | 160 | 42 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 24 | 40 | 40 |  |  | Cable fault
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.5 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 185 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 326.5 | 500 | 498.6 | 537 | 42 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 60 | 60 | 60
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 |  | 90 | GT-4 under maint.
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 316 | 245 | 330 | 330
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 47 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 46 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 52 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 71 | 80 | 80
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1098 | 1186 | 1373 | 1379 | 0 | 490
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 932 | 931 | 952 | 952
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 345 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 55 | 100 | 60 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1292 | 1566 | 1782 | 2158 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 76 | 80 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 38 | 30 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 86 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 33 | 80 | 78 | 78 |  | 17 | Engine problem
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 355 | 572 | 600 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 501 | 852 | 856 | 949 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 70 | 65 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 70 | 70 | 70 | 30 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 10 | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 43 | 45
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 172 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 165 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 343 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 0 | 21 | 21
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 5 | 100 | 100 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 793 | 1050 | 1579 | 1792 | 240 | 19
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 150 | 150
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 20
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 113 | 90 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 186.7 | 272 | 248 | 283 | 170 | 0
| Total |  |  |  |  | 20279 | 19788 | 8089.8 | 10790 | 13684.6 | 15398 | 1502 | 2136
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7656.4446 | 10212 | 12951.5417 | 14573.1581
A. |  | 2020-06-26 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10810 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7644.1 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10790 | MW
3 | Day peak Generation : |  |  | 8089.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10212 | MW
4 | Evening peak Generation : |  |  | 10790 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 219.864 | MKWHr | By Solar | 0.10075 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 130.3806 | MKWHr |  | By Oil: | 47.1895 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 15.0936 | MKWHr |  | By Hydro: | 1.7334 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1502 | MW | Dhaka | 3489 | 3489 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2136 | MW | Chittagong | 992 | 992 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3638 | MW | Khulna | 1424 | 1424 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1110.25 | MMCFD |  |  | Rajshahi | 875 | 875 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 155582975.31 | ii) Oil : | Taka | 332057938.94 | Comilla | 1079 | 1079 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 70048523 | Total | Taka | 557689437.25 | Mymensingh | 914 | 914 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.012 | MKWHr. | Sylhet | 407 | 407 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 94 | MW (E to W) at | 21:00 | hrs | Barisal | 332 | 332 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -25 | MW at | 20:00 | hrs | Rangpur | 700 | 700 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 10212 | 10212 |  | 0
B. |  | 2020-06-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15398 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 4398 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 223.7284 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7639.5 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3796 | MKWHr. | ii) HVDC Flow at Peak Time |  | 931 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9866 | MKWHr. | iii) Maximum HVDC Flow : |  | 942 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.6 |  | (b) Today: | 83.5 |  | (c) Rule Curve: |  | 82.92
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-06-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Sonargoan 104 MW (Orion) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 99 | 63 | 0 | 320 |  | 0 | 390 | 260 | 100 | 95 | 41 | 300 | 0 | 61 | 0 | 50 | 102 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 63 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 45 | 0 | 20 | 40 | 80 | 100 | 0 | 310 | 0 | 185 | 26 | 90 | 41 | 45 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 164 | 159 | 32 | 20 | 0 | 58 | 30 | 47 | 46 | 130 | 254 | 61 | 76 | 0 | 151 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 230 | 0 | 0 | 150 | 0 | 128 | 0 | 100 | 0 | 50 | 0 | 115 | 18 | 51 | 0 | 306 | 54 | 0 | 0 | 104 | 100 | 0 | 108 |  | 931 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 37 | 110 | 0 | 0 | 65 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 78 | 100 | 150 | 0 | 391 | 0 | 0 | 113 | 15 | 113 | 0 | 0 | 0 | 571 |  | 7170 | 3640 | 10810 | 3546 | 931 | 2164 | 2964 | 721 | 98 | 222 | 164 | 0 | 0 | 83.62
2:00 | 35 | 0 | 0 | 0 | 300 | 99 | 63 | 0 | 320 |  | 0 | 390 | 260 | 100 | 95 | 41 | 300 | 0 | 96 | 0 | 60 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 45 | 0 | 20 | 40 | 80 | 100 | 0 | 310 | 0 | 186 | 26 | 91 | 41 | 46 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 158 | 159 | 24 | 20 | 0 | 60 | 0 | 45 | 46 | 130 | 258 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 310 | 23 | 11 | 0 | 165 | 0 | 0 | 130 | 0 | 128 | 0 | 100 | 0 | 36 | 0 | 115 | 0 | 0 | 0 | 306 | 54 | 0 | 0 | 104 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 37 | 110 | 0 | 0 | 65 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 78 | 80 | 150 | 0 | 392 | 0 | 0 | 35 | 15 | 108 | 0 | 0 | 0 | 570 |  | 6977 | 3497 | 10474 | 3558 | 932 | 2184 | 2677 | 719 | 96 | 150 | 158 | 0 | 0 | 83.62
3:00 | 35 | 0 | 0 | 0 | 300 | 99 | 63 | 0 | 320 |  | 0 | 390 | 265 | 100 | 95 | 41 | 300 | 0 | 95 | 0 | 97 | 102 | 16 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 100 | 0 | 0 | 0 | 20 | 40 | 80 | 100 | 0 | 320 | 0 | 193 | 26 | 90 | 41 | 46 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 150 | 159 | 24 | 20 | 0 | 60 | 0 | 45 | 46 | 130 | 257 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 310 | 23 | 11 | 0 | 95 | 0 | 0 | 130 | 0 | 107 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 34 | 0 | 0 | 104 | 100 | 0 | 108 |  | 933 | 0 | 360 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 33 | 110 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 77 | 0 | 170 | 0 | 392 | 0 | 0 | 0 | 15 | 90 | 0 | 0 | 0 | 568 |  | 6812 | 3361 | 10173 | 3607 | 933 | 2179 | 2375 | 717 | 96 | 116 | 150 | 0 | 0 | 83.61
4:00 | 35 | 0 | 0 | 0 | 300 | 99 | 63 | 0 | 320 |  | 0 | 390 | 260 | 100 | 95 | 41 | 300 | 0 | 96 | 0 | 97 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 99 | 0 | 0 | 0 | 20 | 40 | 80 | 100 | 0 | 310 | 0 | 185 | 26 | 91 | 41 | 45 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 144 | 158 | 24 | 20 | 0 | 60 | 0 | 45 | 46 | 130 | 258 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 310 | 23 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 95 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 37 | 110 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 77 | 0 | 170 | 0 | 392 | 0 | 0 | 0 | 15 | 44 | 0 | 0 | 0 | 570 |  | 6647 | 3289 | 9936 | 3569 | 932 | 2182 | 2195 | 719 | 96 | 99 | 144 | 0 | 0 | 83.61
5:00 | 35 | 0 | 0 | 0 | 300 | 99 | 64 | 0 | 320 |  | 0 | 390 | 240 | 100 | 95 | 41 | 300 | 0 | 93 | 0 | 96 | 102 | 0 | 0 | 0 | 0 | 0 | 53 | 35 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 99 | 0 | 0 | 0 | 20 | 42 | 80 | 100 | 0 | 310 | 0 | 182 | 26 | 82 | 41 | 46 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 136 | 160 | 24 | 20 | 0 | 60 | 0 | 45 | 46 | 130 | 255 | 61 | 76 | 0 | 150 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 45 | 0 | 0 | 130 | 0 | 95 | 0 | 100 | 0 | 0 | 0 | 115 | 50 | 0 | 0 | 307 | 0 | 0 | 0 | 105 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 36 | 80 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 75 | 0 | 170 | 0 | 343 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 572 |  | 6637 | 3132 | 9769 | 3553 | 932 | 2113 | 2118 | 722 | 96 | 99 | 136 | 0 | 0 | 83.6
6:00 | 35 | 0 | 0 | 0 | 300 | 99 | 50 | 0 | 315 |  | 0 | 390 | 230 | 32 | 35 | 15 | 250 | 0 | 93 | 0 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 42 | 80 | 100 | 0 | 310 | 0 | 182 | 26 | 80 | 41 | 47 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 128 | 160 | 24 | 20 | 0.1 | 60 | 0 | 11 | 10 | 130 | 250 | 63 | 40 | 0 | 150 | 18 | 0 | 10 | 265 | 23 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 95 | 0.7 | 100 | 0 | 0 | 0 | 115 | 106 | 0 | 0.4 | 52 | 0 | 0 | 0 | 55 | 100 | 0 | 108 |  | 932 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 32 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 77 | 14 | 170 | 0 | 333 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 0 | 462 |  | 5653.2 | 2928.1 | 8581.3 | 3483 | 932 | 1919 | 1359 | 612 | 96 | 51 | 128 | 1.3 | 0 | 83.6
7:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 250 |  | 0 | 300 | 265 | 7 | 48 | 0 | 240 | 0 | 87 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 61 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 42 | 80 | 100 | 0 | 310 | 0 | 183 | 26 | 90 | 41 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 18 | 124 | 157 | 24 | 20 | 0.2 | 60 | 0 | 11 | 10 | 110 | 257 | 60 | 20 | 0 | 150 | 18 | 0 | 10 | 270 | 23 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 103 | 2.76 | 100 | 0 | 0 | 0 | 115 | 53 | 0 | 1 | 52 | 0 | 0 | 0 | 46 | 100 | 0 | 108 |  | 932 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 26 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 53 | 50 | 140 | 0 | 391 | 0 | 0 | 0 | 15 | 0 | 0 | 0.1 | 0 | 372 |  | 5251.96 | 2751.1 | 8003.06 | 3341 | 932 | 1674 | 1294 | 522 | 61 | 51 | 124 | 4.06 | 0 | 83.59
8:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 250 |  | 0 | 300 | 235 | 7 | 48 | 0 | 240 | 0 | 57 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 62 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 40 | 80 | 100 | 0 | 270 | 0 | 182 | 26 | 81 | 40 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 25 | 20 | 92 | 160 | 24 | 20 | 0.6 | 60 | 0 | 11 | 10 | 110 | 248 | 61 | 20 | 0 | 120 | 18 | 0 | 10 | 290 | 23 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 132 | 10.8 | 100 | 0 | 0 | 0 | 115 | 35 | 0 | 1.7 | 52 | 0 | 0 | 0 | 46 | 100 | 0 | 104 |  | 932 | 0 | 235 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 53 | 50 | 140 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 374 |  | 5108.1 | 2697.1 | 7805.2 | 3219 | 932 | 1651 | 1262 | 523 | 62 | 51 | 92 | 13.2 | 0 | 83.59
9:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 254 |  | 0 | 300 | 265 | 7 | 48 | 0 | 238 | 0 | 35 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 63 | 0 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 32 | 80 | 100 | 0 | 260 | 0 | 182 | 26 | 86 | 39 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 25 | 20 | 88 | 160 | 24 | 20 | 0.9 | 60 | 0 | 11 | 10 | 110 | 253 | 61 | 20 | 0 | 70 | 18 | 0 | 10 | 285 | 24 | 0 | 0 | 14 | 0 | 0 | 30 | 0 | 110 | 3.8 | 100 | 0 | 0 | 0 | 115 | 35 | 0 | 2.3 | 52 | 0 | 0 | 0 | 46 | 100 | 0 | 106 |  | 933 | 0 | 235 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 86 | 23 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 50 | 140 | 0 | 336 | 0 | 0 | 0 | 0 | 31 | 0 | 0.1 | 0 | 353 |  | 4980 | 2664.1 | 7644.1 | 3092 | 933 | 1605 | 1221 | 502 | 63 | 133 | 88 | 7.1 | 0 | 83.57
10:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 255 |  | 0 | 300 | 260 | 7 | 48 | 0 | 220 | 0 | 35 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 65 | 0 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 22 | 80 | 100 | 0 | 260 | 0 | 183 | 26 | 86 | 39 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 82 | 157 | 24 | 17 | 1 | 60 | 0 | 11 | 10 | 110 | 287 | 61 | 20 | 0 | 70 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 15 | 0 | 0 | 16 | 0 | 85 | 10.1 | 90 | 0 | 0 | 0 | 115 | 36 | 0 | 5.4 | 52 | 0 | 0 | 0 | 26 | 100 | 0 | 108 |  | 932 | 0 | 235 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 24 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 30 | 140 | 0 | 360 | 0 | 0 | 0 | 0 | 35 | 0 | 0.1 | 0 | 354 |  | 4946.5 | 2674.1 | 7620.6 | 3083 | 932 | 1636 | 1170 | 503 | 65 | 133 | 82 | 16.6 | 0 | 83.58
11:00 | 35 | 0 | 0 | 0 | 300 | 53 | 50 | 0 | 253 |  | 0 | 300 | 270 | 7 | 48 | 0 | 220 | 0 | 35 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 65 | 0 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 22 | 80 | 100 | 0 | 260 | 0 | 183 | 26 | 88 | 38 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 25 | 14 | 88 | 156 | 24 | 17 | 0.5 | 60 | 0 | 11 | 10 | 110 | 300 | 58 | 20 | 0 | 70 | 18 | 0 | 10 | 295 | 24 | 5 | 0 | 34 | 0 | 0 | 16 | 0 | 85 | 7.8 | 90 | 0 | 0 | 0 | 115 | 53 | 0 | 2.5 | 52 | 0 | 0 | 0 | 26 | 100 | 0 | 108 |  | 932 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 30 | 140 | 0 | 364 | 0 | 0 | 0 | 0 | 35 | 0 | 0.2 | 0 | 352 |  | 5007.8 | 2676.2 | 7684 | 3091 | 932 | 1628 | 1236 | 501 | 65 | 132 | 88 | 11 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 53 | 30 | 0 | 254 |  | 0 | 370 | 280 | 7 | 48 | 0 | 280 | 0 | 35 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 66 | 0 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 22 | 80 | 100 | 0 | 340 | 0 | 212 | 26 | 90 | 38 | 10 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 25 | 18 | 92 | 154 | 24 | 17 | 0.5 | 56 | 0 | 11 | 10 | 110 | 316 | 58 | 20 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 85 | 0 | 90 | 0 | 0 | 0 | 115 | 52 | 0 | 2.6 | 52 | 0 | 0 | 0 | 26 | 100 | 0 | 108 |  | 932 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 55 | 140 | 0 | 402 | 0 | 0 | 0 | 0 | 36 | 0 | 1.7 | 0 | 355 |  | 5317.1 | 2772.7 | 8089.8 | 3375 | 932 | 1735 | 1244 | 504 | 66 | 137 | 92 | 4.8 | 0 | 83.57
13:00 | 35 | 0 | 0 | 0 | 300 | 96 | 40 | 0 | 254 |  | 0 | 420 | 275 | 7 | 30 | 0 | 320 | 0 | 94 | 0 | 7 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 25 | 12 | 33 | 25 | 0 | 0 | 75 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 49 | 0 | 0 | 0 | 20 | 36 | 80 | 100 | 0 | 310 | 0 | 182 | 26 | 82 | 38 | 10 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 25 | 14 | 96 | 157 | 24 | 20 | 0.8 | 60 | 0 | 42 | 29 | 163 | 289 | 53 | 40 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 85 | 0 | 100 | 0 | 0 | 0 | 115 | 52 | 0 | 4.2 | 105 | 0 | 0 | 0 | 26 | 100 | 0 | 108 |  | 932 | 0 | 265 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 69 | 40 | 140 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 374 |  | 5620 | 2823.7 | 8443.7 | 3466 | 932 | 2009 | 1271 | 523 | 75 | 66 | 96 | 5.7 | 0 | 83.56
14:00 | 35 | 0 | 0 | 0 | 300 | 95 | 62 | 0 | 254 |  | 0 | 420 | 275 | 7 | 30 | 0 | 320 | 0 | 93 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 25 | 12 | 33 | 25 | 0 | 0 | 75 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 25 | 80 | 100 | 0 | 325 | 0 | 202 | 26 | 91 | 38 | 10 | 0 | 19 | 0 | 0 | 0 | 20 | 5 | 25 | 21 | 102 | 155 | 24 | 20 | 0.6 | 60 | 0 | 47 | 46 | 163 | 301 | 59 | 40 | 0 | 150 | 18 | 0 | 9 | 295 | 24 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 85 | 0 | 100 | 0 | 0 | 0 | 115 | 17 | 0 | 1.1 | 107 | 0 | 0 | 0 | 8 | 100 | 0 | 108 |  | 931 | 0 | 265 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 77 | 0 | 140 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 374 |  | 5646.7 | 2785.2 | 8431.9 | 3503 | 931 | 2058 | 1180 | 523 | 75 | 58 | 102 | 1.9 | 0 | 83.56
15:00 | 35 | 0 | 0 | 0 | 300 | 95 | 61 | 0 | 254 |  | 0 | 420 | 270 | 7 | 30 | 0 | 318 | 0 | 93 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 25 | 12 | 33 | 25 | 0 | 0 | 74 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 26 | 80 | 100 | 0 | 315 | 0 | 194 | 26 | 91 | 38 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 108 | 154 | 24 | 20 | 1.1 | 60 | 0 | 47 | 46 | 163 | 303 | 53 | 40 | 0 | 150 | 18 | 0 | 10 | 315 | 16 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 89 | 8.9 | 100 | 0 | 0 | 0 | 115 | 17 | 0 | 2.1 | 107 | 0 | 0 | 0 | 38 | 100 | 0 | 108 |  | 931 | 0 | 345 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 77 | 0 | 140 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 375 |  | 5705.1 | 2879.2 | 8584.3 | 3570 | 931 | 2098 | 1209 | 524 | 74 | 58 | 108 | 12.3 | 0 | 83.55
16:00 | 35 | 0 | 0 | 0 | 300 | 98 | 61 | 0 | 254 |  | 0 | 400 | 260 | 7 | 45 | 0 | 318 | 0 | 33 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 12 | 33 | 25 | 0 | 0 | 72 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 51 | 0 | 0 | 0 | 20 | 37 | 80 | 100 | 0 | 310 | 0 | 184 | 8 | 84 | 39 | 10 | 0 | 35 | 0 | 0 | 0 | 21 | 5 | 25 | 21 | 104 | 155 | 24 | 20 | 1.1 | 60 | 0 | 47 | 46 | 163 | 288 | 53 | 71 | 0 | 150 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 16 | 0 | 128 | 8.9 | 100 | 0 | 0 | 0 | 115 | 17 | 0 | 2.1 | 78 | 0 | 0 | 0 | 46 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 24 | 0 | 0 | 70 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 79 | 0 | 140 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 375 |  | 5563.1 | 2830.2 | 8393.3 | 3558 | 932 | 2003 | 1137 | 524 | 72 | 51 | 104 | 12.3 | 0 | 83.55
17:00 | 35 | 0 | 0 | 0 | 250 | 24 | 40 | 0 | 254 |  | 0 | 400 | 265 | 7 | 40 | 0 | 318 | 0 | 35 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 12 | 33 | 25 | 0 | 0 | 69 | 0 | 90 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 74 | 0 | 0 | 0 | 20 | 37 | 80 | 80 | 0 | 265 | 0 | 184 | 8 | 90 | 40 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 5 | 16 | 21 | 108 | 155 | 24 | 20 | 0 | 60 | 0 | 11 | 10 | 130 | 298 | 59 | 69 | 0 | 100 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 30 | 0 | 0 | 16 | 0 | 131 | 5 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 46 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 2 | 16 | 86 | 25 | 0 | 0 | 70 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 54 | 0 | 140 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 |  | 5113 | 2834 | 7947 | 3339 | 932 | 1777 | 1115 | 526 | 69 | 76 | 108 | 5 | 0 | 83.55
18:00 | 35 | 0 | 0 | 0 | 250 | 24 | 40 | 0 | 254 |  | 0 | 310 | 265 | 7 | 48 | 0 | 250 | 0 | 35 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 12 | 33 | 25 | 0 | 0 | 67 | 0 | 90 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 37 | 80 | 80 | 0 | 260 | 0 | 185 | 8 | 90 | 40 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 0 | 25 | 21 | 102 | 155 | 24 | 20 | 0.1 | 60 | 0 | 11 | 10 | 110 | 299 | 51 | 20 | 0 | 70 | 18 | 0 | 10 | 300 | 23 | 11 | 0 | 30 | 0 | 0 | 16 | 0 | 131 | 0.9 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0.2 | 70 | 0 | 0 | 0 | 46 | 100 | 0 | 108 |  | 932 | 0 | 285 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 40 | 86 | 24 | 0 | 0 | 70 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 54 | 0 | 140 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 376 |  | 4873.2 | 2772.2 | 7645.4 | 3182 | 932 | 1594 | 1147 | 525 | 67 | 95 | 102 | 1.4 | 0 | 83.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 250 | 96 | 40 | 0 | 283 |  | 0 | 340 | 280 | 35 | 64 | 0 | 250 | 0 | 82 | 0 | 12 | 42 | 10 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 12 | 33 | 25 | 0 | 0 | 65 | 0 | 90 | 0 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 85 | 0 | 3 | 0 | 20 | 40 | 80 | 80 | 0 | 330 | 0 | 208 | 8 | 91 | 40 | 10 | 0 | 25 | 0 | 0 | 1 | 21 | 3 | 25 | 21 | 136 | 153 | 24 | 20 | 0 | 60 | 0 | 43 | 28 | 110 | 326 | 59 | 71 | 0 | 100 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 39 | 0 | 0 | 38 | 0 | 131 | 0 | 100 | 0 | 2 | 0 | 115 | 0 | 0 | 0 | 230 | 1 | 0 | 0 | 64 | 100 | 0 | 108 |  | 932 | 0 | 385 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 32 | 18 | 0 | 70 | 65 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 15 | 20 | 11 | 8 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 166 | 0 | 63 | 3 | 160 | 0 | 362 | 35 | 0 | 21 | 0 | 80 | 0 | 0 | 0 | 422 |  | 5749 | 3251 | 9000 | 3522 | 932 | 1902 | 1728 | 571 | 65 | 144 | 136 | 0 | 0 | 83.54
19:30 | 35 | 0 | 0 | 0 | 250 | 96 | 61 | 0 | 294 |  | 0 | 380 | 240 | 100 | 64 | 10 | 328 | 0 | 82 | 0 | 50 | 66 | 36 | 30 | 0 | 0 | 0 | 17 | 55 | 53 | 19 | 25 | 14 | 33 | 25 | 0 | 0 | 65 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 35 | 0 | 20 | 40 | 135 | 80 | 0 | 310 | 0 | 216 | 8 | 80 | 40 | 10 | 0 | 35 | 0 | 0 | 25 | 21 | 3 | 25 | 21 | 140 | 155 | 24 | 20 | 0 | 60 | 0 | 47 | 46 | 130 | 291 | 61 | 71 | 0 | 150 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 145 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 65 | 0 | 108 | 17 | 0 | 0 | 292 | 54 | 0 | 20 | 105 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 35 | 54 | 0 | 70 | 65 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 30 | 20 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 190 | 0 | 77 | 100 | 195 | 0 | 287 | 105 | 0 | 100 | 0 | 108 | 0 | 0 | 0 | 477 |  | 6821 | 3702 | 10523 | 3743 | 932 | 1928 | 2821 | 626 | 65 | 268 | 140 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 300 | 96 | 62 | 0 | 294 |  | 0 | 340 | 245 | 100 | 64 | 16 | 275 | 0 | 52 | 0 | 80 | 66 | 48 | 30 | 0 | 0 | 0 | 17 | 55 | 35 | 19 | 25 | 28 | 33 | 25 | 0 | 0 | 65 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 42 | 0 | 20 | 40 | 135 | 80 | 0 | 280 | 0 | 182 | 8 | 80 | 40 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 3 | 25 | 21 | 144 | 157 | 24 | 20 | 0 | 60 | 0 | 47 | 46 | 130 | 250 | 52 | 71 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 169 | 0 | 0 | 180 | 0 | 132 | 0 | 100 | 0 | 60 | 0 | 108 | 52 | 0 | 0 | 300 | 42 | 0 | 51 | 103 | 100 | 0 | 108 |  | 932 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 38 | 64 | 0 | 70 | 65 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 184 | 0 | 79 | 90 | 179 | 0 | 285 | 70 | 0 | 102 | 0 | 108 | 0 | 0 | 0 | 489 |  | 6809 | 3677 | 10486 | 3591 | 932 | 1911 | 2911 | 638 | 65 | 294 | 144 | 0 | 0 | 83.65
21:00 | 35 | 0 | 0 | 0 | 300 | 97 | 62 | 0 | 290 |  | 0 | 380 | 255 | 100 | 81 | 40 | 290 | 0 | 87 | 0 | 92 | 66 | 48 | 0 | 0 | 0 | 0 | 30 | 17 | 17 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 67 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 0 | 0 | 20 | 42 | 135 | 80 | 0 | 295 | 0 | 216 | 8 | 80 | 40 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 25 | 21 | 148 | 156 | 24 | 20 | 0 | 60 | 0 | 47 | 46 | 163 | 245 | 52 | 71 | 0 | 150 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 286 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 135 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 17 | 104 | 100 | 0 | 108 |  | 931 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 38 | 76 | 0 | 70 | 65 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 172 | 0 | 80 | 100 | 165 | 0 | 343 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 0 | 572 |  | 7050 | 3740 | 10790 | 3662 | 931 | 2030 | 2971 | 721 | 67 | 260 | 148 | 0 | 0 | 83.54
22:00 | 35 | 0 | 0 | 0 | 300 | 97 | 63 | 0 | 290 |  | 0 | 380 | 250 | 75 | 81 | 15 | 290 | 0 | 89 | 0 | 80 | 32 | 48 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 69 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 0 | 0 | 20 | 42 | 135 | 80 | 0 | 295 | 0 | 212 | 8 | 86 | 40 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 25 | 21 | 148 | 156 | 24 | 20 | 0 | 60 | 0 | 47 | 46 | 163 | 286 | 52 | 71 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 145 | 0 | 0 | 180 | 0 | 130 | 0 | 100 | 0 | 0 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 | 108 |  | 931 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 38 | 110 | 0 | 70 | 65 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 79 | 100 | 161 | 0 | 377 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 572 |  | 6714 | 3664 | 10378 | 3691 | 931 | 2055 | 2515 | 721 | 69 | 248 | 148 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 300 | 97 | 63 | 0 | 290 |  | 0 | 340 | 260 | 33 | 81 | 0 | 290 | 0 | 90 | 0 | 30 | 32 | 48 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 0 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 102 | 0 | 0 | 0 | 20 | 42 | 135 | 80 | 0 | 315 | 0 | 212 | 8 | 90 | 40 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 25 | 21 | 150 | 156 | 24 | 0 | 0 | 60 | 0 | 47 | 46 | 130 | 303 | 52 | 72 | 0 | 150 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 145 | 0 | 0 | 50 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 85 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 | 108 |  | 942 | 0 | 355 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 87 | 37 | 96 | 0 | 70 | 70 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 79 | 100 | 164 | 0 | 400 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 572 |  | 6435 | 3660 | 10095 | 3724 | 942 | 2030 | 2210 | 721 | 71 | 247 | 150 | 0 | 0 | 83.63
24:00 | 35 | 0 | 0 | 0 | 300 | 94 | 63 | 0 | 330 |  | 0 | 340 | 255 | 33 | 64 | 0 | 290 | 0 | 94 | 0 | 30 | 32 | 16 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 0 | 0 | 0 | 20 | 42 | 135 | 80 | 0 | 300 | 0 | 212 | 8 | 91 | 40 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 25 | 20 | 146 | 160 | 24 | 0 | 0 | 60 | 0 | 47 | 46 | 130 | 293 | 52 | 72 | 0 | 151 | 18 | 0 | 10 | 320 | 24 | 11 | 0 | 145 | 0 | 0 | 16 | 0 | 131 | 0 | 100 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 307 | 0 | 0 | 0 | 104 | 100 | 0 | 108 |  | 942 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 37 | 96 | 0 | 70 | 70 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 169 | 0 | 79 | 100 | 178 | 0 | 409 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 572 |  | 6200 | 3629 | 9829 | 3588 | 942 | 2112 | 2088 | 721 | 71 | 161 | 146 | 0 | 0 | 76.33
KWH | 722000 | 0 | 0 | 0 | 6966873 | 1866136 | 1339072 | 0 | 6666000 |  | 0 | 8660250 | 6289455 | 1045440 | 1502760 | 356943 | 6908567 | 0 | 1789000 | 0 | 882240 | 1014480 | 676800 | 38435 | 0 | 0 | 0 | 496080 | 919561 | 231619 | 333216 | 600000 | 551520 | 802200 | 657900 | 0 | 0 | 1521360 | 212000 | 2100000 | 0 | 0 | 0 | 0 | 3106272 | 0 |  | 0 | 0 | 1809150 | 0 | 155520 | 0 | 475920 | 862080 | 2184806 | 2226375 | 0 | 7482500 | 0 | 4670000 | 485090 | 2057530 | 905256 | 489600 | 0 | 776310 | 0 | 0 | 257002 | 488916 | 98820 | 604200 | 490260 | 2986560 | 3664040 | 593280 | 368511 | 7000 | 1413000 | 41160 | 792600 | 847512 | 3248018 | 6259000 | 1365408 | 1309440 | 0 | 3119640 | 427000 | 0 | 243180 | 7358250 | 539304 | 223152 | 0 | 2147781 | 0 | 0 | 1857600 | 0 | 2711520 | 62505 | 2365440 | 0 | 393091 | 0 | 2706000 | 684888 | 88654 | 27120 | 4094836 | 230015 | 0 | 54720 | 1632960 | 2409600 | 0 | 2613120 |  | 22379636 | 0 | 7661952 | 0 | 1645440 | 0 | 0 | 0 | 0 | 12288 | 549750 | 2110725 | 728236 | 1061760 | 0 | 608000 | 1505000 | 0 | 0 | 641104 | 0 | 0 | 0 | 0 | 43597 | 439440 | 256536 | 178560 | 0 | 0 | 3677300 | 0 | 36000 | 0 | 0 | 3870582 | 0 | 1572422 | 1156800 | 3968491 | 0 | 8894727 | 0 | 0 | 575328 | 125568 | 1082880 | 0 | 4129 | 0 | 11416300 |  | 143661419 | 76202551 | 219863970 | 83545656 | 22379636 | 46834899 | 43970566 | 15093600 | 1733360 | 3218939 | 2986560 | 100754 | 0
Fuel Cost | 1184080 | 0 | 0 | 0 | 7733229.03 | 2463299.52 | 2276422.4 | 0 | 6865980 |  | 0 | 9439672.5 | 6981295.05 | 7934889.6 | 10354016.4 | 3019737.78 | 7184909.68 | 0 | 3094970 | 0 | 6643267.2 | 9252057.6 | 6659712 | 354370.7 | 0 | 0 | 0 | 3621384 | 7108206.53 | 2283763.34 | 249912 | 450000 | 0 | 0 | 0 | 0 | 0 | 410767.2 | 57240 | 3801000 | 0 | 0 | 0 | 0 | 5280662.4 | 0 |  | 0 | 0 | 17548755 | 0 | 1353024 | 0 | 599659.2 | 2560377.6 | 3233512.88 | 3295035 | 0 | 5537050 | 0 | 4296400 | 625766.1 | 2366159.5 | 1022939.28 | 685440 | 0 | 1327490.1 | 0 | 0 | 2454369.1 | 620923.32 | 74115 | 1057350 | 367695 | 22399200 | 3883882.4 | 5386982.4 | 468008.97 | 111580 | 2317320 | 65856 | 1410828 | 1322118.72 | 3702740.52 | 6509360 | 2689853.76 | 2501030.4 | 0 | 5396977.2 | 935130 | 0 | 496087.2 | 7431832.5 | 404478 | 169595.52 | 0 | 16237224.36 | 0 | 0 | 9659520 | 0 | 26681356.8 | 730683.45 | 19278336 | 0 | 2771291.55 | 0 | 24678720 | 6472191.6 | 772176.34 | 0 | 30956960.16 | 2003430.65 | 0 | 546105.6 | 13994467.2 | 16047936 | 0 | 0 |  | 128906703.36 | 0 | 8045049.6 | 0 | 12933158.4 | 0 | 0 | 0 | 0 | 128778.24 | 5728395 | 2385119.25 | 1128765.8 | 10362777.6 | 0 | 1246400 | 3085250 | 0 | 0 | 5673770.4 | 0 | 0 | 0 | 0 | 422890.9 | 843724.8 | 397630.8 | 135169.92 | 0 | 0 | 19930966 | 0 | 1027080 | 0 | 0 | 5109168.24 | 0 | 2358633 | 19677168 | 4643134.47 | 0 | 8805779.73 | 0 | 0 | 5459862.72 | 1185361.92 | 8403148.8 | 0 | 45625.45 | 0 | 50117557 |  | 402164167.31 | 308187069.4 | 710351236.71 | 98939355.62 | 128906703.36 | 56643619.69 | 300596952.4 | 70048523 | 468007.2 | 31460986.54 | 22399200 | 887888.9 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 53 | 30 | 0 | 254 |  | 0 | 370 | 280 | 7 | 48 | 0 | 280 | 0 | 35 | 0 | 7 | 16 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 22 | 33 | 25 | 0 | 0 | 66 | 0 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 50 | 0 | 0 | 0 | 20 | 22 | 80 | 100 | 0 | 340 | 0 | 212 | 26 | 90 | 38 | 10 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 25 | 18 | 92 | 154 | 24 | 17 | 0.5 | 56 | 0 | 11 | 10 | 110 | 316 | 58 | 20 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 85 | 0 | 90 | 0 | 0 | 0 | 115 | 52 | 0 | 2.6 | 52 | 0 | 0 | 0 | 26 | 100 | 0 | 108 |  | 932 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 87 | 26 | 0 | 0 | 0 | 70 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 17 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 33 | 55 | 140 | 0 | 402 | 0 | 0 | 0 | 0 | 36 | 0 | 1.7 | 0 | 355 |  | 8089.8 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 97 | 62 | 0 | 290 | 0 | 0 | 380 | 255 | 100 | 81 | 40 | 290 | 0 | 87 | 0 | 92 | 66 | 48 | 0 | 0 | 0 | 0 | 30 | 17 | 17 | 19 | 25 | 30 | 33 | 25 | 0 | 0 | 67 | 0 | 90 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 20 | 42 | 135 | 80 | 0 | 295 | 0 | 216 | 8 | 80 | 40 | 10 | 0 | 43 | 0 | 0 | 52 | 21 | 5 | 25 | 21 | 148 | 156 | 24 | 20 | 0 | 60 | 0 | 47 | 46 | 163 | 245 | 52 | 71 | 0 | 150 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 286 | 0 | 0 | 185 | 0 | 131 | 0 | 100 | 0 | 135 | 0 | 115 | 17 | 0 | 0 | 307 | 0 | 0 | 17 | 104 | 100 | 0 | 108 |  | 931 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 38 | 76 | 0 | 70 | 65 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 172 | 0 | 80 | 100 | 165 | 0 | 343 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 0 | 572 |  | 10790 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 42 | 320 | 0 | 100 | 0 | 100 | 102 | 149 | 100 | 0 | 0 | 52 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 100 | 100 | 50 | 22 | 35 | 135 | 100 | 0 | 360 | 360 | 215 | 26 | 90 | 42 | 50 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 32 | 22 | 173 | 160 | 40 | 22 | 0 | 60 | 30 | 51 | 44 | 163 | 330 | 66 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 |  | 0 |  | 952 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 70 | 70 | 50 | 40 | 100 | 0 | 50 | 45 | 43 | 35 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 20 | 0 | 0 | 200 | 0 | 78 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 78 | 0 | 360 | 0 | 0 | 450 | 305 | 100 | 100 | 41 | 320 | 0 | 100 | 0 | 100 | 102 | 100 | 100 | 0 | 0 | 49 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 70 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 22 | 10 | 100 | 100 | 0 | 360 | 100 | 215 | 26 | 90 | 40 | 50 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 32 | 21 | 154 | 150 | 40 | 22 | 1.6 | 60 | 30 | 51 | 44 | 163 | 330 | 61 | 80 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 100 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 |  | 0 |  | 952 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 80 | 0 | 70 | 70 | 0 | 0 | 100 | 0 | 50 | 43 | 43 | 0 | 21 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 90 | 0 | 8 | 70 | 600
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 97 | 20 | 0 | 300 | 0 | 0 | 360 | 265 | 0 | 64 | 0 | 260 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 70 | 35 | 95 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 135 | 80 | 0 | 310 | 35 | 176 | 8 | 91 | 40 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 5 | 25 | 0 | 112 | 157 | 24 | 0 | 0.2 | 60 | 0 | 11 | 46 | 163 | 307 | 40 | 40 | 0 | 70 | 18 | 0 | 10 | 310 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 2.8 | 106 | 0 | 0 | 0 | 17 | 100 | 0 | 108 | 0 | 941 | 0 | 235 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 23 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 22 | 50 | 169 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 276 | 0
199
| Minimum Generation |  | 7644.1 | 9:00
| Highest Generation |  | 10810 | 1:00
| Day Peak Generation |  | 8089.8 | 12:00
| Evening Peak Generation |  | 10790 | 21:00
| HVDC Max Flow |  | 942 | 23:00
| HVDC EvPeak Flow |  | 931 | 21:00
| Load factor L.F |  | 84.75%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-06-27
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-06-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8089.8 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7639.5 | MW
Evening Peak Generation : |  | 10790 | MW Hour : | 21:00 | Available Max Generation : |  | 15398 | MW
E.P. Demand (at gen end) : |  | 10790 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10810 | MW Hour : | 1:00 | Reserve(Generation end) |  | 4398 | MW
Total Gen. (MKWH) : |  | 219.864 | System Load Factor : | 84.75% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -25 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-06-27
Actual : | 83.5 | Ft.(MSL) , | Rule curve : | 82.92 | Ft.( MSL )
Gas Consumed : | Total = | 1110.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155582975.31
: |  | Coal : | 70048523 | Oil : | 332057938.94 | Total : | 557689437.25
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3877.98 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1318.2206 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1180.9916 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1067.0934 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 964.3346 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 778.1826 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 435.7742 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 200.3784 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 600.1699 |  |  | 0 | 0%
Total | 0 |  | 10423.1253 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 | 10)
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Ashuganj(S) 360 MW
9) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Haripur S/S-HPL 230 kV Ckt was under shut down from 08:29 to 21:18 for D/W.
b) Ashuganj-Ghorashal 132 kV Ckts 1 & 2 were under shut down from 09:49 to 17:40 for D/W.
c) Savar 132/33 kV T-2 transformer was under shut down from 10:41 to 12:01 for C/M.
d) Sirajganj-Bogura 230 kV Ckt-2 was under shut down from 08:18 to 11:30 for C/M.
e) Dhamrai 132/33 kV T-1 transformer,33 kV Bus was under shut down from 08:35 to 12:08 for C/M.
f) Rajshahi 132/33 kV T-3 transformer, 33 kV Bus was under shut down from 08:50 to 10:40 for C/M. |  |  |  |  | About 22 MW power interruption occurred under Rajshahi S/S area
from 8:50 to 10:40.
g) Savar 132/33 kV T-1 transformer ,33 kV CB tripped at 11:28 showing O/C,E/F relay and was switched on |  |  |  |  | About 110 MW power interruption occurred under Savar S/S area
at 11:37. |  |  |  |  | from 11:28 to 11:37.
h) Dhamrai 132/33 kV T-2 transformer was under shut down from 14:07 to18:16 for R/H maintenance at
33 kV Bus DS.
i) Ishurdi-Bheramara 132 kV Ckt-1 tripped at 16:16 showing Dist. Y,Z2,CAT,CASCD at Ishurdi end and
Dist.C-phase at Bheramara end.
j) Bheramara HVDC 230 kV 20DF22 filter tripped at 22:27 operating Diff. relay
k) Mymensingh 132/33 kV T-2 transformer was under shut down from 22:58 to 00:50(27/06/2020) for R/H maint. |  |  |  |  | About 45 MW power interruption occurred under Mymensingh S/S area
at Sombhuganj feeder loop. |  |  |  |  | from 22:58 to 00:50(27/06/2020).
l) Sikalbaha 150 MW GT tripped at 23:47 due to problem with inlet guide vane and was synchronized at
03:24(27/6/2020).
m) Bheramara HVDC 230 kV 20DF12 filter tripped at 06:43(27/6/2020) showing capacitor unbalance and was
switched on at 10:12.
n) Bottail 132 kv Bus was shut down at 06:52(27/6/2020) for Bus reconductoring. |  |  |  |  | About 125 MW power interruption has been occuring under Bottail,Jhenaidah
Chuadanga,Magura,Joshore,Benapol S/S areas from 06:52(27/6/2020) to till now.
o) Sonargaon 132/33 kV T-1 transformer was under shut down from 07:05(27/6/2020) to 07:45 for 132 kV
CB maintenance.
p) Bhandaria 132/33 kV T-1 transformer was shut down at 07:11(27/6/2020) for C/M.
q) Ashuganj(S) CCPP GT was synchronized at 07:26(27/6/2020).
r) Sonargaon 132/33 kV T-2 transformer was shut down at 07:46(27/6/2020) for 132 kV CB maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-06-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 722000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6966873
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 62 | 1339072 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 1866136 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 290 | 6666000 | FGMO
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8660250 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1045440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 255 | 6289455 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 81 | 1502760 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 356943 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 38435 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 333216
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 87 | 1789000 | Low demand
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 92 | 882240
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 6908567
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 66 | 1014480 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 30 | 496080 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 676800 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 919561
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 231619
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1151520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 657900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 2147781 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 131 | 2711520 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 684888 | Low demand
| Sonargoan 104 MW (Orion) |  | IPP | 18.5*6 | 0 | 108 | 2613120
| Dhaka area Total |  |  |  | 5791 | 2961 | 59473856
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 62505
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 67 | 1733360 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3106272 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 88654 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1809150
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2365440
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 475920
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 862080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 155520 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27120
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 307 | 4094836
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 230015
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2409600
| Chattogram area Total |  |  |  | 2266 | 968 | 19520472
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2184806 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2226375 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 4670000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7482500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 905256
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 489600 | Engine problem
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 485090 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 776310 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 393091
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2057530
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 488916
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 98820 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2986560
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 604200 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 257002
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 490260 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 54720 | Low demand
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 1632960
| Cumilla Area Total |  |  |  | 2980 | 1435 | 28283996
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 156 | 3664040 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 368511
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 24 | 593280 | Engine problem
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7000
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 185 | 1857600 | Engine problem
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2706000 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 500 | 9196431
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1413000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 41160
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3248018
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 245 | 6259000 | FGMO & ST under S/D
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 792600
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 847512
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 223152
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1365408 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1309440 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 3119640
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 427000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 539304
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7358250 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 243180
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1186 | 27186664
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 931 | 22379636
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1645440
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 12288 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 7661952
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 549750
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 1156800
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 0
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 125568 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1566 | 33531434
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 76 | 1061760
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 38 | 728236
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2110725 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 80 | 1572422 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 572 | 11416300
| Barisal Area Total |  |  |  | 1054 | 852 | 16889443
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 65 | 1505000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 608000
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 172 | 3870582 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 165 | 3968491 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 343 | 8894727 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 43597
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 439440
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 256536
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 178560
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Engine problem
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 641104
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 575328
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1050 | 20981365
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3677300 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 36000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1082880
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 4129
| Rangpur Area Total |  |  |  | 605 | 272 | 4800309
| Total |  |  |  | 19788 | 10790 | 219863970
| Eastern Grid Total |  |  |  | 13662 | 7050 | 143661419
| Western Grid Total |  |  |  | 6126 | 3740 | 76202551
| National Grid Total |  |  |  | 19788 | 10790 | 219863970
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-06-26
(a) ENTIRE EASTERN GRID : |  | 6881 | MW | (b) ENTIRE WESTERN GRID : |  | 3331 | MW
i) Dhaka area |  | 3489 | MW | i) Khulna area |  | 1424 | MW
ii) Chittagong area |  | 992 | MW | ii) Rajshahi area |  | 875 | MW
iii) Comilla area |  | 1079 | MW | iii) Barisal area |  | 332 | MW
iv) Mymensingh area |  | 914 | MW | iv) Rangpur area |  | 700 | MW
v) Sylhet area |  | 407 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10212 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 5:00 | Sherpur | 110 | 22:00 | Benapol | 48 | 21:00
Munsiganj | 114 | 21:00 | Srimongal | 50 | 20:00 | Jhenida | 106 | 21:00
Sonargaon | 70 | 21:00 | Shahjibazar | 103 | 22:00 | Bottail | 116 | 19:30
Shyampur | 196 | 1:00 | Fenchuganj | 31 | 20:00 | G.K Project | 54 | 20:00
Bhulta | 193 | 1:00 | Kulawara | 42 | 19:00 | Faridpur | 185 | 0.91667
Madanganj | 57 | 0:00 | Sylhet | 98 | 21:00 | Madaripur | 99 | 0.91667
Shitalakhya | 98 | 1:00 | Chatak | 23 | 21:00 | Sariatpur | 66 | 21:00
Rahim steel | 15 | 1:00 | Sunamganj | 30 | 20:00 | Gopalganj | 98 | 21:00
Matuail | 72 | 1:00 | Biani Bazar | 40 | 20:00 | Bagerhat | 93 | 0.8125
Ghorasal | 75 | 1:00 | Comilla (S) | 150 | 23:00 | Mongla | 40 | 1:00
Narsingdi | 159 | 1:00 | Comilla(N) | 111 | 21:00 | Satkhira | 102 | 0.8125
Haripur (SBU) | 92 | 2:00 | Chandpur | 100 | 22:00 | Gallamari | 50 | 19:30
Ullon | 54 | 13:00 | Feni | 112 | 22:00 | Magura | 54 | 0.8125
Hasnabad | 176 | 1:00 | Chowmuhani | 156 | 23:00 | Norail | 36 | 1:00
Magbazar | 79 | 15:00 | Ashuganj | 62 | 23:00 | Chuadanga | 89 | 19:30
Maniknagar | 80 | 1:00 | Daudkandi | 130 | 21:00 | Barisal(N) | 42 | 0.8125
Bangabhaban | 14 | 11:00 | B.Baria | 147 | 21:00 | Barisal (S) | 94 | 0.91667
Narinda | 74 | 1:00 | Ramganj | 112 | 22:00 | Patuakhali | 118 | 0.91667
Dhanmondi | 115 | 12:00 | Chaddagram | 36 | 22:00 | Bhandaria | 54 | 22:00
Lalbag | 68 | 1:00 | PHP | 11 | 18:30 | Borhan Uddin | 42 | 21:00
Madartek | 68 | 19:30 | Madunaghat | 49 | 22:00 | Ishurdi | 54 | 19:30
Dhaka University |  |  | Hathazari | 90 | 0.8125 | Ruppur Paromanobik | 1 | 1:00
Mirpur | 91 | 21:00 | Khulshi | 169 | 0.041667 | Natore | 99 | 1:00
Kalyanpur | 84 | 21:00 | Halishahar | 118 | 0.83333 | Bogra | 142 | 20:00
Gulshan | 92 | 15:00 | Baraulia | 141 | 0.083333 | Noagaon | 116 | 20:00
Uttara | 78 | 1:00 | Sikalbaha | 24 | 0.8125 | Rajshahi | 132 | 20:00
Uttara New | 19 | 21:00 | Dohazari | 100 | 0.875 | Rajshahi New | 10 | 19:30
Kamrangirchar | 77 | 1:00 | Cox'sbazar | 89 | 0.041667 | C.Nawabganj | 62 | 1:00
Savar | 101 | 1:00 | Chandraghona | 30 | 0.875 | Amnura | 32 | 1:00
Bhasantec | 135 | 21:00 | Kaptai | 4.5 | 0.79167 | Pabna | 117 | 20:00
Agargaon | 57 | 20:00 | A. Khaer Stl. | 9 | 0.375 | Shahjadpur | 97 | 21:00
Satmosjid | 92 | 21:00 | Bakulia | 88 | 0.8125 | Serajganj | 85 | 19:30
Tongi | 120 | 0.41667 | Julda | 20 | 0.041667 | Niyamatpur | 46 | 1:00
Kabirpur | 171 | 2:00 | TK chemical | 16 | 0.041667 | Joypurhat | 40 | 21:00
Basundhara | 101 | 21:00 | Modern Steel | 16 | 0.041667 | Sherpur(Bogura) | 42 | 19:30
Manikganj | 70 | 22:00 | Shahmirpur | 28 | 0.041667 | Mohastangor | 55 | 19:30
Joydevpur | 151 | 1:00 | Khagrachhari | 24 | 0.8125 | Rangpur | 135 | 20:00
New Tongi | 81 | 1:00 | Matarbari | 28.5 | 0.83333 | Lalmonirhat | 51 | 19:30
Kodda | 164 | 1:00 | Baroiar Hat | 36 | 0.8125 | Saidpur | 89 | 20:00
Dhamrai | 76 | 19:30 | Rangamati | 12 | 0.8125 | Purbasadipur | 107 | 20:00
Rajendrapur | 80 | 1:00 | Abul Khair 230 | 35 | 0.125 | Thakurgaon | 75 | 21:00
Valuka | 86 | 22:00 | BSRM | 154 | 0.54167 | Palashbari | 117 | 21:00
Tangail | 194 | 22:00 | GPH Ispat | 63 | 0.83333 | Barapukuria | 43 | 21:00
Mymensing | 203 | 19:00 | Goalpara | 31 | 1:00 | Panchagar | 46 | 20:00
Kishorganj | 136 | 21:00 | Central s/s | 78 | 19:30 | Joldhaka | 31 | 20:00
Netrokona | 107 | 19:30 | Noapara | 63 | 22:00 | Kurigram | 52 | 21:00
Jamalpur | 130 | 21:00 | Jessore | 106 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-06-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 394 | 24:00 | 387 | 1:00 | Kaliakoir | 375 | 0.91667 | 367 | 0.41667
| Bheramara | 396 | 18:30 | 394 | 13:00 | Bhulta | 388 | 0.083333 | 378 | 0.625
| Ashuganj(N) | 393 | 1:00 | 384 | 10:00 | Gopalganj | 406 | 0.041667 | 384 | 0.91667
| Payra | 416 | 1:00 | 404 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 21:00 | 226 | 1:00 | Comilla (N) | 236 | 20:00 | 229 | 12:00
| Ishurdi | 236 | 6:00 | 225 | 22:00 | Hathazari | 229 | 19:30 | 221 | 7:00
| Ashuganj | 235 | 19:30 | 230 | 10:00 | Megnaghat | 232 | 1:00 | 225 | 12:00
| Serajganj | 232 | 6:00 | 226 | 4:00 | Fenchuganj | 237 | 3:00 | 233 | 17:00
| Baghabari | 239 | 10:00 | 236 | 1:00 | Siddhirganj | 239 | 1:00 | 223 | 9:00
| Barapukuria | 234 | 3:00 | 227 | 20:00 | Maniknagar | 228 | 1:00 | 221 | 15:00
| Bogra | 230 | 5:00 | 221 | 21:00 | Agargaon | 226 | 2:00 | 217 | 15:00
| Rajshahi | 232 | 18:00 | 221 | 3:00 | Barisal | 245 | 7:00 | 230 | 21:00
| Khulna South | 232 | 6:00 | 211 | 16:00 | AKSML | 227 | 1:00 | 218 | 10:00
| Rampura | 229 | 20:00 | 221 | 9:00 | BSRM | 228 | 20:00 | 218 | 10:00
| Haripur | 230 | 20:00 | 223 | 11:00 | Bibiyana | 235 | 3:00 | 231 | 12:00
| Hasnabad | 226 | 1:00 | 218 | 15:00 | Bhulta | 231 | 20:00 | 224 | 12:00
| Shyampur | 225 | 2:00 | 217 | 13:00 | Ashuganj (S) | 235 | 1:00 | 229 | 10:00
| Aminbazar | 226 | 1:00 | 219 | 13:00 | Kaliakoir | 229 | 2:00 | 222 | 10:00
| Tongi | 227 | 19:00 | 217 | 7:00 | GPH | 226 | 2:00 | 218 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 19:30 | 130 | 12:00 | Hathazari | 136 | 0.83333 | 130 | 0.16667
| Munsiganj | 135 | 21:00 | 128 | 13:00 | Khulshi | 135 | 0.8125 | 126 | 0.5
| Sonargaon | 136 | 21:00 | 129 | 4:00 | Halishahar | 138 | 0.8125 | 129 | 0.45833
| Shyampur | 138 | 20:00 | 133 | 10:00 | Baraulia | 136 | 0.83333 | 129 | 0.45833
| Bhulta | 127 | 19:30 | 123 | 1:00 | Sikalbaha | 138 | 19:30 | 128 | 0.5
| Madanganj | 133 | 18:00 | 130 | 3:00 | Dohazari | 136 | 20:00 | 127 | 0.25
| Shitalakhya | 141 | 20:00 | 130 | 12:00 | Cox'sbazar | 119 | 0.70833 | 109 | 0.083333
| Rahim steal | 135 | 19:30 | 130 | 13:00 | Chandraghona | 137 | 0.83333 | 129 | 0.5
| Matuail | 135 | 19:30 | 130 | 12:00 | Kaptai | 134 | 21:00 | 130 | 0.25
| Ghorasal | 140 | 10:00 | 135 | 1:00 | A. Khaer Stl. | 135 | 0.83333 | 127 | 11:00
| Narsinghdi | 130 | 9:00 | 123 | 23:00 | Bakulia | 137 | 0.8125 | 127 | 0.45833
| Haripur (SBU) | 134 | 3:00 | 131 | 9:00 | Julda | 138 | 0.79167 | 128 | 0.41667
| Ullon | 134 | 20:00 | 130 | 14:00 | TK Chemical | 137 | 0.83333 | 129 | 9:00
| Hasnabad | 138 | 19:00 | 130 | 10:00 | Modern Steel | 134 | 0.875 | 128 | 0.375
| Magbazar | 134 | 5:00 | 130 | 15:00 | Shahmirpur | 137 | 0.8125 | 129 | 0.45833
| Maniknagar | 134 | 20:00 | 130 | 11:00 | Khagrachhari | 134 | 0.8125 | 128 | 0.5
| Bangabhaban | 134 | 20:00 | 130 | 11:00 | Matarbari | 120 | 0.75 | 109 | 0.041667
| Narinda | 134 | 20:00 | 130 | 11:00 | Baroiar Hat | 134 | 0.8125 | 126 | 0.95833
| Dhanmondi | 134 | 20:00 | 130 | 14:00 | Rangamati | 136 | 0.83333 | 130 | 9:00
| Lalbag | 138 | 20:00 | 129 | 12:00 | Goalpara S/S | 139 | 13:00 | 126 | 16:00
| Madartek | 134 | 5:00 | 130 | 12:00 | Khulna Central S/S | 138 | 0.54167 | 126 | 16:00
| Dhaka University |  |  |  |  | Noapara | 135 | 19:30 | 124 | 5:00
| Mirpur | 131 | 6:00 | 128 | 18:00 | Jessore | 138 | 19:00 | 120 | 16:00
| Kalyanpur | 133 | 21:00 | 129 | 12:00 | Benapol | 131 | 19:00 | 119 | 22:00
| Gulshan | 133 | 21:00 | 130 | 12:00 | Jhenida | 134 | 0.25 | 113 | 23:00
| Uttara | 130 | 21:00 | 128 | 12:00 | Bottail | 137 | 6:00 | 116 | 1:00
| Uttara New | 132 | 20:00 | 128 | 12:00 | G.K Project | 138 | 0.41667 | 124 | 4:00
| Kamrangirchar | 136 | 20:00 | 128 | 12:00 | Faridpur | 135 | 8:00 | 125 | 1:00
| Savar | 128 | 20:00 | 126 | 12:00 | Madaripur | 138 | 0.375 | 130 | 1:00
| Bhasantec | 128 | 20:00 | 124 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 127 | 1:00
| Agargaon | 130 | 20:00 | 125 | 12:00 | Gopalganj | 140 | 6:00 | 127 | 21:00
| Satmosjid | 130 | 6:00 | 125 | 12:00 | Bagerhat | 138 | 0.8125 | 125 | 22:00
| Tongi | 136 | 0.79167 | 131 | 10:00 | Mongla | 135 | 0.8125 | 121 | 3:00
| Kabirpur | 134 | 23:00 | 128 | 22:00 | Satkhira | 140 | 0.25 | 123 | 16:00
| Basundhara | 134 | 4:00 | 129 | 15:00 | Gallamari | 142 | 6:00 | 127 | 16:00
| Manikganj | 138 | 8:00 | 131 | 22:00 | Magura | 125 | 0.25 | 110 | 6:00
| Joydevpur | 141 | 8:00 | 136 | 22:00 | Norail | 123 | 0.75 | 108 | 1:00
| New Tongi | 135 | 0.29167 | 129 | 12:0 | Chuadanga | 130 | 22:00 | 102 | 6:00
| Kodda | 132 | 20:00 | 125 | 0.041667 | Barisal(N) | 138 | 18:00 | 130 | 21:00
| Dhamrai | 132 | 23:00 | 128 | 22:00 | Barisal (S) | 136 | 0.75 | 129 | 22:00
| Rajendrapur | 132 | 6:00 | 123 | 4:00 | Patuakhali | 133 | 0.77083 | 123 | 1:00
| Valuka | 129 | 9:00 | 117 | 2:00 | Bhandaria | 134 | 8:00 | 125 | 1:00
| Tangail | 135 | 6:00 | 125 | 22:00 | Ishurdi | 137 | 6:00 | 131 | 1:00
| Mymensing | 133 | 9:00 | 120 | 21:00 | Ruppur Paromanobik | 136 | 6:00 | 131 | 20:00
| Kishorganj | 132 | 8:00 | 121 | 21:00 | Natore | 134 | 6:00 | 128 | 3:00
| Netrokona | 132 | 9:00 | 116 | 21:00 | Bogra | 132 | 2:00 | 128 | 21:00
| Jamalpur | 138 | 9:00 | 126 | 16:00 | Noagaon | 131 | 19:00 | 123 | 21:00
| Sherpur | 138 | 23:00 | 125 | 0.66667 | Rajshahi | 132 | 6:00 | 127 | 5:00
| Srimongal | 136 | 7:00 | 132 | 0.875 | Rajshahi New | 133 | 19:00 | 126 | 3:00
| Shahjibazar | 133 | 4:00 | 130 | 0.58333 | C.Nawabganj | 131 | 19:00 | 123 | 3:00
| Fenchuganj | 136 | 6:00 | 133 | 0.45833 | Amnura | 132 | 19:00 | 123 | 16:00
| Khulawara | 134 | 16:00 | 132 | 0.041667 | Pabna | 134 | 8:00 | 129 | 20:00
| Sylhet | 134 | 1:00 | 132 | 0.95833 | Shahjadpur | 137 | 18:00 | 134 | 20:00
| Chatak | 134 | 15:00 | 131 | 19:00 | Serajganj | 133 | 10:00 | 129 | 21:00
| Sunamganj | 133 | 9:00 | 130 | 0.77083 | Niyamatpur | 129 | 19:00 | 122 | 21:00
| Biani Bazar | 135 | 16:00 | 130 | 1904-01-02 | Joypurhat | 132 | 19:00 | 123 | 21:00
| Comilla(s) | 125 | 10:00 | 120 | 19:00 | Sherpur(Bogura) | 134 | 6:00 | 128 | 21:00
| Comilla(n) | 137 | 19:30 | 131 | 14:00 | Mohastangor | 133 | 19:00 | 126 | 21:00
| Chandpur | 130 | 8:00 | 122 | 23:00 | Rangpur | 132 | 6:00 | 122 | 20:00
| Feni | 130 | 8:00 | 126 | 16:00 | Lalmonirhat | 128 | 6:00 | 118 | 19:30
| Chowmuhani | 129 | 20:00 | 122 | 15:00 | Saidpur | 131 | 5:00 | 120 | 20:00
| Ashuganj | 135 | 9:00 | 130 | 16:00 | Purbasadipur | 129 | 14:00 | 112 | 19:30
| Daudkandi | 133 | 19:30 | 128 | 14:00 | Thakurgaon | 128 | 6:00 | 110 | 19:30
| B.Baria | 135 | 9:00 | 130 | 16:00 | Palashbari | 130 | 6:00 | 120 | 20:00
| Ramganj | 123 | 20:00 | 120 | 19:00 | Barapukuria | 134 | 3:00 | 127 | 20:00
| Chaddagram | 133 | 20:00 | 127 |  | Panchagar | 124 | 6:00 | 102 | 20:00
| PHP | 133 | 20:00 | 125 | 14:00 | Joldhaka | 130 | 6:00 | 116 | 20:00
| Madanhat | 138 | 20:00 | 131 | 11:00 | Kurigram | 131 | 5:00 | 118 | 21:00

## L-Curve
Date | 2020-06-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 357 | 6200 | 3629 | 9829 |  |  |  | QF-LDC-12
0:30 | 282.5 | 6685 | 3634.5 | 10319.5 | Date: | 2020-06-26
1:00 | 208 | 7170 | 3640 | 10810
1:30 | 224 | 7073.5 | 3568.5 | 10642
2:00 | 240 | 6977 | 3497 | 10474
2:30 | 230 | 6894.5 | 3429 | 10323.5 | [5 empty] | Gen. at Eve. Peak | 10790 | 10790 MW (21:00 )
3:00 | 220 | 6812 | 3361 | 10173 | [6 empty] | 21:00
3:30 | 227 | 6729.5 | 3325 | 10054.5 | [5 empty] | Gen. at Day Peak | 8089.8 | 8089.8 MW (12:00 )
4:00 | 234 | 6647 | 3289 | 9936 | [6 empty] | 12:00
4:30 | 247 | 6642 | 3210.5 | 9852.5 | [5 empty] | Highest Generation | 10810
5:00 | 260 | 6637 | 3132 | 9769 | [6 empty] | 1:00
5:30 | 387 | 6145.1 | 3030.05 | 9175.15
6:00 | 514 | 5653.2 | 2928.1 | 8581.3
6:30 | 522.5 | 5452.58 | 2839.6 | 8292.18
7:00 | 531 | 5251.96 | 2751.1 | 8003.06
7:30 | 517.5 | 5180.03 | 2724.1 | 7904.13
8:00 | 504 | 5108.1 | 2697.1 | 7805.2
8:30 | 544.5 | 5044.05 | 2680.6 | 7724.65
9:00 | 585 | 4980 | 2664.1 | 7644.1
9:30 | 613.5 | 4963.25 | 2669.1 | 7632.35
10:00 | 642 | 4946.5 | 2674.1 | 7620.6
10:30 | 596.5 | 4977.15 | 2675.15 | 7652.3
11:00 | 551 | 5007.8 | 2676.2 | 7684
11:30 | 535.5 | 5162.45 | 2724.45 | 7886.9
12:00 | 520 | 5317.1 | 2772.7 | 8089.8
12:30 | 421.5 | 5468.55 | 2798.2 | 8266.75
13:00 | 323 | 5620 | 2823.7 | 8443.7
13:30 | 333 | 5633.35 | 2804.45 | 8437.8
14:00 | 343 | 5646.7 | 2785.2 | 8431.9
14:30 | 346.5 | 5675.9 | 2832.2 | 8508.1
15:00 | 350 | 5705.1 | 2879.2 | 8584.3
15:30 | 355 | 5634.1 | 2854.7 | 8488.8
16:00 | 360 | 5563.1 | 2830.2 | 8393.3
16:30 | 418.5 | 5338.05 | 2832.1 | 8170.15
17:00 | 477 | 5113 | 2834 | 7947
17:30 | 468.5 | 4993.1 | 2803.1 | 7796.2
18:00 | 460 | 4873.2 | 2772.2 | 7645.4
18:30 | 472.5 | 5311.1 | 3011.6 | 8322.7
19:00 | 485 | 5749 | 3251 | 9000
19:30 | 23 | 6821 | 3702 | 10523
20:00 | 25 | 6809 | 3677 | 10486 |  |  |  | Executive Engineer
20:30 | 59.5 | 6929.5 | 3708.5 | 10638 |  |  |  | Network Operation Division
21:00 | 94 | 7050 | 3740 | 10790
21:30 | 262 | 6882 | 3702 | 10584
22:00 | 430 | 6714 | 3664 | 10378 |  |  |  |  | Page 6 of 7
22:30 | 384 | 6574.5 | 3662 | 10236.5
23:00 | 338 | 6435 | 3660 | 10095
23:30 | 347.5 | 6317.5 | 3644.5 | 9962
24:00 | 357 | 6200 | 3629 | 9829
10790 MW (21:00 )
8089.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-06-26 |  | Energy | 219863970
[10 empty] | 2020-06-26 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3588 | 942 | 2112 | 2210 | 721 | 71 | 161 | 0 | 146
0:30 | 3567 | 936.5 | 2138 | 2587 | 721 | 84.5 | 191.5 | 0 | 155 | Date: | 2020-06-26
1:00 | 3546 | 931 | 2164 | 2964 | 721 | 98 | 222 | 0 | 164
1:30 | 3552 | 931.5 | 2174 | 2820.5 | 720 | 97 | 186 | 0 | 161 | [7 empty] | Total Energy | 219.864 | Total Energy Gen 219.864 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 219.864 MKWHr
2:00 | 3558 | 932 | 2184 | 2677 | 719 | 96 | 150 | 0 | 158 | [7 empty] | Energy not Served | 0
2:30 | 3582.5 | 932.5 | 2181.5 | 2526 | 718 | 96 | 133 | 0 | 154 | [7 empty] | Energy Requirement | 219.864
3:00 | 3607 | 933 | 2179 | 2375 | 717 | 96 | 116 | 0 | 150
3:30 | 3588 | 932.5 | 2180.5 | 2285 | 718 | 96 | 107.5 | 0 | 147 | [6 empty] | Shortage
4:00 | 3569 | 932 | 2182 | 2195 | 719 | 96 | 99 | 0 | 144
4:30 | 3561 | 932 | 2147.5 | 2156.5 | 720.5 | 96 | 99 | 0 | 140
5:00 | 3553 | 932 | 2113 | 2118 | 722 | 96 | 99 | 0 | 136
5:30 | 3518 | 932 | 2016 | 1738.5 | 667 | 96 | 75 | 0 | 132
6:00 | 3483 | 932 | 1919 | 1359 | 612 | 96 | 51 | 0 | 128
6:30 | 3412 | 932 | 1796.5 | 1326.5 | 567 | 78.5 | 51 | 0 | 126 |  |  |  |  | Coal
7:00 | 3341 | 932 | 1674 | 1294 | 522 | 61 | 51 | 0 | 124
7:30 | 3280 | 932 | 1662.5 | 1278 | 522.5 | 61.5 | 51 | 0 | 108 |  |  |  | Oil |  |  |  | ,
8:00 | 3219 | 932 | 1651 | 1262 | 523 | 62 | 51 | 0 | 92
8:30 | 3155.5 | 932.5 | 1628 | 1241.5 | 512.5 | 62.5 | 92 | 0 | 90
9:00 | 3092 | 933 | 1605 | 1221 | 502 | 63 | 133 | 0 | 88
9:30 | 3087.5 | 932.5 | 1620.5 | 1195.5 | 502.5 | 64 | 133 | 0 | 85
10:00 | 3083 | 932 | 1636 | 1170 | 503 | 65 | 133 | 0 | 82
10:30 | 3087 | 932 | 1632 | 1203 | 502 | 65 | 132.5 | 0 | 85
11:00 | 3091 | 932 | 1628 | 1236 | 501 | 65 | 132 | 0 | 88
11:30 | 3233 | 932 | 1681.5 | 1240 | 502.5 | 65.5 | 134.5 | 0 | 90
12:00 | 3375 | 932 | 1735 | 1244 | 504 | 66 | 137 | 0 | 92
12:30 | 3420.5 | 932 | 1872 | 1257.5 | 513.5 | 70.5 | 101.5 | 0 | 94
13:00 | 3466 | 932 | 2009 | 1271 | 523 | 75 | 66 | 0 | 96
13:30 | 3466 | 932 | 2009 | 1271 | 523 | 75 | 66 | 0 | 96
14:00 | 3466 | 932 | 2009 | 1271 | 523 | 75 | 66 | 0 | 96
14:30 | 3518 | 931.5 | 2053.5 | 1240 | 523.5 | 74.5 | 62 | 0 | 102
15:00 | 3570 | 931 | 2098 | 1209 | 524 | 74 | 58 | 0 | 108
15:30 | 3564 | 931.5 | 2050.5 | 1173 | 524 | 73 | 54.5 | 0 | 106
16:00 | 3558 | 932 | 2003 | 1137 | 524 | 72 | 51 | 0 | 104
16:30 | 3448.5 | 932 | 1890 | 1126 | 525 | 70.5 | 63.5 | 0 | 106
17:00 | 3339 | 932 | 1777 | 1115 | 526 | 69 | 76 | 0 | 108
17:30 | 3260.5 | 932 | 1685.5 | 1131 | 525.5 | 68 | 85.5 | 0 | 105
18:00 | 3182 | 932 | 1594 | 1147 | 525 | 67 | 95 | 0 | 102
18:30 | 3352 | 932 | 1748 | 1437.5 | 548 | 66 | 119.5 | 0 | 119
19:00 | 3522 | 932 | 1902 | 1728 | 571 | 65 | 144 | 0 | 136
19:30 | 3743 | 932 | 1928 | 2821 | 626 | 65 | 268 | 0 | 140
20:00 | 3591 | 932 | 1911 | 2911 | 638 | 65 | 294 | 0 | 144
20:30 | 3626.5 | 931.5 | 1970.5 | 2941 | 679.5 | 66 | 277 | 0 | 146
21:00 | 3662 | 931 | 2030 | 2971 | 721 | 67 | 260 | 0 | 148
21:30 | 3676.5 | 931 | 2042.5 | 2743 | 721 | 68 | 254 | 0 | 148
22:00 | 3691 | 931 | 2055 | 2515 | 721 | 69 | 248 | 0 | 148
22:30 | 3707.5 | 936.5 | 2042.5 | 2362.5 | 721 | 70 | 247.5 | 0 | 149
23:00 | 3724 | 942 | 2030 | 2210 | 721 | 71 | 247 | 0 | 150
23:30 | 3656 | 942 | 2071 | 2210 | 721 | 71 | 204 | 0 | 148 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 3588 | 942 | 2112 | 2210 | 721 | 71 | 161 | 0 | 146
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 219.864 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 219.864 MKWHr
Note on W13: Author:

## Generation
g | 2020-06-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 63 | 61 | 61 | 61 | 61 | 61 | 61 | 62 | 63 | 65 | 65 | 66 | 75 | 75 | 74 | 72 | 69 | 67 |  | 65 | 65 | 65 | 67 | 69 | 71 | 71 | 1521360
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | [20 empty] | 212000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.7 | 2.76 | 10.8 | 3.8 | 10.1 | 7.8 |  |  |  | 8.9 | 8.9 | 5 | 0.9 | [8 empty] | 62505
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 140 | 140 | 140 | 140 | 140 | 104 | 104 | 104 | 104 | 139 | 139 | 140 | 139 | 70 | 70 |  | 70 | 139 | 140 | 140 | 139 | 139 | 0 | 3106272
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 102 | 102 | 100 | 99 | 99 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 49 | 51 | 51 | 51 | 74 | 85 |  | 85 | 102 | 102 | 102 | 102 | 102 | 102 | 1809150
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | [24 empty] | 0 | 88654
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 61 | 96 | 95 | 96 | 93 | 93 | 87 | 57 | 35 | 35 | 35 | 35 | 94 | 93 | 93 | 33 | 35 | 35 |  | 82 | 82 | 52 | 87 | 89 | 90 | 94 | 1789000
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 300 | 250 | 240 | 240 | 238 | 220 | 220 | 280 | 320 | 320 | 318 | 318 | 318 | 250 |  | 250 | 328 | 275 | 290 | 290 | 290 | 290 | 6908567
18 | Kodda 300 MW PP Unit-2 (Summit) | 230 | 165 | 95 | 45 | 45 | 15 | 15 | 15 | 14 | 15 | 34 | 45 | 45 | 45 | 45 | 30 | 30 | 30 |  | 39 | 145 | 169 | 286 | 145 | 145 | 145 | 2147781
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 485090
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 722000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 250 |  | 250 | 250 | 300 | 300 | 300 | 300 | 300 | 6966873
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 2184806
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2226375
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 39 | 39 | 38 | 38 | 38 | 38 | 38 | 39 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 905256
33 | Ashuganj 225 MW CCPP | 185 | 186 | 193 | 185 | 182 | 182 | 183 | 182 | 182 | 183 | 183 | 212 | 182 | 202 | 194 | 184 | 184 | 185 |  | 208 | 216 | 182 | 216 | 212 | 212 | 212 | 4670000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 320 | 310 | 310 | 310 | 310 | 270 | 260 | 260 | 260 | 340 | 310 | 325 | 315 | 310 | 265 | 260 |  | 330 | 310 | 280 | 295 | 295 | 315 | 300 | 7482500
35 | Ashuganj 55 MW PP (Precision) | 45 | 46 | 46 | 45 | 46 | 47 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 489600
36 | Chandpur 150 MW CCPP | 90 | 91 | 90 | 91 | 82 | 80 | 90 | 81 | 86 | 86 | 88 | 90 | 82 | 91 | 91 | 84 | 90 | 90 |  | 91 | 80 | 80 | 80 | 86 | 90 | 91 | 2057530
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 390 | 390 | 390 | 390 | 390 | 390 | 300 | 300 | 300 | 300 | 300 | 370 | 420 | 420 | 420 | 400 | 400 | 310 |  | 340 | 380 | 340 | 380 | 380 | 340 | 340 | 8660250
41 | Haripur 360MW CCPP(HPL) | 320 | 320 | 320 | 320 | 320 | 315 | 250 | 250 | 254 | 255 | 253 | 254 | 254 | 254 | 254 | 254 | 254 | 254 |  | 283 | 294 | 294 | 290 | 290 | 290 | 330 | 6666000
42 | RPCL 210MW CCPP | 159 | 159 | 159 | 158 | 160 | 160 | 157 | 160 | 160 | 157 | 156 | 154 | 157 | 155 | 154 | 155 | 155 | 155 |  | 153 | 155 | 157 | 156 | 156 | 156 | 160 | 3664040
43
44 | Fenchugonj CCPP Phase-1 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 56 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1413000
45 | Fenchugonj CCPP Phase-2 | 30 | 0 | [24 empty] | 41160
46 | Shajibazar 330 MW CCPP | 254 | 258 | 257 | 258 | 255 | 250 | 257 | 248 | 253 | 287 | 300 | 316 | 289 | 301 | 303 | 288 | 298 | 299 |  | 326 | 291 | 250 | 245 | 286 | 303 | 293 | 6259000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 61 | 63 | 60 | 61 | 61 | 61 | 58 | 58 | 53 | 59 | 53 | 53 | 59 | 51 |  | 59 | 61 | 52 | 52 | 52 | 52 | 52 | 1365408
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 76 | 76 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 71 | 69 | 20 |  | 71 | 71 | 71 | 71 | 71 | 72 | 72 | 1309440
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 151 | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 70 | 70 | 70 | 150 | 150 | 150 | 150 | 150 | 100 | 70 |  | 100 | 150 | 150 | 150 | 150 | 150 | 151 | 3119640
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 427000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 243180
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 223152
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 45 | 45 | 45 | 45 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 42 | 47 | 47 | 47 | 11 | 11 |  | 43 | 47 | 47 | 47 | 47 | 47 | 47 | 792600
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 539304
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 310 | 310 | 310 | 290 | 265 | 270 | 290 | 285 | 300 | 295 | 310 | 310 | 295 | 315 | 290 | 290 | 300 |  | 310 | 270 | 280 | 290 | 280 | 295 | 320 | 7358250
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 17 | 17 | [16 empty] | 17 | 53 | 35 | 17 | 17 | 17 | 17 | 231619
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 475920
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | [6 empty] | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 333216
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 |  | 0 | 368511
63 | Impoprt (Tripura) | 164 | 158 | 150 | 144 | 136 | 128 | 124 | 92 | 88 | 82 | 88 | 92 | 96 | 102 | 108 | 104 | 108 | 102 |  | 136 | 140 | 144 | 148 | 148 | 150 | 146 | 2986560
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 40 | 32 | 22 | 22 | 22 | 36 | 25 | 26 | 37 | 37 | 37 |  | 40 | 40 | 40 | 42 | 42 | 42 | 42 | 862080
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 488916
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | 5 | 5 | 5 | 5 |  |  | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 98820
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 20 | 20 | 15 | 14 | 18 | 14 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 490260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 22 | 22 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 14 | 28 | 30 | 30 | 30 | 30 | 551520
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 657900
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 53 | 53 | 53 | 53 | 53 | 53 | 96 | 95 | 95 | 98 | 24 | 24 |  | 96 | 96 | 96 | 97 | 97 | 97 | 94 | 1866136
| Feni Lanka Power | [20 empty] | 20 | 51 | 17 |  |  | 0 | 54720
| Chowmuhani 113 MW | 104 | 104 | 104 | 104 | 105 | 55 | 46 | 46 | 46 | 26 | 26 | 26 | 26 | 8 | 38 | 46 | 46 | 46 |  | 64 | 105 | 103 | 104 | 104 | 104 | 104 | 1632960
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 60 | 97 | 97 | 96 | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 12 | 50 | 80 | 92 | 80 | 30 | 30 | 882240
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | 48 | 16 | 16 | [5 empty] | 82 | 82 | 82 | 82 | 16 | [6 empty] | 10 | 36 | 48 | 48 | 48 | 48 | 16 | 676800
80 | Jamalpur 95 MW PP(Powerpac) | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 593280
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 1 | 25 | 43 | 52 | 52 | 52 | 52 | 257002
| Gazipur 100 MW PP | 18 |  |  |  | 50 | 106 | 53 | 35 | 35 | 36 | 53 | 52 | 52 | 17 | 17 | 17 |  |  |  |  | 17 | 52 | 17 | 17 | 17 | 17 | 684888
| Kaptai 7 MW Solar PP | [5 empty] | 0.4 | 1 | 1.7 | 2.3 | 5.4 | 2.5 | 2.6 | 4.2 | 1.1 | 2.1 | 2.1 | 0 | 0.2 | [8 empty] | 27120
| Jodiac Power | 54 | 54 | 34 | [16 empty] | 1 | 54 | 42 |  |  |  | 0 | 230015
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 95 | 95 | 95 | 95 | 95 | 35 | 48 | 48 | 48 | 48 | 48 | 48 | 30 | 30 | 30 | 45 | 40 | 48 |  | 64 | 64 | 64 | 81 | 81 | 81 | 64 | 1502760
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [20 empty] | 30 | 30 |  |  |  | 0 | 38435
86 | Meghnaghat CCPP(Summit) | 260 | 260 | 265 | 260 | 240 | 230 | 265 | 235 | 265 | 260 | 270 | 280 | 275 | 275 | 270 | 260 | 265 | 265 |  | 280 | 240 | 245 | 255 | 250 | 260 | 255 | 6289455
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 32 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 35 | 100 | 100 | 100 | 75 | 33 | 33 | 1045440
| Sonargoan 104 MW (Orion) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 104 | 106 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2613120
88 | Ghorashal 78.5 MW PP(MAX) | 63 | 63 | 63 | 63 | 64 | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 40 | 62 | 61 | 61 | 40 | 40 |  | 40 | 61 | 62 | 62 | 63 | 63 | 63 | 1339072
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 29 | 46 | 46 | 46 | 10 | 10 |  | 28 | 46 | 46 | 46 | 46 | 46 | 46 | 847512
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 17 | 19 | 43 | 35 | 10 | 10 |  | 25 | 35 | 43 | 43 | 43 | 43 | 43 | 776310
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 7 | 7 |  | 42 | 66 | 66 | 66 | 32 | 32 | 32 | 1014480
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | 45 | 45 | [17 empty] | 3 | 35 | 42 |  |  |  | 0 | 155520
97 | Katpotti 52 MW PP (Sinha)
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 41 | 41 | 41 | 41 | 41 | 15 | [14 empty] | 10 | 16 | 40 | 15 |  | 0 | 356943
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 |  | 35 | 55 | 17 | 55 | 55 | 55 | 17 | 17 | 17 |  | 35 | 55 | 55 | 17 | 17 | 17 | 17 | 919561
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 130 | 110 |  | 110 | 130 | 130 | 163 | 163 | 130 | 130 | 3248018
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.2 | 0.6 | 0.9 | 1 | 0.5 | 0.5 | 0.8 | 0.6 | 1.1 | 1.1 | 0 | 0.1 | [8 empty] | 7000
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | [14 empty] | 17 | 17 | 17 | 30 | 53 | 53 | 53 | 496080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 150 | 130 | 130 | 130 | 130 | 50 | 50 | 50 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 38 | 185 | 180 | 185 | 180 | 50 | 16 | 1857600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 128 | 128 | 107 | 95 | 95 | 95 | 103 | 132 | 110 | 85 | 85 | 85 | 85 | 85 | 89 | 128 | 131 | 131 |  | 131 | 131 | 132 | 131 | 130 | 131 | 131 | 2711520
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2365440
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | 50 | 36 | [17 empty] | 2 | 65 | 60 | 135 |  |  | 0 | 393091
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 108 | 108 | 115 | 115 | 85 | 35 | 2706000
| Anwara 300 MW PP (United) | 306 | 306 | 307 | 307 | 307 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 105 | 107 | 107 | 78 | 70 | 70 |  | 230 | 292 | 300 | 307 | 307 | 307 | 307 | 4094836
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2409600
120 | Eastern Zone Total | 7170 | 6977 | 6812 | 6647 | 6637 | 5653.2 | 5251.96 | 5108.1 | 4980 | 4946.5 | 5007.8 | 5317.1 | 5620 | 5646.7 | 5705.1 | 5563.1 | 5113 | 4873.2 |  | 5749 | 6821 | 6809 | 7050 | 6714 | 6435 | 6200 | 143661419
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 99 | 66 | 49 | 49 | 55 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 16 | 16 | 16 |  | 73 | 115 | 115 | 115 | 115 | 115 | 99 | 1645440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [19 empty] | 35 | 105 | 70 | 35
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 80 | 16 | [13 empty] | 18 | 54 | 64 | 76 | 110 | 96 | 96 | 1061760
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 77 | 77 | 75 | 77 | 53 | 53 | 33 | 33 | 33 | 33 | 69 | 77 | 77 | 79 | 54 | 54 |  | 63 | 77 | 79 | 80 | 79 | 79 | 79 | 1572422
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 |  | 87 | 86 | 86 | 86 | 86 | 87 | 86 | 2110725
140 | Bhola 33 MW PP (Venture) | 37 | 37 | 33 | 37 | 36 | 32 | 26 | 24 | 23 | 24 | 22 | 26 | 26 | 27 | 26 | 24 | 25 | 24 |  | 32 | 35 | 38 | 38 | 38 | 37 | 37 | 728236
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 80 |  |  |  | 14 | 50 | 50 | 50 | 30 | 30 | 55 | 40 | [6 empty] | 3 | 100 | 90 | 100 | 100 | 100 | 100 | 1156800
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 549750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 10 | [8 empty] | 12288
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [18 empty] | 0 | 125568
146 | Bheramara HVDC | 931 | 932 | 933 | 932 | 932 | 932 | 932 | 932 | 933 | 932 | 932 | 932 | 932 | 931 | 931 | 932 | 932 | 932 |  | 932 | 932 | 932 | 931 | 931 | 942 | 942 | 22379636
147 | Bheramara 410 MW CCPP | 345 | 345 | 360 | 345 | 345 | 325 | 240 | 235 | 235 | 235 | 240 | 240 | 265 | 265 | 345 | 345 | 345 | 285 |  | 385 | 345 | 345 | 345 | 340 | 355 | 345 | 7661952
148 | Payra 1320 MW | 571 | 570 | 568 | 570 | 572 | 462 | 372 | 374 | 353 | 354 | 352 | 355 | 374 | 374 | 375 | 375 | 377 | 376 |  | 422 | 477 | 489 | 572 | 572 | 572 | 572 | 11416300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3677300
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 70 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 70 | 70 | 1505000
156 | Baghabari 100 MW GTPP | [15 empty] | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 608000
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 176 | 147 | 165 | 154 | 154 | 155 |  | 166 | 190 | 184 | 172 | 163 | 153 | 169 | 3870582
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 170 | 170 | 170 | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 160 | 195 | 179 | 165 | 161 | 164 | 178 | 3968491
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 391 | 392 | 392 | 392 | 343 | 333 | 391 | 352 | 336 | 360 | 364 | 402 | 390 | 412 | 408 | 339 | 364 | 331 |  | 362 | 287 | 285 | 343 | 377 | 400 | 409 | 8894727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 21 | 0 | 0 | 10 | 21 | 439440
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256536
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 |  | 0 | 178560
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 15 | 30 | 34 |  |  |  |  | 43597
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | 72 | 32 | [9 empty] | 5 | 1 | 7 | 7 |  |  |  |  | 24 | 90 | 100 | 100 | 98 | 97 | 43 | 641104
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 35 | [17 empty] | 21 | 100 | 102 | 113 | 35 |  | 0 | 575328
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [19 empty] | 10 | 10 | 10 | 10 |  |  |  | 36000
176 | Rangpur 113 MW PP (Confidence) | 113 | 108 | 90 | 44 |  |  |  |  | 31 | 35 | 35 | 36 | [7 empty] | 80 | 108 | 108 | 113 | 113 | 113 | 113 | 1082880
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 1.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | [8 empty] | 4129
178
178