## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May 2020
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | May 2020 |  | April 2020 |  | May 2019
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11977 | 18/05/20 | 10344 | 14/04/20 | 12893 | 29/05/19 | 12893 | 29/05/19
|  |  | 22:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 2679.2 | 21/05/20 | 4292.2 | 25/04/20 | 4900 | 25/05/19 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11941 | 18/05/20 | 10344 | 14/04/20 | 12893 | 29/05/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9490.1 | 18/05/20 | 8389.7 | 05/04/20 | 10364.4 | 29/05/19 | 10636.2 | 01/09/19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11941 | 18/05/20 | 10344 | 14/04/20 | 12893 | 29/05/19 | 12893 | 29/05/19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9477.5161 |  | 8896.9333 |  | 11307.071 |  | 11679.07 | 2019-09-19
7 | Average Generation (MW) at Day Peak | 7427.4674 |  | 7031.8517 |  | 9118.159 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, HVDC (MW) | 949 | 10/05/2020 | 949 | 09/04/2020 | 946 | 08/05/19 | 956 | 27/3/2019
|  |  | 1:00 |  | 22:00 |  | 1:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 190 | 17/05/2020 | 142 | 14/04/2020 | 190 | 11'/05/19 | 194 | 12/06/19
|  |  | 21:00 |  | 20:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 2010-05-04
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 3143.7123 |  | 3300.8626 |  | 3572.9103 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 69.8388 |  | 99.2395 |  | 123.0983
22 | Net Generation of BPDB (MKWH) | 3073.8735 |  | 3201.6231 |  | 3449.812
23 | Net Generation of IPP & RPCL (MKWH) | 124.5045 |  | 134.1374 |  | 2244.8907
24 | Net Generation of REB (MKWH) | 118.008 |  | 101.3435 |  | 136.4
24 | Net Generation of Rental Power Plant (MKWH) | 375.5825 |  | 202.4975 |  | 497.3361
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3691.9684 |  | 3639.6015 |  | 6328.4388 |  | 6553.86 | Sep-19
26 | Energy Generation by Gas (MKWH) | 4152.6276 |  | 3983.5017 |  | 4635.99 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 175.8613 |  | 102.8552 |  | 292.2378 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 644.461 |  | 295.0235 |  | 1321.8953 |  | 1524.02 | July-19
29 | Energy Generation by Hydro (MKWH) | 38.7155 |  | 24.8805 |  | 24.0671 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 15.7592 |  | 5.7632 |  | 3.9774 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 325.8707 |  | 416.1569 |  | 173.674 |  | 416.1569 | 2020-04-17
32 | Enegry Import from India (HVDC & AC) (MKWH) | 568.5998 |  | 403.908 |  | 762.9273 |  | 762.62 | August-19
33 | Monthly Load Factor (%) | 66.4568 |  | 70.2513 |  | 75.2134 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May' 2020
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11977 | 18/05/20 | 22:00
Generation Period
| Dhaka | MW | 3611
| Chattogram | MW | 1159
| Cumilla | MW | 1174
| Mymensingh | MW | 1010
| Sylhet | MW | 444
a) | Total supply in East zone | MW | 7398
| Khulna | MW | 1574
| Barisal | MW | 367
| Rajshahi | MW | 1270
| Rangpur | MW | 774
b) | Total supply in West zone | MW | 3985
c) | Total supply in both zone ( a+b) | MW | 11383
Ref: | 27.21.0000.603.16.087.20.285 | Date: 18/06/2020
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May' 2020
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 420 | 20/05/20 | 3:00
| b) Ishurdi end | MW | 283 | 10/05/20 | 23:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 730 | 10/05/20 | 23:00
| b) Ishurdi end | MW | 167 | 20/05/20 | 3:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 1.2913 | 29/05/20
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 1.2375 | 29/05/20
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 10.5838
| b) Ishurdi end | MKWH | 38.0127
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 36.8723
| b) Ishurdi end | MKWH | 10.2756
23 | Transmission loss of EWI/ NO-1 | % | 2.91
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 370 | 20/05/20 | 3:00
| b)Serajganj end | MW | 570 | 27/05/20 | 22:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 560 | 27/05/20 | 22:00
| b)Sirajganj end | MW | 340 | 20/05/20 | 3:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.914 | 19/05/20
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 2.88 | 19/05/20
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 25.512
| b)Sirajganj end | MKWH | 88.914
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 86.724
| b)Sirajganj end | MKWH | 25.35
30 | Transmission loss of EWI /NO-2 | % | 1.775
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | 132/33 kV Transformers-T3 | 2020-05-06 18:53 | 2020-05-06 19:08 | 0:15 | T | Tripped showing differential relay | 35 | 8.75 | Power interruption
Kabirpur | 132/33 kV Transformers-T2 & T3 | 2020-05-07 10:28 | 2020-05-07 11:48 | 1:20 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformers-T3 | 2020-05-09 12:54 | 2020-05-09 13:03 | 0:09 | T | Tripped showing O/C & E/F relay | 35 | 5.25 | Power interruption
Tangail | 132/33 kV Transformers-T1 & T2 | 2020-05-10 23:52 | 2020-05-11 00:15 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kishireganj | 132/33 kV Transformer-T2 | 2020-05-14 16:55 | 2020-05-14 18:03 | 1:08 | T | Tripped showing differential relay | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T2 | 2020-05-14 06:18 | 2020-05-14 07:45 | 1:27 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kishireganj | 132/33 kV Transformer-T3 | 2020-05-15 10:05 | 2020-05-15 11:18 | 1:13 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T2 with 33 kV full Bus | 2020-05-17 00:38 | 2020-05-17 01:24 | 0:46 | E/O | Due to red-hot maintenance at 33 kV side | 10 | 7.6667 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-05-20 09:30 | 2020-05-20 12:20 | 2:50 | E/O | Due to Breaker maintenance | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T3 | 2020-05-27 12:55 | 2020-05-27 23:10 | 10:15 | E/O | Due to 33 kV R-phase CT burnt | 0 | 0 | No interruption
|  |  | Total : | 19:46 |  | Unserved Energy: |  | 21.6667
Dhaka (South) Grid Circle :
Madanganj | 132/33 kV Transformer-T1 | 2020-05-08 00:26 | 2020-05-08 00:45 | 0:19 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Hasnabad | 33 all incoming CB | 2020-05-20 20:08 | 2020-05-20 20:42 | 0:34 | T | Tripped showing 33 kV Lalbagh feeder fault | 78 | 44.2 | Power interruption
Shyampur | 132/33 kV Transformer-T1 | 2020-05-22 07:34 | 2020-05-22 07:34 | 0:00 | T | Due to backup pro.relay | 0 | 0 | No interruption
Gulshan | 132/33 kV Transformer-T2 | 2020-05-24 13:50 | 2020-05-24 18:26 | 4:36 | T | Tripped showing differential relay | 44 | 202.4 | Power interruption
Siddhirganj | 132/33 kV Transformers-T1 & T2 | 2020-05-28 08:27 | 2020-05-28 08:39 | 0:12 | T | Tripped showing O/C & E/F relay at 33 kV side | 58 | 11.6 | Power interruption
|  |  | Total : | 5:41 |  | Unserved Energy: |  | 258.2
Chattogram Grid Circle :
Dohazari | 132/33 kV Transformer-T1 | 2020-05-01 11:50 | 2020-05-01 15:50 | 4:00 | T | Tripped showing E/F relay at 33 kV side | 52 | 208 | Power interruption
Madunaghat | 132/33 kV Transformer-T1 | 2020-05-02 10:06 | 2020-05-02 12:18 | 2:12 | E/O | Due to Oil filling | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1, & T3 | 2020-05-05 13:00 | 2020-05-05 14:17 | 1:17 | T | Tripped showing O/C relay at 33 kV feeder burst | 65 | 83.4167 | Power interruption
Hathazari | 132 kV main Bus -1 & 2 | 2020-05-06 09:21 | 2020-05-06 09:38 | 0:17 | T
| 132/33 kV Transformers-MT1 MT2 & MT4 | 2020-05-06 09:21 | 2020-05-06 09:43 | 0:22 | T
Halishahar | 132/33 kV Transformer-T3 | 2020-05-08 07:39 | 2020-05-08 07:39 | 0:00 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2020-05-30 08:26 | 2020-05-30 08:45 | 0:19 | T | Tripped showing O/C relay at 33 kV feeder burst | 37 | 11.7167 | Power interruption
|  |  | Total : | 8:27 |  | Unserved Energy: |  | 303.1333
Cumilla Grid Circle :
Ramganj | 132/33 kV Transformers-T1 | 2020-05-09 19:50 | 2020-05-09 20:08 | 0:18 | T | Tripped showing O/C relay | 88 | 26.4 | Power interruption
| 132/33 kV Transformers-T2 | 2020-05-09 19:50 | 2020-05-09 21:45 | 1:55 | T
Sreemongal | 132/33 kV Transformer-T3 | 2020-05-10 08:01 | 2020-05-10 10:15 | 2:14 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T4 | 2020-05-10 08:10 | 2020-05-10 09:08 | 0:58 | E/O |  | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T2 | 2020-05-10 09:04 | 2020-05-10 10:07 | 1:03 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Ashuganj | Ashuganj 230 kV Bus-1 | 2020-05-10 19:08 | 2020-05-10 20:45 | 1:37 | E/O | Due to bursting of Y-phase CT | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 | 2020-05-15 09:30 | 2020-05-15 10:45 | 1:15 | E/O | Due to red-hot maintenance at 33 kV side | 10 | 12.5 | Power interruption
Chowmuhani | 132/33 kV Transformers-T1 & T3 | 2020-05-23 08:30 | 2020-05-23 13:10 | 4:40 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T2 & 33 kV Bus | 2020-05-26 08:30 | 2020-05-26 09:59 | 1:29 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 15:29 |  | Unserved Energy: |  | 38.9
Khulna Grid Circle :
Mongla | 132/33 kV Transformer-T1 | 2020-05-01 19:12 | 2020-05-01 19:37 | 0:25 | T | Tripped showing E/F relay at 33 kV side | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T1 | 2020-05-03 09:06 | 2020-05-03 09:25 | 0:19 | T | Tripped showing O/C relay | 35 | 11.0833 | Power interruption
| 132/33 kV Transformers-T2 | 2020-05-03 09:06 | 2020-05-03 10:08 | 1:02 | T
Bagerhat | 132/33 kV Transformer-T1 | 2020-05-06 14:11 | 2020-05-06 15:06 | 0:55 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Gopalganj(N) | 400/132 kV Transformer-T01 | 2020-05-08 09:24 | 2020-05-08 10:18 | 0:54 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 400/132 kV Transformer-T02 | 2020-05-08 09:25 | 2020-05-08 10:16 | 0:51 | E/O |  | 0 | 0 | No interruption
Barisal | 132/33 kV Transformer-T2 | 2020-05-09 08:10 | 2020-05-09 09:09 | 0:59 | E/O | Due to red-hot maintenance | 20 | 19.6667 | Power interruption
Barisal(S) | 132/33 kV Transformer-T2 | 2020-05-11 07:53 | 2020-05-11 09:17 | 1:24 | E/O | Due to red-hot maintenance | 30 | 42 | Power interruption
Gopalganj(N) | 400/132 kV Transformers-T01 & T2 | 2020-05-11 14:07 | 2020-05-11 15:00 | 0:53 | T | Tripped showing closed block relay | 0 | 0 | No interruption
| 132 kV capacitor bank-1 | 2020-05-11 17:26 | 2020-05-11 17:26 | 0:00 | E/O | Due to bursting of Y-phase L/A | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | 132/33 kV Transformer-T3 | 2020-05-18 08:16 | 2020-05-18 09:21 | 1:05 | E/O | Due to red-hot maintenance 33 kV side | 10 | 10.8333 | Power interruption
Faridpur | 132/33 kV Transformers-T1 & T2 | 2020-05-20 09:52 | 2020-05-20 09:57 | 0:05 | T | Tripped showing 33 kV feeder fault | 55 | 4.5833 | Power interruption
| 132/33 kV Transformer-T1 | 2020-05-23 00:22 | 2020-05-23 01:15 | 0:53 | T | Tripped showing 33 kV feeder fault | 70 | 61.8333 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2020-05-29 09:25 | 2020-05-29 09:36 | 0:11 | T | Tripped showing 33 kV feeder fault | 90 | 16.5 | Power interruption
Sirajganj | 230 kV Bus-2 | 2020-05-29 11:32 | 2020-05-29 14:02 | 2:30 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformers-T1 | 2020-05-31 08:02 | 2020-05-31 08:20 | 0:18 | T | Due to fuse burn of auxiliary X-former | 40 | 12 | Power interruption
| 132/33 kV Transformers-T2 | 2020-05-31 08:02 | 2020-05-31 09:51 | 1:49 | T
|  |  | Total : | 14:33 |  | Unserved Energy: |  | 178.5
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T2 | 2020-05-17 07:58 | 2020-05-17 09:08 | 1:10 | E/O | Due to red-hot maintenance at 33 kV side | 5 | 5.8333 | Power interruption
| 132/33 kV Transformer-T1 | 2020-05-23 08:01 | 2020-05-23 09:20 | 1:19 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bottail | 33 kV Bus | 2020-05-24 07:10 | 2020-05-24 10:19 | 3:09 | E/O | Due to emergency maintenance | 50 | 157.5 | Power interruption
Shahjadpur | 132/33 kV Transformer-T3 | 2020-05-26 19:41 | 2020-05-26 20:59 | 1:18 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 6:56 |  |  |  | 163.3333
Bogura Grid Circle:
Naogaon | 132/33 kV Transformer-T3 | 2020-05-01 19:15 | 2020-05-01 19:25 | 0:10 | T | Tripped showing E/F relay at 33 kV side | 20 | 3.3333 | Power interruption
Barapukuria | 132/33 kV Transformer-T5 | 2020-05-01 12:12 | 2020-05-01 12:12 | 0:00 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2020-05-07 09:15 | 2020-05-07 10:10 | 0:55 | E/O | Due to red-hot maintenance at 33 kV side | 9 | 8.25 | Power interruption
Saidpur | 132/33 kV Transformer-T5 | 2020-05-09 08:20 | 2020-05-09 09:15 | 0:55 | E/O | Due to red-hot maintenance at 33 kV side | 14 | 12.8333 | Power interruption
Joldhaka | 132/33 kV Transformer-T1 | 2020-05-09 21:25 | 2020-05-09 22:17 | 0:52 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Baghabari | 230/132 kV Transformer-T2 | 2020-05-12 08:17 | 2020-05-12 11:26 | 3:09 | E/O | Due to Oil leakage | 0 | 0 | No interruption
C.nawabganj | 132/33 kV Transformer-T2 | 2020-05-13 09:53 | 2020-05-17 11:59 | 98:06 | E/O | Due to gas filling | 0 | 0 | No interruption
Rangpur | 33 kV bus-2 | 2020-05-14 15:50 | 2020-05-14 16:55 | 1:05 | E/O | Due to red-hot maintenance | 30 | 32.5 | Power interruption
Purbasadipur | 132/33 kV Transformer-T1 | 2020-05-14 15:10 | 2020-05-14 15:50 | 0:40 | E/O | Due to red-hot maintenance at 33 kV side | 15 | 10 | Power interruption
Saidpur | 33 kV bus | 2020-05-15 08:40 | 2020-05-15 10:45 | 2:05 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 41.6667 | Power interruption
Baghabari | 230/132 kV Transformers-T1 & T2 | 2020-05-20 01:00 | 2020-05-20 02:58 | 1:58 | E/O | Due to heavy fiashing at 132 kV side | 0 | 0 | No interruption
Purbasadipur | 132 kV Bus | 2020-05-23 08:32 | 2020-05-23 11:08 | 2:36 | E/O | Due to red-hot maintenance | 110 | 286 | Power interruption
Saidpur | 33 kV bus | 2020-05-23 10:48 | 2020-05-23 12:40 | 1:52 | E/O | Due to red-hot maintenance | 20 | 37.3333 | Power interruption
Rangpur | 33 kV bus | 2020-05-23 11:30 | 2020-05-23 12:44 | 1:14 | E/O | Due to red-hot maintenance | 65 | 80.1667 | Power interruption
Pabna | 132/33 kV Transformers-T1 | 2020-05-24 05:40 | 2020-05-24 06:16 | 0:07 | T | Tripped showing E/F relay | 0 | 0
| 132/33 kV Transformers-T2 | 2020-05-24 05:40 | 2020-05-24 06:15 | 0:35 | T |  | 35 | 20.4167 | Power interruption
Palashbari | 132/33 kV Transformers-T3 ,T4 & 33 kV Bus | 2020-05-24 12:00 | 2020-05-24 13:50 | 1:50 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T5 | 2020-05-24 11:29 | 2020-05-24 13:10 | 1:41 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-05-25 21:56 | 2020-05-25 22:24 | 0:28 | E/O | Due to red-hot maintenance at 33 kV side | 45 | 21 | Power interruption
| 132/33 kV Transformer-T2 | 2020-05-26 15:51 | 2020-05-26 17:10 | 1:19 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T03 | 2020-05-27 05:08 | 2020-05-27 05:08 | 0:00 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2020-05-27 22:14 | 2020-05-28 00:17 | 2:03 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformers-T1 & T3 bus | 2020-05-28 08:15 | 2020-05-28 09:40 | 1:25 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T03 | 2020-05-30 11:54 | 2020-05-30 12:51 | 0:57 | E/O | Due to Oil filling | 0 | 0 | No interruption
| 230/132 kV Transformer-T01 | 2020-05-30 10:45 | 2020-05-30 11:47 | 1:02 | E/O |  | 0 | 0 | No interruption
Norail | 132/33 kV Transformer-13 | 2020-05-30 09:27 | 2020-05-30 10:15 | 0:48 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 127:52 |  |  |  | 553.5
Others :
Ashuganj | 230/132 kV Transformer-OAT12 | 2020-05-05 18:30 | 2020-05-05 22:10 | 3:40 | T | Tripped showing E/F relay at 132 kV side | 0 | 0 | No interruption
Ullon | 132/33 kV Transformer-T2 | 2020-05-19 11:25 | 2020-05-19 11:55 | 0:30 | T | Tripped showing O/C relay | 60 | 30 | Power interruption
|  |  | Total : | 3:40 |  | Unserved Energy: |  | 30
Total outage period of Sub-station Equipment : |  |  |  | 202:24 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2020-05-02 18:10 | 2020-05-02 19:45 | 1:35 | T | Tripped showing dist.(Z3) relay | 0 | 0 | No interruption
Tongi | Tongi-Ghorashal 230 kV line-1 | 2020-05-10 17:09 | 2020-05-10 17:40 | 0:31 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh 132 kV line | 2020-05-11 00:05 | 2020-05-11 01:37 | 1:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakori 132 kV line-1 | 2020-05-11 22:20 | 2020-05-12 00:08 | 1:48 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2020-05-13 15:30 | 2020-05-13 15:55 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Aminbazar-Manikganj P.P 132 kV line-1 | 2020-05-13 15:49 | 2020-05-13 16:18 | 0:29 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line | 2020-05-13 21:38 | 2020-05-13 22:18 | 0:40 | T | Tripped showing General trip | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kadda 132 kV line-2 | 2020-05-14 19:14 | 2020-05-14 19:32 | 0:18 | T | Tripped showing dist.67N.AR block relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 & 2 | 2020-05-15 15:21 | 2020-05-15 15:49 | 0:28 | E/O | Due to bursting of L/A | 107 | 49.9333 | Power interruption
| Kaliakoir-Tangail 132 kV line-1 | 2020-05-15 15:21 | 2020-05-15 15:47 | 0:26 | T | Tripped showing dist.A/R block relay | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-2 | 2020-05-15 15:21 | 2020-05-15 15:46 | 0:25 | T |  | 0 | 0 | No interruption
Amibazar | Amibazar-Savar 132 k line-1 | 2020-05-20 17:41 | 2020-05-20 17:54 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Amibazar-Savar 132 k line-2 | 2020-05-20 17:41 | 2020-05-20 18:04 | 0:23 | T |  | 0 | 0 | No interruption
| Amibazar-Manikganj Power line-2 | 2020-05-21 01:23 | 2020-05-21 01:40 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-05-21 19:56 | 2020-05-22 00:02 | 4:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-1 | 2020-05-26 08:26 | 2020-05-26 14:22 | 5:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV line-2 | 2020-05-26 08:26 | 2020-05-26 08:50 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-RPCL 132 kV line-2 | 2020-05-26 08:26 | 2020-05-26 08:45 | 0:19 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-05-26 21:22 | 2020-05-27 11:05 | 13:43 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-1 | 2020-05-26 22:32 | 2020-05-27 01:36 | 3:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Kaliakoir-Tangail 132 kV line-2 | 2020-05-26 22:32 | 2020-05-27 02:37 | 4:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-2 | 2020-05-27 02:14 | 2020-05-27 03:10 | 0:56 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-05-27 00:36 | 2020-05-27 01:25 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-2 | 2020-05-27 02:23 | 2020-05-27 05:10 | 2:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-1 | 2020-05-27 10:20 | 2020-05-27 11:34 | 1:14 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kadda | Kadda-Rajendrapur 132 kV line-1 | 2020-05-30 06:25 | 2020-05-30 06:59 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2020-05-30 03:45 | 2020-05-30 10:50 | 7:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 54:32 |  | Unserved Energy: |  | 49.9333
Dhaka (South) Grid Circle :
Shyampur(N) | Shyampur(N)-Shyampur (O) 132 kV line-1 | 2020-05-05 11:29 | 2020-05-05 11:54 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line-1 | 2020-05-05 15:29 | 2020-05-05 15:34 | 0:05 | T | Tripped showing auto reclosing lock & E/F. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-1 | 2020-05-05 18:31 | 2020-05-05 19:47 | 1:16 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ghorashal-Bhulta 230 kV line-2 | 2020-05-05 18:31 | 2020-05-05 22:45 | 4:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV line | 2020-05-08 23:55 | 2020-05-09 00:14 | 0:19 | T | Tripped showing dist. relay | 72 | 22.8 | Power interruption
Meghnaghat | Meghnaghat-Shyampur 230 k line-2 | 2020-05-11 05:17 | 2020-05-11 07:53 | 2:36 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2020-05-13 16:14 | 2020-05-13 17:16 | 1:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ghorashal-Bhulta 230 kV line-2 | 2020-05-15 15:43 | 2020-05-15 23:52 | 8:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV line-4 | 2020-05-15 15:42 | 2020-05-15 17:08 | 1:26 | T | Tripped showing SOFT .AR block relay | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV line | 2020-05-15 15:40 | 2020-05-15 17:08 | 1:28 | T | Tripped showing dist. relay | 32 | 46.9333 | Power interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2020-05-20 11:24 | 2020-05-20 11:42 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2020-05-20 17:20 | 2020-05-20 17:47 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV line-1 | 2020-05-20 20:06 | 2020-05-20 20:24 | 0:18 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2020-05-27 02:15 | 2020-05-27 02:34 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 k line-2 | 2020-05-27 02:45 | 2020-05-27 02:57 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Meghnaghat-Cumilla(N) 230 k line-2 | 2020-05-27 03:00 | 2020-05-27 14:26 | 11:26 | T | Tripped showing SOTF dist.(Z1) relay | 0 | 0 | No interruption
Narshingdi | Narshingdi-B.baria 132 kV line-2 | 2020-05-30 07:15 | 2020-05-30 07:36 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 k line-2 | 2020-05-31 14:30 | 2020-05-31 21:15 | 6:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 41:06 |  | Unserved Energy: |  | 69.7333
Page: 2/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Chittagong Grid Circle :
Khulshi | Khulshi-Haishahar 132 kV line-1 | 2020-05-06 06:36 | 2020-05-06 06:55 | 0:19 | T | Tripped showing dist.C-phase relay | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV line | 2020-05-06 09:21 | 2020-05-06 09:38 | 0:17 | T | Due to insulator breaking at R-phase | 520 | 147.3333 | Power interruption
| Hathazari-Baraulia 132 kV line-1 &2 | 2020-05-06 09:21 | 2020-05-06 09:38 | 0:17 | T
| Hathazari-Kaptai 132 kV line-1 &2 | 2020-05-06 09:21 | 2020-05-06 09:40 | 0:19 | T
| Hathazari-Madunaghat 132 kV line | 2020-05-06 09:21 | 2020-05-06 09:41 | 0:20 | T
| Hathazari-Baraulia 132 kV line-1 &2 | 2020-05-06 09:21 | 2020-05-06 09:41 | 0:20 | T
Juldah | Jiuldah-Shahmirpur 132 kV line-1 | 2020-05-07 23:20 | 2020-05-08 00:27 | 1:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2020-05-12 04:43 | 2020-05-12 05:54 | 1:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-2 | 2020-05-12 12:05 | 2020-05-12 13:40 | 1:35 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV line-2 | 2020-05-17 12:10 | 2020-05-17 12:26 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'xbazar 132 kV line-1 | 2020-05-22 10:44 | 2020-05-22 11:18 | 0:34 | T | Tripped showing dist. relay | 75 | 42.5 | Power interruption
| Dohazari-Cox'xbazar 132 kV line-2 | 2020-05-22 10:44 | 2020-05-22 17:05 | 6:21 | T |  | 0 | 0
| Dohazari-Cox'xbazar 132 kV line-1 | 2020-05-23 20:03 | 2020-05-23 20:58 | 0:55 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2020-05-29 21:02 | 2020-05-29 22:23 | 1:21 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV line-2 | 2020-05-30 12:30 | 2020-05-30 12:58 | 0:28 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-2 | 2020-05-30 12:30 | 2020-05-30 12:48 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai(O) 132 kV line-1 | 2020-05-30 12:30 | 2020-05-30 12:55 | 0:25 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 16:23 |  | Unserved Energy: |  | 189.8333
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ghorashal 230 kV line-1 | 2020-05-05 18:30 | 2020-05-05 19:32 | 1:02 | T | Tripped showing dist.(B-phase) relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2020-05-05 18:33 | 2020-05-06 14:10 | 19:37 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-S.M Nagar 132 kV line-1 | 2020-05-06 22:16 | 2020-05-07 07:07 | 8:51 | T | Due to S.M.Nagar Bus ault | 80 | 112 | Power interruption 22:16 to 23:40
| Cumilla(S)-S.M Nagar 132 kV line-2 | 2020-05-06 22:16 | 2020-05-07 07:44 | 9:28 | T
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-05-10 19:08 | 2020-05-10 20:49 | 1:41 | T | Tripped showing A/R block relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2020-05-13 06:09 | 2020-05-13 06:14 | 0:05 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2020-05-13 16:31 | 2020-05-13 17:43 | 1:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet S/S | Sylhet S/S-Fenchuganj S/S & Fencguganj P/S 132 line | 2020-05-25 04:42 | 2020-05-25 05:37 | 0:55 | T | Tripped showing dist. relay | 26 | 112 | Power interruption
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV line-1 | 2020-05-26 05:25 | 2020-05-27 14:29 | 33:04 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Meghnaghat 230 kV line-2 | 2020-05-26 05:25 | 2020-05-26 05:54 | 0:29 | T |  | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV line-2 | 2020-05-26 21:45 | 2020-05-26 21:51 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-05-27 01:22 | 2020-05-27 05:16 | 3:54 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV line-2 | 2020-05-27 01:34 | 2020-05-27 03:29 | 1:55 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV line-2 | 2020-05-27 03:40 | 2020-05-27 11:30 | 7:50 | T | Tripped showing SOTF. relay | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2020-05-27 01:40 | 2020-05-27 04:27 | 2:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV line-1 | 2020-05-27 02:59 | 2020-05-27 04:09 | 1:10 | T | Tripped showing Dir & O/C relay | 0 | 0 | No interruption
| Cumilla(N)-Chaddagram 132 kV line | 2020-05-27 03:30 | 2020-05-27 04:09 | 0:39 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2020-05-27 12:16 | 2020-05-27 12:32 | 0:16 | T | Tripped showing dist. & E/F relay | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-1 | 2020-05-27 13:32 | 2020-05-27 13:57 | 0:25 | T |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV line-2 | 2020-05-28 02:27 | 2020-05-28 21:28 | 19:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2020-05-28 08:30 | 2020-05-28 17:47 | 9:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-2 | 2020-05-29 15:56 | 2020-05-30 00:45 | 8:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 132:33 |  | Unserved Energy: |  | 224
Khulna Grid Circle :
Bhola | Bhola-Barisal(N) 230 kV line-1 | 2020-05-05 08:45 | 2020-05-05 20:35 | 11:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bhola-Barisal(N) 230 kV line-2 | 2020-05-05 08:45 | 2020-05-05 20:00 | 11:15 | T |  | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV line | 2020-05-07 21:11 | 2020-05-07 21:56 | 0:45 | T | Tripped showing dist. relay | 77 | 57.75 | Power interruption
Mongla | Mongla-Bagerhat 132 kV line | 2020-05-07 20:37 | 2020-05-07 20:49 | 0:12 | T |  | 8 | 1.6 | Power interruption
Page: 3/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal | Barisal-Bhandaria 132 kV line | 2020-05-07 21:03 | 2020-05-07 23:18 | 2:15 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV line-2 | 2020-05-08 06:50 | 2020-05-08 09:18 | 2:28 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2020-05-08 21:35 | 2020-05-08 21:45 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Faridpur-Bheramara 132 kV line-2 | 2020-05-15 00:26 | 2020-05-15 00:46 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-05-16 20:38 | 2020-05-16 22:43 | 2:05 | E/O | Due to red-hot maintenance of Y-phase CT | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-05-19 05:49 | 2020-05-19 06:14 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(New) | Gopalganj(New)-Payra 400 kV line-2 | 2020-05-20 08:10 | 2020-05-21 16:07 | 31:57 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barisal (S) 132 kV line | 2020-05-20 23:00 | 2020-05-21 07:59 | 8:59 | E/O | Due to Voltage flautuation | 0 | 0 | No interruption
| Barisal(S)-Patuakhali 132 kV line | 2020-05-21 00:28 | 2020-05-21 02:58 | 2:30 | E/O |  | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2020-05-22 17:59 | 2020-05-22 21:49 | 3:50 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(New) | Gopalganj(New)-Payra 400 kV line-2 | 2020-05-22 23:39 | 2020-05-22 23:39 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Gopalganj(New)-Payra 400 kV line-2 | 2020-05-23 11:30 | 2020-05-23 16:08 | 4:38 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV line-1 | 2020-05-24 01:34 | 2020-05-24 02:23 | 0:49 | T | Tripped showing dist. relay | 135 | 110.25 | Power interruption
Barisal(N) | Barisal(N)-Bhola 230 kV line-2 | 2020-05-29 09:30 | 2020-05-29 11:08 | 1:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-2 | 2020-05-29 16:44 | 2020-05-29 16:51 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kVline | 2020-05-30 14:54 | 2020-05-30 15:28 | 0:34 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 86:47 |  | Unserved Energy: |  | 169.6
HVDC Grid Circle :
Baghabari | Baghabari-Ishurdi 230 kV line-1 | 2020-05-01 07:33 | 2020-05-01 08:10 | 0:37 | T | Tripped showing dist. relay | 64 | 39.4667 | Power interruption
Bheramara HVDC | Bheramara-Ishurdi 230 kV line-3 | 2020-05-01 07:33 | 2020-05-01 08:47 | 1:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-1 | 2020-05-10 17:37 | 2020-05-10 17:59 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 | 2020-05-10 19:00 | 2020-05-10 19:33 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Pabna | Pabna-Ishurdi 132 kV line | 2020-05-11 07:54 | 2020-05-11 07:54 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ishurdi | Ishurdi-HVDC Bheramara 230 kV line-3 | 2020-05-20 21:52 | 2020-05-20 23:04 | 1:12 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
| Ishurdi-Pabna 132 kV line | 2020-05-20 23:58 | 2020-05-21 00:12 | 0:14 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Jhenidah | Jhenidah-Kustia 132 kV line | 2020-05-22 07:02 | 2020-05-22 07:48 | 0:46 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bharamara | Bharamara-Kustia 132 kV line-1 | 2020-05-22 07:01 | 2020-05-22 07:50 | 0:49 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bharamara-Ishurdi 132 kVline-2 | 2020-05-26 11:31 | 2020-05-26 11:31 | 0:00 | T | Due to MCB trip | 0 | 0 | No interruption
| Bharamara-Bottail 132 kV line-1 | 2020-05-27 08:52 | 2020-05-27 10:03 | 1:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Bharamara-HVDC 230 kV line-1 | 2020-05-28 00:58 | 2020-05-28 11:42 | 10:44 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bheramara-HVDC 230 kV line | 2020-05-30 20:28 | 2020-05-30 21:47 | 1:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 19:01 |  | Unserved Energy: |  | 39.4667
Bogura Grid Circle :
Palashbari | Palashbari-Rangpur Confidence 132 kV line-1 | 2020-05-05 14:42 | 2020-05-05 15:43 | 1:01 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2020-05-05 14:56 | 2020-05-05 16:38 | 1:42 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
| Bogura-Barapukuria 230 kV line-2 | 2020-05-05 14:56 | 2020-05-05 17:37 | 2:41 | T |  | 0 | 0 | No interruption
| Bogura-Sherpur 132 kV line-1 | 2020-05-05 15:01 | 2020-05-05 18:08 | 3:07 | T | Tripped showing dist. (B-phase) relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mahastanghor 132 kV line-1 | 2020-05-06 04:09 | 2020-05-06 04:18 | 0:09 | T | Tripped showing dist.B-phase relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-05-07 16:38 | 2020-05-08 12:24 | 19:46 | T | Tripped showing dist. (A-phase) relay | 0 | 0 | No interruption
Mahastangar | Mahastangar-Palshbari 132 132 kV line-2 | 2020-05-10 14:57 | 2020-05-10 16:05 | 1:08 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-2 | 2020-05-10 22:59 | 2020-05-10 23:05 | 0:06 | T | Tripped showing dist. (C-phase) relay | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-2 | 2020-05-16 18:05 | 2020-05-16 18:28 | 0:23 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-2 | 2020-05-16 20:22 | 2020-05-16 20:27 | 0:05 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-05-16 23:11 | 2020-05-17 00:02 | 0:51 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Bogura-Confidenance Power-132 kV line | 2020-05-16 23:11 | 2020-05-17 00:07 | 0:56 | T | Tripped showing dist relay | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur Confidence 132 kV line | 2020-05-17 00:34 | 2020-05-17 02:25 | 1:51 | T | Tripped showing dist relay | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV line-2 | 2020-05-18 11:53 | 2020-05-18 13:11 | 1:18 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Baghabari-Sirajganj 230 kV line-1 | 2020-05-21 00:01 | 2020-05-21 00:01 | 0:00 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 kV line-2 | 2020-05-21 00:08 | 2020-05-21 00:51 | 0:43 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Rajshahi-Natore 132 kV line-1 | 2020-05-21 04:32 | 2020-05-21 05:03 | 0:31 | T | Tripped showing dist .(C-phase) relay | 0 | 0 | No interruption
| Rajshahi-NPSI 132 kV line | 2020-05-21 04:32 | 2020-05-21 05:50 | 1:18 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Rajshahi-Natore 132 kV line-1 & 2 | 2020-05-21 21:40 | 2020-05-21 21:55 | 0:15 | E/O | Due to bursting of B-phase L/A | 0 | 0 | No interruption
| Rajshahi-Rajshahi (new) 132 kV line-1 & 2 | 2020-05-21 21:39 | 2020-05-21 22:00 | 0:21 | T | Tripped showing dist.phase relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2020-05-24 23:18 | 2020-05-24 23:52 | 0:34 | T | Tripped showing dist relay | 0 | 0 | No interruption
Page: 4/4 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2020
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Barapukuria | Barapukuria-Rangpur 132 kV line-2 | 2020-05-24 23:18 | 2020-05-24 23:54 | 0:36 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Barapukuria-Bogura 230 kV line-2 | 2020-05-24 23:18 | 2020-05-25 01:12 | 1:54 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Barapukuria-Bogura 230 kV line-1 | 2020-05-24 23:18 | 2020-05-25 10:40 | 11:22 | T |  | 0 | 0 | No interruption
Barapukuria P/S | Barapukuria-Barapukuria S/S 230 kV line-1 | 2020-05-24 23:18 | 2020-05-25 00:58 | 1:40 | T | Tripped showing 87 LR,R-phase relay | 0 | 0 | No interruption
| Barapukuria P/S-Barapukuria 230 kV line-2 | 2020-05-24 01:54 | 2020-05-24 10:18 | 8:24 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2020-05-26 23:04 | 2020-05-26 23:49 | 0:45 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Bogura-Bogura Confidence 132 kV line | 2020-05-26 23:04 | 2020-05-26 23:52 | 0:48 | T | Tripped showing dist relay | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV line | 2020-05-27 04:27 | 2020-05-27 05:05 | 0:38 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 64:53 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Haripur 132 kV line | 2020-05-07 13:25 | 2020-05-07 13:53 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line-2 | 2020-05-08 23:42 | 2020-05-09 00:20 | 0:38 | T |  | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV line | 2020-05-09 00:07 | 2020-05-09 00:10 | 0:03 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line | 2020-05-26 21:22 | 2020-05-26 21:37 | 0:15 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 1:24 |  |  |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 435:40 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:May 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV Transformer-T2 | 2020-05-02 07:54 | 2020-05-02 11:58 | 4:04 | S/O | Due to C/M work | 7 | 28.4667 | Power interruption
Mymensingh | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2020-05-02 08:05 | 2020-05-02 09:27 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Kadda | 33 kV Bus-1 | 2020-05-08 10:14 | 2020-05-08 11:35 | 1:21 | S/O | Due to DS problem | 50 | 67.5 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-05-09 16:52 | 2020-05-09 19:07 | 2:15 | S/O | Due to replacement work | 8 | 18 | Power interruption
Mymensingh | 132/33 kV Transformer-T3 | 2020-05-11 14:03 | 2020-05-11 15:35 | 1:32 | S/O | Due to neutral wire | 40 | 61.3333 | Power interruption
Jamalpur | 132/33 kV Transformer-T4 | 2020-05-13 06:12 | 2020-05-13 09:44 | 3:32 | S/O | Due to high temperature at 33 kV CT | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-05-15 10:13 | 2020-05-15 13:10 | 2:57 | S/O | Due to C/M work | 10 | 29.5 | Power interruption
Savar | 132/33 kV Transformer-T3 | 2020-05-16 09:18 | 2020-05-16 14:30 | 5:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/230 kV Transformer-T1 | 2020-05-17 11:17 | 2020-05-17 13:28 | 2:11 | S/O | Due to replacement work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-T2 | 2020-05-21 13:10 | 2020-05-21 17:37 | 4:27 | S/O | Due to insulator resistance test | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2020-05-21 15:25 | 2020-05-21 16:45 | 1:20 | S/O | Due to tightening nut bult | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2020-05-24 14:40 | 2020-05-24 14:48 | 0:08 | S/O | Due to removing kite | 0 | 0 | No interruption
Kadda | 132/33 kV Transformers-T2 & T4 | 2020-05-28 09:24 | 2020-05-28 10:26 | 1:02 | S/O | Due to maintenance by PBS | 30 | 31 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 | 2020-05-30 07:22 | 2020-05-30 10:22 | 3:00 | S/O | Due to maintenancework | 28 | 84 | Power interruption
|  |  | Total : | 34:23 |  | Unserved Energy: |  | 319.8
Dhaka (South) Grid Circle :
Rampura | 230/132 kV Transformer-T01 | 2020-05-03 13:01 | 2020-05-03 13:25 | 0:24 | S/O | Due to Isolator problem | 0 | 0 | No interruption
|  |  | Total : | 0:24 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Madunaghat | 132/33 kV Transformer-T1 | 2020-05-04 10:44 | 2020-05-04 12:10 | 1:26 | S/O | Due to 33 kV feeder maintenance by PDB | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2020-05-13 11:28 | 2020-05-13 12:10 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132 kV main Bus | 2020-05-14 05:16 | 2020-05-14 07:57 | 2:41 | S/O | Due to C/M work | 62 | 166.3667 | Power interruption
Cox'sbazar | 132/33 kV Transformers-T1 & T2 | 2020-05-28 07:17 | 2020-05-28 08:40 | 1:23 | S/O |  | 40 | 55.3333 | Power interruption
|  |  | Total : | 6:12 |  | Unserved Energy : |  | 221.7
Cumilla Grid Circle :
Sunamganj | 132/33 kV Transformer-T1 | 2020-05-06 01:30 | 2020-05-06 06:47 | 5:17 | S/O | Due to replacement work By 33 kV PBS feeder | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV Transformer-T2 | 2020-05-16 08:51 | 2020-05-16 12:32 | 3:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T2 | 2020-05-16 09:48 | 2020-05-16 14:49 | 5:01 | S/O | Due to 33 kV loop change | 0 | 0 | No interruption
Shahjibazar | 132/33 kV Transformer-T1 | 2020-05-19 09:43 | 2020-05-19 10:52 | 1:09 | S/O | Due to 33 kV incoming loop | 0 | 0 | No interruption
|  |  | Total : | 15:08 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Barisal | 230/132 kV Transformer-T1 | 2020-05-09 09:11 | 2020-05-09 20:02 | 10:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 33 kV full Bus | 2020-05-09 12:03 | 2020-05-09 12:45 | 0:42 | S/O | Due to PT fuse changing | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 with 33 kV Bus | 2020-05-16 09:39 | 2020-05-16 10:02 | 0:23 | S/O | Due to measurement of bus clamp | 20 | 7.6667 | Power interruption
Khulna(S) | 132 kV Bus | 2020-05-26 07:45 | 2020-05-26 07:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2020-05-28 10:26 | 2020-05-28 12:04 | 1:38 | S/O | Due to installation work | 30 | 49 | Power interruption
|  |  | Total : | 13:34 |  | Unserved Energy : |  | 56.6667
HVDC Grid Circle :
Purbasadipur | 132/33 kV Transformer-T1 | 2020-05-02 10:16 | 2020-05-02 13:30 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | 132/33 kV Transformer-T1 | 2020-05-02 05:24 | 2020-05-02 05:24 | 0:00 | S/O | Due to maintenance work by PBS | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T1 | 2020-05-19 05:36 | 2020-05-19 11:41 | 6:05 | S/O | Due to Bus extension work | 30 | 182.5 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2020-05-20 21:50 | 2020-05-23 00:48 | 50:58 | S/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Ishurdi | 230/132 kV Transformer-T2 |  | 2020-05-21 14:35 |  |  | After maintenance work | 0 | 0 | No interruption
Jessore | 132/33 kV Transformers-T1 & T2 | 2020-05-23 15:46 | 2020-05-23 16:41 | 0:55 | S/O | Due to 33 PBS work | 0 | 0 | No interruption
|  |  | Total : | 61:12 |  | Unserved Energy : |  | 182.5
Page: 2/2 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:May 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Purbasadipur | 132/33 kV Transformer-T2 | 2020-05-11 00:40 | 2020-05-11 02:12 | 1:32 | S/O | Due to DS connecting | 0 | 0 | No interruption
| 132/33 kV Transformers-T1 & T3 | 2020-05-12 00:44 | 2020-05-12 01:34 | 0:50 | S/O |  | 82 | 68.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2020-05-15 09:22 | 2020-05-15 12:15 | 2:53 | S/O | Due to C/M work | 15 | 43.25 | Power interruption
Rajshahi | 132/33 kV Transformer-T3 | 2020-05-19 10:08 | 2020-05-19 11:13 | 1:05 | S/O | Due to C/M work | 12 | 13 | Power interruption
| 132/33 kV Transformer-T3 | 2020-05-27 09:35 | 2020-05-27 11:58 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2020-05-28 09:23 | 2020-05-28 19:59 | 10:36 | S/O | Due to install relay at 132 kV side | 0 | 0 | No interruption
|  |  | Total : | 19:19 |  | Unserved Energy : |  | 124.5833
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 150:12 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2020-05-07 08:12 | 2020-05-07 12:53 | 4:41 | S/O | Due to maintenance work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2020-05-09 06:55 | 2020-05-09 12:46 | 5:51 | S/O | Due to changing work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2020-05-10 09:08 | 2020-05-10 13:05 | 3:57 | S/O | Due to replacement work | 0 | 0 | No interruption
Amibazar | Amibazar-Mirpur 132 kV line-1 &2 | 2020-05-14 06:32 | 2020-05-14 06:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV line | 2020-05-14 17:09 | 2020-05-14 18:18 | 1:09 | S/O | Due to maintenance work | 0 | 0 | No interruption
Amibazar | Amibazar-Mirpur 132 kV line-1 | 2020-05-15 06:04 | 2020-05-15 21:18 | 15:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| Amibazar-Mirpur 132 kV line-2 | 2020-05-15 06:04 | 2020-05-15 21:17 | 15:13 | S/O
| Amibazar-Mirpur 132 kV line-1 | 2020-05-16 06:27 | 2020-05-16 22:35 | 16:08 | S/O | Due to SOTF maintenance | 0 | 0 | No interruption
| Amibazar-Mirpur 132 kV line-2 | 2020-05-16 06:28 | 2020-05-16 22:35 | 16:07 | S/O |  | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2020-05-16 06:05 | 2020-05-16 07:36 | 1:31 | S/O | Due to replacement work | 0 | 0 | No interruption
| Kaliakoir-Tongi 230 kV line-2 | 2020-05-16 08:17 | 2020-05-16 10:57 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Amibazar | Amibazar-Kallyanpur 132 kV line-2 | 2020-05-18 12:58 | 2020-05-18 22:40 | 9:42 | S/O | Due to replacement work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 & 2 |  | 2020-05-19 20:25 |  | S/O | After maintenance work | 0 | 0 | No interruption
Amibazar | Amibazar-Mirpur 132 kV line-1 & 2 | 2020-05-21 07:22 | 2020-05-22 02:48 | 19:26 | S/O | Due to project work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2020-05-21 12:45 | 2020-05-21 15:05 | 2:20 | S/O | Due to winding temperature high | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-05-23 11:50 | 2020-05-23 14:29 | 2:39 | S/O | Due to removing kite | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV line-1 | 2020-05-27 12:36 | 2020-05-27 13:06 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh-Jamalpur 132 kV line-1 | 2020-05-29 11:19 | 2020-05-29 12:42 | 1:23 | S/O | Due to removing kite | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-2 | 2020-05-31 11:14 | 2020-05-31 13:50 | 2:36 | S/O | Due to removing kite | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2020-05-31 13:57 | 2020-05-31 15:27 | 1:30 | S/O | Due to kite swinging in conductor | 0 | 0 | No interruption
|  |  | Total : | 117:56 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Shyampur 230 kV line | 2020-05-04 07:40 | 2020-05-04 10:07 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2020-05-07 11:53 | 2020-05-07 15:16 | 3:23 | S/O | Due to S/S work | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV line-1 | 2020-05-08 00:25 | 2020-05-08 09:29 | 9:04 | S/O | Due to remove GI wire on the line | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2020-05-12 05:26 | 2020-05-12 05:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line | 2020-05-15 21:39 | 2020-05-15 22:00 | 0:21 | S/O | Due to mad climbing. | 0 | 0 | No interruption
Sonargaon | Sonargaon-Orion P/S 132 kV line | 2020-05-16 08:30 | 2020-05-16 15:32 | 7:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Patulla(new) 132 kV line |  | 2020-05-20 12:17 |  |  | New connection | 0 | 0 | No interruption
Shyampur | Shyampur-Patulla(new) 132 kV line |  | 2020-05-20 13:04 |  |  |  | 0 | 0 | No interruption
Fatulla(new) | Fatulla(new) 132 Bus-1 & 2 |  | 2020-05-20 12:27 |  |  |  | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 |  | 2020-05-27 23:25 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Ghorashal-Ishurdi 230 kV line-2 | 2020-05-27 07:24 | 2020-05-27 11:11 | 3:47 | S/O | Due to OPGW work | 0 | 0 | No interruption
|  |  | Total : | 26:04 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Abulkhair | Abulkhair -Hathazari 230 kV line | 2020-05-19 08:51 | 2020-05-19 09:20 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari S/S | Dohazari S/S-Dohazari P/P 132 kV line-1 | 2020-05-30 10:48 | 2020-05-30 11:51 | 1:03 | S/O | Due to temparature high | 0 | 0 | No interruption
|  |  | Total : | 1:32 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2020-05-05 21:13 | 2020-05-05 22:36 | 1:23 | S/O | Due to PT change | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV line-1 | 2020-05-06 11:19 | 2020-05-06 11:19 | 0:00 | S/O | Due to PT replacement wprk | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV line-1 | 2020-05-14 18:55 | 2020-05-07 11:19 |  | S/O | Due to replacement work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/P 132 kV line | 2020-05-30 11:44 | 2020-05-30 12:35 | 0:51 | S/O | Due to replacement work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2020-05-31 11:42 | 2020-05-31 16:21 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 6:53 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2020
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Gopalganj(N) | Gopalganj(N)- Madaripur 132 kV line-1 | 2020-05-08 09:40 | 2020-05-08 12:38 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Bheramara HVDC 230 kV line-1 | 2020-05-20 19:00 | 2020-05-20 23:56 | 4:56 | S/O | Due to high Voltage | 0 | 0 | No interruption
| Khulna(S)-Khulna© 132 kV line-1 | 2020-05-25 12:47 | 2020-05-25 12:55 | 0:08 | S/O | Due to protection work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2020-05-26 18:02 | 2020-05-26 19:04 | 1:02 | S/O | Due to removing kite | 0 | 0 | No interruption
|  |  | Total : | 9:04 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Shahjadpur | Shahjadpur-Baghabari 132 kV line-1 | 2020-05-01 16:01 | 2020-05-01 16:01 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2020-05-06 14:24 | 2020-05-06 15:26 | 1:02 | S/O | Due to kite removal | 0 | 0 | No interruption
| Bheramara HVDC-Pole -1 | 2020-05-20 21:52 | 2020-05-21 10:16 | 12:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Bheramara HVDC-Pole -2 | 2020-05-20 21:52 | 2020-05-21 17:31 | 19:39 | S/O |  | 0 | 0 | No interruption
Bottail | Bottail-Bheramara 132 kV line-1 |  | 2020-05-23 01:50 |  |  | After maintenance work | 0 | 0 | No interruption
| Bottail-Jhenidah 132 k line-2 |  | 2020-05-23 01:53 |  |  | After maintenance work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV line-2 | 2020-05-26 10:28 | 2020-05-26 11:05 | 0:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Jessore | Jessore-Noapara 132 kV line-2 | 2020-05-27 11:44 | 2020-05-27 12:19 | 0:35 | S/O | Due to kite removal | 0 | 0 | No interruption
|  |  | Total : | 34:17 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Naogaon | Naogaon-Santahar P/S 132 kV line | 2020-05-04 11:00 | 2020-05-04 12:20 | 1:20 | S/O | Due to P/P work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastangar 132 kV line-1 | 2020-05-04 14:24 | 2020-05-04 16:20 | 1:56 | S/O | Due to maintenance work | 0 | 0 | No interruption
Bhola | Bhola-Barishal (N) 230 kV line-2 | 2020-05-06 07:32 | 2020-05-06 07:32 | 0:00 | S/O | Due to control voltage | 0 | 0 | No interruption
Madaripur | Madaripur-Barishal (N) 230 kV line-2 | 2020-05-06 07:32 | 2020-05-06 12:14 | 4:42 | S/O |  | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV line | 2020-05-18 10:32 | 2020-05-18 16:40 | 6:08 | S/O | Due to removing Jumper | 0 | 0 | No interruption
| Baghabari-Ishurdi 132 kV line-4 |  | 2020-05-21 14:46 |  |  | After maintenance work | 0 | 0 | No interruption
| Baghabari-Sirajganj 230 kV line-1 |  | 2020-05-21 16:20 |  |  | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 14:06 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 209:52 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May' 2020
| Area | Previous Month (April 2020) |  |  |  | Current Month (May2020)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30 | 8 | 23 | 61 | 27 | 10 | 33 | 70
2 | Dhaka (South) Grid Circle. | 27 | 3 | 17 | 47 | 22 | 1 | 9 | 32
3 | Chattogram Grid Circle. | 20 | 2 | 14 | 36 | 19 | 5 | 6 | 30
4 | Cumilla Grid Circle. | 35 | 10 | 11 | 56 | 24 | 7 | 9 | 40
5 | Khulna Grid Circle. | 29 | 7 | 15 | 51 | 23 | 14 | 9 | 46
6 | Bheramara HVDC Grid Circle | 5 | 4 | 7 | 16 | 12 | 5 | 11 | 28
7 | Bogura Grid Circle. | 18 | 24 | 12 | 54 | 31 | 24 | 11 | 66
8 | Others | 1 | 1 | 1 | 3 | 6 |  |  | 6
9 | Total | 165 | 59 | 100 | 324 | 164 | 66 | 88 | 318
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May' 2020
| Area | Previous Month (April 2020) |  |  |  | Current Month (May 2020)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 436.3833 | 118.6667 | 72.3333 | 627.3833 | 14 | 57.6 | 319.8 | 391.4
2 | Dhaka (South) Grid Circle. | 46.5333 | 0 | 0 | 46.5333 | 327.93 | 0 | 0 | 327.93
3 | Chattogram Grid Circle. | 443.15 | 74.8 | 6.67 | 524.62 | 492.96 | 0 | 221.7 | 714.66
4 | Cumilla Grid Circle. | 63.8 | 139.43 | 79.9 | 283.13 | 250.4 | 12.5 | 0 | 262.9
5 | Khulna Grid Circle. | 371.27 | 76.07 | 144.15 | 591.49 | 275.6 | 72.5 | 56.67 | 404.77
6 | Bheramara HVDC Grid Circle | 9.6 | 55.33 |  | 64.93 | 39.47 | 163.33 | 182.5 | 385.3
7 | Bogura Grid Circle. | 10.67 | 236.58 | 181.3 | 428.55 | 23.75 | 529.75 | 124.58 | 678.08
8 | Others |  | 46.67 | 35 | 81.67 | 30 |  |  | 30
9 | Total | 1381.4067 | 747.5467 | 519.3533 | 2648.3067 | 1454.11 | 835.68 | 905.25 | 3195.04
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May' 2020
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 3 | 7 | 10 | 2 |  | 8 | 341.47
2 | Dhaka (South) | 5031.6 | 3 |  | 3 | 1 | 1 | 1 | 258.2
3 | Chattogram | 2042 | 3 | 2 | 5 | 1 |  | 4 | 524.83
4 | Khulna | 2434 | 8 | 2 | 10 | 5 | 2 | 3 | 235.17
5 | Bheramara (HVDC) | 2423.3 | 2 | 1 | 3 |  |  | 3 | 345.83
6 | Bogura | 3145.6 | 10 | 3 | 13 | 2 | 5 | 6 | 678.08
7 | Cumilla | 2981 | 2 |  | 2 | 1 |  | 1 | 38.9
8 | Others | - | 1 |  | 1 | 1 |  |  | 30
| Total | 23365.5 | [6 empty] | 2452.48
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.95%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May' 2020
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 |  | 1 | 1 |  |  | 49.93
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | 1 |  | 1 | 69.73
3 | Chattogram | 917 | 20+9(Partial) | 2 | - | 2 | 1 | 1 | - | 189.83
4 | Khulna | 1238.4 | 21 | 2 |  | 2 |  | 2 |  | 169.6
5 | Bheramara (HVDC) | 598.7 |  | 1 |  | 1 | 1 | - |  | 39.47
6 | Bogura | 1803.3 | 38 | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | 17 | 2 |  | 2 |  | 1 | 1 | 224
7 | Others | - |  | - | - | - | - | - | - | -
| Total | 8862.13 | 174 | [6 empty] | 742.56
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.83%
2 | Dhaka (South) | 99.85%
3 | Chattogram | 99.88%
4 | Khulna | 99.71%
5 | Bheramara (HVDC) | 99.92% | [7 empty] | Executive Engineer
6 | Bogura | 100% | [7 empty] | Information Management Division
7 | Cumilla | 99.43% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May' 2020
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2020-05-18 | 19 | - | 3 | 2hour 23 min | 1 | 28 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month:May' 2020
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 3 | 0:15 | 35 | 8.75 | Due to tripping of 132/33 kV Transformer T3
|  | 0:09 | 35 | 5.25 | Due to tripping of 132/33 kV Transformer T3
|  | 0:46 | 10 | 7.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Kaliakoir | 1 | 0:28 | 107 | 49.9333 | Due to tripping of Kaliakoir -Kabirpur 132 kV line-1 & 2
Manikganj | 1 | 4:04 | 7 | 28.4667 | Due to S/D of132/33 kV Transformer-T2
Kadda | 1 | 1:21 | 50 | 67.5 | Due to S/D of 33 kV Bus-1
Jamalpur | 1 | 2:15 | 8 | 18 | Due to S/D of132/33 kV Transformer-T4
Mymensingh | 1 | 1:32 | 40 | 61.3333 | Due to S/D of132/33 kV Transformer-T3
Kishoreganj | 1 | 2:57 | 10 | 29.5 | Due to S/D of132/33 kV Transformer-T2
Kadda | 1 | 1:02 | 30 | 31 | Due to S/D of132/33 kV Transformer-T2 & T4
Kabirpur | 1 | 3:00 | 28 | 84 | Due to S/D of132/33 kV Transformer-T3
Hasnabad | 1 | 0:34 | 78 | 44.2 | Due to tripping of 33 kV CB
Gulshan | 1 | 4:36 | 44 | 202.4 | Due to tripping of 132/33 kV Transformer-T2
Siddhirganj | 1 | 0:12 | 58 | 11.6 | Due to tripping of 132/33 kV Transformers-T1 & T2
Haripur | 2 | 0:19 | 72 | 22.8 | Due to tripping of Haripur-Bhulta 132 kV line
|  | 1:28 | 32 | 46.9333 | Due to tripping of Haripur-Narsinghdi 132 kV line
Ullon | 1 | 0:30 | 60 | 30 | Due to tripping of 132/33 kV Transformer-T2
Dohazari | 1 | 4:00 | 52 | 208 | Due to tripping of 132/33 kV Transformer-T1
Halishahar | 1 | 1:17 | 65 | 83.4167 | Due to tripping of 132/33 kV Transformer-T1 & T3
Madunaghat |  | 0:19 | 37 | 11.7167 | Due to tripping of 132/33 kV Transformers-T1 ,& T3
Hathazari | 1 | 0:17 | 520 | 147.3333 | Due to insulator breaking at R-phase at Hathazari end
Dohazari | 1 | 0:34 | 75 | 42.5 | Due to tripping of Dohazari-Cox'sbazar 132 kV line-1 & 2
Khulshi | 1 | 2:41 | 62 | 166.3667 | Due to S/D of kV main Bus
Cox'sbazar | 1 | 1:23 | 40 | 55.3333 | Due to S/D of 132/33 kV Transformers-T1 & T2
Ramganj | 1 | 0:18 | 88 | 26.4 | Due to trippnig of 132/33 kV Transformers-T1 & T2
Sreemongal | 1 | 1:15 | 10 | 12.5 | Due to red-hot maintenance of 132/33 kV Transformer T1
Cumilla(S) | 1 | 8:51 | 80 | 112 | Due to trippnig of Cumilla(S)-SM.Nagar 132 kV line-1 & 2
Sylhet S/S | 1 | 0:55 | 26 | 112 | Due to tripping of sylhet S/S-Sylhet P/S 132 kV line
Gopalganj | 1 | 0:19 | 35 | 11.0833 | Due to trippnig of 132/33 kV Transformers-T1 & T2
Barisal |  | 0:59 | 20 | 19.6667 | Due to red-hot maintenance of 132/33 kV Transformer T2
Barisal(S) | 1 | 1:24 | 30 | 42
Madaripur | 1 | 1:05 | 10 | 10.8333 | Due to red-hot maintenance of 132/33 kV Transformer T3
Faridpur | 1 | 0:05 | 55 | 4.5833 | Due to tripping of 132/33 kV Transformers T1 & T2
| ! | 0:53 | 70 | 61.8333 | Due to trippnig of 132/33 kV Transformer-T1
|  | 0:11 | 90 | 16.5 | Due to tripping of 132/33 kV Transformers T1 & T2
Gopalganj | 1 | 0:18 | 40 | 12 | Due to tripping of 132/33 kV Transformers T1 & T2
Barisal | 1 | 0:45 | 77 | 57.75 | Due to tripping of Barisal-Patuakhali 132 kV line
Mongla |  | 0:12 | 8 | 1.6 | Due to tripping of Mongla-Bagerhat 132 kV line
Faridpur | 3 | 0:49 | 135 | 110.25 | Due to tripping of Faridpur-Bheramara 132 kV line-1
|  | 0:23 | 20 | 7.6667 | Due to S/D of 132/33 kV Transformer T1
|  | 1:38 | 30 | 49
Ishurdi | 1 | 1:10 | 5 | 5.8333 | Due to red-hot maintenance of 132/33 kV Transformer T2
Bottail |  | 3:09 | 50 | 157.5 | Due to Emergency maintenance work
Baghabari | 1 | 0:37 | 64 | 39.4667 | Due to tripping of Baghabari-Ishurdi 230 kV line
Bottail | 1 | 6:05 | 30 | 182.5 | Due to S/D of 132/33 kV Transformer T1
Naogaon | 2 | 0:10 | 20 | 3.3333 | Due to tripping of 132/33 kV Transformer T3
|  | 0:55 | 9 | 8.25 | Due to red-hot maintenance of 132/33 kV Transformer T1
Saidpur | 1 | 0:55 | 14 | 12.8333
Rangpur | 1 | 1:05 | 30 | 32.5 | Due to red-hot maintenance of 33 kV Bus-2
Purbasadipur | 1 | 0:40 | 15 | 10 | Due to red-hot maintenance of 132/33 kV Transformer T1
Saidpur | 1 | 2:05 | 20 | 41.6667 | Due to red-hot maintenance of 33 kV Bus
Purbasadipur | 1 | 2:36 | 110 | 286 | Due to red-hot maintenance of 132 kV Bus
Saidpur | 1 | 1:52 | 20 | 37.3333 | Due to red-hot maintenance of 33 kV Bus
Rangpur | 1 | 1:14 | 65 | 80.1667 | Due to red-hot maintenance of 33 kV Bus
Pabna | 1 | 0:35 | 35 | 20.4167 | Due to trippnig of 132/33 kV Transformer-T2
Rajshahi | 1 | 0:28 | 45 | 21 | Due to red-hot maintenance of 132/33 kV Transformer T3
Purbasadipur | 2 | 0:50 | 82 | 68.3333 | Due to S/D of 132/33 kV TransformersT1 & T3
|  | 2:53 | 15 | 43.25 | Due to S/D of 132/33 kV TransformerT2
Rajshahi | 1 | 1:05 | 12 | 13 | Due to S/D of 132/33 kV TransformerT3
| Total Unserved energy : |  |  | 3195.05 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:May'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 126 | 11 | 2020-05-03 | 15:00
2 | Munsiganj | 126 | 16 | 2020-05-03 | 21:00
3 | Sonargaon | 76 | 13 | 2020-05-03 | 2:00
4 | Shyampur | 176 | 18 | 2020-05-03 | 0.41667
5 | Bhulta | 146 | 18 | 2020-05-03 | 0:00
6 | Madanganj | 69 | 11 | 2020-05-03 | 22:00
7 | Shitalakhya | 106 | 19 | 2020-05-03 | 12:00
8 | Rahim steel | 28 | 11 | 2020-05-03 | 14:00
9 | Matuail | 85 | 18 | 2020-05-03 | 0.41667
10 | Ghorasal | 79 | 18 | 2020-05-03 | 0:00
11 | Narsingdi | 149 | 19 | 2020-05-03 | 21:00
12 | Haripur (SBU) | 87 | 12 | 2020-05-03 | 15:00
13 | Ullon | 63 | 19 | 2020-05-03 | 0.16667
14 | Hasnabad | 205 | 18 | 2020-05-03 | 0.91667
15 | Magbazar | 99 | 17 | 2020-05-03 | 14:00
16 | Maniknagar | 137 | 26 | 2020-05-03 | 0.25
17 | Bangabhaban | 30 | 31 | 2020-05-03 | 0.5
18 | Narinda | 84 | 17 | 2020-05-03 | 0.54167
19 | Dhanmondi | 116 | 17 | 2020-05-03 | 0.54167
20 | Lalbag | 73 | 13 | 2020-05-03 | 14:00
21 | Madartek | 70 | 18 | 2020-05-03 | 21:00
22 | Dhaka University | - | - | - | -
23 | Mirpur | 98 | 17 | 2020-05-03 | 0.875
24 | Kalyanpur | 87 | 16 | 2020-05-03 | 21:00
25 | Gulshan | 110 | 19 | 2020-05-03 | 13:00
26 | Uttara | 78 | 17 | 2020-05-03 | 0.79167
27 | Uttara(new) | 22 | 13 | 2020-05-03 | 0.625
28 | Kamrangirchar | 72 | 17 | 2020-05-03 | 17:00
29 | Savar | 124 | 11 | 2020-05-03 | 18:00
30 | Bhasantec | 136 | 17 | 2020-05-03 | 21:00
31 | Agargaon | 60 | 17 | 2020-05-03 | 0.875
32 | Satmosjid | 97 | 17 | 2020-05-03 | 0.875
33 | Tongi | 128 | 9 | 2020-05-03 | 15:00
34 | Kabirpur | 207 | 12 | 2020-05-03 | 0.58333
35 | Basundhara | 120 | 18 | 2020-05-03 | 21:00
36 | Manikganj | 82 | 4 | 2020-05-03 | 19:30
37 | Joydevpur | 168 | 16 | 2020-05-03 | 14:00
38 | New Tongi | 96 | 18 | 2020-05-03 | 11:00
39 | Kodda | 193 | 11 | 2020-05-03 | 14:00
40 | Dhamrai | 96 | 17 | 2020-05-03 | 20:00
41 | Rajendrapur | 88 | 17 | 2020-05-03 | 21:00
42 | Valuka | 94 | 16 | 2020-05-03 | 0.91667
43 | Tangail | 213 | 16 | 2020-05-03 | 21:00
44 | Mymensing | 234 | 19 | 2020-05-03 | 21:00
45 | Kishorganj | 144 | 17 | 2020-05-03 | 21:00
46 | Netrokona | 120 | 19 | 2020-05-03 | 21:00
47 | Jamalpur | 146 | 19 | 2020-05-03 | 22:00
48 | Sherpur | 120 | 19 | 2020-05-03 | 22:00
49 | Srimongal | 49 | 11 | 2020-05-03 | 0.8125
50 | Shahjibazar | 118 | 18 | 2020-05-03 | 21:00
51 | Fenchuganj | 45 | 19 | 2020-05-03 | 21:00
52 | Kulawara | 47 | 11 | 2020-05-03 | 19:30
53 | Sylhet | 122 | 12 | 2020-05-03 | 21:00
54 | Chatak | 33 | 17 | 2020-05-03 | 21:00
55 | Sunamganj | 58 | 23 | 2020-05-03 | 20:00
56 | Bianibazar | 67 | 17 | 2020-05-03 | 21:00
57 | Cumilla (S) | 190 | 17 | 2020-05-03 | 0.875
58 | Cumilla(N) | 145 | 9 | 2020-05-03 | 23:00
59 | Chandpur | 107 | 22 | 2020-05-03 | 24:00
60 | Feni | 129 | 18 | 2020-05-03 | 19:30
61 | Chowmuhani | 189 | 18 | 2020-05-03 | 19:30
62 | Ashuganj | 67 | 18 | 2020-05-03 | 23:00
63 | Daudkandi | 152 | 17 | 2020-05-03 | 0.875
64 | B.Baria | 157 | 23 | 2020-05-03 | 21:00
65 | Ramganj | 124 | 17 | 2020-05-03 | 21:00
66 | Chaddagram | 45 | 15 | 2020-05-03 | 13:00
67 | PHP | 11 | 3 | 2020-05-03 | 14:00
68 | Madanhat | 62 | 16 | 2020-05-03 | 14:00
69 | Hathazari | 102 | 16 | 2020-05-03 | 0.79167
70 | Khulshi | 196 | 11 | 2020-05-03 | 14:00
71 | Halishahar | 147 | 15 | 2020-05-03 | 8:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:May'2020
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
72 | Baraulia | 161 | 13 | 2020-05-03 | 0:00
73 | Sikalbaha | 29 | 22 | 2020-05-03 | 21:00
74 | Dohazari | 104 | 17 | 2020-05-03 | 22:00
75 | Cox'sbazar | 100 | 18 | 2020-05-03 | 20:00
76 | Chandraghona | 32 | 5 | 2020-05-03 | 14:00
77 | Kaptai | 4.3 | 17 | 2020-05-03 | 19:00
78 | A. Khaer Stl. | 23 | 23 | 2020-05-03 | 10:00
79 | Bakulia | 102 | 14 | 2020-05-03 | 0.33333
80 | Julda | 20 | 5 | 2020-05-03 | 0.041667
81 | TK chemical | 19 | 2 | 2020-05-03 | 21:00
82 | Modern Steel | 16 | 11 | 2020-05-03 | 4:00
83 | Shahmirpur | 31.5 | 9 | 2020-05-03 | 22:00
84 | Khagrachhari | 26 | 12 | 2020-05-03 | 19:00
85 | Matarbari | 35.5 | 18 | 2020-05-03 | 21:00
86 | Baroiar Hat | 42 | 22 | 2020-05-03 | 19:00
87 | Rangamati | 12 | 11 | 2020-05-03 | 0.8125
88 | Abul Khair 230 | 153 | 12 | 2020-05-03 | 15:00
89 | BSRM | 113 | 9 | 2020-05-03 | 2:00
90 | GPH Ispat | 73 | 31 | 2020-05-03 | 11:00
91 | Goalpara | 32 | 13 | 2020-05-03 | 21:00
92 | Central s/s | 99 | 10 | 2020-05-03 | 21:00
93 | Noapara | 71 | 17 | 2020-05-03 | 0.8125
94 | Jashore | 128 | 10 | 2020-05-03 | 21:00
95 | Benapol | 46 | 10 | 2020-05-03 | 20:00
96 | Jhenidah | 114 | 12 | 2020-05-03 | 21:00
97 | Bottail | 132 | 17 | 2020-05-03 | 21:00
98 | G.K Project | 62 | 16 | 2020-05-03 | 21:00
99 | Faridpur | 194 | 17 | 2020-05-03 | 21:00
100 | Madaripur | 108 | 17 | 2020-05-03 | 22:00
101 | Sariatpur | 74 | 18 | 2020-05-03 | 21:00
102 | Gopalganj | 108 | 17 | 2020-05-03 | 21:00
103 | Bagerhat | 102 | 18 | 2020-05-03 | 21:00
104 | Mongla | 60 | 19 | 2020-05-03 | 14:00
105 | Satkhira | 118 | 17 | 2020-05-03 | 22:00
106 | Gallamari | 54 | 13 | 2020-05-03 | 15:00
107 | Magura | 58 | 10 | 2020-05-03 | 21:00
108 | Norail | 42 | 12 | 2020-05-03 | 22:00
109 | Chuadanga | 97 | 14 | 2020-05-03 | 23:00
110 | Barsal(N) | 50 | 18 | 2020-05-03 | 20:00
111 | Barsal(S) | 110 | 17 | 2020-05-03 | 19:30
112 | Patuakhali | 123 | 16 | 2020-05-03 | 22:00
113 | Bhandaria | 61 | 18 | 2020-05-03 | 21:00
114 | Borhan Uddin | 45 | 11 | 2020-05-03 | 21:00
115 | Ishurdi | 68 | 16 | 2020-05-03 | 21:00
116 | Ruppur Paromanobik | 2 | 2 | 2020-05-03 | 0.625
117 | Natore | 128 | 16 | 2020-05-03 | 21:00
118 | Bogura | 161 | 19 | 2020-05-03 | 22:00
119 | Naogaon | 131 | 17 | 2020-05-03 | 21:00
120 | Rajshahi | 158 | 17 | 2020-05-03 | 21:00
121 | Rajshahi New | 12 | 17 | 2020-05-03 | 0.875
122 | C.Nawabganj | 77 | 19 | 2020-05-03 | 22:00
123 | Amnura | 46 | 17 | 2020-05-03 | 21:00
124 | Pabna | 121 | 16 | 2020-05-03 | 21:00
125 | Shahjadpur | 121 | 17 | 2020-05-03 | 20:00
126 | Serajganj | 109 | 17 | 2020-05-03 | 21:00
127 | Niyamatpur | 62 | 19 | 2020-05-03 | 0.95833
128 | Joypurhat | 61 | 16 | 2020-05-03 | 21:00
129 | Sherpur(Bogura) | 50 | 19 | 2020-05-03 | 3:00
130 | Mohastangar | 53 | 31 | 2020-05-03 | 21:00
131 | Rangpur | 147 | 18 | 2020-05-03 | 20:00
132 | Lalmonirhat | 58 | 18 | 2020-05-03 | 21:00
133 | Saidpur | 111 | 18 | 2020-05-03 | 21:00
134 | Purbasadipur | 103 | 18 | 2020-05-03 | 20:00
135 | Thakurgaon | 81 | 18 | 2020-05-03 | 20:00
136 | Palshbari | 123 | 12 | 2020-05-03 | 0.875
137 | Barapukuria | 50 | 18 | 2020-05-03 | 21:00
138 | Panchugar | 46 | 29 | 2020-05-03 | 0.83333
139 | Joldhaka | 28 | 10 | 2020-05-03 | 0.83333
140 | Kurigram | 55 | 10 | 2020-05-03 | 21:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May' 2020
Area | MW | Date | Hour | Remarks
Dhaka | 3656 | 17.05.2020 | 14:00
Chattogram | 1286 | 17.05.2020 | 24:00
Khulna | 1588 | 17.05.2020 | 21:00
Rajshahi | 1284 | 18.05.2020 | 21:00
Cumilla | 1225 | 17.05.2020 | 21:00
Mymensingh | 1010 | 18.05.2020 | 22:00
Sylhet | 519 | 19.05.2020 | 21:00
Barisal | 380 | 18.05.2020 | 21:00
Rangpur | 786 | 18.05.2020 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May'2020
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 408 | 7 | 2020-05-03 | 20:00 | 386 | 25 | 2020-05-03 | 18:30
2 | Bheramara | 400 | 418 | 27 | 2020-05-03 | 21:00 | 385 | 8 | 2020-05-03 | 19:30
3 | Ashuganj(N) | 400 | 408 | 27 | 2020-05-03 | 7:00 | 376 | 10 | 2020-05-03 | 22:00
4 | Payra | 400 | 437 | 22 | 2020-05-03 | 6:00 | 380 | 29 | 2020-05-03 | 12:00
5 | Kaliakoir | 400 | 400 | 27 | 2020-05-03 | 6:00 | 365 | 18 | 2020-05-03 | 9:00
6 | Bhulta | 400 | 404 | 27 | 2020-05-03 | 7:00 | 373 | 11 | 2020-05-03 | 10:00
7 | Gopalganj | 400 | 432 | 22 | 2020-05-03 | 6:00 | 321 | 23 | 2020-05-03 | 14:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 245 | 7 | 2020-05-03 | 19:30 | 230 | 5 | 2020-05-03 | 23:00
2 | Ishurdi | 230 | 245 | 21 | 2020-05-03 | 4:00 | 224 | 4 | 2020-05-03 | 21:00
3 | Ashuganj | 230 | 246 | 14 | 2020-05-03 | 19:30 | 230 | 5 | 2020-05-03 | 16:00
4 | Serajganj | 230 | 240 | 2 | 2020-05-03 | 17:00 | 225 | 16 | 2020-05-03 | 19:30
5 | Baghabari | 230 | 250 | 21 | 2020-05-03 | 4:00 | 230 | 2 | 2020-05-03 | 17:00
6 | Barapukuria | 230 | 243 | 27 | 2020-05-03 | 7:00 | 216 | 25 | 2020-05-03 | 1:00
7 | Bogura | 230 | 248 | 21 | 2020-05-03 | 5:00 | 215 | 15 | 2020-05-03 | 19:30
8 | Khulna South | 230 | 255 | 21 | 2020-05-03 | 5:00 | 206 | 15 | 2020-05-03 | 15:00
9 | Rampura | 230 | 236 | 27 | 2020-05-03 | 7:00 | 219 | 17 | 2020-05-03 | 12:00
10 | Haripur | 230 | 238 | 27 | 2020-05-03 | 7:00 | 219 | 17 | 2020-05-03 | 9:00
11 | Hasnabad | 230 | 240 | 27 | 2020-05-03 | 7:00 | 220 | 17 | 2020-05-03 | 12:00
12 | Shyampur | 230 | 241 | 27 | 2020-05-03 | 7:00 | 216 | 17 | 2020-05-03 | 12:00
13 | Aminbazar | 230 | 242 | 27 | 2020-05-03 | 7:00 | 221 | 13 | 2020-05-03 | 12:00
14 | Tongi | 230 | 235 | 10 | 2020-05-03 | 18:00 | 214 | 17 | 2020-05-03 | 7:00
15 | Comilla (N) | 230 | 240 | 7 | 2020-05-03 | 21:00 | 225 | 17 | 2020-05-03 | 13:00
16 | Hathazari | 230 | 229 | 6 | 2020-05-03 | 10:00 | 213 | 1 | 2020-05-03 | 19:00
17 | Megnaghat | 230 | 246 | 27 | 2020-05-03 | 7:00 | 221 | 17 | 2020-05-03 | 12:00
18 | Fenchuganj | 230 | 248 | 27 | 2020-05-03 | 8:00 | 227 | 19 | 2020-05-03 | 21:00
19 | Siddhirganj | 230 | 240 | 28 | 2020-05-03 | 3:00 | 221 | 17 | 2020-05-03 | 9:00
20 | Maniknagar | 230 | 242 | 27 | 2020-05-03 | 7:00 | 219 | 17 | 2020-05-03 | 10:00
21 | Agargaon | 230 | 243 | 27 | 2020-05-03 | 7:00 | 218 | 17 | 2020-05-03 | 10:00
22 | Barisal | 230 | 258 | 6 | 2020-05-03 | 7:00 | 216 | 23 | 2020-05-03 | 14:00
23 | AKSML | 230 | 229 | 21 | 2020-05-03 | 2:00 | 210 | 9 | 2020-05-03 | 12:00
24 | BSRM | 230 | 229 | 21 | 2020-05-03 | 2:00 | 214 | 11 | 2020-05-03 | 10:00
25 | Bibiyana | 230 | 242 | 1 | 2020-05-03 | 5:00 | 213 | 11 | 2020-05-03 | 9:00
26 | Bhulta | 230 | 241 | 27 | 2020-05-03 | 7:00 | 222 | 17 | 2020-05-03 | 10:00
27 | Ashuganj (S) | 230 | 242 | 21 | 2020-05-03 | 5:00 | 227 | 5 | 2020-05-03 | 16:00
28 | Kaliakoir | 230 | 242 | 7 | 2020-05-03 | 20:00 | 221 | 17 | 2020-05-03 | 9:00
29 | GPH | 230 | 225 | 19 | 2020-05-03 | 18:30 | 211 | 1 | 2020-05-03 | 19:30
132 kV Substation
1 | Siddhirganj | 132 | 138 | 7 | 2020-05-03 | 0.83333 | 126 | 17 | 2020-05-03 | 0.375
2 | Munsiganj | 132 | 140 | 19 | 2020-05-03 | 0.91667 | 125 | 5 | 2020-05-03 | 0.66667
3 | Sonargaon | 132 | 138 | 27 | 2020-05-03 | 0.29167 | 125 | 17 | 2020-05-03 | 0.41667
4 | Shyampur | 132 | 142 | 27 | 2020-05-03 | 0.29167 | 125 | 17 | 2020-05-03 | 0.41667
5 | Bhulta | 132 | 134 | 27 | 2020-05-03 | 0.29167 | 121 | 17 | 2020-05-03 | 0.45833
6 | Madanganj | 132 | 137 | 19 | 2020-05-03 | 1:00 | 124 | 5 | 2020-05-03 | 0.66667
7 | Shitalakhya | 132 | 146 | 27 | 2020-05-03 | 0.29167 | 123 | 17 | 2020-05-03 | 0.375
8 | Rahim Steal | 132 | 138 | 27 | 2020-05-03 | 8:00 | 126 | 17 | 2020-05-03 | 0.375
9 | Matuail | 132 | 138 | 27 | 2020-05-03 | 0.29167 | 126 | 17 | 2020-05-03 | 0.375
10 | Ghorasal | 132 | 146 | 27 | 2020-05-03 | 0.33333 | 133 | 6 | 2020-05-03 | 0.75
11 | Narsinghdi | 132 | 140 | 27 | 2020-05-03 | 0.29167 | 124 | 4 | 2020-05-03 | 0.58333
12 | Haripur (SBU) | 132 | 138 | 27 | 2020-05-03 | 0.29167 | 126 | 19 | 2020-05-03 | 0.54167
13 | Ullon | 132 | 136 | 7 | 2020-05-03 | 0.83333 | 122 | 17 | 2020-05-03 | 0.41667
14 | Hasnabad | 132 | 142 | 27 | 2020-05-03 | 0.29167 | 124 | 17 | 2020-05-03 | 0.375
15 | Magbazar | 132 | 137 | 27 | 2020-05-03 | 0.29167 | 121 | 17 | 2020-05-03 | 0.41667
16 | Maniknagar | 132 | 140 | 27 | 2020-05-03 | 0.29167 | 128 | 17 | 2020-05-03 | 0.5
17 | Bangabhaban | 132 | 140 | 27 | 2020-05-03 | 0.29167 | 128 | 17 | 2020-05-03 | 0.5
18 | Narinda | 132 | 140 | 27 | 2020-05-03 | 0.29167 | 128 | 17 | 2020-05-03 | 0.5
19 | Dhanmondi | 132 | 136 | 7 | 2020-05-03 | 0.83333 | 122 | 17 | 2020-05-03 | 0.41667
20 | Lalbag | 132 | 144 | 27 | 2020-05-03 | 7:00 | 121 | 17 | 2020-05-03 | 0.5
21 | Madartek | 132 | 135 | 7 | 2020-05-03 | 0.83333 | 121 | 17 | 2020-05-03 | 0.41667
22 | Dhaka University | 132 | - | - | - | - | - | - | - | -
23 | Mirpur | 132 | 141 | 27 | 2020-05-03 | 0.29167 | 122 | 16 | 2020-05-03 | 14:00
24 | Kalyanpur | 132 | 142 | 27 | 2020-05-03 | 0.29167 | 127 | 11 | 2020-05-03 | 0.41667
25 | Gulshan | 132 | 137 | 9 | 2020-05-03 | 0.041667 | 121 | 17 | 2020-05-03 | 0.5
26 | Uttara | 132 | 141 | 7 | 2020-05-03 | 0.8125 | 122 | 17 | 2020-05-03 | 0.41667
27 | Uttara(New) | 132 | 139 | 27 | 2020-05-03 | 0.29167 | 122 | 18 | 2020-05-03 | 0.375
28 | Kamrangirchar | 132 | 144 | 27 | 2020-05-03 | 0.29167 | 120 | 17 | 2020-05-03 | 0.5
29 | Savar | 132 | 141 | 27 | 2020-05-03 | 0.29167 | 124 | 5 | 2020-05-03 | 0.66667
30 | Bhasantec | 132 | 138 | 20 | 2020-05-03 | 0.5 | 124 | 5 | 2020-05-03 | 0.66667
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
31 | Agargaon | 132 | 139 | 20 | 2020-05-03 | 0.5 | 124 | 5 | 2020-05-03 | 0.125
32 | Satmosjid | 132 | 139 | 20 | 2020-05-03 | 0.5 | 125 | 5 | 2020-05-03 | 0.125
33 | Tongi | 132 | 145 | 27 | 2020-05-03 | 0.25 | 126 | 17 | 2020-05-03 | 0.33333
34 | Kabirpur | 132 | 140 | 7 | 2020-05-03 | 0.83333 | 120 | 7 | 2020-05-03 | 0.45833
35 | Basundhara | 132 | 136 | 27 | 2020-05-03 | 7:00 | 121 | 17 | 2020-05-03 | 0.58333
36 | Manikganj | 132 | 147 | 21 | 2020-05-03 | 4:00 | 124 | 2 | 2020-05-03 | 0.375
37 | Joydevpur | 132 | 145 | 27 | 2020-05-03 | 0.33333 | 131 | 5 | 2020-05-03 | 0.66667
38 | New Tongi | 132 | 143 | 27 | 2020-05-03 | 0.33333 | 125 | 13 | 2020-05-03 | 0.45833
39 | Kodda | 132 | 146 | 27 | 2020-05-03 | 0.25 | 116 | 16 | 2020-05-03 | 0.58333
40 | Dhamrai | 132 | 142 | 27 | 2020-05-03 | 0.25 | 120 | 11 | 2020-05-03 | 0.33333
41 | Rajendrapur | 132 | 145 | 7 | 2020-05-03 | 0.83333 | 118 | 11 | 2020-05-03 | 0.33333
42 | Valuka | 132 | 142 | 27 | 2020-05-03 | 0.25 | 111 | 11 | 2020-05-03 | 0.91667
43 | Tangail | 132 | 143 | 7 | 2020-05-03 | 0.8125 | 123 | 5 | 2020-05-03 | 0.41667
44 | Mymensing | 132 | 142 | 21 | 2020-05-03 | 0.20833 | 114 | 11 | 2020-05-03 | 0.8125
45 | Kishorganj | 132 | 141 | 21 | 2020-05-03 | 0.29167 | 118 | 11 | 2020-05-03 | 0.8125
46 | Netrokona | 132 | 141 | 21 | 2020-05-03 | 0.20833 | 111 | 18 | 2020-05-03 | 0.875
47 | Jamalpur | 132 | 141 | 21 | 2020-05-03 | 0.20833 | 114 | 3 | 2020-05-03 | 14:00
48 | Sherpur | 132 | 142 | 21 | 2020-05-03 | 0.25 | 113 | 3 | 2020-05-03 | 14:00
49 | Srimongal | 132 | 142 | 27 | 2020-05-03 | 0.77083 | 132 | 11 | 2020-05-03 | 0.8125
50 | Shahjibazar | 132 | 141 | 27 | 2020-05-03 | 19:00 | 130 | 10 | 2020-05-03 | 0.91667
51 | Fenchuganj | 132 | 138 | 1 | 2020-05-03 | 0.25 | 131 | 26 | 2020-05-03 | 24:00
52 | Khulawara | 132 | 139 | 13 | 2020-05-03 | 0.25 | 131 | 10 | 2020-05-03 | 0.95833
53 | Sylhet | 132 | 137 | 2 | 2020-05-03 | 0.70833 | 130 | 23 | 2020-05-03 | 24:00
54 | Chattak | 132 | 139 | 11 | 2020-05-03 | 0.375 | 129 | 10 | 2020-05-03 | 19:30
55 | Sunamganj | 132 | 139 | 5 | 2020-05-03 | 0.8125 | 125 | 19 | 2020-05-03 | 0.875
56 | Biani Bazar | 132 | 138 | 2 | 2020-05-03 | 0.70833 | 126 | 18 | 2020-05-03 | 19:00
57 | Comilla(South) | 132 | 136 | 15 | 2020-05-03 | 0.75 | 118 | 17 | 2020-05-03 | 0.875
58 | Comilla (North) | 132 | 142 | 27 | 2020-05-03 | 0.41667 | 128 | 7 | 2020-05-03 | 0.5
59 | Chandpur | 132 | 142 | 20 | 2020-05-03 | 23:00 | 115 | 26 | 2020-05-03 | 0.91667
60 | Feni | 132 | 138 | 7 | 2020-05-03 | 0.91667 | 120 | 5 | 2020-05-03 | 0.79167
61 | Chowmuhani | 132 | 138 | 15 | 2020-05-03 | 0.77083 | 115 | 5 | 2020-05-03 | 0.79167
62 | Ashuganj | 132 | 147 | 7 | 2020-05-03 | 0.875 | 132 | 10 | 2020-05-03 | 0.95833
63 | Daudkandi | 132 | 139 | 27 | 2020-05-03 | 0.41667 | 122 | 16 | 2020-05-03 | 0.5
64 | Brahminbaria | 132 | 141 | 27 | 2020-05-03 | 0.33333 | 126 | 11 | 2020-05-03 | 0.875
65 | Ramganj | 132 | 136 | 7 | 2020-05-03 | 0.91667 | 111 | 22 | 2020-05-03 | 0.875
66 | Chaddagram | 132 | 139 | 27 | 2020-05-03 | 0.375 | 120 | 22 | 2020-05-03 | 0.875
67 | PHP | 132 | 137 | 21 | 2020-05-03 | 0.041667 | 121 | 5 | 2020-05-03 | 0.66667
68 | Madanhat | 132 | 137 | 6 | 2020-05-03 | 0.45833 | 126 | 5 | 2020-05-03 | 0.79167
69 | Hathazari | 132 | 136 | 6 | 2020-05-03 | 0.45833 | 126 | 1 | 2020-05-03 | 0.79167
70 | Khulshi | 132 | 133 | 6 | 2020-05-03 | 0.45833 | 121 | 1 | 2020-05-03 | 0.77083
71 | Halishahar | 132 | 136 | 19 | 2020-05-03 | 0.8125 | 124 | 1 | 2020-05-03 | 0.125
72 | Baraulia | 132 | 135 | 24 | 2020-05-03 | 0.8125 | 119 | 2 | 2020-05-03 | 0.91667
73 | Sikalbaha | 132 | 136 | 12 | 2020-05-03 | 0.77083 | 123 | 2 | 2020-05-03 | 0.33333
74 | Dohazari | 132 | 145 | 6 | 2020-05-03 | 0.41667 | 117 | 1 | 2020-05-03 | 0.79167
75 | Cox'sbazar | 132 | 134 | 6 | 2020-05-03 | 0.45833 | 106 | 22 | 2020-05-03 | 0.54167
76 | Chandraghona | 132 | 136 | 6 | 2020-05-03 | 0.45833 | 124 | 1 | 2020-05-03 | 0.79167
77 | Kaptai | 132 | 135 | 6 | 2020-05-03 | 0.45833 | 125 | 1 | 2020-05-03 | 0.79167
78 | A. Khaer Stl. | 132 | 133 | 6 | 2020-05-03 | 0.45833 | 125 | 1 | 2020-05-03 | 0.16667
79 | Bakulia | 132 | 135 | 6 | 2020-05-03 | 0.41667 | 120 | 1 | 2020-05-03 | 0.79167
80 | Julda | 132 | 135 | 6 | 2020-05-03 | 0.45833 | 121 | 1 | 2020-05-03 | 0.77083
81 | TK Chemical | 132 | 135 | 19 | 2020-05-03 | 0.8125 | 122 | 1 | 2020-05-03 | 0.79167
82 | Modern Steel | 132 | 136 | 6 | 2020-05-03 | 0.41667 | 123 | 1 | 2020-05-03 | 0.77083
83 | Shahmirpur | 132 | 135 | 6 | 2020-05-03 | 0.45833 | 123 | 1 | 2020-05-03 | 0.79167
84 | Khagrachhari | 132 | 136 | 6 | 2020-05-03 | 0.45833 | 123 | 1 | 2020-05-03 | 0.79167
85 | Matarbari | 132 | 132 | 27 | 2020-05-03 | 0.54167 | 109 | 23 | 2020-05-03 | 20:00
86 | Baroiar Hat | 132 | 137 | 27 | 2020-05-03 | 0.41667 | 120 | 5 | 2020-05-03 | 0.75
87 | Rangamati | 132 | 136 | 6 | 2020-05-03 | 0.45833 | 122 | 1 | 2020-05-03 | 0.79167
88 | Goalpara | 132 | 145 | 6 | 2020-05-03 | 0.29167 | 120 | 10 | 2020-05-03 | 14:00
89 | Khulna Central | 132 | 145 | 21 | 2020-05-03 | 0.20833 | 119 | 10 | 2020-05-03 | 14:00
90 | Noapara | 132 | 145 | 6 | 2020-05-03 | 0.29167 | 117 | 10 | 2020-05-03 | 14:00
91 | Jessore | 132 | 144 | 20 | 2020-05-03 | 0.83333 | 113 | 10 | 2020-05-03 | 0.54167
92 | Benapol | 132 | 143 | 20 | 2020-05-03 | 0.83333 | 114 | 10 | 2020-05-03 | 0.58333
93 | Jhenida | 132 | 144 | 20 | 2020-05-03 | 0.83333 | 107 | 18 | 2020-05-03 | 0.875
94 | Bottail | 132 | 143 | 20 | 2020-05-03 | 0.875 | 120 | 18 | 2020-05-03 | 0.875
95 | G.K Project | 132 | 146 | 10 | 2020-05-03 | 0.91667 | 132 | 6 | 2020-05-03 | 0.83333
96 | Faridpur | 132 | 145 | 21 | 2020-05-03 | 0.29167 | 118 | 23 | 2020-05-03 | 0.54167
97 | Madaripur | 132 | 149 | 6 | 2020-05-03 | 0.33333 | 115 | 23 | 2020-05-03 | 0.58333
98 | Sariatpur | 132 | 148 | 6 | 2020-05-03 | 0.29167 | 113 | 11 | 2020-05-03 | 0.625
99 | Gopalganj | 132 | 150 | 6 | 2020-05-03 | 0.29167 | 115 | 23 | 2020-05-03 | 0.58333
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May'2020
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
100 | Bagerhat | 132 | 147 | 6 | 2020-05-03 | 0.29167 | 115 | 5 | 2020-05-03 | 0.8125
101 | Mongla | 132 | 145 | 20 | 2020-05-03 | 0.875 | 114 | 13 | 2020-05-03 | 0.45833
102 | Satkhira | 132 | 146 | 21 | 2020-05-03 | 0.20833 | 116 | 13 | 2020-05-03 | 0.79167
103 | Gallamari | 132 | 144 | 6 | 2020-05-03 | 0.29167 | 121 | 10 | 2020-05-03 | 0.58333
104 | Magura | 132 | 146 | 20 | 2020-05-03 | 0.83333 | 103 | 18 | 2020-05-03 | 0.875
105 | Norail | 132 | 144 | 20 | 2020-05-03 | 0.83333 | 102 | 16 | 2020-05-03 | 0.8125
106 | Chuadanga | 132 | 143 | 20 | 2020-05-03 | 0.83333 | 95 | 18 | 2020-05-03 | 0.875
107 | Barisal(N) | 132 | 148 | 6 | 2020-05-03 | 0.29167 | 120 | 11 | 2020-05-03 | 0.58333
108 | Barisal(S) | 132 | 148 | 21 | 2020-05-03 | 0.041667 | 120 | 5 | 2020-05-03 | 0.8125
109 | Patuakhali | 132 | 145 | 20 | 2020-05-03 | 0.95833 | 114 | 5 | 2020-05-03 | 0.8125
110 | Bhandaria | 132 | 146 | 6 | 2020-05-03 | 0.29167 | 115 | 19 | 2020-05-03 | 0.5
111 | Ishurdi | 132 | 143 | 7 | 2020-05-03 | 0.875 | 129 | 2 | 2020-05-03 | 0.75
112 | Ruppur paromanobik | 132 | 143 | 20 | 2020-05-03 | 0.95833 | 130 | 4 | 2020-05-03 | 0.875
113 | Natore | 132 | 145 | 21 | 2020-05-03 | 0.16667 | 124 | 15 | 2020-05-03 | 0.79167
114 | Bogra | 132 | 146 | 21 | 2020-05-03 | 0.16667 | 122 | 15 | 2020-05-03 | 19:00
115 | Noagaon | 132 | 147 | 21 | 2020-05-03 | 0.20833 | 114 | 16 | 2020-05-03 | 0.875
116 | Rajshahi | 132 | 144 | 20 | 2020-05-03 | 0.875 | 123 | 15 | 2020-05-03 | 0.79167
117 | Rajshahi New | 132 | 144 | 20 | 2020-05-03 | 0.875 | 123 | 15 | 2020-05-03 | 0.79167
118 | C.Nawabganj | 132 | 146 | 21 | 2020-05-03 | 0.083333 | 122 | 15 | 2020-05-03 | 0.79167
119 | Amnura | 132 | 144 | 21 | 2020-05-03 | 0.125 | 120 | 25 | 2020-05-03 | 0.875
120 | Pabna | 132 | 144 | 20 | 2020-05-03 | 0.875 | 126 | 4 | 2020-05-03 | 0.875
121 | Shahjadpur | 132 | 146 | 21 | 2020-05-03 | 4:00 | 125 | 18 | 2020-05-03 | 9:00
122 | Serajganj | 132 | 144 | 27 | 2020-05-03 | 0.25 | 124 | 15 | 2020-05-03 | 19:00
123 | Niyamatpur | 132 | 147 | 21 | 2020-05-03 | 0.16667 | 111 | 16 | 2020-05-03 | 0.875
124 | Joypurhat | 132 | 147 | 21 | 2020-05-03 | 0.20833 | 112 | 16 | 2020-05-03 | 0.875
125 | Sherpur(Bogura) | 132 | 146 | 27 | 2020-05-03 | 0.25 | 123 | 15 | 2020-05-03 | 0.79167
126 | Mohastangor | 132 | 146 | 21 | 2020-05-03 | 0.16667 | 120 | 15 | 2020-05-03 | 0.8125
127 | Rangpur | 132 | 143 | 21 | 2020-05-03 | 0.20833 | 114 | 15 | 2020-05-03 | 0.8125
128 | Lalmonirhat | 132 | 140 | 21 | 2020-05-03 | 0.20833 | 107 | 19 | 2020-05-03 | 0.875
129 | Saidpur | 132 | 143 | 21 | 2020-05-03 | 0.20833 | 108 | 19 | 2020-05-03 | 0.875
130 | Purbasadipur | 132 | 143 | 21 | 2020-05-03 | 0.25 | 103 | 18 | 2020-05-03 | 0.875
131 | Thakurgaon | 132 | 141 | 21 | 2020-05-03 | 0.5 | 102 | 19 | 2020-05-03 | 0.875
132 | Palashbari | 132 | 142 | 21 | 2020-05-03 | 0.20833 | 113 | 15 | 2020-05-03 | 0.8125
133 | Barapukuria | 132 | 143 | 27 | 2020-05-03 | 0.29167 | 118 | 15 | 2020-05-03 | 0.79167
134 | Panchagar | 132 | 140 | 5 | 2020-05-03 | 0.625 | 98 | 15 | 2020-05-03 | 0.875
135 | Joldhaka | 132 | 143 | 21 | 2020-05-03 | 0.20833 | 105 | 18 | 2020-05-03 | 0.875
136 | Kurigram | 132 | 143 | 21 | 2020-05-03 | 0.375 | 106 | 19 | 2020-05-03 | 0.875
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:May' 2020
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 158 | 380
Hasnabad | TR2 | 225 | 125 | 380 | 16.05.2020 | 13:00
| TR3 | 225 | 130 | 380
| TR1 | 225 | 190 | 535
Tongi | TR2 | 225 | 190 | 535 | 17.05.2020 | 09:00
| TR3 | 225 | 190 | 535
Haripur | TR1 | 225 | 86 | 225 | 05.05.2020 | 09:00
| TR3 | 225 | 86 | 225
| TR1 | 225 | 147 | 405
Rampura | TR2 | 225 | 147 | 405 | 17.05.2020 | 14:00
| TR3 | 225 | 147 | 405
| TR1 | 225 | 97 | 269
Aminbazar | TR2 | 225 | 97 | 269 | 31.05.2020 | 14:00
| TR3 | 225 | 101 | 282
Maniknagar | TR1 | 300 | 93 | 270 | 31.05.2020 | 13:00
| TR2 | 300 | 93 | 270
Cumilla (N) | TR1 | 225 | 200 | 577 | 07.05.2020 | 19:30
| TR2 | 225 | 199 | 557
Fenchuganj | TR1 | 300 | 204 | 497 | 13.05.2020 | 7:00
| MT1 | 150 | 97 | 300
Hathazari | MT2 | 150 | 97 | 300 | 27.05.2020 | 07:00
| MT3 | 150 | 97 | 300
| MT4 | 150 | 97 | 300
| TR1 | 225 | 140 | 390
Ishurdi | TR2 | 225 | 140 | 390 | 30.05.2020 | 21:00
| TR3 | 225 | 140 | 390
Khulna(S) | TR1 | 225 | 119 | 334
| TR2 | 225 | 119 | 334 | 05.05.2020 | 19:00
| TR3 | 300 | 153 | 430
Bogra | TR1 | 225 | 134 | 400 | 16.05.2020 | 21:00
| TR2 | 225 | 134 | 400
| TR3 | 225 | 181 | 587
Baghabari | TR1 | 300 | 168 | 470 | 19.05.2020 | 19:30
| TR2 | 225 | 125 | 350
Barapukuria | TR1 | 225 | 153 | 800 | 08.05.2020 | 21:00 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 142 | 750 |  |  | 132 kV current is being provided
| TR6 | 300 | 186 | 986
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:MAY' 2020
Name of the | Transofrmer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 400 kV side ) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 177.5 | 323 | 17.05.2020 | 1:00
| TR2(400/230 kV) | 520 | 179.8 | 331
| TR1(400/132 kV) | 325 | 244.5 | 418 | 09.05.2020 | 20:30
| TR2(400/132 kV) | 325 | 246.6 | 420
Bibiyana | ICT1(400/230 kV) | 520 | 145 | 230 | 25.05.2020 | 3:00
| ICT2(400/230kV) | 520 | 143 | 230
Bhulta | ATR1(400/230 kV) | 520 | 195 | 343 | 17.05.2020 | 8:45
| ATR2(400/230kV) | 520 | 195 | 343
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May' 2020 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May' 2020 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-05-20 | 8056 | 8056 | - | - | - | - | - | - | - | - | - | - | - | - | 01-05-20 | 5636.8 | 5636.8 | - | - | - | - | - | - | - | - | - | - | - | -
02-05-20 | 7976 | 7976 | - | - | - | - | - | - | - | - | - | - | - | - | 02-05-20 | 6619.6 | 6619.6 | - | - | - | - | - | - | - | - | - | - | - | -
03-05-20 | 9279 | 9279 | - | - | - | - | - | - | - | - | - | - | - | - | 03-05-20 | 6923.4 | 6923.4 | - | - | - | - | - | - | - | - | - | - | - | -
04-05-20 | 10273 | 10273 | - | - | - | - | - | - | - | - | - | - | - | - | 04-05-20 | 7706.9 | 7706.9 | - | - | - | - | - | - | - | - | - | - | - | -
05-05-20 | 8170 | 8170 | - | - | - | - | - | - | - | - | - | - | - | - | 05-05-20 | 8474.7 | 8474.7 | - | - | - | - | - | - | - | - | - | - | - | -
06-05-20 | 9126 | 9126 | - | - | - | - | - | - | - | - | - | - | - | - | 06-05-20 | 6007.3 | 6007.3 | - | - | - | - | - | - | - | - | - | - | - | -
07-05-20 | 7103 | 7103 | - | - | - | - | - | - | - | - | - | - | - | - | 07-05-20 | 7838.1 | 7838.1 | - | - | - | - | - | - | - | - | - | - | - | -
08-05-20 | 9924 | 9924 | - | - | - | - | - | - | - | - | - | - | - | - | 08-05-20 | 6724.8 | 6724.8 | - | - | - | - | - | - | - | - | - | - | - | -
09-05-20 | 10539 | 10539 | - | - | - | - | - | - | - | - | - | - | - | - | 09-05-20 | 8106.8 | 8106.8 | - | - | - | - | - | - | - | - | - | - | - | -
10-05-20 | 10210 | 10210 | - | - | - | - | - | - | - | - | - | - | - | - | 10-05-20 | 8971.2 | 8971.2 | - | - | - | - | - | - | - | - | - | - | - | -
11-05-20 | 11068 | 11068 | - | - | - | - | - | - | - | - | - | - | - | - | 11-05-20 | 8619.2 | 8619.2 | - | - | - | - | - | - | - | - | - | - | - | -
12-05-20 | 11513 | 11513 | - | - | - | - | - | - | - | - | - | - | - | - | 12-05-20 | 9211.8 | 9211.8 | - | - | - | - | - | - | - | - | - | - | - | -
13-05-20 | 9803 | 9803 | - | - | - | - | - | - | - | - | - | - | - | - | 13-05-20 | 9204.3 | 9204.3 | - | - | - | - | - | - | - | - | - | - | - | -
14-05-20 | 10285 | 10285 | - | - | - | - | - | - | - | - | - | - | - | - | 14-05-20 | 9040.7 | 9040.7 | - | - | - | - | - | - | - | - | - | - | - | -
15-05-20 | 10142 | 10142 | - | - | - | - | - | - | - | - | - | - | - | - | 15-05-20 | 8033.1 | 8033.1 | - | - | - | - | - | - | - | - | - | - | - | -
16-05-20 | 11305 | 11305 | - | - | - | - | - | - | - | - | - | - | - | - | 16-05-20 | 8359.5 | 8359.5 | - | - | - | - | - | - | - | - | - | - | - | -
17-05-20 | 11828 | 11828 | - | - | - | - | - | - | - | - | - | - | - | - | 17-05-20 | 9209.1 | 9209.1 | - | - | - | - | - | - | - | - | - | - | - | -
18-05-20 | 11941 | 11941 | - | - | - | - | - | - | - | - | - | - | - | - | 18-05-20 | 9490.1 | 9490.1 | - | - | - | - | - | - | - | - | - | - | - | -
19-05-20 | 10788 | 10788 | - | - | - | - | - | - | - | - | - | - | - | - | 19-05-20 | 9442 | 9442 | - | - | - | - | - | - | - | - | - | - | - | -
20-05-20 | 6330 | 6330 | - | - | - | - | - | - | - | - | - | - | - | - | 20-05-20 | 7109.3 | 7109.3 | - | - | - | - | - | - | - | - | - | - | - | -
21-05-20 | 7411 | 7411 | - | - | - | - | - | - | - | - | - | - | - | - | 21-05-20 | 4344.87 | 4344.87 | - | - | - | - | - | - | - | - | - | - | - | -
22-05-20 | 9308 | 9308 | - | - | - | - | - | - | - | - | - | - | - | - | 22-05-20 | 6143.1 | 6143.1 | - | - | - | - | - | - | - | - | - | - | - | -
23-05-20 | 10242 | 10242 | - | - | - | - | - | - | - | - | - | - | - | - | 23-05-20 | 7249.5 | 7249.5 | - | - | - | - | - | - | - | - | - | - | - | -
24-05-20 | 9574 | 9574 | - | - | - | - | - | - | - | - | - | - | - | - | 24-05-20 | 6606.5 | 6606.5 | - | - | - | - | - | - | - | - | - | - | - | -
25-05-20 | 8929 | 8929 | - | - | - | - | - | - | - | - | - | - | - | - | 25-05-20 | 6056.9 | 6056.9 | - | - | - | - | - | - | - | - | - | - | - | -
26-05-20 | 8341 | 8341 | - | - | - | - | - | - | - | - | - | - | - | - | 26-05-20 | 5863.02 | 5863.02 | - | - | - | - | - | - | - | - | - | - | - | -
27-05-20 | 6958 | 6958 | - | - | - | - | - | - | - | - | - | - | - | - | 27-05-20 | 4434.5 | 4434.5 | - | - | - | - | - | - | - | - | - | - | - | -
28-05-20 | 8468 | 8468 | - | - | - | - | - | - | - | - | - | - | - | - | 28-05-20 | 6522.5 | 6522.5 | - | - | - | - | - | - | - | - | - | - | - | -
29-05-20 | 9155 | 9155 | - | - | - | - | - | - | - | - | - | - | - | - | 29-05-20 | 6772.1 | 6772.1 | - | - | - | - | - | - | - | - | - | - | - | -
30-05-20 | 9184 | 9184 | - | - | - | - | - | - | - | - | - | - | - | - | 30-05-20 | 7183.1 | 7183.1
31-05-20 | 10574 | 10574 | - | - | - | - | - | - | - | - | - | - | - | - | 31-05-20 | 8346.7 | 8346.7 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:May' 2020
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11977 | 18/05/20 | 22:00
2 | Maximum Day Peak Genaration | MW | 9490.1 | 18/05/20 | 12:00
3 | Maximum Evening Peak Demand | MW | 11941 | 18/05/20 | 21:00
4 | Minimum Generation | MW | 2679.2 | 21/05/20 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9477.5161
6 | Average of the daily day peak Genaration | MW | 7427.4674
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 5921.895
12 | Total Generation by BPDB | MKWH | 3143.7123 | % of total Gen. | 53.09%
13 | Total Generation by IPP | MKWH | 1591.4881 | '' | 26.87%
14 | A) Total Generation by RPCL | MKWH | 124.5045 | '' | 2.102%
| B) Total Generation by REB | MKWH | 118.008 | " | 1.993%
| C) Total Generation by RENTAL | MKWH | 375.5825 | " | 6.342%
| D) Total Imported from India (HVDC) | MKWH | 481.0775 | " | 8.124%
| E) Total Imported from Tripura, India (A.C) | MKWH | 87.5222 | " | 1.478%
15 | Fuel wise Generation.
| A) Gas | MKWH | 4152.6276 | % of total Gen. | 70.12%
| B) Oil | MKWH | 820.3222 | '' | 13.85%
| C) Hydro | MKWH | 38.7155 | '' | 0.6538%
| D) Solar | MKWH | 15.7592 | '' | 0.2661%
| E) Coal | MKWH | 325.8707 | '' | 5.503%
| F) HVDC (Import from India) | MKWH | 481.0775 | '' | 8.124%
| G) A.C (Import from Tripura, India) | MKWH | 87.5222 | '' | 1.478%
16 | Maximun of the daily total Generation . | MKWH | 264.4007 | 30-05-2020
17 | Monthly Load factor | % | 66.4568
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 12454.8817
| A) Gas | M.Taka | 4803.5122
| B) Liquid fuel | M.Taka | 6143.1634
| C) Coal | M.Taka | 1508.206
| D) HVDC (Import from India) | M.Taka | 2352.0331
| E) Tripura(Import from India) | M.Taka | 634.2048
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 763.6777 | 18/05/2020
| A) Gas | M.Taka | 173.654 | 18/05/2020
| B) Liquid fuel | M.Taka | 542.5253 | 18/05/2020
| C) Coal | M.Taka | 86.9997 | 14/05/2020
| D) HVDC (Import from India) | M.Taka | 112.5338 | 24-05-2020
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 2.7844
| B) Excluding Hydro & Solar | Taka/KWHR | 2.8097
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/2020 | 06:00
b) | Actual | FT (MSL) | 78.75 | 31/05/2020 | 06:00
22 | Peak Genaration of May 2019 | MW | 12893 | 29/05/19 | 21:00
23 | Peak Demand of May 2019 | MW | 12893 | 29/05/19 | 21:00
24 | Maximum peak Generation recorded upto 31/05/2020 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/05/2020 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/05/2020 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.