## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-07-06 | Monday
|  | Date (day): | 2020-07-06 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13739.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15275 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-07-05 | 2020-07-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 50 | 66 | 66 | 66 |  | 12 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 97 | 100 | 104
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 338 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 351 | 353 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 130 | 140 | 150 | 150 | 155 |  | GT-1 Under shut down.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 97 | 96 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 41 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 85 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 73 | 82 | 82 | 82 |  | 18 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 300 | 320 | 325
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 93 | 93 | 93 | 93 |  | 9 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 133 | 100 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 54 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 265 | 286 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 62 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 112 | 129 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 0 | 100 | 100
| Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6119 | 5895 | 3230 | 3325 | 3944 | 4287 | 629 | 789
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 108 | 109 | 107 | 109 | 121 |  | Low water level & Unit-2 under maint.
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 140 | 150 | 150
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 100 | 102
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 0 | 80 | 100
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.1 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 306 | 308 | 300 | 300
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 30 | 0 | 10 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 909.1 | 1016 | 1405 | 1538 | 381 | 229
56 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 100 | 100 | 29 |  | Gas Shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
57 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 192 | 215 | 215 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 320 | 360 | 360 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 255 | 290 | 360 | 360 |  |  | FGMO
60 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 37 | 37 | 37 |  | 8 | Engine problem
61 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 40 | 150 | 150
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 84 | 90 | 90 | 90 |  | 73
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 10 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 154 | 154 | 173
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 32 | 32 |  | 8 | Engine problem
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 70 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1156 | 1412 | 2091 | 2361 | 525 | 97
76 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 126 | 150 | 150 | 52 |  | Gas shortage
77 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 95 | 95 | 95
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.9 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 80 | 180 | 170 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 390.9 | 538 | 553.6 | 582 | 52 | 0
82 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 91 | 91 | 91
83 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
84 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
85 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 302 | 309 | 330 | 330
86 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
87 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 48 | 44 | 44
88 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
89 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 40 | 61 | 66
90 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 76 | 75 | 76 |  | 10 | Engine problem
91 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 151 | 100 | 150
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 9 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 1184 | 1294 | 1349 | 1406 | 0 | 410
98 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 930 | 951 | 951
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
103 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 350 | 410 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 16 | 40 | 40 | 40
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 60 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 0 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 15 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1311 | 1548 | 1781 | 2157 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 80 | 110
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 36 | 33 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 68 | 68 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 76 | 78 | 78 | 78 |  | 17 | Engine problem
112 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 360 | 588 | 600 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 523 | 880 | 859 | 949 | 0 | 143
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 43 | 45
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 155 | 200 | 200 |  |  | FGMO
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 166 | 210 | 210 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 376 | 411 | 410 | 410 |  |  | FGMO
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 9 | 11 | 11
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 70 | 113
131 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 831 | 1131 | 1509 | 1722 | 360 | 0
132 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
133 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 |  |  | Coal Shortage.
134 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
135 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10 | Engine problem
136 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 90 | 113
137 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7.9 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 191.9 | 271 | 248 | 273 | 170 | 30
| Total |  |  |  |  | 20383 | 19892 | 9726.9 | 11415 | 13739.6 | 15275 | 2117 | 1698
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9432.9201 | 11070 | 13324.3427 | 14813.3377
A. |  | 2020-07-05 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11527 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8580.9 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11415 | MW
3 | Day peak Generation : |  |  | 9726.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11070 | MW
4 | Evening peak Generation : |  |  | 11415 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 244.1903 | MKWHr | By Solar | 0.10531 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 144.2118 | MKWHr |  | By Oil: | 59.0457 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 13.1896 | MKWHr |  | By Hydro: | 2.435 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2117 | MW | Dhaka | 3745 | 3745 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1698 | MW | Chittagong | 1066 | 1066 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3815 | MW | Khulna | 1422 | 1422 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1163.73 | MMCFD |  |  | Rajshahi | 1245 | 1245 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 165903188.862 | ii) Oil : | Taka | 466547309.47 | Comilla | 1054 | 1054 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 61687697 | Total | Taka | 694138195.332 | Mymensingh | 979 | 979 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.2185 | MKWHr. | Sylhet | 462 | 462 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -80 | MW (E to W) at | 21:00 | hrs | Barisal | 320 | 320 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -423 | MW at | 1:00 | hrs | Rangpur | 777 | 777 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.4° C |  |  | Total | 11070 | 11070 |  | 0
B. |  | 2020-07-06 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15275 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 3375 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 252.092 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8405.2 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8371 | MKWHr. | ii) HVDC Flow at Peak Time |  | 930 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3658 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.47 |  | (b) Today: | 83.41 |  | (c) Rule Curve: |  | 84.8
.

## YesterdayGen
2020-07-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 99 | 66 | 323 | 357 |  | 0 | 420 | 125 | 0 | 97 | 50 | 332 | 0 | 0 | 0 | 100 | 93 | 115 | 87 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 17 | 0 | 51 | 18 | 17 | 41 | 0 | 80 | 0 | 320 | 280 | 192 | 8 | 80 | 38 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 156 | 157 | 24 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 305 | 59 | 70 | 0 | 0 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 270 | 0 | 0 | 180 | 0 | 127 | 0 | 100 | 0 | 147 | 0 | 115 | 105 | 17 | 0 | 307 | 54 | 0 | 85 | 105 | 100 | 0 | 0 |  | 916 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 26 | 37 | 40 | 65 | 37 | 110 | 0 | 0 | 65 | 0 | 0 | 99 | 0 | 0 | 0 | 52 | 33 | 22 | 9 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 188 | 0 | 77 | 70 | 187 | 0 | 383 | 70 | 0 | 112 | 105 | 113 | 0 | 0 | 0 | 0 |  | 7796 | 3431 | 11227 | 4017 | 916 | 2156 | 3401 | 149 | 105 | 327 | 156 | 0 | 0 | 83.47
2:00 | 35 | 0 | 0 | 0 | 300 | 100 | 66 | 323 | 353 |  | 0 | 420 | 130 | 0 | 97 | 55 | 332 | 0 | 0 | 0 | 100 | 93 | 0 | 87 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 10 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 51 | 18 | 17 | 41 | 0 | 80 | 0 | 320 | 280 | 189 | 8 | 89 | 38 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 152 | 157 | 24 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 301 | 59 | 70 | 0 | 0 | 18 | 0 | 9 | 285 | 24 | 11 | 0 | 275 | 0 | 0 | 180 | 0 | 127 | 0 | 100 | 0 | 145 | 0 | 115 | 52 | 17 | 0 | 307 | 54 | 0 | 6 | 104 | 100 | 0 | 0 |  | 915 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 7 | 40 | 68 | 35 | 110 | 0 | 0 | 65 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 33 | 22 | 9 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 77 | 0 | 185 | 0 | 417 | 35 | 0 | 112 | 0 | 113 | 0 | 0 | 0 | 103 |  | 7473 | 3220 | 10693 | 4004 | 915 | 2190 | 2936 | 252 | 105 | 139 | 152 | 0 | 0 | 83.47
3:00 | 35 | 0 | 0 | 0 | 300 | 100 | 66 | 325 | 354 |  | 0 | 420 | 130 | 0 | 97 | 55 | 333 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 51 | 0 | 17 | 41 | 0 | 80 | 0 | 320 | 280 | 187 | 8 | 84 | 38 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 146 | 157 | 24 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 304 | 59 | 70 | 0 | 0 | 18 | 0 | 9 | 305 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 127 | 0 | 100 | 0 | 145 | 0 | 115 | 0 | 0 | 0 | 307 | 54 | 0 | 0 | 104 | 100 | 0 | 0 |  | 916 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 25 | 110 | 0 | 0 | 65 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 77 | 0 | 189 | 0 | 407 | 35 | 0 | 112 | 0 | 113 | 0 | 0 | 0 | 178 |  | 7338 | 3234 | 10572 | 4030 | 916 | 2191 | 2767 | 327 | 105 | 90 | 146 | 0 | 0 | 83.47
4:00 | 35 | 0 | 0 | 0 | 300 | 99 | 66 | 322 | 356 |  | 0 | 420 | 140 | 0 | 97 | 55 | 331 | 0 | 0 | 0 | 100 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 80 | 0 | 320 | 280 | 193 | 8 | 92 | 35 | 10 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 25 | 21 | 140 | 157 | 24 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 309 | 59 | 70 | 0 | 0 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 129 | 0 | 100 | 0 | 145 | 0 | 115 | 0 | 0 | 0 | 307 | 39 | 0 | 0 | 104 | 100 | 0 | 0 |  | 916 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 30 | 16 | 0 | 0 | 65 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 183 | 0 | 401 | 35 | 0 | 70 | 0 | 80 | 0 | 0 | 0 | 210 |  | 7261 | 3069 | 10330 | 4029 | 916 | 2197 | 2509 | 359 | 105 | 75 | 140 | 0 | 0 | 83.47
5:00 | 35 | 0 | 0 | 0 | 300 | 100 | 66 | 359 | 354 |  | 0 | 420 | 135 | 0 | 97 | 41 | 330 | 0 | 0 | 0 | 90 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 145 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 80 | 0 | 340 | 300 | 175 | 8 | 90 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 132 | 157 | 24 | 22 | 0 | 91 | 30 | 47 | 48 | 163 | 318 | 61 | 70 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 214 | 0 | 0 | 180 | 0 | 107 | 0 | 100 | 0 | 30 | 0 | 115 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 104 | 100 | 0 | 0 |  | 915 | 0 | 375 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 31 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 203 | 0 | 75 | 0 | 198 | 0 | 409 | 35 | 0 | 35 | 0 | 41 | 0 | 0 | 0 | 231 |  | 6956 | 2991 | 9947 | 4147 | 915 | 2226 | 2042 | 380 | 105 | 0 | 132 | 0 | 0 | 83.47
6:00 | 35 | 0 | 0 | 0 | 300 | 97 | 50 | 328 | 309 |  | 0 | 360 | 130 | 1 | 97 | 41 | 260 | 0 | 0 | 0 | 90 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 28 | 33 | 0 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 41 | 0 | 80 | 0 | 295 | 275 | 208 | 8 | 87 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 25 | 21 | 118 | 158 | 24 | 22 | 0.1 | 91 | 30 | 47 | 48 | 163 | 302 | 61 | 71 | 0 | 0 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 164 | 0 | 0 | 80 | 0 | 93 | 0.1 | 100 | 0 | 10 | 0 | 115 | 0 | 0 | 0.3 | 197 | 0 | 0 | 0 | 88 | 100 | 0 | 0 |  | 916 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 69 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 74 | 0 | 170 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 0.8 | 0 | 281 |  | 6369.5 | 2780.8 | 9150.3 | 3853 | 916 | 2072 | 1655 | 430 | 105 | 0 | 118 | 1.3 | 0 | 83.47
7:00 | 35 | 0 | 0 | 0 | 300 | 54 | 40 | 324 | 280 |  | 0 | 360 | 135 | 59 | 97 | 41 | 260 | 0 | 0 | 0 | 90 | 93 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 17 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 80 | 0 | 295 | 275 | 197 | 8 | 82 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 114 | 157 | 24 | 22 | 0.4 | 91 | 30 | 47 | 48 | 130 | 302 | 61 | 71 | 0 | 0 | 18 | 0 | 8 | 280 | 24 | 11 | 0 | 95 | 0 | 0 | 8 | 0 | 95 | 0.7 | 100 | 0 | 10 | 0 | 24 | 0 | 0 | 0.7 | 161 | 0 | 0 | 0 | 17 | 100 | 0 | 0 |  | 916 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 152 | 0 | 75 | 0 | 160 | 0 | 378 | 0 | 0 | 0 | 0 | 35 | 0 | 0.8 | 0 | 282 |  | 5939.8 | 2680.8 | 8620.6 | 3823 | 916 | 1918 | 1309 | 431 | 107 | 0 | 114 | 2.6 | 0 | 83.47
8:00 | 35 | 0 | 0 | 0 | 300 | 51 | 40 | 322 | 280 |  | 0 | 360 | 130 | 100 | 97 | 41 | 260 | 0 | 0 | 0 | 90 | 93 | 0 | 4 | 0 | 0 | 0 | 53 | 55 | 17 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 80 | 0 | 295 | 275 | 191 | 8 | 80 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 116 | 158 | 24 | 20 | 0.6 | 91 | 30 | 47 | 48 | 130 | 302 | 61 | 71 | 0 | 0 | 18 | 0 | 8 | 285 | 24 | 11 | 0 | 95 | 0 | 0 | 8 | 0 | 97 | 4.1 | 100 | 0 | 10 | 0 | 24 | 0 | 0 | 1.4 | 161 | 0 | 0 | 0 | 17 | 100 | 0 | 0 |  | 915 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 144 | 0 | 75 | 0 | 156 | 0 | 329 | 0 | 0 | 0 | 0 | 35 | 0 | 1.8 | 0 | 285 |  | 5968.1 | 2612.8 | 8580.9 | 3808 | 915 | 1841 | 1351 | 434 | 108 | 0 | 116 | 7.9 | 0 | 83.46
9:00 | 35 | 0 | 0 | 0 | 300 | 53 | 40 | 334 | 300 |  | 0 | 360 | 130 | 100 | 97 | 41 | 260 | 0 | 0 | 0 | 82 | 93 | 0 | 50 | 0 | 0 | 0 | 53 | 55 | 45 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 0 | 80 | 0 | 295 | 285 | 201 | 8 | 90 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 18 | 116 | 156 | 24 | 22 | 0.5 | 91 | 30 | 47 | 45 | 163 | 308 | 60 | 71 | 0 | 0 | 18 | 0 | 8 | 305 | 24 | 11 | 0 | 105 | 0 | 0 | 29 | 0 | 109 | 6.7 | 100 | 0 | 10 | 0 | 84 | 34 | 0 | 3.1 | 252 | 0 | 0 | 0 | 17 | 100 | 0 | 0 |  | 915 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 156 | 0 | 77 | 0 | 167 | 0 | 366 | 0 | 0 | 0 | 0 | 35 | 0 | 1.4 | 0 | 283 |  | 6383.3 | 2681.4 | 9064.7 | 3888 | 915 | 1948 | 1645 | 432 | 109 | 0 | 116 | 11.7 | 0 | 83.46
10:00 | 35 | 0 | 0 | 0 | 300 | 53 | 40 | 336 | 351 |  | 0 | 360 | 135 | 100 | 97 | 41 | 260 | 0 | 0 | 0 | 82 | 90 | 0 | 62 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 80 | 0 | 310 | 305 | 206 | 8 | 92 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 124 | 153 | 24 | 22 | 0.7 | 89 | 30 | 47 | 41 | 163 | 309 | 59 | 70 | 0 | 0 | 18 | 0 | 8 | 315 | 24 | 11 | 0 | 185 | 0 | 0 | 80 | 41 | 112 | 0 | 100 | 0 | 10 | 0 | 115 | 34 | 0 | 2.4 | 306 | 0 | 0 | 0 | 17 | 100 | 0 | 0 |  | 916 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 77 | 0 | 170 | 0 | 366 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 281 |  | 6747.1 | 2710 | 9457.1 | 3945 | 916 | 2002 | 1928 | 430 | 109 | 0 | 124 | 3.1 | 0 | 83.46
11:00 | 35 | 0 | 0 | 0 | 300 | 54 | 40 | 341 | 351 |  | 0 | 360 | 130 | 100 | 97 | 41 | 330 | 0 | 0 | 0 | 75 | 90 | 0 | 82 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 75 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 2 | 0 | 80 | 0 | 260 | 255 | 184 | 8 | 80 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 128 | 153 | 24 | 22 | 2.5 | 91 | 30 | 47 | 43 | 163 | 305 | 60 | 72 | 0 | 0 | 18 | 0 | 8 | 310 | 24 | 11 | 0 | 215 | 0 | 0 | 80 | 61 | 112 | 0 | 100 | 0 | 10 | 0 | 109 | 34 | 0 | 2.2 | 306 | 14 | 0 | 0 | 17 | 90 | 0 | 0 |  | 915 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 77 | 0 | 172 | 0 | 358 | 17 | 0 | 0 | 0 | 35 | 0 | 7.9 | 0 | 296 |  | 6753.7 | 2748.9 | 9502.6 | 3852 | 915 | 1995 | 2045 | 445 | 110 | 0 | 128 | 12.6 | 0 | #REF!
12:00 | 35 | 0 | 0 | 0 | 300 | 94 | 50 | 327 | 351 |  | 0 | 360 | 130 | 100 | 97 | 41 | 328 | 0 | 0 | 0 | 73 | 93 | 0 | 85 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 2 | 0 | 80 | 0 | 260 | 255 | 182 | 8 | 84 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 126 | 153 | 24 | 22 | 2.9 | 91 | 30 | 47 | 47 | 163 | 302 | 60 | 73 | 0 | 0 | 18 | 0 | 8 | 310 | 24 | 11 | 0 | 265 | 0 | 0 | 80 | 62 | 112 | 0 | 100 | 0 | 10 | 0 | 109 | 34 | 0 | 4.1 | 306 | 30 | 0 | 0 | 17 | 100 | 0 | 0 |  | 917 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 76 | 0 | 170 | 0 | 376 | 17 | 0 | 0 | 0 | 35 | 0 | 7.9 | 0 | 360 |  | 6870 | 2856.9 | 9726.9 | 3859 | 917 | 2067 | 2126 | 509 | 108 | 0 | 126 | 14.9 | 0 | 83.46
13:00 | 35 | 0 | 0 | 0 | 300 | 94 | 65 | 323 | 300 |  | 0 | 360 | 130 | 100 | 96 | 41 | 300 | 0 | 0 | 0 | 68 | 93 | 0 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 10 | 25 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 30 | 0 | 18 | 7 | 0 | 80 | 0 | 270 | 255 | 184 | 8 | 90 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 134 | 138 | 24 | 22 | 2.9 | 91 | 30 | 44 | 44 | 130 | 307 | 59 | 73 | 0 | 0 | 18 | 0 | 8 | 290 | 24 | 11 | 0 | 268 | 0 | 0 | 113 | 63 | 83 | 6 | 100 | 0 | 10 | 0 | 109 | 52 | 0 | 1.1 | 306 | 54 | 0 | 0 | 17 | 100 | 0 | 0 |  | 916 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 67 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 75 | 0 | 184 | 0 | 340 | 17 | 0 | 0 | 0 | 35 | 0 | 5.5 | 0 | 450 |  | 6825 | 2953.5 | 9778.5 | 3823 | 916 | 1938 | 2204 | 600 | 107 | 41 | 134 | 15.5 | 0 | 83.46
14:00 | 35 | 0 | 0 | 0 | 300 | 94 | 66 | 326 | 300 |  | 0 | 360 | 140 | 100 | 96 | 41 | 326 | 0 | 0 | 0 | 70 | 93 | 0 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 68 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 5 | 0 | 80 | 0 | 275 | 270 | 197 | 8 | 91 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 146 | 120 | 24 | 22 | 2.2 | 89 | 30 | 47 | 44 | 163 | 312 | 59 | 73 | 0 | 0 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 268 | 0 | 0 | 120 | 11 | 95 | 3.4 | 100 | 0 | 10 | 0 | 109 | 52 | 0 | 4.3 | 306 | 54 | 0 | 0 | 17 | 100 | 0 | 0 |  | 916 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 67 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 151 | 0 | 76 | 0 | 183 | 0 | 339 | 17 | 0 | 0 | 0 | 35 | 0 | 2.5 | 0 | 454 |  | 6922.9 | 2944.5 | 9867.4 | 3845 | 916 | 2002 | 2198 | 604 | 103 | 41 | 146 | 12.4 | 0 | 83.46
15:00 | 35 | 0 | 0 | 0 | 300 | 90 | 65 | 352 | 350 |  | 0 | 420 | 135 | 100 | 96 | 41 | 327 | 0 | 0 | 0 | 73 | 93 | 0 | 100 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 65 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 45 | 0 | 18 | 3 | 0 | 80 | 0 | 260 | 320 | 186 | 8 | 90 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 25 | 9 | 152 | 121 | 24 | 22 | 1.5 | 89 | 30 | 47 | 42 | 163 | 310 | 59 | 73 | 0 | 30 | 18 | 0 | 8 | 320 | 16 | 11 | 0 | 269 | 0 | 0 | 120 | 51 | 94 | 0 | 100 | 0 | 10 | 0 | 109 | 52 | 0 | 1.1 | 307 | 54 | 0 | 0 | 21 | 100 | 0 | 0 |  | 929 | 0 | 357 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 66 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 76 | 0 | 195 | 0 | 341 | 17 | 0 | 0 | 0 | 35 | 0 | 2.4 | 0 | 474 |  | 7179.6 | 2996.4 | 10176 | 3973 | 929 | 2111 | 2241 | 624 | 100 | 41 | 152 | 5 | 0 | 83.45
16:00 | 35 | 0 | 0 | 0 | 300 | 90 | 65 | 325 | 347 |  | 0 | 390 | 140 | 75 | 85 | 41 | 327 | 0 | 0 | 0 | 70 | 93 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 66 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 5 | 0 | 80 | 0 | 260 | 285 | 181 | 8 | 84 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 10 | 25 | 9 | 146 | 123 | 24 | 22 | 0.4 | 90 | 30 | 44 | 44 | 130 | 306 | 59 | 73 | 0 | 80 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 285 | 0 | 0 | 110 | 73 | 123 | 0 | 100 | 0 | 30 | 0 | 109 | 52 | 0 | 2.3 | 252 | 54 | 0 | 0 | 55 | 100 | 0 | 0 |  | 928 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 67 | 26 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 77 | 0 | 179 | 0 | 315 | 17 | 0 | 0 | 0 | 34 | 0 | 4.9 | 0 | 494 |  | 7036.7 | 2988.9 | 10025.6 | 3944 | 928 | 1991 | 2223 | 644 | 101 | 41 | 146 | 7.6 | 0 | 83.45
17:00 | 35 | 0 | 0 | 0 | 300 | 94 | 40 | 323 | 250 |  | 0 | 330 | 135 | 41 | 64 | 41 | 250 | 0 | 0 | 0 | 40 | 93 | 0 | 100 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 69 | 35 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 7 | 0 | 80 | 0 | 260 | 285 | 181 | 8 | 80 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 10 | 25 | 21 | 140 | 124 | 24 | 22 | 0.2 | 90 | 30 | 47 | 45 | 110 | 301 | 59 | 73 | 0 | 80 | 18 | 0 | 7 | 285 | 16 | 11 | 0 | 245 | 0 | 0 | 110 | 72 | 128 | 0 | 100 | 0 | 30 | 0 | 115 | 52 | 0 | 1.9 | 161 | 54 | 0 | 0 | 8 | 100 | 0 | 0 |  | 929 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 63 | 22 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 76 | 0 | 175 | 0 | 301 | 17 | 0 | 0 | 0 | 35 | 0 | 2.8 | 0 | 491 |  | 6431.1 | 2916.8 | 9347.9 | 3776 | 929 | 1777 | 1935 | 641 | 104 | 41 | 140 | 4.9 | 0 | 83.45
18:00 | 35 | 0 | 0 | 0 | 250 | 54 | 40 | 299 | 250 |  | 0 | 300 | 125 | 41 | 64 | 41 | 250 | 0 | 0 | 0 | 40 | 93 | 0 | 82 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 104 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 10 | 0 | 80 | 0 | 260 | 255 | 181 | 8 | 80 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 10 | 25 | 21 | 120 | 142 | 24 | 22 | 0.3 | 90 | 30 | 14 | 25 | 110 | 302 | 40 | 40 | 0 | 80 | 18 | 0 | 9 | 240 | 23 | 11 | 0 | 245 | 0 | 0 | 110 | 0 | 130 | 0.8 | 100 | 0 | 30 | 0 | 115 | 52 | 0 | 0.4 | 124 | 54 | 0 | 0 | 8 | 100 | 0 | 0 |  | 929 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 16 | 50 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 163 | 0 | 280 | 17 | 0 | 0 | 0 | 35 | 0 | 1.1 | 0 | 494 |  | 5991.5 | 2845.1 | 8836.6 | 3622 | 929 | 1563 | 1800 | 644 | 105 | 51 | 120 | 2.6 | 0 | 83.45
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 250 | 54 | 40 | 294 | 250 |  | 0 | 300 | 120 | 45 | 64 | 41 | 250 | 0 | 0 | 0 | 42 | 93 | 84 | 40 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 6 | 0 | 71 | 35 | 90 | 0 | 1 | 0 | 0 | 104 | 0 |  | 0 | 0 | 97 | 20 | 42 | 13 | 18 | 27 | 0 | 80 | 0 | 290 | 260 | 154 | 8 | 90 | 37 | 10 | 0 | 43 | 0 | 0 | 7 | 21 | 11 | 25 | 21 | 154 | 142 | 84 | 22 | 0 | 90 | 30 | 14 | 25 | 110 | 303 | 40 | 40 | 0 | 80 | 18 | 0 | 9 | 240 | 23 | 11 | 0 | 245 | 0 | 0 | 110 | 0 | 130 | 0 | 100 | 0 | 50 | 0 | 115 | 52 | 0 | 0 | 140 | 54 | 0 | 0 | 12 | 100 | 0 | 0 |  | 929 | 0 | 265 | 0 | 46 | 0 | 0 | 0 | 0 | 10 | 16 | 50 | 30 | 57 | 0 | 0 | 55 | 0 | 0 | 90 | 0 | 0 | 13 | 47 | 12 | 22 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 138 | 0 | 53 | 0 | 130 | 0 | 312 | 17 | 0 | 27 | 7 | 45 | 0 | 0 | 0 | 506 |  | 6428 | 3046 | 9474 | 3576 | 929 | 1596 | 2151 | 656 | 106 | 306 | 154 | 0 | 0 | 83.44
19:30 | 35 | 0 | 0 | 0 | 301 | 97 | 65 | 325 | 300 |  | 0 | 300 | 115 | 100 | 70 | 41 | 250 | 0 | 0 | 0 | 65 | 93 | 133 | 40 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 24 | 33 | 33 | 36 | 0 | 70 | 35 | 90 | 0 | 10 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 20 | 88 | 50 | 18 | 29 | 0 | 80 | 0 | 310 | 285 | 182 | 8 | 91 | 37 | 10 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 15 | 154 | 142 | 95 | 22 | 0 | 91 | 30 | 39 | 35 | 110 | 306 | 61 | 76 | 0 | 80 | 18 | 0 | 9 | 270 | 23 | 11 | 0 | 250 | 0 | 0 | 160 | 0 | 130 | 0 | 100 | 0 | 80 | 0 | 115 | 52 | 0 | 0 | 265 | 54 | 0 | 0 | 46 | 100 | 0 | 0 |  | 929 | 0 | 344 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 32 | 90 | 0 | 0 | 55 | 0 | 0 | 100 | 0 | 0 | 33 | 52 | 31 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 132 | 0 | 75 | 85 | 130 | 0 | 374 | 17 | 0 | 108 | 17 | 113 | 0 | 0 | 0 | 547 |  | 7400 | 3686 | 11086 | 3871 | 929 | 1903 | 3018 | 697 | 105 | 409 | 154 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 324 | 320 |  | 0 | 300 | 130 | 97 | 90 | 42 | 300 | 0 | 0 | 0 | 76 | 93 | 133 | 35 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 15 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 75 | 50 | 18 | 34 | 0 | 80 | 0 | 310 | 260 | 182 | 8 | 91 | 37 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 154 | 142 | 95 | 22 | 0 | 90 | 30 | 47 | 43 | 110 | 306 | 40 | 76 | 0 | 50 | 18 | 0 | 9 | 290 | 24 | 11 | 0 | 270 | 0 | 0 | 160 | 0 | 130 | 0 | 100 | 0 | 100 | 0 | 115 | 34 | 0 | 0 | 235 | 54 | 0 | 0 | 46 | 100 | 0 | 0 |  | 930 | 0 | 344 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 32 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 39 | 52 | 34 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 132 | 0 | 76 | 85 | 130 | 0 | 410 | 17 | 0 | 108 | 17 | 111 | 0 | 0 | 0 | 595 |  | 7372 | 3807 | 11179 | 3862 | 930 | 2002 | 2960 | 745 | 108 | 418 | 154 | 0 | 0 | 83.43
21:00 | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 338 | 353 |  | 0 | 420 | 140 | 100 | 96 | 55 | 300 | 0 | 0 | 0 | 82 | 93 | 133 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 8 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 0 | 25 | 18 | 16 | 0 | 80 | 0 | 320 | 290 | 192 | 8 | 90 | 37 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 154 | 126 | 95 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 309 | 40 | 76 | 0 | 151 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 129 | 0 | 100 | 0 | 40 | 0 | 115 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 70 | 100 | 0 | 0 |  | 930 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 36 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 155 | 0 | 78 | 98 | 166 | 0 | 411 | 0 | 0 | 111 | 15 | 113 | 0 | 0 | 0 | 588 |  | 7585 | 3830 | 11415 | 4079 | 930 | 2189 | 2839 | 738 | 109 | 377 | 154 | 0 | 0 | 83.44
22:00 | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 335 | 352 |  | 0 | 420 | 135 | 100 | 96 | 55 | 300 | 0 | 0 | 0 | 82 | 93 | 133 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 0 | 25 | 18 | 38 | 0 | 80 | 0 | 330 | 290 | 193 | 8 | 91 | 37 | 42 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 30 | 21 | 160 | 126 | 95 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 307 | 40 | 76 | 0 | 150 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 130 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 103 | 100 | 0 | 0 |  | 929 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 35 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 26 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 7 | 0 | 0 | 198 | 0 | 78 | 99 | 190 | 0 | 410 | 0 | 0 | 111 | 15 | 113 | 0 | 0 | 0 | 588 |  | 7641 | 3886 | 11527 | 4157 | 929 | 2245 | 2821 | 738 | 109 | 368 | 160 | 0 | 0 | 76.35
23:00 | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 326 | 353 |  | 0 | 420 | 140 | 100 | 96 | 55 | 280 | 0 | 0 | 0 | 82 | 93 | 105 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 0 | 25 | 18 | 40 | 0 | 80 | 0 | 320 | 285 | 190 | 8 | 91 | 37 | 49 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 32 | 21 | 156 | 142 | 95 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 308 | 40 | 76 | 0 | 150 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 130 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 104 | 100 | 0 | 0 |  | 929 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 69 | 36 | 80 | 0 | 0 | 55 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 25 | 22 | 8 | 11 | 0 | 0 | 150 | 0 | 7 | 0 | 0 | 191 | 0 | 78 | 99 | 187 | 0 | 380 | 0 | 0 | 111 | 15 | 113 | 0 | 0 | 0 | 587 |  | 7581 | 3805 | 11386 | 4110 | 929 | 2210 | 2797 | 737 | 108 | 339 | 156 | 0 | 0 | 83.43
24:00 | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 328 | 352 |  | 0 | 420 | 130 | 100 | 97 | 55 | 300 | 0 | 0 | 0 | 82 | 93 | 98 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 102 | 0 | 0 | 25 | 17 | 41 | 0 | 80 | 0 | 320 | 280 | 183 | 8 | 90 | 37 | 50 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 32 | 21 | 150 | 142 | 95 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 304 | 40 | 76 | 0 | 150 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 283 | 0 | 0 | 180 | 0 | 130 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 113 | 100 | 0 | 0 |  | 929 | 0 | 345 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 69 | 36 | 80 | 0 | 0 | 50 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 26 | 21 | 8 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 193 | 0 | 77 | 99 | 185 | 0 | 379 | 0 | 0 | 111 | 15 | 113 | 0 | 0 | 0 | 588 |  | 7579 | 3800 | 11379 | 4109 | 929 | 2218 | 2793 | 738 | 108 | 334 | 150 | 0 | 0 | 76.33
KWH | 720000 | 0 | 0 | 0 | 7074818 | 1985318 | 1381408 | 8045368 | 7763000 |  | 0 | 9052500 | 3204276 | 1608960 | 2233032 | 1117272 | 7246258 | 0 | 0 | 0 | 1910400 | 2230128 | 793440 | 1198983 | 0 | 0 | 0 | 1208880 | 1306067 | 1167063 | 386100 | 600000 | 625140 | 770900 | 778600 | 90864 | 0 | 1599038 | 836000 | 2100000 | 0 | 26200 | 0 | 0 | 3283767 | 0 |  | 0 | 0 | 555498 | 29400 | 513600 | 213600 | 398496 | 521280 | 0 | 1959210 | 0 | 7559300 | 6857000 | 4610000 | 217454 | 2073390 | 680832 | 373440 | 0 | 1020400 | 0 | 0 | 205200 | 482832 | 211140 | 618800 | 437260 | 3365760 | 3358480 | 953280 | 463716 | 13800 | 2127000 | 735600 | 1056000 | 1083168 | 3315763 | 6947000 | 1314336 | 1674240 | 0 | 912420 | 423000 | 0 | 204840 | 7327700 | 530040 | 264000 | 0 | 5735779 | 0 | 0 | 3120000 | 408343 | 2802240 | 16200 | 2331840 | 0 | 1144145 | 0 | 2576400 | 746412 | 42654 | 28440 | 6297818 | 725089 | 0 | 145920 | 1343160 | 2416320 | 0 | 0 |  | 21837091 | 0 | 8511840 | 0 | 1200960 | 0 | 0 | 0 | 42240 | 80384 | 601125 | 1595000 | 630143 | 931104 | 0 | 0 | 1460000 | 0 | 0 | 1164864 | 0 | 0 | 38290 | 352252 | 226299 | 497520 | 199980 | 223686 | 0 | 0 | 3675100 | 0 | 48000 | 0 | 0 | 4333155 | 0 | 1819685 | 581760 | 4441336 | 0 | 8928181 | 454080 | 0 | 1075776 | 289152 | 1557120 | 0 | 46871 | 0 | 9514500 |  | 167832815 | 76357494 | 244190309 | 95159820 | 21837091 | 49052020 | 56096654 | 13189600 | 2435038 | 2949015 | 3365760 | 105311 | 0
Fuel Cost | 1180800 | 0 | 0 | 0 | 7853047.98 | 2620619.76 | 2348393.6 | 8125821.68 | 7995890 |  | 0 | 9867225 | 3556746.36 | 12212006.4 | 15385590.48 | 9452121.12 | 7536108.32 | 0 | 0 | 0 | 14385312 | 20338767.36 | 7807449.6 | 11054623.26 | 0 | 0 | 0 | 8824824 | 10095897.91 | 11507241.18 | 289575 | 450000 | 0 | 0 | 0 | 878654.88 | 0 | 431740.26 | 225720 | 3801000 | 0 | 243398 | 0 | 0 | 5582403.9 | 0 |  | 0 | 0 | 5388330.6 | 280770 | 4468320 | 1691712 | 502104.96 | 1548201.6 | 0 | 2899630.8 | 0 | 5593882 | 6857000 | 4241200 | 280515.66 | 2384398.5 | 769340.16 | 522816 | 0 | 1744884 | 0 | 0 | 1959660 | 613196.64 | 158355 | 1082900 | 327945 | 25243200 | 3559988.8 | 8655782.4 | 588919.32 | 219972 | 3488280 | 1176960 | 1879680 | 1689742.08 | 3779969.82 | 7224880 | 2589241.92 | 3197798.4 | 0 | 1578486.6 | 926370 | 0 | 417873.6 | 7400977 | 397530 | 200640 | 0 | 43362489.24 | 0 | 0 | 16224000 | 6827494.96 | 27574041.6 | 189378 | 19004496 | 0 | 8066222.25 | 0 | 23496768 | 7053593.4 | 371516.34 | 0 | 47611504.08 | 6315525.19 | 0 | 1456281.6 | 11510881.2 | 16092691.2 | 0 | 0 |  | 125781644.16 | 0 | 8937432 | 0 | 9439545.6 | 0 | 0 | 0 | 443097.6 | 842424.32 | 6263722.5 | 1802350 | 976721.65 | 9087575.04 | 0 | 0 | 2993000 | 0 | 0 | 10309046.4 | 0 | 0 | 371030.1 | 3413321.88 | 2195100.3 | 955238.4 | 309969 | 169330.302 | 0 | 0 | 19919042 | 0 | 1369440 | 0 | 0 | 5719764.6 | 0 | 2729527.5 | 9895737.6 | 5196363.12 | 0 | 8838899.19 | 4740595.2 | 0 | 10209114.24 | 2729594.88 | 12083251.2 | 0 | 517924.55 | 0 | 41768655 |  | 536739315.97 | 310008458.332 | 846747774.302 | 106798246.602 | 125781644.16 | 59104942.26 | 437821390.55 | 61687697 | 657460.26 | 28725918.92 | 25243200 | 927274.55 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 300 | 94 | 50 | 327 | 351 |  | 0 | 360 | 130 | 100 | 97 | 41 | 328 | 0 | 0 | 0 | 73 | 93 | 0 | 85 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 2 | 0 | 80 | 0 | 260 | 255 | 182 | 8 | 84 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 0 | 25 | 15 | 126 | 153 | 24 | 22 | 2.9 | 91 | 30 | 47 | 47 | 163 | 302 | 60 | 73 | 0 | 0 | 18 | 0 | 8 | 310 | 24 | 11 | 0 | 265 | 0 | 0 | 80 | 62 | 112 | 0 | 100 | 0 | 10 | 0 | 109 | 34 | 0 | 4.1 | 306 | 30 | 0 | 0 | 17 | 100 | 0 | 0 |  | 917 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 68 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 76 | 0 | 170 | 0 | 376 | 17 | 0 | 0 | 0 | 35 | 0 | 7.9 | 0 | 360 |  | 9726.9 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 300 | 97 | 66 | 338 | 353 | 0 | 0 | 420 | 140 | 100 | 96 | 55 | 300 | 0 | 0 | 0 | 82 | 93 | 133 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 8 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 25 | 18 | 16 | 0 | 80 | 0 | 320 | 290 | 192 | 8 | 90 | 37 | 10 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 154 | 126 | 95 | 22 | 0 | 91 | 30 | 47 | 48 | 130 | 309 | 40 | 76 | 0 | 151 | 18 | 0 | 9 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 180 | 0 | 129 | 0 | 100 | 0 | 40 | 0 | 115 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 70 | 100 | 0 | 0 |  | 930 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 36 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 9 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 155 | 0 | 78 | 98 | 166 | 0 | 411 | 0 | 0 | 111 | 15 | 113 | 0 | 0 | 0 | 588 |  | 11415 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 300 | 104 | 66 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 325 | 0 | 0 | 0 | 82 | 93 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 74 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 18 | 20 | 0 | 100 | 0 | 360 | 360 | 215 | 8 | 90 | 37 | 10 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 32 | 21 | 173 | 150 | 95 | 22 | 0 | 91 | 30 | 51 | 44 | 163 | 330 | 66 | 76 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 0 |  | 951 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 60 | 50 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 10 | 0 | 0 | 200 | 0 | 78 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 0 | 300 | 100 | 66 | 412 | 360 | 0 | 0 | 450 | 150 | 100 | 100 | 55 | 320 | 0 | 0 | 0 | 82 | 93 | 100 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 72 | 35 | 100 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 18 | 10 | 0 | 100 | 0 | 360 | 360 | 215 | 8 | 90 | 37 | 10 | 0 | 43 | 0 | 0 | 52 | 22 | 10 | 32 | 21 | 154 | 150 | 95 | 22 | 1.6 | 91 | 30 | 51 | 44 | 163 | 330 | 61 | 75 | 0 | 100 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 10 | 50 | 114 | 113 | 100 | 0 | 0 |  | 951 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 33 | 80 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 50 | 43 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 90 | 0 | 8 | 70 | 600
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 74 | 40 | 323 | 310 | 0 | 0 | 350 | 130 | 16 | 30 | 15 | 270 | 0 | 0 | 0 | 15 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 0 | 80 | 0 | 280 | 270 | 163 | 8 | 91 | 35 | 5 | 0 | 43 | 0 | 0 | 0 | 21 | 8 | 32 | 15 | 110 | 157 | 24 | 22 | 0.3 | 91 | 30 | 22 | 20 | 130 | 308 | 40 | 40 | 0 | 100 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 70 | 0 | 93 | 2.9 | 40 | 0 | 0 | 0 | 115 | 0 | 0 | 1.6 | 124 | 0 | 0 | 0 | 17 | 60 | 0 | 0 | 0 | 941 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 9 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 160 | 0 | 55 | 0 | 162 | 0 | 372 | 0 | 0 | 0 | 0 | 34 | 0 | 2.4 | 0 | 540 | 0
199
| Minimum Generation |  | 8580.9 | 8:00
| Highest Generation |  | 11527 | 22:00
| Day Peak Generation |  | 9726.9 | 12:00
| Evening Peak Generation |  | 11415 | 21:00
| HVDC Max Flow |  | 930 | 20:00
| HVDC EvPeak Flow |  | 930 | 21:00
| Load factor L.F |  | 88.27%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-07-06
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-07-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9726.9 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8405.2 | MW
Evening Peak Generation : |  | 11415 | MW Hour : | 21:00 | Available Max Generation : |  | 15275 | MW
E.P. Demand (at gen end) : |  | 11415 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11900 | MW
Maximum Generation : |  | 11527 | MW Hour : | 22:00 | Reserve(Generation end) |  | 3375 | MW
Total Gen. (MKWH) : |  | 244.1903 | System Load Factor : | 88.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -423 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-07-06
Actual : | 83.41 | Ft.(MSL) , | Rule curve : | 84.8 | Ft.( MSL )
Gas Consumed : | Total = | 1163.73 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165903188.862
: |  | Coal : | 61687697 | Oil : | 466547309.47 | Total : | 694138195.332
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4290.8475 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1461.6117 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1309.9986 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1183.8516 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1069.7428 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 863.2508 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 479.4882 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 222.1792 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 665.7972 |  |  | 0 | 0%
Total | 0 |  | 11546.7677 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4,5.
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2
6) Kaptai-2,4
7) Raozan # 2
8) Sirajganj #1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Hasnabad 132 reserve Bus was shut down at 09:50 for C/M.
b) Hasnabad 132/33 kV T-5 transformer was under shut down from 09:56 to 17:42 for C/M.
c) Megnaghat-Shyampur 230 kV Ckt-2 was under shut down from 08:06 to 17:24 for D/W.
d) Rampur-Agrabad 132 kV Ckt-1 tripped at 12:40 showing gen.trip,dist.B-phase.
e) Kulshi-Rampur 132 kV Ckt tripped at 12:42 showing dist.B-phase and was switched on at 12:55.
f) After maintenance Sylhet-150 MW GT was synchronized at 14:41.
g) Rampura-Mogbazar 132 kV Ckt-1 was under shut down from 16:44 to 05:35(6/7/20) for replacing R-phase
PT at Rampura end.
h) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 20:21 showing dist.Z1,3-phase, auto reclosure block at both
ends and was switched on at 21:06.
i) Madanganj 132/33 kV t-1 transformer tripped at 19:039 showing E/F relay due to 33 kV Mondalpara feeder
fault and was switched on at 20:06.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-07-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 720000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7074818
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 66 | 1381408 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 1985318
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8045368 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 353 | 7763000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9052500 | Frequency Control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1608960
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 140 | 3204276 | FGMO & GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 96 | 2233032
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1117272
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 1198983 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 386100
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 82 | 1910400 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7246258
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 2230128 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel Shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1208880
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 793440
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1306067
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1167063
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1225140 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 770900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 778600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 90864 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 5735779 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 408343 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 129 | 2802240 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 746412 | Reserve
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 5895 | 3325 | 74191549
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 26200 | Low demand
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 16200
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 213600 | Low demand
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 109 | 2435038 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3283767 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 42654 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 555498
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 29400 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2331840
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 398496
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 521280
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 513600 | Reserve
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28440
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 308 | 6297818
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 725089 | Reserve
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2416320
| Chattogram area Total |  |  |  | 2266 | 1016 | 21935240
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1959210 | Gas shortage.
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 192 | 4610000 | FGMO
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7559300 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6857000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 680832 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 373440 | Gas shortage.
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1020400 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 1144145 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2073390 | Engine problem
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 482832
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 3365760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 618800 | Engine problem
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 205200 | Reserve
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 437260
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 145920 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 1343160 | Low demand
| Cumilla Area Total |  |  |  | 2980 | 1412 | 33305243
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 126 | 3358480 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 463716
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 953280
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13800
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 3120000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2576400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 538 | 10485676
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2127000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 735600 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3315763 | Frequency Control
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 309 | 6947000 | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1056000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 1083168
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1314336 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1674240 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 151 | 912420
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 530040
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7327700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 204840
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1294 | 27915107
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 930 | 21837091
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1200960
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 42240 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 80384 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8511840 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 601125
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 581760
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 454080 | Reserve
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 15 | 289152 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1548 | 33598632
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 931104
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 36 | 630143
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1595000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 78 | 1819685 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 588 | 9514500
| Barisal Area Total |  |  |  | 1054 | 880 | 14490432
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1460000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 38290 | Engine problem
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 155 | 4333155 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 166 | 4441336 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 411 | 8928181 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 226299
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 497520
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 9 | 199980
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223686
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 352252
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1164864
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 1075776
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1131 | 22941339
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3675100 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 48000 | Low demand
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1557120
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46871
| Rangpur Area Total |  |  |  | 605 | 271 | 5327091
| Total |  |  |  | 19892 | 11415 | 244190309
| Eastern Grid Total |  |  |  | 13766 | 7585 | 167832815
| Western Grid Total |  |  |  | 6126 | 3830 | 76357494
| National Grid Total |  |  |  | 19892 | 11415 | 244190309
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-07-05
(a) ENTIRE EASTERN GRID : |  | 7306 | MW | (b) ENTIRE WESTERN GRID : |  | 3764 | MW
i) Dhaka area |  | 3745 | MW | i) Khulna area |  | 1422 | MW
ii) Chittagong area |  | 1066 | MW | ii) Rajshahi area |  | 1245 | MW
iii) Comilla area |  | 1054 | MW | iii) Barisal area |  | 320 | MW
iv) Mymensingh area |  | 979 | MW | iv) Rangpur area |  | 777 | MW
v) Sylhet area |  | 462 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11070 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 12:00 | Sherpur | 110 | 22:00 | Jhenida | 108 | 21:00
Munsiganj | 122 | 22:00 | Srimongal | 41 | 19:30 | Bottail | 117 | 19:30
Sonargaon | 78 | 9:00 | Shahjibazar | 114 | 22:00 | G.K Project | 54 | 20:00
Shyampur | 200 | 0:00 | Fenchuganj | 46 | 19:00 | Faridpur | 178 | 0.875
Bhulta | 193 | 12:00 | Kulawara | 46 | 20:00 | Madaripur | 95 | 0.91667
Madanganj | 54 | 13:00 | Sylhet | 109 | 14:00 | Sariatpur | 62 | 1:00
Shitalakhya | 110 | 10:00 | Chatak | 30 | 20:00 | Gopalganj | 87 | 19:30
Rahim steel | 16 | 7:00 | Sunamganj | 40 | 22:00 | Bagerhat | 87 | 20:00
Matuail | 78 | 9:00 | Biani Bazar | 54 | 19:30 | Mongla | 52 | 12:00
Ghorasal | 75 | 21:00 | Comilla (S) | 160 | 22:00 | Satkhira | 102 | 0.83333
Narsingdi | 156 | 22:00 | Comilla(N) | 93 | 21:00 | Gallamari | 40 | 19:30
Haripur (SBU) | 96 | 19:00 | Chandpur | 101 | 19:30 | Magura | 52 | 0.83333
Ullon | 52 | 12:00 | Feni | 110 | 21:00 | Norail | 39 | 21:00
Hasnabad | 196 | 23:00 | Chowmuhani | 146 | 19:30 | Chuadanga | 84 | 1:00
Magbazar | 95 | 15:00 | Ashuganj | 54 | 23:00 | Barisal(N) | 40 | 0.875
Maniknagar | 106 | 11:00 | Daudkandi | 136 | 23:00 | Barisal (S) | 92 | 0.041667
Bangabhaban | 32 | 11:00 | B.Baria | 148 | 21:00 | Patuakhali | 111 | 0.041667
Narinda | 88 | 15:00 | Ramganj | 102 | 21:00 | Bhandaria | 50 | 20:00
Dhanmondi | 155 | 13:00 | Chaddagram | 36 | 19:00 | Borhan Uddin | 41 | 21:00
Lalbag | 90 | 13:00 | PHP | 9 | 17:00 | Ishurdi | 60 | 21:00
Madartek | 66 | 22:00 | Madunaghat | 52 | 20:00 | Ruppur Paromanobik | 2 | 9:00
Dhaka University |  |  | Hathazari | 93 | 0.79167 | Natore | 114 | 1:00
Fatullah | 27 | 0.45833 | Khulshi | 165 | 0.125 | Bogra | 163 | 22:00
Mirpur | 98 | 12:00 | Halishahar | 127 | 0.625 | Noagaon | 124 | 1:00
Kalyanpur | 87 | 14:00 | Baraulia | 140 | 0.041667 | Rajshahi | 144 | 21:00
Gulshan | 118 | 12:00 | Sikalbaha | 22 | 0.79167 | Rajshahi New | 11 | 23:00
Uttara | 74 | 12:00 | Dohazari | 84 | 0.83333 | C.Nawabganj | 69 | 21:00
Uttara New | 28 | 12:00 | Cox'sbazar | 85 | 0.79167 | Amnura | 48 | 22:00
Kamrangirchar | 86 | 12:00 | Chandraghona | 30 | 0.8125 | Pabna | 113 | 20:00
Savar | 126 | 14:00 | Kaptai | 4.2 | 0.79167 | Shahjadpur | 100 | 20:00
Bhasantec | 141 | 12:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 102 | 21:00
Agargaon | 65 | 12:00 | Bakulia | 94 | 0.625 | Niyamatpur | 58 | 21:00
Satmosjid | 95 | 12:00 | Julda | 20 | 0.25 | Joypurhat | 43 | 20:00
Tongi | 115 | 0.875 | TK chemical | 16 | 0.79167 | Sherpur(Bogura) | 48 | 20:00
Kabirpur | 226 | 12:00 | Modern Steel | 15 | 0.45833 | Mohastangor | 58 | 20:00
Basundhara | 125 | 15:00 | Shahmirpur | 27 | 0.041667 | Rangpur | 150 | 20:00
Manikganj | 68 | 21:00 | Khagrachhari | 22 | 0.8125 | Lalmonirhat | 58 | 22:00
Joydevpur | 170 | 19:30 | Matarbari | 29 | 0.16667 | Saidpur | 103 | 20:00
New Tongi | 99 | 15:00 | Baroiar Hat | 34 | 0.77083 | Purbasadipur | 107 | 20:00
Korda | 216 | 17:00 | Rangamati | 12 | 0.79167 | Thakurgaon | 81 | 20:00
Dhamrai | 86 | 21:00 | Abul Khair 230 | 145 | 0.54167 | Palashbari | 119 | 1:00
Rajendrapur | 96 | 21:00 | BSRM | 144 | 0.125 | Barapukuria | 47 | 22:00
Valuka | 104 | 15:00 | GPH Ispat | 65 | 0.79167 | Panchagar | 50 | 21:00
Tangail | 179 | 21:00 | Goalpara | 27 | 0.041667 | Joldhaka | 31 | 21:00
Mymensing | 216 | 21:00 | Central s/s | 78 | 20:00 | Kurigram | 56 | 19:30
Kishorganj | 148 | 21:00 | Noapara | 58 | 21:00
Netrokona | 104 | 22:00 | Jessore | 110 | 20:00
Jamalpur | 136 | 23:00 | Benapol | 40 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-07-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 397 | 1:00 | 389 | 12:00 | Kaliakoir | 378 | 0.041667 | 368 | 0.41667
| Bheramara | 397 | 6:00 | 386 | 21:00 | Bhulta | 392 | 0.041667 | 382 | 0.5
| Ashuganj(N) | 398 | 1:00 | 388 | 15:00 | Gopalganj | 419 | 0.33333 | 390 | 0.95833
| Payra | 418 | 7:00 | 401 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 232 | 8:00 | Comilla (N) | 235 | 1:00 | 230 | 16:00
| Ishurdi | 235 | 5:00 | 224 | 20:00 | Hathazari | 226 | 19:30 | 221 | 15:00
| Ashuganj | 238 | 19:00 | 232 | 23:00 | Megnaghat | 232 | 5:00 | 228 | 10:00
| Serajganj | 232 | 18:00 | 225 | 22:00 | Fenchuganj | 238 | 6:00 | 234 | 1:00
| Baghabari | 242 | 19:00 | 235 | 19:30 | Siddhirganj | 231 | 4:00 | 226 | 14:00
| Barapukuria | 234 | 19:00 | 221 | 21:00 | Maniknagar | 230 | 6:00 | 224 | 15:00
| Bogra | 227 | 18:00 | 222 | 17:00 | Agargaon | 227 | 1:00 | 220 | 10:00
| Rajshahi | 232 | 18:00 | 219 | 21:00 | Barisal | 244 | 3:00 | 233 | 24:00
| Khulna South | 227 | 18:00 | 211 | 2:00 | AKSML | 224 | 2:00 | 218 | 10:00
| Rampura | 229 | 1:00 | 221 | 14:00 | BSRM | 226 | 19:30 | 219 | 10:00
| Haripur | 230 | 1:00 | 225 | 10:00 | Bibiyana | 237 | 17:00 | 232 | 12:00
| Hasnabad | 230 | 8:00 | 223 | 15:00 | Bhulta | 232 | 1:00 | 226 | 10:00
| Shyampur | 226 | 1:00 | 220 | 10:00 | Ashuganj (S) | 237 | 4:00 | 232 | 10:00
| Aminbazar | 228 | 2:00 | 222 | 12:00 | Kaliakoir | 231 | 3:00 | 222 | 10:00
| Tongi | 230 | 4:00 | 222 | 9:00 | GPH | 224 | 3:00 | 218 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 132 | 19:00 | 128 | 16:00 | Hathazari | 135 | 0.8125 | 131 | 0.375
| Munsiganj | 134 | 6:00 | 129 | 17:00 | Khulshi | 134 | 0.79167 | 129 | 0.41667
| Sonargaon | 131 | 19:30 | 128 | 3:00 | Halishahar | 138 | 0.8125 | 130 | 0.33333
| Shyampur | 136 | 7:00 | 132 | 10:00 | Baraulia | 136 | 0.79167 | 131 | 0.5
| Bhulta | 126 | 6:00 | 121 | 12:00 | Sikalbaha | 138 | 19:00 | 132 | 0.70833
| Madanganj | 131 | 3:00 | 127 | 15:00 | Dohazari | 136 | 19:00 | 129 | 0.75
| Shitalakhya | 142 | 1:00 | 137 | 11:00 | Cox'sbazar | 130 | 0.33333 | 121 | 0.875
| Rahim steal | 132 | 5:00 | 129 | 16:00 | Chandraghona | 136 | 0.8125 | 132 | 0.20833
| Matuail | 132 | 19:00 | 128 | 16:00 | Kaptai | 135 | 1:00 | 132 | 0.16667
| Ghorasal | 138 | 1:00 | 136 | 13:00 | A. Khaer Stl. | 133 | 0.041667 | 130 | 7:00
| Narsinghdi | 128 | 7:00 | 123 | 23:00 | Bakulia | 137 | 0.8125 | 130 | 0.70833
| Haripur (SBU) | 132 | 1:00 | 129 | 15:00 | Julda | 138 | 0.79167 | 131 | 0.70833
| Ullon | 135 | 3:00 | 129 | 15:00 | TK Chemical | 137 | 0.77083 | 132 | 8:00
| Hasnabad | 137 | 17:00 | 135 | 11:00 | Modern Steel | 134 | 0.83333 | 130 | 0.33333
| Magbazar | 135 | 3:00 | 128 | 15:00 | Shahmirpur | 136 | 0.83333 | 131 | 0.70833
| Maniknagar | 135 | 3:00 | 129 | 11:00 | Khagrachhari | 135 | 0.91667 | 131 | 0.625
| Bangabhaban | 135 | 3:00 | 129 | 11:00 | Matarbari | 132 | 0.33333 | 125 | 0.70833
| Narinda | 135 | 3:00 | 129 | 11:00 | Baroiar Hat | 130 | 0.041667 | 126 | 0.625
| Dhanmondi | 135 | 3:00 | 129 | 15:00 | Rangamati | 135 | 0.79167 | 131 | 17:00
| Lalbag | 138 | 1:00 | 132 | 21:00 | Goalpara S/S | 137 | 18:30 | 124 | 10:00
| Madartek | 134 | 1:00 | 128 | 15:00 | Khulna Central S/S | 136 | 0.083333 | 124 | 10:00
| Dhaka University |  |  |  |  | Noapara | 134 | 18:00 | 124 | 9:00
| Fatuiiah | 136 | 0.041667 | 132 | 9:00 | Jessore | 131 | 18:00 | 119 | 21:00
| Mirpur | 133 | 6:00 | 125 | 11;00 | Benapol | 132 | 18:30 | 118 | 1:00
| Kalyanpur | 132 | 6:00 | 126 | 10:00 | Jhenida | 128 | 18:30 | 112 | 21:00
| Gulshan | 133 | 6:00 | 129 | 10:00 | Bottail | 133 | 0.75 | 123 | 20:00
| Uttara | 131 | 6:00 | 125 | 11;00 | G.K Project | 139 | 18:00 | 133 | 20:00
| Uttara New | 131 | 6:00 | 127 | 11;00 | Faridpur | 135 | 0.33333 | 122 | 20:00
| Kamrangirchar | 134 | 6:00 | 126 | 11;00 | Madaripur | 138 | 9:00 | 130 | 1:00
| Savar | 132 | 6:00 | 127 | 11;00 | Shariyatpur S/S | 139 | 0.33333 | 127 | 22:00
| Bhasantec | 132 | 6:00 | 129 | 11;00 | Gopalganj | 140 | 0.33333 | 126 | 22:00
| Agargaon | 133 | 6:00 | 128 | 11;00 | Bagerhat | 137 | 1:00 | 123 | 9:00
| Satmosjid | 133 | 6:00 | 127 | 10:00 | Mongla | 133 | 0.77083 | 117 | 10:00
| Tongi | 138 | 0.16667 | 130 | 9:00 | Satkhira | 135 | 0.75 | 125 | 21:00
| Kabirpur | 136 | 9:00 | 124 | 11:00 | Gallamari | 137 | 0.75 | 126 | 10:00
| Basundhara | 134 | 8:00 | 128 | 15:00 | Magura | 127 | 18:30 | 110 | 21:00
| Manikganj | 140 | 1:00 | 130 | 9:00 | Norail | 125 | 0.75 | 107 | 21:00
| Joydevpur | 141 | 19:00 | 134 | 13:00 | Chuadanga | 124 | 0.75 | 102 | 21:00
| New Tongi | 137 | 0.041667 | 126 | 10:00 | Barisal(N) | 138 | 3:00 | 132 | 20:00
| Kodda | 140 | 1:00 | 121 | 0.5 | Barisal (S) | 137 | 2:00 | 130 | 21:00
| Dhamrai | 132 | 19:00 | 124 | 21:00 | Patuakhali(S) | 134 | 0.33333 | 125 | 21:00
| Rajendrapur | 134 | 1:00 | 120 | 12:00 | Bhandaria | 135 | 0.29167 | 125 | 1:00
| Valuka | 126 | 17:00 | 113 | 1:00 | Ishurdi | 136 | 5:00 | 130 | 20:00
| Tangail | 134 | 7:00 | 125 | 21:00 | Ruppur Paromanobik | 135 | 3:00 | 130 | 20:00
| Mymensing | 130 | 17:00 | 116 | 20:00 | Natore | 135 | 19:00 | 125 | 21:00
| Kishorganj | 130 | 17:00 | 118 | 22:00 | Bogra | 135 | 19:00 | 123 | 21:00
| Netrokona | 128 | 17:00 | 112 | 20:00 | Noagaon | 130 | 19:00 | 118 | 21:00
| Jamalpur | 138 | 18:30 | 126 | 7:00 | Rajshahi | 133 | 18:00 | 124 | 21:00
| Sherpur | 137 | 17:00 | 126 | 0.33333 | Rajshahi New | 134 | 19:00 | 124 | 21:00
| Srimongal | 137 | 6:00 | 132 | 0.041667 | C.Nawabganj | 132 | 19:00 | 122 | 21:00
| Shahjibazar | 134 | 6:00 | 129 | 0.875 | Amnura | 134 | 19:00 | 123 | 21:00
| Fenchuganj | 136 | 9:00 | 131 | 0.041667 | Pabna | 134 | 18:30 | 127 | 20:00
| Khulawara | 135 | 8:00 | 129 | 0.041667 | Shahjadpur | 136 | 17:00 | 132 | 21:00
| Sylhet | 132 | 7:00 | 127 | 0.041667 | Serajganj | 134 | 19:00 | 126 | 20:00
| Chatak | 131 | 8:00 | 125 | 1:00 | Niyamatpur | 128 | 19:00 | 115 | 21:00
| Sunamganj | 130 | 7:00 | 122 | 0.041667 | Joypurhat | 130 | 19:00 | 115 | 21:00
| Biani Bazar | 131 | 7:00 | 124 | 0.041667 | Sherpur(Bogura) | 135 | 19:00 | 123 | 21:00
| Comilla(s) | 127 | 6:00 | 120 | 19:30 | Mohastangor | 134 | 19:00 | 120 | 21:00
| Comilla(n) | 135 | 8:00 | 132 | 15:00 | Rangpur | 131 | 19:00 | 116 | 21:00
| Chandpur | 129 | 13:00 | 126 | 20:00 | Lalmonirhat | 124 | 6:00 | 110 | 22:00
| Feni | 128 | 22:00 | 127 | 17:00 | Saidpur | 130 | 6:00 | 112 | 20:00
| Chowmuhani | 126 | 7:00 | 121 | 17:00 | Purbasadipur | 126 | 6:00 | 104 | 21:00
| Ashuganj | 135 | 14:00 | 130 | 22:00 | Thakurgaon | 126 | 6:00 | 104 | 22:00
| Daudkandi | 131 | 8:00 | 126 | 23:00 | Palashbari | 129 | 19:00 | 115 | 21:00
| B.Baria | 132 | 7:00 | 125 | 21:00 | Barapukuria | 134 | 19:00 | 121 | 21:00
| Ramganj | 122 | 18:30 | 118 | 23:00 | Panchagar | 122 | 6:00 | 93 | 21:00
| Chaddagram | 130 | 19:00 | 127 | 14:00 | Joldhaka | 128 | 6:00 | 107 | 21:00
| PHP | 129 | 8:00 | 125 | 20:00 | Kurigram | 130 | 19:00 | 112 | 21:00
| Madanhat | 138 | 19:30 | 132 | 16:00

## L-Curve
Date | 2020-07-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 2 | 7579 | 3800 | 11379 |  |  |  | QF-LDC-12
0:30 | 212.5 | 7687.5 | 3615.5 | 11303 | Date: | 2020-07-05
1:00 | 423 | 7796 | 3431 | 11227
1:30 | 417 | 7634.5 | 3325.5 | 10960
2:00 | 411 | 7473 | 3220 | 10693
2:30 | 369.5 | 7405.5 | 3227 | 10632.5 | [5 empty] | Gen. at Eve. Peak | 11415 | 11415 MW (21:00 )
3:00 | 328 | 7338 | 3234 | 10572 | [6 empty] | 21:00
3:30 | 341 | 7299.5 | 3151.5 | 10451 | [5 empty] | Gen. at Day Peak | 9726.9 | 9726.9 MW (12:00 )
4:00 | 354 | 7261 | 3069 | 10330 | [6 empty] | 12:00
4:30 | 302.5 | 7108.5 | 3030 | 10138.5 | [5 empty] | Highest Generation | 11527
5:00 | 251 | 6956 | 2991 | 9947 | [6 empty] | 22:00
5:30 | 176 | 6662.75 | 2885.9 | 9548.65
6:00 | 101 | 6369.5 | 2780.8 | 9150.3
6:30 | 74.5 | 6154.65 | 2730.8 | 8885.45
7:00 | 48 | 5939.8 | 2680.8 | 8620.6
7:30 | 41.5 | 5953.95 | 2646.8 | 8600.75
8:00 | 35 | 5968.1 | 2612.8 | 8580.9
8:30 | 27.5 | 6175.7 | 2647.1 | 8822.8
9:00 | 20 | 6383.3 | 2681.4 | 9064.7
9:30 | 25.5 | 6565.2 | 2695.7 | 9260.9
10:00 | 31 | 6747.1 | 2710 | 9457.1
10:30 | 19.5 | 6750.4 | 2729.45 | 9479.85
11:00 | 8 | 6753.7 | 2748.9 | 9502.6
11:30 | 10 | 6811.85 | 2802.9 | 9614.75
12:00 | 12 | 6870 | 2856.9 | 9726.9
12:30 | 11 | 6847.5 | 2905.2 | 9752.7
13:00 | 10 | 6825 | 2953.5 | 9778.5
13:30 | 62 | 6873.95 | 2949 | 9822.95
14:00 | 114 | 6922.9 | 2944.5 | 9867.4
14:30 | 109 | 7051.25 | 2970.45 | 10021.7
15:00 | 104 | 7179.6 | 2996.4 | 10176
15:30 | 151 | 7108.15 | 2992.65 | 10100.8
16:00 | 198 | 7036.7 | 2988.9 | 10025.6
16:30 | 187.5 | 6733.9 | 2952.85 | 9686.75
17:00 | 177 | 6431.1 | 2916.8 | 9347.9
17:30 | 173.5 | 6211.3 | 2880.95 | 9092.25
18:00 | 170 | 5991.5 | 2845.1 | 8836.6
18:30 | 176 | 6209.75 | 2945.55 | 9155.3
19:00 | 182 | 6428 | 3046 | 9474
19:30 | 138 | 7400 | 3686 | 11086
20:00 | 112 | 7372 | 3807 | 11179 |  |  |  | Executive Engineer
20:30 | 96 | 7478.5 | 3818.5 | 11297 |  |  |  | Network Operation Division
21:00 | 80 | 7585 | 3830 | 11415
21:30 | 67 | 7613 | 3858 | 11471
22:00 | 54 | 7641 | 3886 | 11527 |  |  |  |  | Page 6 of 7
22:30 | 46 | 7611 | 3845.5 | 11456.5
23:00 | 38 | 7581 | 3805 | 11386
23:30 | 20 | 7580 | 3802.5 | 11382.5
24:00 | 2 | 7579 | 3800 | 11379
11415 MW (21:00 )
9726.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-07-05 |  | Energy | 244190309
[10 empty] | 2020-07-05 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4109 | 929 | 2218 | 2797 | 738 | 108 | 334 | 0 | 150
0:30 | 4063 | 922.5 | 2187 | 3099 | 443.5 | 106.5 | 330.5 | 0 | 153 | Date: | 2020-07-05
1:00 | 4017 | 916 | 2156 | 3401 | 149 | 105 | 327 | 0 | 156
1:30 | 4010.5 | 915.5 | 2173 | 3168.5 | 200.5 | 105 | 233 | 0 | 154 | [7 empty] | Total Energy | 244.1903 | Total Energy Gen 244.190 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 244.190 MKWHr
2:00 | 4004 | 915 | 2190 | 2936 | 252 | 105 | 139 | 0 | 152 | [7 empty] | Energy not Served | 0
2:30 | 4017 | 915.5 | 2190.5 | 2851.5 | 289.5 | 105 | 114.5 | 0 | 149 | [7 empty] | Energy Requirement | 244.1903
3:00 | 4030 | 916 | 2191 | 2767 | 327 | 105 | 90 | 0 | 146
3:30 | 4029.5 | 916 | 2194 | 2638 | 343 | 105 | 82.5 | 0 | 143 | [6 empty] | Shortage
4:00 | 4029 | 916 | 2197 | 2509 | 359 | 105 | 75 | 0 | 140
4:30 | 4088 | 915.5 | 2211.5 | 2275.5 | 369.5 | 105 | 37.5 | 0 | 136
5:00 | 4147 | 915 | 2226 | 2042 | 380 | 105 | 0 | 0 | 132
5:30 | 4000 | 915.5 | 2149 | 1848.5 | 405 | 105 | 0 | 0 | 125
6:00 | 3853 | 916 | 2072 | 1655 | 430 | 105 | 0 | 0 | 118
6:30 | 3838 | 916 | 1995 | 1482 | 430.5 | 106 | 0 | 0 | 116 |  |  |  |  | Coal
7:00 | 3823 | 916 | 1918 | 1309 | 431 | 107 | 0 | 0 | 114
7:30 | 3815.5 | 915.5 | 1879.5 | 1330 | 432.5 | 107.5 | 0 | 0 | 115 |  |  |  | Oil |  |  |  | ,
8:00 | 3808 | 915 | 1841 | 1351 | 434 | 108 | 0 | 0 | 116
8:30 | 3848 | 915 | 1894.5 | 1498 | 433 | 108.5 | 0 | 0 | 116
9:00 | 3888 | 915 | 1948 | 1645 | 432 | 109 | 0 | 0 | 116
9:30 | 3916.5 | 915.5 | 1975 | 1786.5 | 431 | 109 | 0 | 0 | 120
10:00 | 3945 | 916 | 2002 | 1928 | 430 | 109 | 0 | 0 | 124
10:30 | 3898.5 | 915.5 | 1998.5 | 1986.5 | 437.5 | 109.5 | 0 | 0 | 126
11:00 | 3852 | 915 | 1995 | 2045 | 445 | 110 | 0 | 0 | 128
11:30 | 3855.5 | 916 | 2031 | 2085.5 | 477 | 109 | 0 | 0 | 127
12:00 | 3859 | 917 | 2067 | 2126 | 509 | 108 | 0 | 0 | 126
12:30 | 3841 | 916.5 | 2002.5 | 2165 | 554.5 | 107.5 | 20.5 | 0 | 130
13:00 | 3823 | 916 | 1938 | 2204 | 600 | 107 | 41 | 0 | 134
13:30 | 3823 | 916 | 1938 | 2204 | 600 | 107 | 41 | 0 | 134
14:00 | 3823 | 916 | 1938 | 2204 | 600 | 107 | 41 | 0 | 134
14:30 | 3898 | 922.5 | 2024.5 | 2222.5 | 612 | 103.5 | 41 | 0 | 143
15:00 | 3973 | 929 | 2111 | 2241 | 624 | 100 | 41 | 0 | 152
15:30 | 3958.5 | 928.5 | 2051 | 2232 | 634 | 100.5 | 41 | 0 | 149
16:00 | 3944 | 928 | 1991 | 2223 | 644 | 101 | 41 | 0 | 146
16:30 | 3860 | 928.5 | 1884 | 2079 | 642.5 | 102.5 | 41 | 0 | 143
17:00 | 3776 | 929 | 1777 | 1935 | 641 | 104 | 41 | 0 | 140
17:30 | 3699 | 929 | 1670 | 1867.5 | 642.5 | 104.5 | 46 | 0 | 130
18:00 | 3622 | 929 | 1563 | 1800 | 644 | 105 | 51 | 0 | 120
18:30 | 3599 | 929 | 1579.5 | 1975.5 | 650 | 105.5 | 178.5 | 0 | 137
19:00 | 3576 | 929 | 1596 | 2151 | 656 | 106 | 306 | 0 | 154
19:30 | 3871 | 929 | 1903 | 3018 | 697 | 105 | 409 | 0 | 154
20:00 | 3862 | 930 | 2002 | 2960 | 745 | 108 | 418 | 0 | 154
20:30 | 3970.5 | 930 | 2095.5 | 2899.5 | 741.5 | 108.5 | 397.5 | 0 | 154
21:00 | 4079 | 930 | 2189 | 2839 | 738 | 109 | 377 | 0 | 154
21:30 | 4118 | 929.5 | 2217 | 2830 | 738 | 109 | 372.5 | 0 | 157
22:00 | 4157 | 929 | 2245 | 2821 | 738 | 109 | 368 | 0 | 160
22:30 | 4133.5 | 929 | 2227.5 | 2809 | 737.5 | 108.5 | 353.5 | 0 | 158
23:00 | 4110 | 929 | 2210 | 2797 | 737 | 108 | 339 | 0 | 156
23:30 | 4109.5 | 929 | 2214 | 2797 | 737.5 | 108 | 336.5 | 0 | 153 | Max Temp. in Dhaka |  | 31.4° C
24:00 | 4109 | 929 | 2218 | 2797 | 738 | 108 | 334 | 0 | 150
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 244.190 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 244.190 MKWHr
Note on W13: Author:

## Generation
g | 2020-07-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 70 | 70 | 70 | 70 | 70 | 70 | 72 | 73 | 74 | 74 | 75 | 73 | 72 | 68 | 65 | 66 | 69 | 70 |  | 71 | 70 | 73 | 74 | 74 | 73 | 73 | 1599038
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 1 | 10 | 15 | 8 |  |  | 0 | 26200
| Teknaf 20MW PP (Solartech) | [5 empty] | 0.1 | 0.7 | 4.1 | 6.7 | 0 |  |  | 6 | 3.4 |  |  |  | 0.8 | [8 empty] | 16200
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 139 | 139 | 139 | 139 | 145 | 140 | 142 | 142 | 142 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 104 | 104 |  | 104 | 140 | 140 | 140 | 140 | 140 | 140 | 3283767
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [18 empty] | 97 | 102 | 102 | 102 | 102 | 102 | 102 | 555498
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | [23 empty] | 0 | 42654
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 332 | 332 | 333 | 331 | 330 | 260 | 260 | 260 | 260 | 260 | 330 | 328 | 300 | 326 | 327 | 327 | 250 | 250 |  | 250 | 250 | 300 | 300 | 300 | 280 | 300 | 7246258
18 | Kodda 300 MW PP Unit-2 (Summit) | 270 | 275 | 286 | 286 | 214 | 164 | 95 | 95 | 105 | 185 | 215 | 265 | 268 | 268 | 269 | 285 | 245 | 245 |  | 245 | 250 | 270 | 286 | 286 | 286 | 283 | 5735779
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 720000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 |  | 250 | 301 | 300 | 300 | 300 | 300 | 300 | 7074818
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1959210
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 680832
33 | Ashuganj 225 MW CCPP | 192 | 189 | 187 | 193 | 175 | 208 | 197 | 191 | 201 | 206 | 184 | 182 | 184 | 197 | 186 | 181 | 181 | 181 |  | 154 | 182 | 182 | 192 | 193 | 190 | 183 | 4610000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 300 | 275 | 275 | 275 | 285 | 305 | 255 | 255 | 255 | 270 | 320 | 285 | 285 | 255 |  | 260 | 285 | 260 | 290 | 290 | 285 | 280 | 6857000
| Ashuganj 450 MW CCPP(North) | 320 | 320 | 320 | 320 | 340 | 295 | 295 | 295 | 295 | 310 | 260 | 260 | 270 | 275 | 260 | 260 | 260 | 260 |  | 290 | 310 | 310 | 320 | 330 | 320 | 320 | 7559300
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 42 | 49 | 50 | 373440
36 | Chandpur 150 MW CCPP | 80 | 89 | 84 | 92 | 90 | 87 | 82 | 80 | 90 | 92 | 80 | 84 | 90 | 91 | 90 | 84 | 80 | 80 |  | 90 | 91 | 91 | 90 | 91 | 91 | 90 | 2073390
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 323 | 323 | 325 | 322 | 359 | 328 | 324 | 322 | 334 | 336 | 341 | 327 | 323 | 326 | 352 | 325 | 323 | 299 |  | 294 | 325 | 324 | 338 | 335 | 326 | 328 | 8045368
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 360 | 420 | 390 | 330 | 300 |  | 300 | 300 | 300 | 420 | 420 | 420 | 420 | 9052500
41 | Haripur 360MW CCPP(HPL) | 357 | 353 | 354 | 356 | 354 | 309 | 280 | 280 | 300 | 351 | 351 | 351 | 300 | 300 | 350 | 347 | 250 | 250 |  | 250 | 300 | 320 | 353 | 352 | 353 | 352 | 7763000
42 | RPCL 210MW CCPP | 157 | 157 | 157 | 157 | 157 | 158 | 157 | 158 | 156 | 153 | 153 | 153 | 138 | 120 | 121 | 123 | 124 | 142 |  | 142 | 142 | 142 | 126 | 126 | 142 | 142 | 3358480
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 89 | 91 | 91 | 91 | 89 | 89 | 90 | 90 | 90 |  | 90 | 91 | 90 | 91 | 91 | 91 | 91 | 2127000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 735600
46 | Shajibazar 330 MW CCPP | 305 | 301 | 304 | 309 | 318 | 302 | 302 | 302 | 308 | 309 | 305 | 302 | 307 | 312 | 310 | 306 | 301 | 302 |  | 303 | 306 | 306 | 309 | 307 | 308 | 304 | 6947000
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 61 | 61 | 61 | 61 | 60 | 59 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 40 |  | 40 | 61 | 40 | 40 | 40 | 40 | 40 | 1314336
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 70 | 70 | 70 | 70 | 71 | 71 | 71 | 71 | 70 | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 40 |  | 40 | 76 | 76 | 76 | 76 | 76 | 76 | 1674240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [14 empty] | 30 | 80 | 80 | 80 |  | 80 | 80 | 50 | 151 | 150 | 150 | 150 | 912420
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 7 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 204840
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 44 | 47 | 14 |  | 14 | 39 | 47 | 47 | 47 | 47 | 47 | 1056000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 23 |  | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 530040
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 305 | 310 | 300 | 310 | 280 | 285 | 305 | 315 | 310 | 310 | 290 | 310 | 320 | 285 | 285 | 240 |  | 240 | 270 | 290 | 310 | 315 | 300 | 310 | 7327700
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1167063
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 398496
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 386100
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 463716
63 | Impoprt (Tripura) | 156 | 152 | 146 | 140 | 132 | 118 | 114 | 116 | 116 | 124 | 128 | 126 | 134 | 146 | 152 | 146 | 140 | 120 |  | 154 | 154 | 154 | 154 | 160 | 156 | 150 | 3365760
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 42 | 42 | 41 | 35 | 7 | 4 | 2 | 2 | 2 | 7 | 5 | 3 | 5 | 7 | 10 |  | 27 | 29 | 34 | 16 | 38 | 40 | 41 | 521280
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482832
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  |  |  |  | 8 | 10 | 10 | 10 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 211140
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 30 | 32 | 32 | 618800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 9 | 9 | 21 | 21 |  | 21 | 15 | 21 | 21 | 21 | 21 | 21 | 437260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 10 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 29 | 29 | 28 | 10 | 29 | 29 | 29 | 29 | 29 |  | 29 | 24 | 29 | 29 | 29 | 29 | 29 | 625140
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 770900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 778600
73 | Ghorashal 108MW PP (Regent) | 99 | 100 | 100 | 99 | 100 | 97 | 54 | 51 | 53 | 53 | 54 | 94 | 94 | 94 | 90 | 90 | 94 | 54 |  | 54 | 97 | 97 | 97 | 97 | 97 | 97 | 1985318
| Feni Lanka Power | 85 | 6 | [23 empty] | 0 | 145920
| Chowmuhani 113 MW | 105 | 104 | 104 | 104 | 104 | 88 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 55 | 8 | 8 |  | 12 | 46 | 46 | 70 | 103 | 104 | 113 | 1343160
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 82 | 82 | 75 | 73 | 68 | 70 | 73 | 70 | 40 | 40 |  | 42 | 65 | 76 | 82 | 82 | 82 | 82 | 1910400
78 | Gazipur 52 MW PP | 51 | [18 empty] | 6 | 36 |  |  |  |  | 0 | 90864
79 | Kodda 150MW PP | 115 | [18 empty] | 84 | 133 | 133 | 133 | 133 | 105 | 98 | 793440
80 | Jamalpur 95 MW PP(Powerpac) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 84 | 95 | 95 | 95 | 95 | 95 | 95 | 953280
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 8 | [15 empty] | 7 | 43 | [5 empty] | 205200
| Gazipur 100 MW PP | 105 | 52 | [6 empty] | 34 | 34 | 34 | 34 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 34 |  |  |  | 0 | 746412
| Kaptai 7 MW Solar PP | [5 empty] | 0.3 | 0.7 | 1.4 | 3.1 | 2.4 | 2.2 | 4.1 | 1.1 | 4.3 | 1.1 | 2.3 | 1.9 | 0.4 | [8 empty] | 28440
| Jodiac Power | 54 | 54 | 54 | 39 | [6 empty] | 14 | 30 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 |  |  |  | 0 | 725089
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 96 | 85 | 64 | 64 |  | 64 | 70 | 90 | 96 | 96 | 96 | 97 | 2233032
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 87 | 87 | [5 empty] | 4 | 50 | 62 | 82 | 85 | 100 | 100 | 100 | 100 | 100 | 82 |  | 40 | 40 | 35 |  |  |  | 0 | 1198983
86 | Meghnaghat CCPP(Summit) | 125 | 130 | 130 | 140 | 135 | 130 | 135 | 130 | 130 | 135 | 130 | 130 | 130 | 140 | 135 | 140 | 135 | 125 |  | 120 | 115 | 130 | 140 | 135 | 140 | 130 | 3204276
87 | Meghnaghat 100 MW(IEL) | [5 empty] | 1 | 59 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 75 | 41 | 41 |  | 45 | 100 | 97 | 100 | 100 | 100 | 100 | 1608960
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX) | 66 | 66 | 66 | 66 | 66 | 50 | 40 | 40 | 40 | 40 | 40 | 50 | 65 | 66 | 65 | 65 | 40 | 40 |  | 40 | 65 | 66 | 66 | 66 | 66 | 66 | 1381408
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 20 | 20 | [5 empty] | 29400
92 | Fenchuganj 44MW (Energyprima) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 41 | 43 | 47 | 44 | 44 | 42 | 44 | 45 | 25 |  | 25 | 35 | 43 | 48 | 48 | 48 | 48 | 1083168
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1020400
94 | Gagnagar 102 MW PP (Digital Power) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 90 | 90 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2230128
95 | Patenga 50MW PP (Baraka) | 18 | 18 | [17 empty] | 13 | 50 | 50 | 25 | 25 | 25 | 25 | 213600
96 | Chattogram 108 MW PP (ECPV) | 51 | 51 | 51 | [7 empty] | 11 | 11 | 30 | 45 | 45 | 24 | 11 | 11 |  | 42 | 88 | 75 |  |  |  | 0 | 513600
97 | Katpotti 52 MW PP (Sinha) | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 50 | 55 | 55 | 55 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 42 | 55 | 55 | 55 | 55 | 1117272
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1306067
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 130 | 110 | 110 |  | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 3315763
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.4 | 0.6 | 0.5 | 0.7 | 2.5 | 2.9 | 2.9 | 2.2 | 1.5 | 0.4 | 0.2 | 0.3 | [8 empty] | 13800
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 17 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1208880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 180 | 180 | 180 | 180 | 180 | 80 | 8 | 8 | 29 | 80 | 80 | 80 | 113 | 120 | 120 | 110 | 110 | 110 |  | 110 | 160 | 160 | 180 | 180 | 180 | 180 | 3120000
112 | Aurahati 100MW PP (Aggreko) | [9 empty] | 41 | 61 | 62 | 63 | 11 | 51 | 73 | 72 | [8 empty] | 0 | 408343
114 | Kodda 149 MW PP Unit-1 (Summit) | 127 | 127 | 127 | 129 | 107 | 93 | 95 | 97 | 109 | 112 | 112 | 112 | 83 | 95 | 94 | 123 | 128 | 130 |  | 130 | 130 | 130 | 129 | 130 | 130 | 130 | 2802240
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2331840
116 | Chandpur 200MW (Desh energy)
117 | Ashuganj 150MW PP (Midland) | 147 | 145 | 145 | 145 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 |  | 50 | 80 | 100 | 40 |  |  | 0 | 1144145
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 24 | 24 | 84 | 115 | 109 | 109 | 109 | 109 | 109 | 109 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2576400
| Anwara 300 MW PP (United) | 307 | 307 | 307 | 307 | 253 | 197 | 161 | 161 | 252 | 306 | 306 | 306 | 306 | 306 | 307 | 252 | 161 | 124 |  | 140 | 265 | 235 | 308 | 308 | 308 | 307 | 6297818
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2416320
120 | Eastern Zone Total | 7796 | 7473 | 7338 | 7261 | 6956 | 6369.5 | 5939.8 | 5968.1 | 6383.3 | 6747.1 | 6753.7 | 6870 | 6825 | 6922.9 | 7179.6 | 7036.7 | 6431.1 | 5991.5 |  | 6428 | 7400 | 7372 | 7585 | 7641 | 7581 | 7579 | 167832815
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 83 | 83 | 83 | 83 | 32 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 46 | 115 | 115 | 115 | 115 | 115 | 115 | 1200960
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 26 | [25 empty] | 42240
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 35 | 35 | 35 | 35 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 454080
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 16 | [15 empty] | 57 | 90 | 110 | 110 | 110 | 80 | 80 | 931104
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 77 | 77 | 77 | 77 | 75 | 74 | 75 | 75 | 77 | 77 | 77 | 76 | 75 | 76 | 76 | 77 | 76 | 76 |  | 53 | 75 | 76 | 78 | 78 | 78 | 77 | 1819685
| Bhola 225 MW CCPP | 65 | 68 | 68 | 68 | 67 | 69 | 67 | 64 | 69 | 68 | 68 | 68 | 67 | 67 | 66 | 67 | 63 | 50 |  | 50 | 65 | 68 | 68 | 68 | 69 | 69 | 1595000
140 | Bhola 33 MW PP (Venture) | 37 | 35 | 25 | 30 | 31 | 27 | 20 | 19 | 18 | 18 | 19 | 19 | 18 | 26 | 22 | 26 | 22 | 24 |  | 30 | 32 | 32 | 36 | 35 | 36 | 36 | 630143
141 | Noapara 100 MW PP (Bangla Trac) | 70 | [19 empty] | 85 | 85 | 98 | 99 | 99 | 99 | 581760
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | 40 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 601125
143 | Gopalganj 100 MW Peaking PP | 37 | 7 | [15 empty] | 10 |  | 10 | [6 empty] | 80384
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | [18 empty] | 7 | 17 | 17 | 15 | 15 | 15 | 15 | 289152
146 | Bheramara HVDC | 916 | 915 | 916 | 916 | 915 | 916 | 916 | 915 | 915 | 916 | 915 | 917 | 916 | 916 | 929 | 928 | 929 | 929 |  | 929 | 929 | 930 | 930 | 929 | 929 | 929 | 21837091
147 | Bheramara 410 MW CCPP | 340 | 345 | 345 | 345 | 375 | 345 | 345 | 340 | 345 | 370 | 340 | 345 | 340 | 360 | 357 | 345 | 305 | 290 |  | 265 | 344 | 344 | 350 | 350 | 345 | 345 | 8511840
148 | Payra 1320 MW |  | 103 | 178 | 210 | 231 | 281 | 282 | 285 | 283 | 281 | 296 | 360 | 450 | 454 | 474 | 494 | 491 | 494 |  | 506 | 547 | 595 | 588 | 588 | 587 | 588 | 9514500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3675100
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 60 | 60 | 60 | 55 | 50 | 1460000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 187 | 190 | 184 | 203 | 167 | 152 | 144 | 156 | 158 | 160 | 182 | 186 | 151 | 164 | 184 | 183 | 158 |  | 138 | 132 | 132 | 155 | 198 | 191 | 193 | 4333155
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 185 | 189 | 183 | 198 | 170 | 160 | 156 | 167 | 170 | 172 | 170 | 184 | 183 | 195 | 179 | 175 | 163 |  | 130 | 130 | 130 | 166 | 190 | 187 | 185 | 4441336
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 383 | 417 | 407 | 401 | 409 | 374 | 378 | 329 | 366 | 366 | 358 | 376 | 340 | 339 | 341 | 315 | 301 | 280 |  | 312 | 374 | 410 | 411 | 410 | 380 | 379 | 8928181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 497520
163 | Bogura 20 MW PP (Energyprima) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 8 | 8 |  | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 199980
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 |  | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 223686
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 13 | 33 | 39 |  |  |  |  | 38290
168 | Santahar 50 MW Peaking PP | 33 | 33 | [17 empty] | 12 | 31 | 34 | 34 | 26 | 25 | 26 | 226299
169 | Natore 52 MW PP (Rajlanka) | 52 | [18 empty] | 47 | 52 | 52 | 52 | 52 | 52 | 52 | 352252
170 | Chapainawabganj 100 MW Peaking PP | 99 | 99 | 90 | 75 | [8 empty] | 41 | 41 | 41 | 41 | 41 | 41 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1164864
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 112 | 112 | 112 | 70 | 35 | [14 empty] | 27 | 108 | 108 | 111 | 111 | 111 | 111 | 1075776
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [20 empty] | 10 | 10 | 8 | 7 | 7 | 8 | 48000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 80 | 41 | 35 | 35 | 35 | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 |  | 45 | 113 | 111 | 113 | 113 | 113 | 113 | 1557120
177 | Sympa Solar Power 8MW | [5 empty] | 0.8 | 0.8 | 1.8 | 1.4 |  | 7.9 | 7.9 | 5.5 | 2.5 | 2.4 | 4.9 | 2.8 | 1.1 | [8 empty] | 46871
178
178