## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2020-07-13 | Monday
|  | Date (day): | 2020-07-13 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13628.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15235 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2020-07-12 | 2020-07-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 33 | 33 | 35 | 35 |  | 50 | Unit-2 Under maint
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 270 | 300 | 300
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 94 | 100 | 104
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 332 | 324 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 354 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 17/07/2020
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 60 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 335 | 300 | 305 | 305
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 81 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 45 | 45 | 45 |  | 10 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 205 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 65 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 328 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 76 | 68 | 76 | 76 |  | 26 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 52 | 52
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 65 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel Shortage.
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 25 | 55 | 55 | 55 |  | 25 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 286 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 20 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 100 | 0 | 80 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 105 | 115 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 35 | 52 | 100 | 100
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6119 | 5895 | 2949 | 3236 | 4000 | 4289 | 213 | 1046
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
40 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2.7 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 111 | 104 | 105 | 105 | 125 |  | Low water level & Unit-4 under maint.
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 144 | 140 | 150 | 150
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 100 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 64 | 100 | 102
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 30 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 44 | 80 | 100
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1.2 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 285 | 214 | 300 | 300
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 50 | 54
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 50 | 110
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| Chattogram area Total |  |  |  |  | 2326 | 2266 | 907.9 | 957 | 1432 | 1523 | 395 | 230
57 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas Shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 120 | 100 | 135
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas Shortage
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 141 | 45 | 110 | 110 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 320 | 360 | 360 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 290 | 360 | 360 |  |  | FGMO
61 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 40 | 30 | 34 |  | 11 | Engine problem
62 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 54 | 51 | 55
63 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 45 | 45 | 150 |  | Gas shortage
64 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 43 | 43 |  | 8 | Engine problem
65 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 150 | 150
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 87 | 96 | 95 | 95 |  | 68 | ST under shut down
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 144 | 154 | 173
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 21 | 21 | 21
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 113 | 113 | 113
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1324 | 1483 | 2064 | 2376 | 419 | 87
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 122 | 105 | 160 | 160 | 42 |  | Gas shortage
78 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
79 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
80 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0.6 | 0 | 1.6 | 0
81 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 170 | 200
82 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 291.6 | 437 | 563.6 | 592 | 42 | 0
83 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 91 | 91 | 89 | 89
84 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30
85 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 163 | 163 | 163
86 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 107 | 47 | 157 | 330
87 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 49 | 51 | 51
88 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 39 | 42 | 44 | 44
89 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
90 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 61 | 61 | 66
91 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 74 | 74 | 74 |  | 12 | Engine problem
92 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 150 | 150 | 150
93 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
94 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
95 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 25
96 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 341 | 341 |  |  | FGMO
97 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maintenance
98 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 0 | 0 | 0 | 0 | 0 | 0
| Sylhet Area Total |  |  |  |  | 2033 | 1988 | 941 | 1049 | 1223 | 1402 | 0 | 412
99 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 949 | 945 | 960 | 960
100 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 32 | 51 | 115 | 115
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 225
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 315 | 410 | 410
105 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 33 | 40 | 40 | 40
106 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 24 | 60 | 100
107 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105
108 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 0 | 0 | 100 | 105
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1354 | 1428 | 1790 | 2166 | 0 | 0
109 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 80 | 110
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 28 | 37 | 33 | 33
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 68 | 68 |  | 126 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 75 | 75 | 78 | 79 |  | 16 | Engine problem
113 | Payra 1320 MW |  | Coal | BCPCL | 1*622 | 622 | 622 | 498 | 531 | 600 | 660
| Barisal Area Total |  |  |  |  | 1054 | 1054 | 666 | 818 | 859 | 950 | 0 | 142
114 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
115 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
116 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 35 | 0 | 40
117 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage.
118 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
119 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 43 | 45
120 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | S/D for ST Under maint.
121 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 176 | 188 | 200 | 200 |  |  | FGMO
122 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 179 | 210 | 210 |  |  | FGMO
123 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 408 | 404 | 410 | 410 |  |  | FGMO
124 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 35
125 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
126 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 11 | 11
127 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
128 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 25 | 52 | 52
129 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
130 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 111 | 70 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 816 | 1208 | 1449 | 1662 | 431 | 0
133 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
134 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 |  |  | Coal Shortage.
135 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
136 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 12 |  | 8 | Engine problem
137 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 90 | 113
138 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 151.4 | 270 | 248 | 275 | 170 | 28
| Total |  |  |  |  | 20383 | 19892 | 9400.9 | 10886 | 13628.6 | 15235 | 1670 | 1945
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9073.6043 | 10507 | 13154.1154 | 14704.588
A. |  | 2020-07-12 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10886 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8021.1 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10886 | MW
3 | Day peak Generation : |  |  | 9400.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10507 | MW
4 | Evening peak Generation : |  |  | 10886 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 226.8442 | MKWHr | By Solar | 0.071326 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 133.4828 | MKWHr |  | By Oil: | 48.7416 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 16.1785 | MKWHr |  | By Hydro: | 2.5463 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1670 | MW | Dhaka | 3546 | 3546 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1945 | MW | Chittagong | 1132 | 1132 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3615 | MW | Khulna | 1324 | 1324 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1127.33 | MMCFD |  |  | Rajshahi | 1147 | 1147 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 157096666.648 | ii) Oil : | Taka | 351187221.42 | Comilla | 1015 | 1015 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 74783733 | Total | Taka | 583067621.068 | Mymensingh | 891 | 891 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.063 | MKWHr. | Sylhet | 399 | 399 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -15 | MW (E to W) at | 21:00 | hrs | Barisal | 325 | 325 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -87 | MW at | 20:00 | hrs | Rangpur | 728 | 728 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6° C |  |  | Total | 10507 | 10507 |  | 0
B. |  | 2020-07-13 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.7° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15235 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 4235 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 229.2197 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8140.7 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.7709 | MKWHr. | ii) HVDC Flow at Peak Time |  | 945 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0528 | MKWHr. | iii) Maximum HVDC Flow : |  | 950 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.95 |  | (b) Today: | 84.91 |  | (c) Rule Curve: |  | 85.92
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2020-07-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 33 | 0 | 0 | 10 | 300 | 94 | 71 | 345 | 353 |  | 0 | 0 | 285 | 100 | 80 | 47 | 329 | 0 | 155 | 0 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 40 | 0 | 100 | 0 | 340 | 310 | 142 | 8 | 95 | 28 | 54 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 140 | 142 | 95 | 22 | 0 | 91 | 30 | 50 | 39 | 0 | 106 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 315 | 24 | 8 | 0 | 150 | 0 | 0 | 70 | 0 | 133 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 84 | 100 | 0 | 0 |  | 948 | 0 | 375 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 34 | 48 | 0 | 0 | 40 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 76 | 0 | 176 | 0 | 416 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 472 |  | 6623 | 3220 | 9843 | 4076 | 948 | 1704 | 2189 | 621 | 106 | 59 | 140 | 0 | 0 | 83.5
2:00 | 33 | 0 | 0 | 40 | 300 | 94 | 71 | 351 | 353 |  | 0 | 0 | 280 | 100 | 80 | 47 | 329 | 0 | 155 | 0 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 100 | 0 | 335 | 305 | 143 | 8 | 95 | 28 | 55 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 136 | 157 | 95 | 22 | 0 | 91 | 30 | 50 | 39 | 0 | 106 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 315 | 24 | 8 | 0 | 45 | 0 | 0 | 50 | 0 | 116 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 55 | 100 | 0 | 0 |  | 950 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 48 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 77 | 0 | 177 | 0 | 414 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 472 |  | 6363 | 3111 | 9474 | 4112 | 950 | 1703 | 1846 | 621 | 106 | 0 | 136 | 0 | 0 | 83.59
3:00 | 33 | 0 | 0 | 65 | 300 | 94 | 71 | 350 | 354 |  | 0 | 0 | 285 | 100 | 80 | 47 | 330 | 0 | 175 | 0 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 100 | 0 | 335 | 305 | 142 | 8 | 95 | 28 | 55 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 126 | 158 | 95 | 22 | 0 | 91 | 30 | 50 | 39 | 0 | 105 | 52 | 76 | 0 | 101 | 18 | 0 | 10 | 315 | 24 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 79 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 949 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 33 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 75 | 0 | 190 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474 |  | 6127 | 3063 | 9190 | 4171 | 949 | 1683 | 1531 | 624 | 106 | 0 | 126 | 0 | 0 | 83.68
4:00 | 33 | 0 | 0 | 100 | 300 | 94 | 70 | 330 | 354 |  | 0 | 0 | 285 | 100 | 80 | 47 | 329 | 0 | 160 | 0 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 143 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 41 | 0 | 100 | 0 | 315 | 285 | 143 | 8 | 96 | 28 | 53 | 0 | 35 | 0 | 0 | 0 | 21 | 0 | 25 | 14 | 110 | 158 | 65 | 22 | 0 | 91 | 30 | 50 | 39 | 0 | 103 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 950 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 31 | 16 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 76 | 0 | 183 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474 |  | 5950 | 2993 | 8943 | 4086 | 950 | 1680 | 1388 | 623 | 106 | 0 | 110 | 0 | 0 | 83.77
5:00 | 33 | 0 | 0 | 100 | 300 | 91 | 70 | 339 | 320 |  | 0 | 0 | 285 | 50 | 48 | 15 | 329 | 0 | 140 | 0 | 100 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 100 | 0 | 320 | 290 | 140 | 8 | 95 | 25 | 54 | 0 | 35 | 0 | 0 | 0 | 21 | 5 | 25 | 14 | 116 | 158 | 32 | 22 | 0 | 91 | 30 | 50 | 39 | 0 | 108 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 950 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 27 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 76 | 0 | 185 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 |  | 5747 | 2983 | 8730 | 4111 | 950 | 1650 | 1174 | 623 | 106 | 0 | 116 | 0 | 0 | 83.86
6:00 | 33 | 0 | 0 | 110 | 300 | 94 | 70 | 332 | 283 |  | 0 | 0 | 255 | 20 | 48 | 15 | 250 | 0 | 140 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 100 | 0 | 310 | 280 | 130 | 8 | 90 | 25 | 54 | 0 | 35 | 0 | 0 | 0 | 21 | 5 | 25 | 14 | 110 | 160 | 32 | 22 | 0.1 | 91 | 30 | 50 | 39 | 0 | 100 | 52 | 76 | 0 | 50 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 0.4 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 950 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 78 | 0 | 181 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473 |  | 5328.5 | 2828 | 8156.5 | 3925 | 950 | 1506 | 936 | 623 | 106 | 0 | 110 | 0.5 | 0 | 83.95
7:00 | 33 | 0 | 0 | 110 | 250 | 94 | 70 | 330 | 270 |  | 0 | 0 | 280 | 7 | 48 | 15 | 250 | 0 | 80 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 146 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 33 | 0 | 100 | 0 | 315 | 290 | 108 | 8 | 95 | 25 | 52 | 0 | 35 | 0 | 0 | 0 | 21 | 5 | 25 | 14 | 100 | 158 | 32 | 22 | 0.1 | 91 | 30 | 50 | 39 | 0 | 102 | 52 | 76 | 0 | 50 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 20 | 0 | 0 | 0 | 0 | 83 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 1 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 950 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 80 | 0 | 181 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 |  | 5155.1 | 2866 | 8021.1 | 3804 | 950 | 1515 | 921 | 625 | 105 | 0 | 100 | 1.1 | 0 | 84
8:00 | 33 | 0 | 0 | 110 | 250 | 94 | 40 | 341 | 300 |  | 0 | 0 | 285 | 7 | 48 | 15 | 270 | 0 | 120 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 0 | 100 | 0 | 330 | 300 | 95 | 8 | 95 | 25 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 5 | 25 | 14 | 96 | 157 | 32 | 22 | 0.2 | 91 | 30 | 50 | 39 | 0 | 110 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 305 | 24 | 11 | 0 | 30 | 0 | 0 | 0 | 0 | 115 | 1.9 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 1.1 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 |  | 949 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 80 | 0 | 184 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 476 |  | 5313.2 | 2860.1 | 8173.3 | 3939 | 949 | 1469 | 986 | 626 | 105 | 0 | 96 | 3.3 | 0 | 84.04
9:00 | 33 | 0 | 0 | 110 | 280 | 94 | 40 | 342 | 264 |  | 0 | 0 | 333 | 13 | 48 | 30 | 325 | 0 | 160 | 0 | 15 | 40 | 0 | 9 | 0 | 0 | 0 | 5 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 100 | 0 | 305 | 280 | 140 | 8 | 86 | 25 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 25 | 15 | 102 | 157 | 32 | 22 | 0.2 | 91 | 30 | 49 | 39 | 0 | 101 | 52 | 76 | 0 | 100 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 65 | 0 | 0 | 0 | 12 | 115 | 2.1 | 100 | 0 | 0 | 0 | 45 | 0 | 0 | 4.4 | 276 | 0 | 0 | 0 | 3 | 100 | 0 | 0 |  | 949 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 73 | 0 | 185 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 455 |  | 5755.7 | 2865.1 | 8620.8 | 4037 | 949 | 1463 | 1351 | 605 | 107 | 0 | 102 | 6.8 | 0 | 84.08
10:00 | 33 | 0 | 0 | 110 | 280 | 93 | 40 | 323 | 275 |  | 0 | 0 | 332 | 50 | 48 | 30 | 300 | 0 | 0 | 0 | 50 | 76 | 0 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 19 | 33 | 33 | 0 | 0 | 73 | 35 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 100 | 0 | 300 | 300 | 138 | 8 | 96 | 30 | 20 | 0 | 35 | 0 | 0 | 0 | 18 | 8 | 0 | 15 | 116 | 122 | 32 | 20 | 0.5 | 91 | 30 | 47 | 39 | 0 | 100 | 40 | 76 | 0 | 100 | 18 | 0 | 10 | 260 | 24 | 11 | 0 | 155 | 52 | 50 | 0 | 102 | 115 | 2.6 | 100 | 0 | 0 | 0 | 73 | 0 | 0 | 5.1 | 293 | 37 | 0 | 0 | 110 | 100 | 0 | 0 |  | 950 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 76 | 0 | 167 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 452 |  | 6163.2 | 2857.2 | 9020.4 | 3758 | 950 | 1443 | 2035 | 602 | 108 | 0 | 116 | 8.4 | 0 | 84.12
11:00 | 33 | 0 | 0 | 110 | 280 | 91 | 40 | 339 | 304 |  | 0 | 0 | 330 | 50 | 48 | 30 | 300 | 0 | 0 | 0 | 50 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 0 | 0 | 75 | 35 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2 | 0 | 100 | 0 | 280 | 325 | 140 | 8 | 87 | 30 | 20 | 0 | 35 | 0 | 0 | 0 | 18 | 8 | 0 | 15 | 132 | 122 | 32 | 20 | 0.7 | 90 | 30 | 47 | 39 | 0 | 108 | 40 | 76 | 0 | 150 | 18 | 0 | 9 | 300 | 24 | 11 | 0 | 192 | 53 | 50 | 0 | 101 | 108 | 1.4 | 100 | 0 | 0 | 0 | 115 | 1 | 0 | 1.8 | 300 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 950 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 75 | 0 | 170 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 450 |  | 6402.9 | 2872.4 | 9275.3 | 3788 | 950 | 1510 | 2181 | 600 | 110 | 0 | 132 | 4.3 | 0 | 84.16
12:00 | 33 | 0 | 0 | 110 | 300 | 94 | 40 | 332 | 335 |  | 0 | 0 | 335 | 60 | 48 | 30 | 300 | 0 | 0 | 0 | 65 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 75 | 36 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 100 | 0 | 280 | 335 | 141 | 8 | 87 | 30 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 0 | 19 | 132 | 122 | 32 | 22 | 0.6 | 91 | 30 | 47 | 39 | 0 | 107 | 51 | 73 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 20 | 0 | 100 | 105 | 2.7 | 100 | 0 | 0 | 0 | 115 | 35 | 0 | 1.2 | 285 | 54 | 0 | 0 | 108 | 100 | 0 | 0 |  | 949 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 75 | 0 | 192 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 498 |  | 6413.5 | 2987.4 | 9400.9 | 3845 | 949 | 1537 | 2173 | 648 | 111 | 0 | 132 | 5.9 | 0 | 84.2
13:00 | 33 | 0 | 0 | 110 | 310 | 91 | 40 | 348 | 353 |  | 0 | 0 | 335 | 100 | 48 | 30 | 300 | 0 | 57 | 0 | 90 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 76 | 35 | 90 | 0 | 0 | 0 | 0 | 147 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 100 | 0 | 310 | 285 | 141 | 8 | 87 | 30 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 0 | 21 | 126 | 100 | 64 | 0 | 0.4 | 91 | 30 | 47 | 39 | 10 | 101 | 51 | 76 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 20 | 7 | 102 | 102 | 5.3 | 100 | 0 | 2 | 0 | 115 | 35 | 0 | 0.5 | 306 | 54 | 0 | 0 | 104 | 100 | 0 | 0 |  | 949 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 77 | 0 | 186 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 499 |  | 6591.2 | 2996.2 | 9587.4 | 3887 | 949 | 1562 | 2295 | 649 | 111 | 0 | 126 | 8.4 | 0 | 84.23
14:00 | 33 | 0 | 0 | 110 | 300 | 94 | 0 | 322 | 303 |  | 0 | 0 | 330 | 100 | 60 | 28 | 280 | 0 | 71 | 0 | 97 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 77 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 100 | 0 | 300 | 280 | 141 | 8 | 87 | 33 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 0 | 21 | 134 | 101 | 64 | 0 | 0.9 | 91 | 30 | 50 | 39 | 20 | 101 | 52 | 20 | 0 | 150 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 195 | 0 | 20 | 7 | 103 | 102 | 5.9 | 100 | 0 | 10 | 0 | 115 | 35 | 0 | 1.3 | 306 | 54 | 0 | 0 | 108 | 100 | 0 | 0 |  | 950 | 0 | 325 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 198 | 0 | 75 | 0 | 168 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 497 |  | 6446.1 | 2919.6 | 9365.7 | 3809 | 950 | 1385 | 2319 | 647 | 112 | 0 | 134 | 9.7 | 0 | 84.24
15:00 | 33 | 0 | 0 | 110 | 300 | 94 | 0 | 322 | 305 |  | 0 | 0 | 335 | 100 | 78 | 15 | 280 | 0 | 73 | 0 | 98 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 76 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 100 | 0 | 300 | 285 | 141 | 8 | 94 | 33 | 30 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 21 | 72 | 107 | 64 | 22 | 0.7 | 91 | 30 | 50 | 39 | 20 | 15 | 40 | 20 | 0 | 151 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 190 | 0 | 0 | 7 | 103 | 115 | 4.7 | 100 | 0 | 10 | 0 | 115 | 35 | 0 | 2.8 | 306 | 54 | 0 | 0 | 110 | 100 | 0 | 0 |  | 949 | 0 | 325 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 62 | 0 | 157 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8 | 0 | 499 |  | 6377.2 | 2854.8 | 9232 | 3743 | 949 | 1402 | 2296 | 648 | 111 | 0 | 72 | 11 | 0 | 84.29
16:00 | 33 | 0 | 0 | 110 | 300 | 94 | 0 | 335 | 355 |  | 0 | 0 | 332 | 100 | 64 | 15 | 280 | 0 | 77 | 0 | 98 | 76 | 0 | 75 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 100 | 0 | 295 | 285 | 142 | 8 | 97 | 30 | 30 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 106 | 107 | 64 | 22 | 0.4 | 91 | 30 | 50 | 39 | 20 | 0 | 53 | 74 | 0 | 150 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 7 | 0 | 99 | 1.3 | 100 | 0 | 10 | 0 | 115 | 35 | 0 | 1 | 306 | 17 | 0 | 0 | 105 | 100 | 0 | 0 |  | 950 | 0 | 330 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 52 | 0 | 174 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 499 |  | 6328.7 | 2878.2 | 9206.9 | 3770 | 950 | 1528 | 2092 | 648 | 109 | 0 | 106 | 3.9 | 0 | 84.32
17:00 | 33 | 0 | 0 | 110 | 300 | 94 | 0 | 330 | 353 |  | 0 | 0 | 334 | 80 | 64 | 22 | 280 | 0 | 73 | 0 | 90 | 76 | 0 | 40 | 0 | 0 | 0 | 35 | 35 | 35 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 74 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 0 | 100 | 0 | 310 | 285 | 32 | 8 | 90 | 30 | 30 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 102 | 107 | 40 | 22 | 0.2 | 91 | 30 | 50 | 42 | 20 | 0 | 53 | 74 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 195 | 0 | 0 | 7 | 0 | 99 | 1.7 | 100 | 0 | 10 | 0 | 115 | 35 | 0 | 0.3 | 180 | 17 | 0 | 0 | 46 | 100 | 0 | 0 |  | 950 | 0 | 325 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 8 | 63 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 53 | 0 | 169 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 497 |  | 5952.2 | 2813.8 | 8766 | 3663 | 950 | 1504 | 1779 | 646 | 109 | 10 | 102 | 3 | 0 | 84.35
18:00 | 33 | 0 | 0 | 110 | 280 | 94 | 0 | 324 | 352 |  | 0 | 0 | 333 | 74 | 64 | 40 | 280 | 0 | 78 | 0 | 70 | 68 | 0 | 40 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 100 | 0 | 280 | 290 | 39 | 8 | 94 | 38 | 54 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 112 | 124 | 40 | 22 | 0.1 | 91 | 33 | 20 | 10 | 40 | 10 | 52 | 10 | 0 | 151 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 7 | 0 | 96 | 0.1 | 100 | 0 | 10 | 0 | 115 | 35 | 0 | 0 | 179 | 17 | 0 | 0 | 46 | 100 | 0 | 0 |  | 950 | 0 | 327 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 8 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 52 | 0 | 167 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 499 |  | 5827.2 | 2881.2 | 8708.4 | 3675 | 950 | 1456 | 1740 | 648 | 107 | 20 | 112 | 0.4 | 0 | 84.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 33 | 0 | 0 | 110 | 280 | 94 | 0 | 337 | 353 |  | 0 | 0 | 335 | 74 | 64 | 40 | 280 | 0 | 78 | 0 | 70 | 68 | 70 | 40 | 0 | 0 | 4 | 53 | 55 | 55 | 22 | 25 | 20 | 33 | 17 | 0 | 0 | 70 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 85 | 0 | 22 | 3 | 17 | 15 | 0 | 100 | 0 | 290 | 300 | 36 | 8 | 96 | 36 | 54 | 0 | 35 | 0 | 33 | 7 | 21 | 11 | 33 | 21 | 144 | 123 | 88 | 22 | 0 | 91 | 30 | 20 | 30 | 90 | 8 | 62 | 74 | 0 | 150 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 205 | 0 | 0 | 32 | 0 | 108 | 0 | 100 | 0 | 23 | 0 | 115 | 37 | 5 | 0 | 179 | 24 | 0 | 0 | 46 | 100 | 0 | 0 |  | 950 | 0 | 325 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 31 | 80 | 0 | 0 | 0 | 50 | 5 | 50 | 0 | 8 | 22 | 25 | 26 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 76 | 0 | 174 | 0 | 403 | 0 | 0 | 15 | 0 | 31 | 0 | 0 | 0 | 498 |  | 6449 | 3284 | 9733 | 3710 | 950 | 1636 | 2200 | 647 | 105 | 341 | 144 | 0 | 0 | 84.41
19:30 | 33 | 0 | 0 | 110 | 280 | 94 | 0 | 343 | 354 |  | 0 | 0 | 330 | 100 | 64 | 40 | 280 | 0 | 205 | 0 | 90 | 68 | 100 | 40 | 0 | 0 | 18 | 53 | 55 | 55 | 22 | 25 | 26 | 33 | 17 | 0 | 0 | 69 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 85 | 0 | 45 | 22 | 17 | 19 | 0 | 100 | 0 | 310 | 280 | 36 | 45 | 86 | 40 | 54 | 0 | 35 | 0 | 40 | 25 | 21 | 11 | 33 | 21 | 148 | 124 | 95 | 22 | 0 | 91 | 30 | 47 | 42 | 100 | 6 | 62 | 74 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 260 | 0 | 0 | 90 | 0 | 115 | 0 | 100 | 0 | 70 | 0 | 115 | 70 | 17 | 0 | 201 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 950 | 0 | 325 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 34 | 80 | 0 | 0 | 0 | 50 | 12 | 100 | 0 | 8 | 47 | 25 | 26 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 76 | 0 | 177 | 0 | 377 | 0 | 0 | 50 | 0 | 99 | 0 | 0 | 0 | 524 |  | 7145 | 3510 | 10655 | 3856 | 950 | 1684 | 2780 | 673 | 104 | 460 | 148 | 0 | 0 | 0
20:00 | 33 | 0 | 0 | 110 | 280 | 94 | 0 | 332 | 354 |  | 0 | 0 | 250 | 90 | 64 | 37 | 331 | 0 | 178 | 0 | 90 | 68 | 90 | 0 | 0 | 0 | 18 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 69 | 35 | 90 | 0 | 0 | 0 | 0 | 142 | 0 |  | 0 | 0 | 85 | 0 | 44 | 24 | 17 | 22 | 0 | 120 | 0 | 310 | 285 | 40 | 45 | 85 | 40 | 55 | 0 | 35 | 0 | 41 | 25 | 21 | 11 | 33 | 21 | 150 | 121 | 95 | 22 | 0 | 91 | 30 | 47 | 42 | 100 | 30 | 62 | 74 | 0 | 151 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 283 | 0 | 0 | 80 | 0 | 115 | 0 | 100 | 0 | 70 | 0 | 115 | 70 | 0 | 0 | 214 | 54 | 0 | 0 | 88 | 100 | 0 | 0 |  | 947 | 0 | 326 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 36 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 8 | 48 | 25 | 27 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 180 | 0 | 75 | 0 | 171 | 0 | 352 | 0 | 0 | 75 | 0 | 90 | 0 | 0 | 0 | 535 |  | 7072 | 3581 | 10653 | 3935 | 947 | 1659 | 2688 | 684 | 104 | 486 | 150 | 0 | 0 | 84.45
21:00 | 33 | 0 | 0 | 110 | 270 | 94 | 0 | 324 | 354 |  | 0 | 0 | 300 | 100 | 81 | 45 | 328 | 0 | 205 | 0 | 100 | 68 | 65 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 69 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 64 | 0 | 44 | 0 | 17 | 30 | 0 | 120 | 0 | 320 | 290 | 45 | 45 | 96 | 40 | 54 | 0 | 35 | 0 | 0 | 25 | 21 | 11 | 33 | 21 | 144 | 105 | 95 | 22 | 0 | 91 | 30 | 49 | 42 | 163 | 47 | 61 | 74 | 0 | 150 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 100 | 0 | 115 | 0 | 100 | 0 | 70 | 0 | 115 | 52 | 0 | 0 | 214 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 945 | 0 | 315 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 37 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 45 | 25 | 27 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 8 | 0 | 0 | 188 | 0 | 75 | 24 | 179 | 0 | 404 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 531 |  | 7162 | 3724 | 10886 | 3974 | 945 | 1778 | 2867 | 680 | 104 | 394 | 144 | 0 | 0 | 84.46
22:00 | 33 | 0 | 0 | 110 | 270 | 94 | 0 | 328 | 353 |  | 0 | 0 | 295 | 100 | 81 | 37 | 329 | 0 | 200 | 0 | 92 | 68 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 44 | 0 | 17 | 30 | 0 | 120 | 0 | 310 | 280 | 111 | 45 | 94 | 40 | 54 | 0 | 35 | 0 | 0 | 25 | 21 | 11 | 33 | 21 | 158 | 106 | 95 | 22 | 0 | 91 | 30 | 53 | 42 | 163 | 120 | 61 | 74 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 286 | 0 | 0 | 120 | 0 | 115 | 0 | 100 | 0 | 70 | 0 | 115 | 52 | 0 | 0 | 214 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 950 | 0 | 305 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 100 | 0 | 0 | 46 | 25 | 34 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 8 | 0 | 0 | 185 | 0 | 76 | 40 | 180 | 0 | 404 | 17 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 533 |  | 7129 | 3733 | 10862 | 3930 | 950 | 1789 | 2910 | 682 | 106 | 337 | 158 | 0 | 0 | 84.53
23:00 | 33 | 0 | 0 | 110 | 270 | 94 | 0 | 323 | 353 |  | 0 | 0 | 290 | 100 | 81 | 47 | 330 | 0 | 160 | 0 | 92 | 68 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 51 | 0 | 44 | 0 | 17 | 15 | 0 | 120 | 0 | 310 | 280 | 103 | 45 | 96 | 40 | 54 | 0 | 35 | 0 | 0 | 25 | 21 | 11 | 33 | 21 | 150 | 105 | 95 | 22 | 0 | 91 | 30 | 50 | 43 | 163 | 156 | 61 | 74 | 0 | 0 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 286 | 0 | 0 | 120 | 0 | 115 | 0 | 100 | 0 | 10 | 0 | 115 | 52 | 0 | 0 | 215 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 948 | 0 | 270 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 46 | 26 | 15 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 182 | 0 | 76 | 0 | 183 | 0 | 402 | 0 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 532 |  | 7041 | 3532 | 10573 | 3880 | 948 | 1776 | 2762 | 682 | 107 | 268 | 150 | 0 | 0 | 84.57
24:00 | 33 | 0 | 0 | 110 | 270 | 94 | 0 | 333 | 355 |  | 0 | 0 | 280 | 100 | 81 | 47 | 332 | 0 | 153 | 0 | 100 | 68 | 48 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 72 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 44 | 0 | 17 | 16 | 0 | 120 | 0 | 310 | 275 | 103 | 45 | 92 | 40 | 55 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 142 | 142 | 95 | 22 | 0 | 91 | 30 | 50 | 43 | 163 | 156 | 61 | 74 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 286 | 0 | 0 | 120 | 0 | 115 | 0 | 100 | 0 | 0 | 0 | 115 | 52 | 0 | 0 | 217 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 948 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 188 | 0 | 77 | 0 | 190 | 0 | 406 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 533 |  | 6999 | 3360 | 10359 | 3926 | 948 | 1800 | 2597 | 683 | 107 | 156 | 142 | 0 | 0 | 84.61
KWH | 664000 | 0 | 0 | 2362500 | 6857900 | 2221590 | 768320 | 8189852 | 7845000 |  | 0 | 0 | 7244247 | 1837440 | 1598376 | 822130 | 7366694 | 0 | 2954000 | 0 | 1905600 | 1590048 | 364320 | 873140 | 0 | 0 | 34992 | 832680 | 923016 | 837072 | 330480 | 600000 | 607320 | 811900 | 817600 | 0 | 0 | 1702342 | 844000 | 2100000 | 0 | 0 | 0 | 0 | 3402562 | 0 |  | 0 | 0 | 363629 | 0 | 250560 | 31680 | 385728 | 450880 | 0 | 2473750 | 0 | 7866500 | 7145000 | 2695000 | 384727 | 2223330 | 709200 | 1055520 | 0 | 842317 | 0 | 52208 | 115306 | 486936 | 201240 | 564200 | 467830 | 3052800 | 3017400 | 1516800 | 429984 | 5600 | 2150000 | 720720 | 1119000 | 935136 | 989836 | 2007000 | 1264800 | 1602240 | 0 | 2619830 | 423000 | 0 | 244440 | 7379800 | 479808 | 257856 | 0 | 3743562 | 102912 | 0 | 816000 | 0 | 2460960 | 34425 | 2433600 | 0 | 374691 | 0 | 2564400 | 568560 | 21745 | 20160 | 5567673 | 0 | 0 | 0 | 1688400 | 2422080 | 0 | 0 |  | 22770909 | 0 | 8326080 | 0 | 731520 | 0 | 0 | 0 | 0 | 17536 | 584625 | 1553000 | 671401 | 744960 | 0 | 0 | 330000 | 187870 | 79784 | 536944 | 0 | 10784 | 180739 | 121920 | 129335 | 501840 | 263176 | 159534 | 0 | 0 | 3650600 | 0 | 35000 | 0 | 0 | 4428682 | 0 | 1748134 | 85440 | 4517964 | 0 | 9490218 | 69600 | 0 | 532320 | 0 | 735360 | 0 | 11141 | 0 | 12527900 |  | 151109880 | 75734316 | 226844196 | 94969180 | 22770909 | 38513575 | 46794199 | 16178500 | 2546342 | 1947365 | 3052800 | 71326 | 0
Fuel Cost | 1088960 | 0 | 0 | 3472875 | 7612269 | 2932498.8 | 1306144 | 8271750.52 | 8080350 |  | 0 | 0 | 8041114.17 | 13946169.6 | 11012810.64 | 6955219.8 | 7661361.76 | 0 | 5110420 | 0 | 14349168 | 14501237.76 | 3584908.8 | 8050350.8 | 0 | 0 | 318077.28 | 6078564 | 7134913.68 | 8253529.92 | 247860 | 450000 | 0 | 0 | 0 | 0 | 0 | 459632.34 | 227880 | 3801000 | 0 | 0 | 0 | 0 | 5784355.4 | 0 |  | 0 | 0 | 3527201.3 | 0 | 2179872 | 250905.6 | 486017.28 | 1339113.6 | 0 | 3661150 | 0 | 5821210 | 7145000 | 2479400 | 496297.83 | 2556829.5 | 801396 | 1477728 | 0 | 1440362.07 | 0 | 527300.8 | 1101172.3 | 618408.72 | 150930 | 987350 | 350872.5 | 22896000 | 3198444 | 13772544 | 546079.68 | 89264 | 3526000 | 1153152 | 1991820 | 1458812.16 | 1128413.04 | 2087280 | 2491656 | 3060278.4 | 0 | 4532305.9 | 926370 | 0 | 498657.6 | 7453598 | 359856 | 195970.56 | 0 | 28301328.72 | 1747445.76 | 0 | 4243200 | 0 | 24215846.4 | 402428.25 | 19833840 | 0 | 2641571.55 | 0 | 23387328 | 5372892 | 189398.95 | 0 | 42091607.88 | 0 | 0 | 0 | 14469588 | 16131052.8 | 0 | 0 |  | 131160435.84 | 0 | 8742384 | 0 | 5749747.2 | 0 | 0 | 0 | 0 | 183777.28 | 6091792.5 | 1754890 | 1040671.55 | 7270809.6 | 0 | 0 | 676500 | 1848640.8 | 810605.44 | 4751954.4 | 0 | 145799.68 | 1751360.91 | 1181404.8 | 1254549.5 | 963532.8 | 407922.8 | 120767.238 | 0 | 0 | 19786252 | 0 | 998550 | 0 | 0 | 5845860.24 | 0 | 2622201 | 1453334.4 | 5286017.88 | 0 | 9395315.82 | 726624 | 0 | 5051716.8 | 0 | 5706393.6 | 0 | 123108.05 | 0 | 54997481 |  | 450525968.42 | 287900401.128 | 738426369.548 | 110002949.178 | 131160435.84 | 47093717.47 | 331948372.19 | 74783733 | 687512.34 | 19238849.23 | 22896000 | 614800.3 | 0
Yesterday Day Peak | 33 | 0 | 0 | 110 | 300 | 94 | 40 | 332 | 335 |  | 0 | 0 | 335 | 60 | 48 | 30 | 300 | 0 | 0 | 0 | 65 | 76 | 0 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 75 | 36 | 90 | 0 | 0 | 0 | 0 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 100 | 0 | 280 | 335 | 141 | 8 | 87 | 30 | 20 | 0 | 35 | 0 | 0 | 0 | 21 | 8 | 0 | 19 | 132 | 122 | 32 | 22 | 0.6 | 91 | 30 | 47 | 39 | 0 | 107 | 51 | 73 | 0 | 150 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 195 | 0 | 20 | 0 | 100 | 105 | 2.7 | 100 | 0 | 0 | 0 | 115 | 35 | 0 | 1.2 | 285 | 54 | 0 | 0 | 108 | 100 | 0 | 0 |  | 949 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 75 | 0 | 192 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 498 |  | 9400.9 | DayPeak
Yesterday Evening Peak | 33 | 0 | 0 | 110 | 270 | 94 | 0 | 324 | 354 | 0 | 0 | 0 | 300 | 100 | 81 | 45 | 328 | 0 | 205 | 0 | 100 | 68 | 65 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 69 | 35 | 90 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 64 | 0 | 44 | 0 | 17 | 30 | 0 | 120 | 0 | 320 | 290 | 45 | 45 | 96 | 40 | 54 | 0 | 35 | 0 | 0 | 25 | 21 | 11 | 33 | 21 | 144 | 105 | 95 | 22 | 0 | 91 | 30 | 49 | 42 | 163 | 47 | 61 | 74 | 0 | 150 | 18 | 0 | 9 | 280 | 24 | 11 | 0 | 286 | 0 | 0 | 100 | 0 | 115 | 0 | 100 | 0 | 70 | 0 | 115 | 52 | 0 | 0 | 214 | 54 | 0 | 0 | 113 | 100 | 0 | 0 |  | 945 | 0 | 315 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 37 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 45 | 25 | 27 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 8 | 0 | 0 | 188 | 0 | 75 | 24 | 179 | 0 | 404 | 53 | 0 | 111 | 0 | 113 | 0 | 0 | 0 | 531 |  | 10886 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 110 | 300 | 104 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 45 | 335 | 0 | 200 | 0 | 100 | 76 | 149 | 100 | 0 | 0 | 52 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 102 | 100 | 100 | 50 | 17 | 20 | 0 | 135 | 0 | 360 | 360 | 110 | 45 | 95 | 34 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 173 | 160 | 95 | 22 | 0 | 89 | 30 | 51 | 44 | 163 | 330 | 66 | 74 | 0 | 150 | 18 | 0 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 0 |  | 960 | 16 | 410 | 0 | 115 | 225 | 0 | 0 | 30 | 60 | 40 | 68 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 45 | 52 | 35 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 12 | 0 | 0 | 200 | 0 | 79 | 100 | 210 | 0 | 410 | 105 | 100 | 113 | 105 | 113 | 0 | 0 | 113 | 660
Forecast for Day | 35 | 0 | 0 | 110 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 0 | 305 | 100 | 100 | 45 | 335 | 0 | 200 | 0 | 100 | 76 | 149 | 100 | 0 | 0 | 52 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 35 | 0 | 70 | 35 | 90 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 |  | 100 | 80 | 80 | 50 | 17 | 10 | 0 | 100 | 0 | 360 | 360 | 110 | 45 | 95 | 30 | 51 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 154 | 160 | 95 | 22 | 1.6 | 89 | 30 | 51 | 44 | 163 | 157 | 61 | 74 | 0 | 150 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 300 | 100 | 50 | 170 | 80 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 100 | 100 | 5 | 300 | 50 | 50 | 114 | 113 | 100 | 0 | 0 |  | 960 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 43 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 |  | 78 | 60 | 210 | 0 | 410 | 105 | 0 | 70 | 100 | 90 | 0 | 8 | 70 | 600
Generation at 08:00(Today) | 33 | 0 | 0 | 110 | 300 | 74 | 0 | 344 | 353 | 0 | 0 | 0 | 280 | 7 | 48 | 15 | 330 | 0 | 99 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 71 | 35 | 90 | 0 | 25 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8 | 0 | 80 | 0 | 260 | 260 | 95 | 8 | 92 | 30 | 5 | 0 | 10 | 0 | 0 | 0 | 21 | 2 | 33 | 12 | 106 | 157 | 8 | 22 | 1.1 | 91 | 30 | 50 | 43 | 163 | 157 | 61 | 74 | 0 | 141 | 18 | 0 | 10 | 305 | 24 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 82 | 0.63 | 100 | 0 | 0 | 0 | 115 | 0 | 0 | 2.9 | 124 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 949 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 73 | 0 | 172 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 531 | 0
199
| Minimum Generation |  | 8021.1 | 7:00
| Highest Generation |  | 10886 | 21:00
| Day Peak Generation |  | 9400.9 | 12:00
| Evening Peak Generation |  | 10886 | 21:00
| HVDC Max Flow |  | 950 | 2:00
| HVDC EvPeak Flow |  | 945 | 21:00
| Load factor L.F |  | 86.83%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2020-07-13
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2020-07-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9400.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8140.7 | MW
Evening Peak Generation : |  | 10886 | MW Hour : | 21:00 | Available Max Generation : |  | 15235 | MW
E.P. Demand (at gen end) : |  | 10886 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10886 | MW Hour : | 21:00 | Reserve(Generation end) |  | 4235 | MW
Total Gen. (MKWH) : |  | 226.8442 | System Load Factor : | 86.83% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -87 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2020-07-13
Actual : | 84.91 | Ft.(MSL) , | Rule curve : | 85.92 | Ft.( MSL )
Gas Consumed : | Total = | 1127.33 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157096666.648
: |  | Coal : | 74783733 | Oil : | 351187221.42 | Total : | 583067621.068
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3952.045 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1343.9438 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1204.1344 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1088.0389 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 983.2439 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 793.4431 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 443.6161 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 204.2893 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 611.9429 |  |  | 0 | 0%
Total | 0 |  | 10624.6973 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Bibiyana #3
3) Ghorasal Unit-2,3,4.
4) Ashuganj unit-3,5
5) Bhola-225 MW GT-2 & ST
6) Kaptai-2,5
7) Raozan # 2
8) Sirajganj #1
9) Megnaghat-450 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Meghnaghat-Haripur 230 kV Ckt-1 was under shut down from 09:10 to 14:33 for high temperature at different point.
b) Bheramara-Faridpur 132 kV Ckt-1 was under shut down from 10:12 to 11:02 to remove kite.
c) Mahasthangar 132/33 kV T-1 transformer was under shut down from 10:52 to 14:24 for PBS work.
d) Baroirhat 132/33 kV T-2 transformer was under shut down from 11:22 to 12:50 to attend R/H at 33 kV
Breaker terminal.
e) Siddhirganj S/S-Siddhirganj GT(1&2) 132 kV Ckt was under shut down from 11:42 to 11:50 for auxiliary
supply checking.
f) Dohazari-Cox's Bazar 132 kV Ckt-1 was under shut down from 08:18 to 19:33 for D/W.
g) B. Baria-Shahajibazar 132 kV Ckt-2 was under shut down from 09:42 to 14:23 for C/M.
h) Jamalpur 132/33 kV T-3 transformer was under shut down from 09:10 to 11:28 for C/M.
i) Mirpur-Uttara(Old) 132 kV Ckt was under shut down from 08:25 to 16:50 for C/M.
j) Siddhirganj Peaking GT 1&2 tripped at 09:54 due to auxiliary supply failure.
k) Siddhirganj Peaking GT-2 was synchronized at 12:42 and GT-1 at 13:36.
l) Aminbazar-Manikganj 163 MW(New) P.P. 132 kV Ckt-1 was under shut down from 13:23 to 18:48 for maintenance.
m) Kushiara STG was synchronized at 17:16.
n) Khulna(S)-Satkhira 132 kV Ckt-1 tripped at 19:36 from both ends showing Dist. Z2 at Khulna(S) end & Dist. Z1
at Satkhira end and was switched on at 19:56.
o) Ishwardi 230/132 kV T02 transformer tripped at 20:01 showing lock out, winding temperature high and was
switched on at 23:31.
p) Ashuganj 255 MW CCPP STG was synchronized at 21:19.
q) Ashuganj 255 MW CCPP STG tripped at 00:12(13/07/2020) due to turbine control pressure low.
r) Khulshi 33 kV Bus along with T1 transformer's 33 kV side was under shut down from 00:24(13/07/2020) to |  |  |  |  | About 50 MW power interruption occurred under Khulshi S/S area
01:53(13/07/2020) for R/H maintenance by PDB. |  |  |  |  | from 00:24(13/07/2020) to 01:53(13/07/2020).
s) Madunahat 132/33 kV T-1 transformer was shut down at 06:32(13/07/2020) due to LT U/G cable DS R/H.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2020-07-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 33 | 664000 | Unit-2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2362500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 270 | 6857900
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 768320 | Gas shortage
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 94 | 2221590 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 324 | 8189852 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 354 | 7845000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1837440
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 300 | 7244247
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 81 | 1598376 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 45 | 822130 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 873140 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 330480
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 205 | 2954000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1905600
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7366694
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 68 | 1590048 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 34992 | Reserve
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 832680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 65 | 364320 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 923016
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 837072
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel Shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1207320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 286 | 3743562
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 102912 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 115 | 2460960 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 568560 | Engine problem
| Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | On test
| Dhaka area Total |  |  |  | 5895 | 3236 | 68136211
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 34425
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 31680 | Reserve
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 104 | 2546342 | Low water level
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under S/D.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3402562 | FGMO
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 21745 | Reserve
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 64 | 363629
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2433600
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 385728 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 450880
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 250560 | Low demand
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20160
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 214 | 5567673 | Low demand
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 0
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve
| Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2422080
| Chattogram area Total |  |  |  | 2266 | 957 | 20031064
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2473750
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage.
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 45 | 2695000 | ST synchronized process.
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7866500 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7145000 | FGMO
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 709200 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1055520
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 384727 | Gas shortage.
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 842317 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 374691 | Low demand
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 52208
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2223330 | ST under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 0 | Reserve
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 486936
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 201240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 3052800
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 564200
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 115306 | Low demand
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 467830
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
| Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1688400
| Cumilla Area Total |  |  |  | 2980 | 1483 | 32398955
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 105 | 3017400 | Gas shortage.
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 429984
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1516800
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5600
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 816000
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2564400 | #REF!
| Mymensingh Area Total |  |  |  | 637 | 437 | 8350184
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 91 | 2150000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 720720 | # 4 under maint.
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 989836
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 47 | 2007000 | ST synchronized process.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1119000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 42 | 935136
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 257856
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1264800 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 74 | 1602240 | Engine problem
91 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 150 | 2619830
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 423000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 479808
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7379800 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 244440
| Bibiyana South 400 MW |  | PDB | 400 MW | 0 | 0 | 0 | On test
| Sylhet Area Total |  |  |  | 1988 | 1049 | 22193466
98 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 945 | 22770909
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 51 | 731520 | Low demand
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 17536 | Reserve
103 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 315 | 8326080 | FGMO
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 584625
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 24 | 85440 | Low demand
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 69600 | Low demand
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 2284 | 1428 | 32585710
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 744960
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 37 | 671401
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1553000 | GT-2 & ST Under maint.
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 1748134 | Engine problem
| Payra 1320 MW |  | BCPCL | 1*622 | 622 | 531 | 12527900
| Barisal Area Total |  |  |  | 1054 | 818 | 17245395
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 330000 | Gas shortage.
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 187870
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 35 | 79784
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 10784 | Reserve
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 180739
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage.
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4428682 | FGMO
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 179 | 4517964 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 404 | 9490218 | FGMO
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 129335
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 501840
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 11 | 263176
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 159534
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 121920 | Low demand
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 536944
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 111 | 532320
| Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
| Rajshahi Area Total |  |  |  | 2183 | 1208 | 21471110
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3650600 | Coal shortage.
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 35000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 735360
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11141
| Rangpur Area Total |  |  |  | 605 | 270 | 4432101
| Total |  |  |  | 19892 | 10886 | 226844196
| Eastern Grid Total |  |  |  | 13766 | 7162 | 151109880
| Western Grid Total |  |  |  | 6126 | 3724 | 75734316
| National Grid Total |  |  |  | 19892 | 10886 | 226844196
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2020-07-12
(a) ENTIRE EASTERN GRID : |  | 6983 | MW | (b) ENTIRE WESTERN GRID : |  | 3524 | MW
i) Dhaka area |  | 3546 | MW | i) Khulna area |  | 1324 | MW
ii) Chittagong area |  | 1132 | MW | ii) Rajshahi area |  | 1147 | MW
iii) Comilla area |  | 1015 | MW | iii) Barisal area |  | 325 | MW
iv) Mymensingh area |  | 891 | MW | iv) Rangpur area |  | 728 | MW
v) Sylhet area |  | 399 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10507 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 23:00 | Sherpur | 102 | 22:00 | Jhenida | 81 | 19:00
Munsiganj | 112 | 21:00 | Srimongal | 39 | 19:30 | Bottail | 124 | 21:00
Sonargaon | 72 | 1:00 | Shahjibazar | 99 | 22:00 | G.K Project | 49 | 21:00
Shyampur | 194 | 10:00 | Fenchuganj | 36 | 20:00 | Faridpur | 165 | 0.83333
Bhulta | 183 | 23:00 | Kulawara | 40 | 20:00 | Madaripur | 83 | 0.875
Madanganj | 52 | 2:00 | Sylhet | 104 | 18:30 | Sariatpur | 54 | 20:00
Shitalakhya | 112 | 11:00 | Chatak | 20 | 20:00 | Gopalganj | 74 | 22:00
Rahim steel | 26 | 17:00 | Sunamganj | 28 | 1:00 | Bagerhat | 81 | 21:00
Matuail | 81 | 12:00 | Biani Bazar | 46 | 21:00 | Mongla | 48 | 15:00
Ghorasal | 81 | 22:00 | Comilla (S) | 158 | 22:00 | Satkhira | 86 | 0.91667
Narsingdi | 142 | 1:00 | Comilla(N) | 77 | 21:00 | Gallamari | 42 | 22:00
Haripur (SBU) | 102 | 12:00 | Chandpur | 89 | 21:00 | Magura | 52 | 0.8125
Ullon | 70 | 14:00 | Feni | 105 | 21:00 | Norail | 35 | 20:00
Hasnabad | 175 | 21:00 | Chowmuhani | 174 | 20:00 | Chuadanga | 85 | 22:00
Magbazar | 96 | 11:00 | Ashuganj | 60 | 22:00 | Barisal(N) | 36 | 0.79167
Maniknagar | 96 | 12:00 | Daudkandi | 122 | 23:00 | Barisal (S) | 96 | 0.79167
Bangabhaban | 32 | 11:00 | B.Baria | 129 | 22:00 | Patuakhali | 110 | 0.8125
Narinda | 84 | 13:00 | Ramganj | 100 | 21:00 | Bhandaria | 56 | 0.875
Dhanmondi | 165 | 12:00 | Chaddagram | 45 | 14:00 | Borhan Uddin | 43 | 22:00
Lalbag | 89 | 12:00 | PHP | 11 | 9:00 | Ishurdi | 56 | 21:00
Madartek | 63 | 21:00 | Madunaghat | 52 | 19:00 | Ruppur Paromanobik | 2 | 10:00
Dhaka University |  |  | Hathazari | 92 | 0.79167 | Natore | 108 | 21:00
Fatullah | 28 | 0.625 | Khulshi | 184 | 0.58333 | Bogra | 150 | 20:00
Mirpur | 93 | 11:00 | Halishahar | 128 | 0.58333 | Noagaon | 119 | 21:00
Kalyanpur | 96 | 12:00 | Baraulia | 146 | 0.041667 | Rajshahi | 120 | 21:00
Gulshan | 112 | 12:00 | Sikalbaha | 26 | 0.875 | Rajshahi New | 10 | 20:00
Uttara | 74 | 12:00 | Dohazari | 92 | 0.8125 | C.Nawabganj | 71 | 19:30
Uttara New | 28 | 12:00 | Cox'sbazar | 87 | 0.875 | Amnura | 46 | 21:00
Kamrangirchar | 85 | 12:00 | Chandraghona | 26 | 0.79167 | Pabna | 107 | 20:00
Savar | 112 | 12:00 | Kaptai | 4.2 | 0.77083 | Shahjadpur | 91 | 19:00
Bhasantec | 140 | 11:00 | A. Khaer Stl. | 0 | 0.041667 | Serajganj | 83 | 21:00
Agargaon | 64 | 12:00 | Bakulia | 94 | 0.54167 | Niyamatpur | 59 | 21:00
Satmosjid | 93 | 12:00 | Julda | 18 | 0.041667 | Joypurhat | 48 | 21:00
Tongi | 129 | 0.41667 | TK chemical | 15 | 0.79167 | Sherpur(Bogura) | 42 | 20:00
Kabirpur | 226 | 10:00 | Modern Steel | 17 | 0.375 | Mohastangor | 46 | 20:00
Basundhara | 126 | 12:00 | Shahmirpur | 25 | 0.58333 | Rangpur | 134 | 21:00
Manikganj | 68 | 21:00 | Khagrachhari | 22 | 0.875 | Lalmonirhat | 52 | 20:00
Joydevpur | 151 | 21:00 | Matarbari | 33.5 | 0.83333 | Saidpur | 97 | 20:00
New Tongi | 97 | 12:00 | Baroiar Hat | 32 | 0.8125 | Purbasadipur | 104 | 20:00
Korda | 206 | 15:00 | Rangamati | 10 | 0.79167 | Thakurgaon | 78 | 20:00
Dhamrai | 74 | 12:00 | Abul Khair 230 | 125 | 0.58333 | Palashbari | 111 | 19:30
Rajendrapur | 90 | 21:00 | BSRM | 152 | 0.125 | Barapukuria | 45 | 21:00
Valuka | 93 | 11:00 | GPH Ispat | 64 | 0.79167 | Panchagar | 46 | 21:00
Tangail | 165 | 20:00 | Goalpara | 28 | 0.54167 | Joldhaka | 27 | 20:00
Mymensing | 204 | 19:30 | Central s/s | 78 | 20:00 | Kurigram | 55 | 20:00
Kishorganj | 112 | 21:00 | Noapara | 57 | 21:00
Netrokona | 105 | 22:00 | Jessore | 102 | 21:00
Jamalpur | 130 | 19:30 | Benapol | 46 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2020-07-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 398 | 20:00 | 386 | 12:00 | Kaliakoir | 228 | 1904-08-16 | 366 | 0.5
| Bheramara | 396 | 6:00 | 392 | 1:00 | Bhulta | 392 | 0.8125 | 379 | 0.45833
| Ashuganj(N) | 399 | 19:30 | 387 | 10:00 | Gopalganj | 414 | 0.25 | 403 | 0.875
| Payra | 420 | 7:00 | 410 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 19:00 | 230 | 1:00 | Comilla (N) | 236 | 20:00 | 230 | 3:00
| Ishurdi | 235 | 19:00 | 223 | 12:00 | Hathazari | 226 | 19:30 | 219 | 7:00
| Ashuganj | 239 | 20:00 | 231 | 12:00 | Megnaghat | 234 | 19:30 | 229 | 12:00
| Serajganj | 233 | 17:00 | 226 | 4:00 | Fenchuganj | 239 | 20:00 | 231 | 2:00
| Baghabari | 240 | 18:30 | 235 | 12:00 | Siddhirganj | 233 | 19:00 | 226 | 12:00
| Barapukuria | 234 | 7:00 | 226 | 19:30 | Maniknagar | 232 | 20:00 | 223 | 11:00
| Bogra | 229 | 19:00 | 220 | 1:00 | Agargaon | 229 | 19:30 | 221 | 11:00
| Rajshahi | 229 | 18:00 | 220 | 11:00 | Barisal | 243 | 7:00 | 237 | 1:00
| Khulna South | 227 | 22:00 | 208 | 10:00 | AKSML | 225 | 20:00 | 216 | 3:00
| Rampura | 228 | 20:00 | 220 | 12:00 | BSRM | 225 | 19:00 | 216 | 3:00
| Haripur | 232 | 24:00 | 225 | 11:00 | Bibiyana | 238 | 20:00 | 228 | 10:00
| Hasnabad | 231 | 20:00 | 225 | 4:00 | Bhulta | 233 | 19:30 | 224 | 11:00
| Shyampur | 228 | 19:00 | 221 | 8:00 | Ashuganj (S) | 238 | 19:30 | 231 | 10:00
| Aminbazar | 230 | 19:30 | 223 | 10:00 | Kaliakoir | 233 | 19:30 | 223 | 12:00
| Tongi | 230 | 19:30 | 217 | 10:00 | GPH | 222 | 19:30 | 216 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:30 | 128 | 11:00 | Hathazari | 134 | 0.45833 | 130 | 0.33333
| Munsiganj | 136 | 19:00 | 129 | 8:00 | Khulshi | 132 | 0.45833 | 128 | 0.33333
| Sonargaon | 133 | 19:30 | 127 | 11:00 | Halishahar | 137 | 0.8125 | 130 | 0.20833
| Shyampur | 138 | 19:00 | 132 | 11:00 | Baraulia | 135 | 0.83333 | 130 | 0.041667
| Bhulta | 126 | 13:00 | 122 | 11:00 | Sikalbaha | 136 | 20:00 | 130 | 0.125
| Madanganj | 131 | 5:00 | 128 | 8:00 | Dohazari | 132 | 19:00 | 127 | 0.125
| Shitalakhya | 141 | 19:30 | 124 | 6:00 | Cox'sbazar | 128 | 0.8125 | 118 | 0.75
| Rahim steal | 134 | 19:00 | 129 | 12:00 | Chandraghona | 134 | 0.25 | 131 | 0.125
| Matuail | 134 | 19:30 | 128 | 11:00 | Kaptai | 134 | 18:30 | 132 | 0.041667
| Ghorasal | 138 | 18:30 | 136 | 1:00 | A. Khaer Stl. | 132 | 0.8125 | 130 | 1:00
| Narsinghdi | 131 | 19:00 | 126 | 1:00 | Bakulia | 134 | 0.83333 | 130 | 0.33333
| Haripur (SBU) | 134 | 19:00 | 129 | 10:00 | Julda | 135 | 0.79167 | 131 | 0.625
| Ullon | 134 | 3:00 | 128 | 10:00 | TK Chemical | 135 | 0.8125 | 131 | 16:00
| Hasnabad | 140 | 14:00 | 134 | 3:00 | Modern Steel | 134 | 0.8125 | 130 | 0.29167
| Magbazar | 135 | 22:00 | 128 | 12:00 | Shahmirpur | 135 | 0.8125 | 130 | 0.45833
| Maniknagar | 132 | 1:00 | 127 | 11:00 | Khagrachhari | 133 | 0.29167 | 131 | 0.125
| Bangabhaban | 132 | 1:00 | 127 | 11:00 | Matarbari | 128 | 0.29167 | 115 | 0.625
| Narinda | 132 | 1:00 | 127 | 11:00 | Baroiar Hat | 131 | 0.16667 | 127 | 0.041667
| Dhanmondi | 134 | 3:00 | 128 | 10:00 | Rangamati | 134 | 0.8125 | 131 | 3:00
| Lalbag | 138 | 14:00 | 131 | 8:00 | Goalpara S/S | 138 | 22:00 | 122 | 10:00
| Madartek | 134 | 6:00 | 127 | 11:00 | Khulna Central S/S | 137 | 0.91667 | 124 | 10:00
| Dhaka University |  |  |  |  | Noapara | 134 | 22:00 | 122 | 10:00
| Fatuiiah | 138 | 0.79167 | 132 | 11:00 | Jessore | 128 | 22:00 | 118 | 10:00
| Mirpur | 133 | 19:00 | 127 | 12:00 | Benapol | 128 | 22:00 | 119 | 10:00
| Kalyanpur | 132 | 19:00 | 130128 | 12:00 | Jhenida | 126 | 0.91667 | 118 | 10:00
| Gulshan | 133 | 19:00 | 128 | 12:00 | Bottail | 131 | 6:00 | 124 | 20:00
| Uttara | 133 | 19:00 | 128 | 12:00 | G.K Project | 138 | 0.70833 | 133 | 11:00
| Uttara New | 133 | 19:00 | 136 | 12:00 | Faridpur | 134 | 6:00 | 128 | 20:00
| Kamrangirchar | 135 | 19:00 | 128 | 12:00 | Madaripur | 139 | 0.25 | 132 | 21:00
| Savar | 132 | 19:00 | 127 | 12:00 | Shariyatpur S/S | 137 | 0.29167 | 132 | 20:00
| Bhasantec | 132 | 19:00 | 129 | 12:00 | Gopalganj | 139 | 17:00 | 131 | 21:00
| Agargaon | 134 | 19:00 | 128 | 12:00 | Bagerhat | 136 | 22:00 | 120 | 10:00
| Satmosjid | 133 | 19:00 | 130 | 12:00 | Mongla | 133 | 0.91667 | 115 | 10:00
| Tongi | 137 | 0.8125 | 129 | 13:00 | Satkhira | 135 | 0.91667 | 121 | 10:00
| Kabirpur | 134 | 5:00 | 125 | 3:00 | Gallamari | 138 | 22:00 | 128 | 8:00
| Basundhara | 135 | 20:00 | 127 | 12:00 | Magura | 125 | 15:00 | 113 | 20:00
| Manikganj | 136 | 19:30 | 127 | 10:00 | Norail | 123 | 0.70833 | 109 | 20:00
| Joydevpur | 143 | 19:30 | 135 | 11:00 | Chuadanga | 125 | 18:00 | 105 | 20:00
| New Tongi | 135 | 1904-01-02 | 127 | 11:00 | Barisal(N) | 137 | 6:00 | 134 | 1:00
| Kodda | 131 | 20:00 | 120 | 0.41667 | Barisal (S) | 135 | 0.29167 | 132 | 1:00
| Dhamrai | 133 | 19:30 | 126 | 9:00 | Patuakhali(S) | 134 | 0.33333 | 128 | 19:00
| Rajendrapur | 130 | 24:00 | 117 | 10:00 | Bhandaria | 134 | 9:00 | 126 | 19:30
| Valuka | 129 | 17:00 | 119 | 21:00 | Ishurdi | 137 | 19:00 | 131 | 1:00
| Tangail | 135 | 6:00 | 127 | 12:00 | Ruppur Paromanobik | 135 | 17:00 | 130 | 11:00
| Mymensing | 130 | 18:30 | 121 | 21:00 | Natore | 134 | 19:00 | 128 | 1:00
| Kishorganj | 131 | 5:00 | 123 | 21:00 | Bogra | 133 | 19:00 | 125 | 2:00
| Netrokona | 128 | 16:00 | 118 | 21:00 | Noagaon | 130 | 19:00 | 120 | 2:00
| Jamalpur | 138 | 1:00 | 125 | 9:00 | Rajshahi | 133 | 19:00 | 124 | 2:00
| Sherpur | 136 | 1:00 | 122 | 9:00 | Rajshahi New | 133 | 19:00 | 125 | 5:00
| Srimongal | 137 | 7:00 | 134 | 0.041667 | C.Nawabganj | 130 | 19:00 | 122 | 1:00
| Shahjibazar | 135 | 6:00 | 132 | 0.041667 | Amnura | 133 | 19:00 | 121 | 2:00
| Fenchuganj | 136 | 20:00 | 133 | 0.041667 | Pabna | 134 | 19:00 | 129 | 20:00
| Khulawara | 134 | 17:00 | 132 | 0.041667 | Shahjadpur | 137 | 1:00 | 134 | 19:30
| Sylhet | 133 | 7:00 | 131 | 0.041667 | Serajganj | 133 | 18:30 | 128 | 1:00
| Chatak | 133 | 7:00 | 129 | 22:00 | Niyamatpur | 129 | 12:00 | 117 | 3:00
| Sunamganj | 132 | 6:00 | 129 | 0.041667 | Joypurhat | 130 | 18:30 | 120 | 21:00
| Biani Bazar | 132 | 7:00 | 128 | 0.95833 | Sherpur(Bogura) | 133 | 19:00 | 127 | 1:00
| Comilla(s) | 127 | 7:00 | 121 | 20:00 | Mohastangor | 132 | 19:00 | 124 | 1:00
| Comilla(n) | 136 | 19:30 | 133 | 12:00 | Rangpur | 129 | 4:00 | 121 | 19:30
| Chandpur | 130 | 14:00 | 126 | 22:00 | Lalmonirhat | 127 | 9:00 | 116 | 19:30
| Feni | 132 | 9:00 | 127 | 19:00 | Saidpur | 130 | 5:00 | 116 | 21:00
| Chowmuhani | 129 | 15:00 | 122 | 19:00 | Purbasadipur | 127 | 4:00 | 112 | 20:00
| Ashuganj | 137 | 6:00 | 132 | 12:00 | Thakurgaon | 127 | 7:00 | 110 | 21:00
| Daudkandi | 133 | 19:30 | 128 | 11:00 | Palashbari | 126 | 6:00 | 119 | 19:30
| B.Baria | 132 | 7:00 | 129 | 21:00 | Barapukuria | 134 | 7:00 | 126 | 19:30
| Ramganj | 126 | 9:00 | 118 | 19:00 | Panchagar | 121 | 7:00 | 108 | 20:00
| Chaddagram | 132 | 10:00 | 128 | 4:00 | Joldhaka | 129 | 6:00 | 115 | 19:30
| PHP | 130 | 6:00 | 125 | 5:00 | Kurigram | 127 | 6:00 | 115 | 19:30
| Madanhat | 136 | 19:00 | 133 | 1:00

## L-Curve
Date | 2020-07-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 4 | 6999 | 3360 | 10359 |  |  |  | QF-LDC-12
0:30 | 40.5 | 6811 | 3290 | 10101 | Date: | 2020-07-12
1:00 | 77 | 6623 | 3220 | 9843
1:30 | 98.5 | 6493 | 3165.5 | 9658.5
2:00 | 120 | 6363 | 3111 | 9474
2:30 | 143 | 6245 | 3087 | 9332 | [5 empty] | Gen. at Eve. Peak | 10886 | 10886 MW (21:00 )
3:00 | 166 | 6127 | 3063 | 9190 | [6 empty] | 21:00
3:30 | 187.5 | 6038.5 | 3028 | 9066.5 | [5 empty] | Gen. at Day Peak | 9400.9 | 9400.9 MW (12:00 )
4:00 | 209 | 5950 | 2993 | 8943 | [6 empty] | 12:00
4:30 | 228 | 5848.5 | 2988 | 8836.5 | [5 empty] | Highest Generation | 10886
5:00 | 247 | 5747 | 2983 | 8730 | [6 empty] | 21:00
5:30 | 307.5 | 5537.75 | 2905.5 | 8443.25
6:00 | 368 | 5328.5 | 2828 | 8156.5
6:30 | 344 | 5241.8 | 2847 | 8088.8
7:00 | 320 | 5155.1 | 2866 | 8021.1
7:30 | 340 | 5234.15 | 2863.05 | 8097.2
8:00 | 360 | 5313.2 | 2860.1 | 8173.3
8:30 | 367.5 | 5534.45 | 2862.6 | 8397.05
9:00 | 375 | 5755.7 | 2865.1 | 8620.8
9:30 | 341.5 | 5959.45 | 2861.15 | 8820.6
10:00 | 308 | 6163.2 | 2857.2 | 9020.4
10:30 | 314 | 6283.05 | 2864.8 | 9147.85
11:00 | 320 | 6402.9 | 2872.4 | 9275.3
11:30 | 325 | 6408.2 | 2929.9 | 9338.1
12:00 | 330 | 6413.5 | 2987.4 | 9400.9
12:30 | 295 | 6502.35 | 2991.8 | 9494.15
13:00 | 260 | 6591.2 | 2996.2 | 9587.4
13:30 | 261 | 6518.65 | 2957.9 | 9476.55
14:00 | 262 | 6446.1 | 2919.6 | 9365.7
14:30 | 307.5 | 6411.65 | 2887.2 | 9298.85
15:00 | 353 | 6377.2 | 2854.8 | 9232
15:30 | 354 | 6352.95 | 2866.5 | 9219.45
16:00 | 355 | 6328.7 | 2878.2 | 9206.9
16:30 | 341 | 6140.45 | 2846 | 8986.45
17:00 | 327 | 5952.2 | 2813.8 | 8766
17:30 | 331.5 | 5889.7 | 2847.5 | 8737.2
18:00 | 336 | 5827.2 | 2881.2 | 8708.4
18:30 | 257 | 6138.1 | 3082.6 | 9220.7
19:00 | 178 | 6449 | 3284 | 9733
19:30 | 205 | 7145 | 3510 | 10655
20:00 | 87 | 7072 | 3581 | 10653 |  |  |  | Executive Engineer
20:30 | 51 | 7117 | 3652.5 | 10769.5 |  |  |  | Network Operation Division
21:00 | 15 | 7162 | 3724 | 10886
21:30 | 50 | 7145.5 | 3728.5 | 10874
22:00 | 85 | 7129 | 3733 | 10862 |  |  |  |  | Page 6 of 7
22:30 | 59 | 7085 | 3632.5 | 10717.5
23:00 | 33 | 7041 | 3532 | 10573
23:30 | 18.5 | 7020 | 3446 | 10466
24:00 | 4 | 6999 | 3360 | 10359
10886 MW (21:00 )
9400.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2020-07-12 |  | Energy | 226844196
[10 empty] | 2020-07-12 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3926 | 948 | 1800 | 2762 | 683 | 107 | 156 | 0 | 142
0:30 | 4001 | 948 | 1752 | 2475.5 | 652 | 106.5 | 107.5 | 0 | 141 | Date: | 2020-07-12
1:00 | 4076 | 948 | 1704 | 2189 | 621 | 106 | 59 | 0 | 140
1:30 | 4094 | 949 | 1703.5 | 2017.5 | 621 | 106 | 29.5 | 0 | 138 | [7 empty] | Total Energy | 226.8442 | Total Energy Gen 226.844 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.844 MKWHr
2:00 | 4112 | 950 | 1703 | 1846 | 621 | 106 | 0 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 4141.5 | 949.5 | 1693 | 1688.5 | 622.5 | 106 | 0 | 0 | 131 | [7 empty] | Energy Requirement | 226.8442
3:00 | 4171 | 949 | 1683 | 1531 | 624 | 106 | 0 | 0 | 126
3:30 | 4128.5 | 949.5 | 1681.5 | 1459.5 | 623.5 | 106 | 0 | 0 | 118 | [6 empty] | Shortage
4:00 | 4086 | 950 | 1680 | 1388 | 623 | 106 | 0 | 0 | 110
4:30 | 4098.5 | 950 | 1665 | 1281 | 623 | 106 | 0 | 0 | 113
5:00 | 4111 | 950 | 1650 | 1174 | 623 | 106 | 0 | 0 | 116
5:30 | 4018 | 950 | 1578 | 1055 | 623 | 106 | 0 | 0 | 113
6:00 | 3925 | 950 | 1506 | 936 | 623 | 106 | 0 | 0 | 110
6:30 | 3864.5 | 950 | 1510.5 | 928.5 | 624 | 105.5 | 0 | 0 | 105 |  |  |  |  | Coal
7:00 | 3804 | 950 | 1515 | 921 | 625 | 105 | 0 | 0 | 100
7:30 | 3871.5 | 949.5 | 1492 | 953.5 | 625.5 | 105 | 0 | 0 | 98 |  |  |  | Oil |  |  |  | ,
8:00 | 3939 | 949 | 1469 | 986 | 626 | 105 | 0 | 0 | 96
8:30 | 3988 | 949 | 1466 | 1168.5 | 615.5 | 106 | 0 | 0 | 99
9:00 | 4037 | 949 | 1463 | 1351 | 605 | 107 | 0 | 0 | 102
9:30 | 3897.5 | 949.5 | 1453 | 1693 | 603.5 | 107.5 | 0 | 0 | 109
10:00 | 3758 | 950 | 1443 | 2035 | 602 | 108 | 0 | 0 | 116
10:30 | 3773 | 950 | 1476.5 | 2108 | 601 | 109 | 0 | 0 | 124
11:00 | 3788 | 950 | 1510 | 2181 | 600 | 110 | 0 | 0 | 132
11:30 | 3816.5 | 949.5 | 1523.5 | 2177 | 624 | 110.5 | 0 | 0 | 132
12:00 | 3845 | 949 | 1537 | 2173 | 648 | 111 | 0 | 0 | 132
12:30 | 3866 | 949 | 1549.5 | 2234 | 648.5 | 111 | 0 | 0 | 129
13:00 | 3887 | 949 | 1562 | 2295 | 649 | 111 | 0 | 0 | 126
13:30 | 3887 | 949 | 1562 | 2295 | 649 | 111 | 0 | 0 | 126
14:00 | 3887 | 949 | 1562 | 2295 | 649 | 111 | 0 | 0 | 126
14:30 | 3815 | 949 | 1482 | 2295.5 | 648.5 | 111 | 0 | 0 | 99
15:00 | 3743 | 949 | 1402 | 2296 | 648 | 111 | 0 | 0 | 72
15:30 | 3756.5 | 949.5 | 1465 | 2194 | 648 | 110 | 0 | 0 | 89
16:00 | 3770 | 950 | 1528 | 2092 | 648 | 109 | 0 | 0 | 106
16:30 | 3716.5 | 950 | 1516 | 1935.5 | 647 | 109 | 5 | 0 | 104
17:00 | 3663 | 950 | 1504 | 1779 | 646 | 109 | 10 | 0 | 102
17:30 | 3669 | 950 | 1480 | 1759.5 | 647 | 108 | 15 | 0 | 107
18:00 | 3675 | 950 | 1456 | 1740 | 648 | 107 | 20 | 0 | 112
18:30 | 3692.5 | 950 | 1546 | 1970 | 647.5 | 106 | 180.5 | 0 | 128
19:00 | 3710 | 950 | 1636 | 2200 | 647 | 105 | 341 | 0 | 144
19:30 | 3856 | 950 | 1684 | 2780 | 673 | 104 | 460 | 0 | 148
20:00 | 3935 | 947 | 1659 | 2688 | 684 | 104 | 486 | 0 | 150
20:30 | 3954.5 | 946 | 1718.5 | 2777.5 | 682 | 104 | 440 | 0 | 147
21:00 | 3974 | 945 | 1778 | 2867 | 680 | 104 | 394 | 0 | 144
21:30 | 3952 | 947.5 | 1783.5 | 2888.5 | 681 | 105 | 365.5 | 0 | 151
22:00 | 3930 | 950 | 1789 | 2910 | 682 | 106 | 337 | 0 | 158
22:30 | 3905 | 949 | 1782.5 | 2836 | 682 | 106.5 | 302.5 | 0 | 154
23:00 | 3880 | 948 | 1776 | 2762 | 682 | 107 | 268 | 0 | 150
23:30 | 3903 | 948 | 1788 | 2762 | 682.5 | 107 | 212 | 0 | 146 | Max Temp. in Dhaka |  | 31.6° C
24:00 | 3926 | 948 | 1800 | 2762 | 683 | 107 | 156 | 0 | 142
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 226.844 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.844 MKWHr
Note on W13: Author:

## Generation
g | 2020-07-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 70 | 72 | 73 | 75 | 75 | 76 | 77 | 76 | 74 | 74 | 72 |  | 70 | 69 | 69 | 69 | 71 | 72 | 72 | 1702342
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 |  | 1.9 | 2.1 | 2.6 | 1.4 | 2.7 | 5.3 | 5.9 | 4.7 | 1.3 | 1.7 | 0.1 | [8 empty] | 34425
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 143 | 139 | 143 | 144 | 147 | 146 | 142 | 142 | 144 | 144 | 144 | 147 | 140 | 140 | 140 | 140 | 140 |  | 142 | 142 | 142 | 140 | 140 | 140 | 140 | 3402562
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | [18 empty] | 85 | 85 | 85 | 64 | 51 | 51 | 0 | 363629
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 5 | 17 |  |  |  |  | 0 | 21745
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 33 | 40 | 41 |  |  |  | 0 | 52208
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 155 | 155 | 175 | 160 | 140 | 140 | 80 | 120 | 160 |  |  |  | 57 | 71 | 73 | 77 | 73 | 78 |  | 78 | 205 | 178 | 205 | 200 | 160 | 153 | 2954000
17 | Siddhirganj 335 MW CCPP | 329 | 329 | 330 | 329 | 329 | 250 | 250 | 270 | 325 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 331 | 328 | 329 | 330 | 332 | 7366694
18 | Kodda 300 MW PP Unit-2 (Summit) | 150 | 45 |  |  |  |  | 20 | 30 | 65 | 155 | 192 | 195 | 195 | 195 | 190 | 195 | 195 | 195 |  | 205 | 260 | 283 | 286 | 286 | 286 | 286 | 3743562
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 45 | 45 | 45 | 45 | 45 | 45 | 384727
20 | Ghorasal TPP (Unit-1&2) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 664000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 10 | 40 | 65 | 100 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2362500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 280 | 280 | 280 | 300 | 310 | 300 | 300 | 300 | 300 | 280 |  | 280 | 280 | 280 | 270 | 270 | 270 | 270 | 6857900
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 2473750
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 33 | 33 | 30 | 30 | 38 |  | 36 | 40 | 40 | 40 | 40 | 40 | 40 | 709200
33 | Ashuganj 225 MW CCPP | 142 | 143 | 142 | 143 | 140 | 130 | 108 | 95 | 140 | 138 | 140 | 141 | 141 | 141 | 141 | 142 | 32 | 39 |  | 36 | 36 | 40 | 45 | 111 | 103 | 103 | 2695000
34 | Ashuganj 450 MW CCPP(South) | 310 | 305 | 305 | 285 | 290 | 280 | 290 | 300 | 280 | 300 | 325 | 335 | 285 | 280 | 285 | 285 | 285 | 290 |  | 300 | 280 | 285 | 290 | 280 | 280 | 275 | 7145000
| Ashuganj 450 MW CCPP(North) | 340 | 335 | 335 | 315 | 320 | 310 | 315 | 330 | 305 | 300 | 280 | 280 | 310 | 300 | 300 | 295 | 310 | 280 |  | 290 | 310 | 310 | 320 | 310 | 310 | 310 | 7866500
35 | Ashuganj 55 MW PP (Precision) | 54 | 55 | 55 | 53 | 54 | 54 | 52 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 54 |  | 54 | 54 | 55 | 54 | 54 | 54 | 55 | 1055520
36 | Chandpur 150 MW CCPP | 95 | 95 | 95 | 96 | 95 | 90 | 95 | 95 | 86 | 96 | 87 | 87 | 87 | 87 | 94 | 97 | 90 | 94 |  | 96 | 86 | 85 | 96 | 94 | 96 | 92 | 2223330
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 345 | 351 | 350 | 330 | 339 | 332 | 330 | 341 | 342 | 323 | 339 | 332 | 348 | 322 | 322 | 335 | 330 | 324 |  | 337 | 343 | 332 | 324 | 328 | 323 | 333 | 8189852
40 | Meghnaghat 450 MW CCPP(MPL) | [25 empty] | 0 | 0
41 | Haripur 360MW CCPP(HPL) | 353 | 353 | 354 | 354 | 320 | 283 | 270 | 300 | 264 | 275 | 304 | 335 | 353 | 303 | 305 | 355 | 353 | 352 |  | 353 | 354 | 354 | 354 | 353 | 353 | 355 | 7845000
42 | RPCL 210MW CCPP | 142 | 157 | 158 | 158 | 158 | 160 | 158 | 157 | 157 | 122 | 122 | 122 | 100 | 101 | 107 | 107 | 107 | 124 |  | 123 | 124 | 121 | 105 | 106 | 105 | 142 | 3017400
43
44 | Fenchugonj CCPP Phase-1 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2150000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 33 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720720
46 | Shajibazar 330 MW CCPP | 106 | 106 | 105 | 103 | 108 | 100 | 102 | 110 | 101 | 100 | 108 | 107 | 101 | 101 | 15 |  |  | 10 |  | 8 | 6 | 30 | 47 | 120 | 156 | 156 | 2007000
47 | Shahjibazar GTPP Unit- 8 & 9 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 40 | 40 | 51 | 51 | 52 | 40 | 53 | 53 | 52 |  | 62 | 62 | 62 | 61 | 61 | 61 | 61 | 1264800
48 | Shahjibazar 86MW PP (Shahjibazar) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 73 | 76 | 20 | 20 | 74 | 74 | 10 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1602240
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 101 | 100 | 100 | 50 | 50 | 100 | 100 | 100 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 151 |  | 150 | 150 | 151 | 150 |  |  |  | 2619830
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 423000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 244440
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257856
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 20 |  | 20 | 47 | 47 | 49 | 53 | 50 | 50 | 1119000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 479808
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 315 | 315 | 300 | 305 | 295 | 290 | 305 | 300 | 260 | 300 | 290 | 300 | 280 | 285 | 300 | 310 | 300 |  | 310 | 290 | 285 | 280 | 290 | 295 | 310 | 7379800
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 837072
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 385728
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | [6 empty] | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 330480
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 |  |  | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 429984
63 | Impoprt (Tripura) | 140 | 136 | 126 | 110 | 116 | 110 | 100 | 96 | 102 | 116 | 132 | 132 | 126 | 134 | 72 | 106 | 102 | 112 |  | 144 | 148 | 150 | 144 | 158 | 150 | 142 | 3052800
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 20 | 41 | 42 | 42 | 33 | 6 | 2 | 3 | 2 | 3 | 7 | 5 | 3 | 3 | 12 | 10 |  | 15 | 19 | 22 | 30 | 30 | 15 | 16 | 450880
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 486936
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 |  | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201240
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 564200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 19 | 21 | 21 | 21 | 15 | 15 | 15 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 467830
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 29 | 29 | 19 | 18 | 0 | 0 | 30 | 30 | 30 | 30 | 30 |  | 20 | 26 | 30 | 30 | 30 | 30 | 30 | 607320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 17 | 17 | 33 | 33 | 33 | 33 | 33 | 817600
73 | Ghorashal 108MW PP (Regent) | 94 | 94 | 94 | 94 | 91 | 94 | 94 | 94 | 94 | 93 | 91 | 94 | 91 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2221590
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 84 | 55 | [6 empty] | 3 | 110 | 113 | 108 | 104 | 108 | 110 | 105 | 46 | 46 |  | 46 | 113 | 88 | 113 | 113 | 113 | 113 | 1688400
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 7 | 7 | 7 | 15 | 50 | 50 | 65 | 90 | 97 | 98 | 98 | 90 | 70 |  | 70 | 90 | 90 | 100 | 92 | 92 | 100 | 1905600
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [19 empty] | 70 | 100 | 90 | 65 | 48 | 48 | 48 | 364320
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 65 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 64 | 64 | 64 | 64 | 40 | 40 |  | 88 | 95 | 95 | 95 | 95 | 95 | 95 | 1516800
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 7 | 25 | 25 | 25 | 25 | 25 |  | 115306
| Gazipur 100 MW PP | [10 empty] | 1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 37 | 70 | 70 | 52 | 52 | 52 | 52 | 568560
| Kaptai 7 MW Solar PP | [5 empty] | 0.4 | 1 | 1.1 | 4.4 | 5.1 | 1.8 | 1.2 | 0.5 | 1.3 | 2.8 | 1 | 0.3 | [9 empty] | 20160
| Jodiac Power | [9 empty] | 37 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 |  | 24 | 54 | 54 | 54 | 54 | 54 | 54 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 60 | 78 | 64 | 64 | 64 |  | 64 | 64 | 64 | 81 | 81 | 81 | 81 | 1598376
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [8 empty] | 9 | 85 | 100 | 100 | 100 | 100 | 100 | 75 | 40 | 40 |  | 40 | 40 |  |  |  |  | 0 | 873140
86 | Meghnaghat CCPP(Summit) | 285 | 280 | 285 | 285 | 285 | 255 | 280 | 285 | 333 | 332 | 330 | 335 | 335 | 330 | 335 | 332 | 334 | 333 |  | 335 | 330 | 250 | 300 | 295 | 290 | 280 | 7244247
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 50 | 20 | 7 | 7 | 13 | 50 | 50 | 60 | 100 | 100 | 100 | 100 | 80 | 74 |  | 74 | 100 | 90 | 100 | 100 | 100 | 100 | 1837440
| Meghnaghat 104 MW PP (OPCL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX) | 71 | 71 | 71 | 70 | 70 | 70 | 70 | 40 | 40 | 40 | 40 | 40 | 40 | [12 empty] | 0 | 768320
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima) | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 42 | 10 |  | 30 | 42 | 42 | 42 | 42 | 43 | 43 | 935136
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 842317
94 | Gagnagar 102 MW PP (Digital Power) | 76 | 76 | 76 | 76 | 76 | 24 | 24 | 32 | 40 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1590048
95 | Patenga 50MW PP (Baraka) | [19 empty] | 3 | 22 | 24 |  |  |  | 0 | 31680
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 22 | 45 | 44 | 44 | 44 | 44 | 44 | 250560
97 | Katpotti 52 MW PP (Sinha) | [19 empty] | 4 | 18 | 18 |  |  |  | 0 | 34992
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 47 | 47 | 47 | 47 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 28 | 15 | 15 | 22 | 40 |  | 40 | 40 | 37 | 45 | 37 | 47 | 47 | 822130
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | [6 empty] | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 923016
101 | Kushiara 163 MW CCPP (KP) | [12 empty] | 10 | 20 | 20 | 20 | 20 | 40 |  | 90 | 100 | 100 | 163 | 163 | 163 | 163 | 989836
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0.1 | 0.1 | 0.2 | 0.2 | 0.5 | 0.7 | 0.6 | 0.4 | 0.9 | 0.7 | 0.4 | 0.2 | 0.1 | [8 empty] | 5600
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 35 |  |  |  |  | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 832680
104 | Keranigonj 300 MW PP (APR) | [9 empty] | 52 | 53 | [14 empty] | 0 | 102912
105 | Bramhangoan 100 MW PP (Aggreko) | [9 empty] | 50 | 50 | 20 | 20 | 20
106 | Mymensingh 200 MW PP (United) | 70 | 50 | 24 | [9 empty] | 7 | 7 | 7 | 7 | 7 | 7 |  | 32 | 90 | 80 | 100 | 120 | 120 | 120 | 816000
112 | Aurahati 100MW PP (Aggreko) | [8 empty] | 12 | 102 | 101 | 100 | 102 | 103 | 103
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 116 | 79 | 60 | 60 | 60 | 83 | 115 | 115 | 115 | 108 | 105 | 102 | 102 | 115 | 99 | 99 | 96 |  | 108 | 115 | 115 | 115 | 115 | 115 | 115 | 2460960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2433600
116 | Chandpur 200MW (Desh energy) | [25 empty] | 0 | 0
117 | Ashuganj 150MW PP (Midland) | [12 empty] | 2 | 10 | 10 | 10 | 10 | 10 |  | 23 | 70 | 70 | 70 | 70 | 10 |  | 374691
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 45 | 45 | 45 | 73 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2564400
| Anwara 300 MW PP (United) | 307 | 215 | 180 | 160 | 160 | 160 | 160 | 160 | 276 | 293 | 300 | 285 | 306 | 306 | 306 | 306 | 180 | 179 |  | 179 | 201 | 214 | 214 | 214 | 215 | 217 | 5567673
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2422080
120 | Eastern Zone Total | 6623 | 6363 | 6127 | 5950 | 5747 | 5328.5 | 5155.1 | 5313.2 | 5755.7 | 6163.2 | 6402.9 | 6413.5 | 6591.2 | 6446.1 | 6377.2 | 6328.7 | 5952.2 | 5827.2 |  | 6449 | 7145 | 7072 | 7162 | 7129 | 7041 | 6999 | 151109880
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 41 | 32 | 32 | 16 | [7 empty] | 32 | 32 | 32 | 32 | 26 | 16 | 16 |  | 49 | 73 | 83 | 51 | 115 | 77 | 49 | 731520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [22 empty] | 53 | 17 |  | 0 | 69600
130
131
132
133
| Barisal 110 MW PP (Summit ) | 48 | 48 | 32 | 16 | [15 empty] | 80 | 80 | 110 | 110 | 110 | 110 | 110 | 744960
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 76 | 77 | 75 | 76 | 76 | 78 | 80 | 80 | 73 | 76 | 75 | 75 | 77 | 75 | 62 | 52 | 53 | 52 |  | 76 | 76 | 75 | 75 | 76 | 76 | 77 | 1748134
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 65 | 65 | 63 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1553000
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 33 | 31 | 27 | 26 | 24 | 22 | 24 | 26 | 27 | 28 | 26 | 25 | 26 | 25 | 25 | 25 |  | 31 | 34 | 36 | 37 | 33 | 34 | 33 | 671401
141 | Noapara 100 MW PP (Bangla Trac) | [22 empty] | 24 | 40 |  | 0 | 85440
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 33 | 33 | 33 | [5 empty] | 33 | 33 | 33 | 32 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 584625
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 10 | 10 | [8 empty] | 17536
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 948 | 950 | 949 | 950 | 950 | 950 | 950 | 949 | 949 | 950 | 950 | 949 | 949 | 950 | 949 | 950 | 950 | 950 |  | 950 | 950 | 947 | 945 | 950 | 948 | 948 | 22770909
147 | Bheramara 410 MW CCPP | 375 | 365 | 370 | 345 | 365 | 345 | 345 | 350 | 340 | 350 | 345 | 340 | 345 | 325 | 325 | 330 | 325 | 327 |  | 325 | 325 | 326 | 315 | 305 | 270 | 270 | 8326080
148 | Payra 1320 MW | 472 | 472 | 474 | 474 | 473 | 473 | 475 | 476 | 455 | 452 | 450 | 498 | 499 | 497 | 499 | 499 | 497 | 499 |  | 498 | 524 | 535 | 531 | 533 | 532 | 533 | 12527900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 3650600
153 | Baghabari 71 MW GTPP | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | [17 empty] | 0 | 330000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 |  |  | 187870
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 167 | 167 | 167 | 167 | 167 | 169 | 172 | 160 | 190 | 181 | 165 | 176 | 201 | 198 | 165 | 166 | 155 | 162 |  | 171 | 179 | 180 | 188 | 185 | 182 | 188 | 4428682
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 176 | 177 | 190 | 183 | 185 | 181 | 181 | 184 | 185 | 167 | 170 | 192 | 186 | 168 | 157 | 174 | 169 | 167 |  | 174 | 177 | 171 | 179 | 180 | 183 | 190 | 4517964
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 416 | 414 | 415 | 410 | 414 | 313 | 351 | 351 | 396 | 403 | 407 | 408 | 391 | 369 | 383 | 401 | 356 | 404 |  | 403 | 377 | 352 | 404 | 404 | 402 | 406 | 9490218
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 5 | 12 | 35 | 35 |  |  |  | 79784
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501840
163 | Bogura 20 MW PP (Energyprima) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 263176
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 5 |  |  | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 159534
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 8 | 8 |  |  |  | 0 | 10784
167 | Katakhali 50 MW Peaking PP | [19 empty] | 22 | 47 | 48 | 45 | 46 | 46 |  | 180739
168 | Santahar 50 MW Peaking PP | [19 empty] | 26 | 26 | 27 | 27 | 34 | 15 |  | 129335
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 25 | 25 | 25 | 25 | 25 | 26 | 0 | 121920
170 | Chapainawabganj 100 MW Peaking PP | 25 | [18 empty] | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 536944
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 15 | 50 | 75 | 111 | 111 | 111 | 35 | 532320
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [21 empty] | 10 | 8 | 8 | 8 | 8 | 35000
176 | Rangpur 113 MW PP (Confidence) | 110 | 44 | [17 empty] | 31 | 99 | 90 | 113 | 113 | 113 | 113 | 735360
177 | Sympa Solar Power 8MW | [7 empty] | 0.1 | 0.1 | 0.2 | 0.4 | 1.4 | 2.2 | 1.6 | 2.8 | 1.2 | 0.8 | 0.2 | [8 empty] | 11141
178
178